## Measure List 1
EUL ID | MEASURE | Adopted EULs | SOURCE
NONRESIDENTIAL MEASURES:
****************************************************************
NR1 | Ballast – Dimmable: NR | 11 | SERA Report - May 2005/07-14-05
NR2 | Ballast – Electronic: NR | 11 | SERA Report - May 2005/07-14-05
NR3 | Fluorescent Fixture – T8: C/I/A | 11 | SERA Report - May 2005/07-14-05
NR4 | Fixture: T8 Lamp & Electronic Ballast: C/I/A | 11 | SERA Report - May 2005/07-14-05
NR5 | T8 Fixtures – 17 Watt Lamp, 2ft or 32-watt Lamp, 4ft | 11 | SERA Report - May 2005/07-14-05
NR6 | T8 Lamps: C/I/A - | 5 | SERA Report - May 2005/07-14-05
NR7 | High Efficiency Lighting (Other): NR | 16 | CALMAC Report - September 2000
NR8 | High Output T5 Fixture: NR - | 16 | CALMAC Report - September 2000
NR9 | Indoor or Outdoor Lighting System Modification: NR | 16 | CALMAC Report - September 2000
NR10 | Lighting Controls: NR | 16 | CALMAC Report - September 2000
NR11 | Daylighting Controls; NR | 16 | CALMAC Report - September 2000
NR12 | Lighting Power Density: NR | 16 | CALMAC Report - September 2000
NR13 | Exit Sign – CF Hardware Kit/LED/ Electro-Luminescent: NR | 16 | CALMAC Report - September 2000
NR14 | Occupancy Sensor: NR | 8 | CALMAC Report - September 2000
NR15 | Photocell: NR | 8 | CALMAC Report - September 2000
NR16 | Time Clock – Lighting: NR | 8 | CALMAC Report - September 2000
NR17 | Induction Lamps: NR | 2 | CALMAC Report - September 2000
NR18 | Induction Fixture: NR | 16 | CALMAC Report - September 2000
NR19 | Delamp/reflectors: C/I | 11 | SERA Report - May 2005/07-14-05
NR20 | Optical Reflectors- new construction: Ind, NRNC | 12 | SERA Report - May 2005/07-14-05
NR21 | Optical Reflectors- retrofit: NR | 10 | SERA Report - May 2005/07-14-05
NR22 | HID fixture: Interior, >= 176 Watts lamp: Ind | 16 | SERA Report - May 2005/07-14-05
NR23 | HID fixture: Interior, 251-400 Watt lamp: Com | 16 | SERA Report - May 2005/07-14-05
NR24 | CFL Fixture: no add'l description: Com | 12 | SERA Report - May 2005/07-14-05
NR25 | CFL: Education - Primary School: NR | 5.6 | DEER/Metering Study 2005
NR26 | CFL: Education - Secondary School: NR | 3.5 | DEER/Metering Study 2005
NR27 | CFL: Education - Community College: NR | 2.11 | DEER/Metering Study 2005
NR28 | CFL: Education - University: NR | 2.6 | DEER/Metering Study 2005
NR29 | CFL: Grocery: NR | 2.6 | DEER/Metering Study 2005
NR30 | CFL: Health/Medical - Hospital: NR | 0.92 | DEER/Metering Study 2005
NR31 | CFL: Health/Medical - Nursing Home: NR | 0.92 | DEER/Metering Study 2005
NR32 | CFL: Lodging - Hotel: NR | 0.92 | DEER/Metering Study 2005
NR33 | CFL: Lodging - Motel: NR | 0.92 | DEER/Metering Study 2005
NR34 | CFL: Lodging - Guest Rooms: NR | 6.9 | DEER/Metering Study 2005
NR35 | CFL: Manufacturing - Light Industrial: NR | 2.8 | DEER/Metering Study 2005
NR36 | CFL: Office - Large: NR | 2.92 | DEER/Metering Study 2005
NR37 | CFL: Office - Small: NR | 3.21 | DEER/Metering Study 2005
NR38 | CFL: Restaurant - Sit-Down: NR | 2.32 | DEER/Metering Study 2005
NR39 | CFL: Restaurant - Fast-Food: NR | 1.29 | DEER/Metering Study 2005
NR40 | CFL: Retail - 3-Story Large: NR | 1.88 | DEER/Metering Study 2005
NR41 | CFL: Retail - Single-Story Large: NR | 1.83 | DEER/Metering Study 2005
NR42 | CFL: Retail - Small: NR | 2.15 | DEER/Metering Study 2005
NR43 | CFL: Storage - Conditioned: NR | 2.8 | DEER/Metering Study 2005
NR44 | CFL: Storage - Unconditioned: NR | 2.8 | DEER/Metering Study 2005
NR45 | CFL: Warehouse - Refrigerated: NR | 3.08 | DEER/Metering Study 2005
NR46 | HVAC/Refrigeration – SPC: NR | 20 | CALMAC Report - September 2000
NR47 | Chiller – High Efficiency: NR | 20 | CALMAC Report - September 2000
NR48 | Chiller – Variable Speed Drive: NR | 20 | CALMAC Report - September 2000
NR49 | Water Cooled Chillers: NR | 20 | CALMAC Report - September 2000
NR50 | Air Conditioners – High Efficiency: NR | 15 | CALMAC Report - September 2000
NR51 | Packaged HVAC Systems: NR | 15 | CALMAC Report - September 2000
NR52 | Install HVAC EMS: Com | 14 | SERA Report - May 2005/07-14-05
NR53 | AC Packaged Terminal Units: NR | 15 | CALMAC Report - September 2000
NR54 | Evaporative Coolers: NR | 15 | CALMAC Report - September 2000
NR55 | Boiler – High Efficiency: NR | 20 | CALMAC Report - September 2000
NR56 | Cooling Towers/Evaporative Condenser: NR | 15 | CALMAC Report - September 2000
NR57 | Heat Pump – Split System: NR | 20 | CALMAC Report - September 2000
NR58 | Heat Pump with Integrated Water Heating: NR | 20 | CALMAC Report - September 2000
NR59 | Ground Source Heat Pump: NR | 15 | CALMAC Report - September 2000
NR60 | Reduce Internal Load: NR | 15 | CALMAC Report - September 2000
NR61 | Insulation: NR | 20 | CALMAC Report - September 2000
NR62 | Insulation Package: NR | 20 | CALMAC Report - September 2000
NR63 | Reflective Window Film/Windows: NR | 10 | CALMAC Report - September 2000
NR64 | Bypass/Delay Timer: NR | 15 | CALMAC Report - September 2000
NR65 | Set-Back Thermostat: NR | 11 | CALMAC Report - September 2000
NR66 | Time Clock - HVAC: NR | 10 | CALMAC Report - September 2000
NR67 | HVAC/Space Heating/Efficiency (Gas): NR | 15 | CALMAC Report - September 2000
NR68 | Nonresidential Gas – AC: NR | 20 | CALMAC Report - September 2000
NR69 | Adjustable speed drive, application unknown: Ag | 10 | SERA Report - May 2005/07-14-05
NR70 | Adjustable speed drive, application unknown: Com | 10 | SERA Report - May 2005/07-14-05
NR71 | Adjustable Speed Drive: HVAC fan, 50 HP Max: Com | 16 | SERA Report - May 2005/07-14-05
NR72 | Pump repair: Ag | 11 | SERA Report - May 2005/07-14-05
NR73 | Injection molding machines: Ind | 15 | SERA Report - May 2005/07-14-05
NR74 | Plastic extusion equipment: Ind | 15 | SERA Report - May 2005/07-14-05
NR75 | Process cooling: Ind | 15 | SERA Report - May 2005/07-14-05
NR76 | Process equipment insulation: Ind | 15 | SERA Report - May 2005/07-14-05
NR77 | Horizontal Clothes Washer: NR | 10 | CALMAC Report - September 2000
NR78 | Efficient Dishwashing: NR | 5 | CALMAC Report - September 2000
NR79 | Water Heater Controls: NR | 15 | CALMAC Report - September 2000
NR80 | Cooking measures , Assorted: Com | 12 | SERA Report - May 2005
NR81 | Water Heater – Gas: NR | 15 | CALMAC Report - September 2000
NR82 | Domestic Hot Water Boiler (Gas): NR | 20 | CALMAC Report - September 2000
NR83 | Auto Closer for Cooler/Freezer: NR | 8 | CALMAC Report - September 2000
NR84 | Door Gaskets: NR | 4 | CALMAC Report - September 2000
NR85 | Floating Head Pressure: NR | 16 | CALMAC Report - September 2000
NR86 | Heatless Door: NR | 16 | CALMAC Report - September 2000
NR87 | Humidistat Control for Anti-Sweat Heater: NR | 12 | CALMAC Report - September 2000
NR88 | Insulation on Refrigeration Suction Line: NR | 11 | CALMAC Report - September 2000
NR89 | Night Covers for Display Cases: NR | 5 | CALMAC Report - September 2000
NR90 | PSC Evaporator Motor – Walkin/ Display: NR | 16 | CALMAC Report - September 2000
NR91 | Refrigeration Case Doors – Glass/Acrylic: NR | 12 | CALMAC Report - September 2000
NR92 | Refrigerator Case with Doors: NR | 16 | CALMAC Report - September 2000
NR93 | Refrigerator Condensate Evaporator – Elec/Non Elec: NR | 8 | CALMAC Report - September 2000
NR94 | Strip Curtains for Walk-Ins: NR | 4 | CALMAC Report - September 2000
NR95 | Ballast: Electronic, for display case: NR | 16 | CALMAC Report - September 2000
NR96 | Defrost: NR | 16 | CALMAC Report - September 2000
NR97 | FHP & EFF Conditioner: NR | 16 | CALMAC Report - September 2000
NR98 | High-efficiency Liquid Suction Heat Exchangers: NR | 16 | CALMAC Report - September 2000
NR99 | Night Shields on Refrigerator and Freezer Cases: NR | 16 | CALMAC Report - September 2000
NR100 | Refrigerator: Evaporative Fan Controller: NR | 5 | CALMAC Report - September 2000
NR101 | Supermarket Systems: NR | 14 | CALMAC Report - September 2000
NR102 | Kiln/Oven/Furnace: NR | 18 | CALMAC Report - September 2000
NR103 | Thermal Night Curtains: NR | 5 | CALMAC Report - September 2000
NR104 | Custom Measures – SPC: NR | 15 | CALMAC Report - September 2000
NR105 | Plug Load Sensor: NR | 10 | CALMAC Report - September 2000
NR106 | High Efficiency Motors: NR | 15 | CALMAC Report - September 2000
NR107 | Process Overhaul: NR | 20 | CALMAC Report - September 2000
NR108 | System Controls: NR | 15 | CALMAC Report - September 2000
NR109 | Engine- High Efficiency | 15 | CALMAC Report - September 2000
NR110 | Whole Building(NRNC) | 16 | CALMAC Report - September 2000
RESIDENTIAL MEASURES
****************************************************************
R1 | T8 Fixtures ; lamp or ballast: Res | 15 | SERA Report - May 2005/07-14-05
R2 | CFL Fixture: no add'l description: Res | 16 | SERA Report - May 2005/07-14-05
R3 | CFL: Indoor Screw in: Res | 9.4 | DEER/Metering Study 2005
R4 | CFL: Outdoor Screw in: Res | 7.1 | DEER/Metering Study 2005
R5 | Torchiere: Res | 9 | CALMAC Report - September 2000
R6 | Air Conditioners with SEER >= 11.0: Res | 18 | SERA Report - May 2005/07-14-05
R7 | Central Air Conditioners: Res | 18 | SERA Report - May 2005/07-14-05
R8 | Duct Testing and Sealing: Res NC | 18 | SERA Report - May 2005/07-14-05
R9 | High Energy Efficiency Ducts: Res | 18 | SERA Report - May 2005/07-14-05
R10 | Evaporative Cooler: Res | 15 | SERA Report - May 2005/07-14-05
R11 | Glazing - Low E Double / Low Shade Coefficient: Res | 20 | CALMAC Report - September 2000 (capped at 20)
R12 | Heat Pump - Electric: Res | 15 | SERA Report - May 2005/07-14-05
R13 | Insulation - Ceiling / Floor / Walls: Res | 20 | CALMAC Report - September 2000 (capped at 20)
R14 | A/C with Integrated Water Heating: Res | 15 | CALMAC Report - September 2000
R15 | Programmable Thermostat: Res | 12 | CALMAC Report - September 2000
R16 | Gas Cooktops: Res | 20 | SERA Report - May 2005/07-14-05
R17 | Gas Dryer Stub: Res | 18 | SERA Report - May 2005/07-14-05
R18 | Energy-Efficient Furnaces: Res | 18 | SERA Report - May 2005/07-14-05
R19 | Refrigerator Recycling: Res | 10 | SERA Report - May 2005/07-14-05
R20 | Refrigerator - Energy Efficient; 20% more efficient: Res | 18 | SERA Report - May 2005/07-14-05
R21 | Refrigerators: Res | 18 | SERA Report - May 2005/07-14-05
R22 | Advance HVAC DiagnosticTune up | 15 | CALMAC Report - September 2000
R23 | Basic HVAC Diagnostic Tune up | 10 | CALMAC Report - September 2000
R24 | Room A/C | 15 | CALMAC Report - September 2000
R25 | Residential Gas A/C | 20 | CALMAC Report - September 2000(capped at 20)
R26 | Clothes Washer- Horizontal Axis | 14 | CALMAC Report - September 2000
R27 | Dishwasher | 13 | CALMAC Report - September 2000
R28 | Insulation for Pipe | 15 | CALMAC Report - September 2000
R29 | Showerhead- Energy Efficient | 10 | CALMAC Report - September 2000
R30 | Water Heater - Efficient Gas | 13 | CALMAC Report - September 2000
R31 | Water Heater Controls | 15 | CALMAC Report - September 2000

## Measure List 2
NON-WEATHER SENSITIVE
| MeasureID | Measure Name | Measure Description | Customer Baseline | Code Baseline | Common Units (CU) | Adopted EUL | EUL Source/Justification
| D03-901 | High Efficiency Copier | 0-20 copies/minute | No idle-off control | No idle-off control | Copier | 6 | Energy Star
| D03-902 | High Efficiency Copier | 21 44copies/minute | No idle-off control | No idle-off control | Copier | 6 | Energy Star
| D03-903 | High Efficiency Copier | Over 45 copies/minute | No idle-off control | No idle-off control | Copier | 6 | Energy Star
| D03-909 | Point of Use Water Heat | Point of Use Water Heat w/Electronic Ignition, 150 kBtu/hr | Gas Water Heater EF=0.594 | Gas Water Heater EF=0.594 | Bldg SqFt | 20 | US DOE Technical Brief
| D03-910 | Circulation Pump Timeclock | Circulation Pump Timeclock | Gas Water Heater EF=0.594 | Gas Water Heater EF=0.594 | Bldg SqFt | 15 | SERA - Water Heater Controls
| D03-912 | Vending Machine Controller | Cold Drink Vending Machine | Uncontrolled Cold Drink Vending Machine | Uncontrolled Cold Drink Vending Machine | Machine | 10 | NW Regional Technical Forum
| D03-913 | Vending Machine Controller | Uncooled Snack Machine | Uncontrolled Uncooled Snack Machine | Uncontrolled Uncooled Snack Machine | Machine | 10 | NW Regional Technical Forum
| D03-934 | Faucet Aerators | Faucet Aerators | No Faucet Aerators | No Faucet Aerators | Household | 5 | Efficiency Vermont
| D03-935 | Heat Pump Water Heater | Heat pump water heater, EF=2.9 | Electric water heater, EF=0.88 | Electric water heater, EF=0.88 | Tank | 10 | Engineering Judgement
| D03-939 | High Efficiency Water Heater | High Efficiency Water Heater - Electric, EF=0.93, 28-50 gallons | Electric water heater, EF=0.88 | Electric water heater, EF=0.88 | Tank | 15 | Enginering Judgment/DEER 4.0 1996
| D03-940 | Point of Use Water Heat | Point of Use Water Heat w/Electronic Ignition, 150 kBtu/hr | Gas water heater, EF=0.60 | Gas water heater, EF=0.60 | Tank | 20 | US DOE Technical Brief
| D03-941 | Efficient Clothes Dryer | High Efficiency Electric Clothes Dryer with Moisture Sensor. | Electric Clothes Dryer EF=3.01. Single Family, 416 dry cycles | Electric Clothes Dryer EF=3.01. Single Family, 416 dry cycles | Dryer | 18 | SERA - Gas Dryer
| D03-942 | Efficient Clothes Dryer | High Efficiency Gas Clothes Dryer with Moisture Sensor. | Gas Clothes Dryer EF=2.67. Single Family, 416 dry cycles | Gas Clothes Dryer EF=2.67. Single Family, 416 dry cycles | Dryer | 18 | SERA - Gas Dryer
| D03-966 | Efficient Single Speed Pool Pump | Efficient Single Speed Pool Pump, 1.5 hp | Inefficient Single Speed Pool Pump | Inefficient Single Speed Pool Pump | Pump | 10 | ASHRAE
| D03-967 | Efficient Two Speed Pool Pump | Efficient Two Speed Pool Pump, 1.5 hp | Inefficient Single Speed Pool Pump | Inefficient Single Speed Pool Pump | Pump | 10 | ASHRAE
RESIDENTIAL WEATHER SENSITIVE
| D03-408 | Refrigerant charge airflow 1 TBD | -same as name- | Clg Eff Decreased by 15% | Code Baseline matches prototype characteristics | tons cooling | 5 | Engineering Judgement
| D03-409 | Refrigerant charge airflow 2 TBD | -same as name- | Clg Eff Decreased by 15% & Supply Duct Leakage 20% | Code Baseline matches prototype characteristics | tons cooling | 5 | Engineering Judgement
| D03-439 | Low-Income Weatherization w/out Evaporative Cooler | -same as name- | Infiltration per 1994 Analysis | Weatherization code baseline matches measure baseline | 1000 sqft house | 13? | DEER 4.0 1996 - "Weatherization Big 6"
| D03-440 | Low-Income Weatherization w/Evaporative Cooler | -same as name- | Infiltration per 1994 Analysis | Weatherization code baseline matches measure baseline | 1000 sqft house | 13? | DEER 4.0 1996 - "Weatherization Big 6"
| D03-441 | Whole House Fans | -same as name- | No Night Ventilation/Economizer | Night ventilation code baseline matches measure baseline | 1000 sqft house | 15 | Engineering Judgement
| D03-459 | Refrigerant charge airflow 1 + duct sealing | -same as name- | 0 | Code Baseline matches prototype characteristics | tons cooling | 15 | SERA - Duct Sealing -18
| D03-460 | Refrigerant charge airflow 2 + duct sealing | -same as name- | 0 | Code Baseline matches prototype characteristics | tons cooling | 15 | SERA - Duct sealing -18
Non-RESIDENTIAL WEATHER SENSITIVE
| D03-014 | Tank Insulation-Fiber Blanket | Approximately R-12 tank insulation, based on tank size | Approximately R-6 tank insulation, based on tank size | T24 code baseline for DHW tank insulation matches prototype level | sqft building | 10 | Engineering Judgement
| D03-016 | Light Colored Roof | Roof absorptivity = 0.45 | Roof absorptivity = 0.7 | T24 minimimum, cool roof per Section 118(i) | sqft roof | ?? | ??
| D03-044 | Chilled Water Reset | Chilled water loop temperature set to "Load Reset" | Constant chilled water temperature | T24 minimum: variable flow CHW loop w/VSD pump | sqft CHW-served area | 10 | Engineering Judgement
| D03-045 | Hot Water Reset | Hot water loop temperature set to "Load Reset" | Constant hot water temperature | T24 minimum: variable flow HW loop w/VSD pump | sqft HW-served area | 10 | Engineering Judgement
| D03-046 | Variable Flow Chilled Water Loop | 2-way valves, with single speed pump | 3-way valves in chilled water loop | T24 minimum: variable flow CHW loop w/VSD pump | nameplate HP | 10 | Engineering Judgement
| D03-047 | VSD Chilled Water Loop Pump | add variable speed pump to chilled water loop | 2-way valves, with single speed pump | T24 minimum: variable flow CHW loop w/VSD pump | nameplate HP | 10 | Engineering Judgement
| D03-048 | Variable Flow Hot Water Loop | 2-way valves, with single speed pump | 3-way valves in hot water loop | T24 minimum: variable flow HW loop w/VSD pump | nameplate HP | 10 | Engineering Judgement
| D03-049 | VSD Hot Water Loop Pump | add variable speed pump to hot water loop | 2-way valves, with single speed pump | T24 minimum: variable flow HW loop w/VSD pump | nameplate HP | 10 | Engineering Judgement
| D03-050 | Variable Air Volume Box | damper controlled VAV with 30% min-cfm-ratio | Constant Volume air flow | T24 minimum: VAV w/30% min-cfm-ratio & w/VSD fans | sqft served | 10 | Engineering Judgement
| D03-051 | VSD Supply Fan Motors | VFD with 30% min-cfm-ratio | damper controlled VAV with 30% min-cfm-ratio | T24 minimum: VAV w/30% min-cfm-ratio & w/VSD fans | nameplate HP | 10 | Engineering Judgement/DEER 4.0 1996
| D03-052 | Fan Powered Mixing Boxes | Convert VAVS ssytem to PIU system | damper controlled VAV with 30% min-cfm-ratio | T24 minimum: VAV w/30% min-cfm-ratio & w/VSD fans | sqft served | 10 | Engineering Judgement
| D03-055 | Reducing Overventilation | standard ventilation rate | ventilation rate increased by 25% | T24 ventilation matches baseline characteristics | sqft building | 10 | Engineering Judgement
| D03-056 | Air To Air Heat Exchanger | 70% heat recovery effectiveness | no exhaust heat recovery | T24 minimum: no exhaust heat recovery | sqft building | 10 | Engineering Judgement
| D03-057 | Rotary Heat Recovery | 70% sensible and latent recovery effectiveness | no exhaust heat recovery | T24 minimum: no exhaust heat recovery | sqft building | 10 | Engineering Judgement
| D03-058 | Economizer - Packaged System | Add econo with Econo-Lockout=NO, DB limit = 68, Max OSA = 100% | No Economizer | T24 baseline matches prototype | tons served | 15 | ASHRAE/DEER 4.0 1996
| D03-059 | Economizer - Central system | Add ecomizer with Econo-Lockout=NO, DB limit = 68, Max OSA = 100% | No Economizer | T24 baseline matches prototype | tons served | 15 | ASHRAE
| D03-060 | Economizer Maintenance | ecomizer with Econo-Lockout=NO, DB limit = 68, Max OSA = 100% | degraded base econo performance, DB limit = 55, Max OSA = 60% | T24 minimum: economizer matches baseline characteristics | tons served | 4 | Engineering Judgement
| D03-061 | Clean Condenser Coils | standard equipment efficiency | cooling equipment efficiency is degraded by 20% | T24 minimum matches baseline HVAC | tons served | 4 | Engineering Judgement
| D03-063 | Two-Speed Cooling Tower Fans | Two-speed tower fans on all central plants | Single-speed tower fans on all central plants | T24 minimum: two-speed tower fans | tons served cooling cap | 10 | ASHRAE
| D03-064 | VSD Cooling Tower Fans | Variable-speed tower fans on all central plants | Two-speed tower fans on all central plants | T24 minimum: two-speed tower fans | tons served cooling cap | 10 | Engineering Judgement
| D03-069 | Efficient Water Source Heat Pump | 14.0 EER/4.6 COP WLHP | WLHP system with COP = 3.0 | T24 minimum: WLHP EER = 12.0, COP = 4.2 | tons cooling | 15 | Engineering Judgement/DEER 4.0 1996
| D03-070 | Hydronic Heat Pump Var Flow Valve | 2-way valves, with VSD pumping | constant flow hydronic water loop | T24 minimum: variable flow WLHP loop w/VSD pump | tons cooling | 10 | Engineering Judgement
| D03-075 | Duct Insulation Material | Old vintage increases duct insulation to R-4.2, 78-91 vintage to R-8 | Duct insulation level a function of Vintage/System type | T24 minimum duct insulation level, R-8 | sqft served | 20 | Engineering Judgement/DEER 4.0 1996
| D03-093 | Gas Tankless Water Heating | zero tank loss, improved EF | gas water heater with EF based on tank size/vintage | T24 minimum: small storage water heater w/EF based on currnent standards | sqft served | 20 | Engineering Judgement/DEER 4.0 1997
| D03-094 | Point of Use Water Heating | zero tank loss | electric water heater with EF based on tank size | T24 minimum: small storage water heater w/EF based on currnent standards | sqft served | 20 | US DOE Technical Brief
| D03-095 | Circulation Pump Timeclock Retrofit | DHW circulation pump turns off during low operation hours | DHW circulation pump runs continuously | DHW circulation pump turns off during low operation hours | sqft served | 15 | SERA - Water Heater Controls
| D03-098 | Water Side Economizer | Non integrated evaporator precooler heat exchanger | No water economizer | T24 minimum: no water economizer | tons served cooling cap | 10 | Enginnering Judgement