## Data
rtu | workbook | dnv_gl_id | Test_Type | Economizer_opening | Compressor_1_on_off | Compressor_2_on_off | Motor_sheave_setting | Cabinet_sealing | Ductwork_Sealing | Fan_Speed | Pulley_Diameter | Air_Discharge_Configuration | condenser_blockage | evaporator_blockage | Customer | Date | Time | Psy_Room | Average_time | Conditions | Engineer | Tech | OD_Unit_Model | OD_Unit_Serial | Unit_capacity | Refrigerant_type | ID_Unit_type | Refrigerant_charge | Volt_min_max_phs | TU_ID_Tag | Test_Standard | conditions_indoor_dry_bulb | conditions_indoor_wet_bulb | conditions_outdoor_dry_bulb | conditions_outdoor_wet_bulb | refrig_charge_ck_1 | refrig_charge_ck_2 | refrig_charge_factory_ck_1 | refrig_charge_factory_ck_2 | Total_Volts_mean | Total_Volts_std | Total_Amps_mean | Total_Amps_std | Net_Sensible_Capacity_mean | Net_Sensible_Capacity_std | Sensible_ViaGrids_mean | Sensible_ViaGrids_std | Net_Latent_Enthalpy_mean | Net_Latent_Enthalpy_std | Air_Side_Only_Cap_mean | Air_Side_Only_Cap_std | Air_Side_Only_EER_mean | ID_Blower_Motor_mean | ID_Blower_Power_mean | Code_tester_spd_mean | Air_Side_Only_EERs_mean | Enthalpy_evap_out_1_mean | Enthalpy_evap_out_1_std | Total_meas_heat_bal_mean | Cycle_number | Fan_on_time_min | OD_Outdoor_Dry_Air_mean | Cycle_total_time | OD_Outdoor_Wet_Air_mean | Nozzle_Area_mean | ID_Calc_Power_From_CFM_mean | C_test_SCFM_mean | C_test_Spec_vol_mix | Qss_mean | C_test_Spec_heat | Qcyc_mean | C_test_Hum_ratio | Delta_T_mean | C_Net_mean | OD_Off_Watt_hours | D_Net_mean | OD_On_Watt_hours | Integrated_EER_mean | Off_Watt_hours | EER_from_B_sensible_only_mean | ID_Off_Watt_hours | ID_On_Watt_hours | CLF_mean | Cyclic_Watt_hours | CD_mean | OD_SS_Watt_hours | ID_SS_Watt_hours | SEER_mean | Steady_Watt_hours | Watt_hour_ratio | Average_air_side_EER_mean | comments1 | comments2 | In_Dry_Bulb_avg | In_Dry_Bulb_std | In_Wet_Bulb_avg | In_Wet_Bulb_std | OD_Dry_Bulb_avg | OD_Dry_Bulb_std | OD_Wet_Bulb_avg | OD_Wet_Bulb_std | Inlet_Grid_avg | Inlet_Grid_std | Outlet_Grid_avg | Outlet_Grid_std | Nozzle_Temp_avg | Nozzle_Temp_std | B4Nozzle_avg | B4Nozzle_std | Nozzle_Delta_avg | Nozzle_delta_std | Net_Sensible_avg | Net_Sensible_std | Net_Latent_Enthalpy_avg | Net_Latent_Enthalpy_std | Air_Side_Only_EER_avg | Air_Side_Only_EER_std | Ref_Only_Cap_avg | Ref_Only_Cap_std | Meas_Refr_Only_EER_avg | Meas_Refr_Only_EER_std | Total_meas_heat_bal_avg | Total_meas_heat_bal_std | Tu_Total_V1_avg | Tu_Total_V1_std | Tu_Total_V2_avg | Tu_Total_V2_std | Tu_Total_V3_avg | Tu_Total_V3_std | Tu_Total_A1_avg | Tu_Total_A1_std | Tu_Total_A2_avg | Tu_Total_A2_std | Tu_Total_A3_avg | Tu_Total_A3_std | Tu_Total_W1_avg | Tu_Total_W1_std | Tu_Total_W2_avg | Tu_Total_W2_std | Tu_Total_W3_avg | Tu_Total_W3_std | ID_Blower_V1_avg | ID_Blower_V1_std | ID_Blower_V2_avg | ID_Blower_V2_std | ID_Blower_V3_avg | ID_Blower_V3_std | ID_Blower_A1_avg | ID_Blower_A1_std | ID_Blower_A2_avg | ID_Blower_A2_std | ID_Blower_A3_avg | ID_Blower_A3_std | ID_Blower_PF_avg | Comp_1_V1_avg | Comp_1_V1_std | Comp_1_V2_avg | Comp_1_V2_std | Comp_1_V3_avg | Comp_1_V3_std | Comp_1_A1_avg | Comp_1_A1_std | Comp_1_A2_avg | Comp_1_A2_std | Comp_1_A3_avg | Comp_1_A3_std | Comp_1_W_avg | Comp_1_W_std | Comp_1_PF_avg | Comp_2_V1_avg | Comp_2_V2_avg | Comp_2_V3_avg | Comp_2_A1_avg | Comp_2_A2_avg | Comp_2_A3_avg | Comp_2_W_avg | Comp_2_PF_avg | OD_Fan_Volts_avg | OD_Fan_Volts_std | OD_Fan_Amps_avg | OD_Fan_Amps_std | OD_Fan_Watts_avg | OD_Fan_Watts_std | Control_Watts_avg | Control_Watts_std | Total_Power_Individual_avg | Code_Tester_L1_V_avg | Code_Tester_L2_V_avg | Code_Tester_L3_V_avg | Code_Tester_L1_A_avg | Code_Tester_L2_A_avg | Code_Tester_L3_A_avg | Code_Tester_Watts_avg | Code_Tester_PF_avg | Code_Speed_avg | Code_Hz_avg | Control_Volts_avg | Control_Volts_std | Control_Amps_avg | Control_Amps_std | Liq_OD_PSIG_avg | Liq_OD_PSIG_std | Liq_OD_Temp_avg | Liq_OD_Temp_std | Sat_Liq_OD_avg | Sat_Liq_OD_std | SC_Liq_OD_avg | SC_Liq_OD_std | Discharge_PSIG_avg | Discharge_PSIG_std | Discharge_temp_avg | Discharge_temp_std | Sat_Compr_disch_avg | Sat_Compr_disch_std | SH_Compr_disch_avg | SH_Compr_disch_std | Liq_ID_PSIG_avg | Liq_ID_PSIG_std | Liq_ID_temp_avg | Liq_ID_temp_std | Sat_Liq_ID_avg | Sat_Liq_ID_std | SC_Liq_ID_avg | SC_Liq_ID_std | Gas_ID_PSIG_avg | Gas_ID_PSIG_std | Gas_ID_temp_avg | Gas_ID_temp_std | Sat_Gas_ID_avg | Sat_Gas_ID_std | SH_Gas_ID_avg | SH_Gas_ID_std | Suction_PSIG_avg | Suction_PSIG_std | Suction_temp_avg | Suction_temp_std | Sat_Suction_avg | Sat_Suction_std | SH_Suction_avg | SH_Suction_std | Flow_rate_lbs_hr_avg | Flow_rate_lbs_hr_std | Enthalpy_evap_In_1_mean | Enthalpy_evap_In_1_std | Meas_Refr_Only_Cap_mean | Meas_Refr_Only_Cap_std | Gross_ref_meas_cap_avg | Gross_ref_meas_cap_std | Liq_OD_BR_PSIG_avg | Liq_OD_BR_PSIG_std | Liq_OD_BR_temp_avg | Liq_OD_BR_temp_std | Sat_Liq_OD_BR_avg | Sat_Liq_OD_BR_std | SC_Liq_OD_BR_avg | SC_Liq_OD_BR_std | Liq_OD_AR_PSIG_avg | Liq_OD_AR_PSIG_std | Sat_Liq_OD_AR_avg | Sat_Liq_OD_AR_std | SC_Liq_OD_AR_avg | SC_Liq_OD_AR_std | Sat_ID_Gas_avg | Sat_ID_Gas_std | SH_ID_Gas_avg | SH_ID_Gas_std | Cond_Outlet_Sat_Liq_ID_avg | Cond_Outlet_Sat_Liq_ID_std | Liq_1_After_Restriction_avg | Liq_1_After_Restriction_std | Liq_Bef_Drier_PSIG_avg | Liq_Bef_Drier_PSIG_std | Liq_Bef_Drier_temp_avg | Liq_Bef_Drier_temp_std | Sat_Liq_Bef_Drier_avg | Sat_Liq_Bef_Drier_std | SC_Liq_Bef_Drier_avg | SC_Liq_Bef_Drier_std | Liq_After_Restriction__PSIG_avg | Liq_After_Restriction__PSIG_std | Sat_Liq_After_Restriction_avg | Sat_Liq_After_Restriction_std | SC_Liq_After_Restriction_avg | SC_Liq_After_Restriction_std | Gas_SH_ID_avg | Gas_SH_ID_std | Discharge_PSIG_avg_c2 | Discharge_PSIG_std_c2 | Discharge_temp_avg_c2 | Discharge_temp_std_c2 | Sat_Compr_disch_avg_c2 | Sat_Compr_disch_std_c2 | SH_Compr_disch_avg_c2 | SH_Compr_disch_std_c2 | liq_od_psig_avg_c2 | liq_od_psig_std_c2 | Sat_Liq_OD_avg_c2 | Sat_Liq_OD_std_c2 | SC_Liq_OD_avg_c2 | SC_Liq_OD_std_c2 | liq_id_psig_avg_c2 | liq_id_psig_std_c2 | liq_id_temp_avg_c2 | liq_id_temp_std_c2 | sat_liq_id_avg_c2 | sat_liq_id_std_c2 | sc_liq_id_avg_c2 | sc_liq_id_std_c2 | gas_id_psig_avg_c2 | gas_id_psig_std_c2 | sat_gas_id_avg_c2 | sat_gas_id_std_c2 | sh_gas_id_avg_c2 | sh_gas_id_std_c2 | suction_psig_avg_c2 | suction_psig_std_c2 | suction_temp_avg_c2 | suction_temp_std_c2 | sat_suction_avg_c2 | sat_suction_std_c2 | sh_suction_avg_c2 | sh_suction_std_c2 | liquid_bef_filter_temp_avg_c2 | liquid_bef_filter_temp_std_c2 | Flow_rate_lbs_hr_avg_c2 | Flow_rate_lbs_hr_std_c2 | Enthalpy_Evap_In_avg_c2 | Enthalpy_Evap_In_std_c2 | Enthalpy_Evap_Out_avg_c2 | Enthalpy_Evap_Out_std_c2 | Meas_ref_only_cap_avg_c2 | Meas_ref_only_cap_std_c2 | Gross_ref_meas_cap_avg_c2 | Gross_ref_meas_cap_std_c2 | liq_od_br_psig_avg_c2 | liq_od_br_psig_std_c2 | liq_od_br_temp_avg_c2 | liq_od_br_temp_std_c2 | sat_liq_od_br_avg_c2 | sat_liq_od_br_std_c2 | sc_liq_od_br_avg_c2 | sc_liq_od_br_std_c2 | liq_od_ar_psig_avg_c2 | liq_od_ar_psig_std_c2 | sat_liq_od_ar_avg_c2 | sat_liq_od_ar_std_c2 | sc_liq_od_ar_avg_c2 | sc_liq_od_ar_std_c2 | Cond_Outlet_Liq_ID_temp_avg_c2 | Cond_Outlet_Liq_ID_temp_std_c2 | Cond_Outlet_Sat_Liq_ID_avg_c2 | Cond_Outlet_Sat_Liq_ID_std_c2 | Bef_FD_CK1_avg | Bef_FD_CK1_std | Aft_FD_CK1_avg | Aft_FD_CK1_std | Bef_FD_CK2_avg | Bef_FD_CK2_std | Aft_FD_CK2_avg | Aft_FD_CK2_std | Inside_Supply_Duct_1_avg | Inside_Supply_Duct_1_std | Inside_Supply_Duct_2_avg | Inside_Supply_Duct_2_std | Inside_Supply_Duct_3_avg | Inside_Supply_Duct_3_std | Inside_Supply_Duct_4_avg | Inside_Supply_Duct_4_std | Inside_Supply_Duct_5_avg | Inside_Supply_Duct_5_std | Inside_Supply_Duct_6_avg | Inside_Supply_Duct_6_std | liq_od_backup_ck1_avg | liq_od_backup_ck1_std | liq_id_backup_ck1_avg | liq_id_backup_ck1_std | gas_id_backup_ck1_avg | gas_id_backup_ck1_std | suction_backup_ck1_avg | suction_backup_ck1_std | discharge_backup_ck2_avg | discharge_backup_ck2_std | liq_od_backup_ck2_avg | liq_od_backup_ck2_std | liq_id_backup_ck2_avg | liq_id_backup_ck2_std | gas_id_backup_ck2_avg | gas_id_backup_ck2_std | suction_backup_ck2_avg | suction_backup_ck2_std | Liq_ID_Temp_CK1_avg | Liq_ID_Temp_CK1_std | Liq_ID_Temp_CK2_avg | Liq_ID_Temp_CK2_std | OD_Inlet_Grid_Econo_avg | OD_Inlet_Grid_Econo_std | Liq_Upstream_CK1_avg | Liq_Upstream_CK1_std | Liq_Downstream_CK1_avg | Liq_Downstream_CK1_std | Liq_Upstream_CK2_avg | Liq_Upstream_CK2_std | Liq_Downstream_CK2_avg | Liq_Downstream_CK2_std | liq_aft_filter_temp_ck1_avg | liq_aft_filter_temp_ck1_std | liq_aft_filter_temp_ck2_avg | liq_aft_filter_temp_ck2_std | Economizer_Inlet_A1_temp_avg | Economizer_Inlet_A1_temp_std | Economizer_Inlet_A2_temp_avg | Economizer_Inlet_A2_temp_std | Economizer_Inlet_B1_temp_avg | Economizer_Inlet_B1_temp_std | Economizer_Inlet_B2_temp_avg | Economizer_Inlet_B2_temp_std | Economizer_Inlet_C1_temp_avg | Economizer_Inlet_C1_temp_std | Economizer_Inlet_C2_temp_avg | Economizer_Inlet_C2_temp_std | CK1_Liq_ID_Temp_avg | CK1_Liq_ID_Temp_std | Inside_Supply_Duct_6_avg | Inside_Supply_Duct_6_std | Liq_OD_Temp_CK1_avg | Liq_OD_Temp_CK1_std | Liq_OD_Temp_CK2_avg | Liq_OD_Temp_CK2_std | Liq_Bef_Filter_Temp_CK1_avg | Liq_Bef_Filter_Temp_CK1_std | Liq_Bef_Filter_Temp_CK2_avg | Liq_Bef_Filter_Temp_CK2_std | Liq_Aft_Restric_Temp_CK1_avg | Liq_Aft_Restric_Temp_CK1_std | Liq_Aft_Restric_Temp_CK2_avg | Liq_Aft_Restric_Temp_CK2_std | Suction_CK1_avg | Suction_CK1_std | Suction_CK2_avg | Suction_CK2_std | liq_od_backup_2_ck1_avg | liq_od_backup_2_ck1_std | liq_od_backup_2_ck2_avg | liq_od_backup_2_ck2_std | gas_id_ck1_avg | gas_id_ck1_std | Liq_OD_BR_1_avg | Liq_OD_BR_1_std | gas_id_ck2_avg | gas_id_ck2_std | Liq_OD_BR_2_avg | Liq_OD_BR_2_std | liq_aft_dryer_b4_restr_ck1_avg | liq_aft_dryer_b4_restr_ck1_std | liq_aft_dryer_b4_restr_ck2_avg | liq_aft_dryer_b4_restr_ck2_std | Liq_2_After_Restriction_avg | Liq_2_After_Restriction_std | Compressor_Top_avg | Compressor_Top_std | Compressor_Middle_avg | Compressor_Middle_std | discharge_backup_ck1_avg | discharge_backup_ck1_std | OD_Inlet_Grid_1_avg | OD_Inlet_Grid_1_std | OD_Inlet_Grid_2_avg | OD_Inlet_Grid_2_std | Inside_Return_Duct_1_avg | Inside_Return_Duct_1_std | Inside_Return_Duct_2_avg | Inside_Return_Duct_2_std | Inside_Return_Duct_3_avg | Inside_Return_Duct_3_std | Inside_Return_Duct_4_avg | Inside_Return_Duct_4_std | Inside_Return_Duct_5_avg | Inside_Return_Duct_5_std | Inside_Return_Duct_6_avg | Inside_Return_Duct_6_std | Inside_Return_Duct_7_avg | Inside_Return_Duct_7_std | Return_Coil_Face_A1_avg | Return_Coil_Face_A1_std | Return_Coil_Face_A2_avg | Return_Coil_Face_A2_std | Return_Coil_Face_A3_avg | Return_Coil_Face_A3_std | Return_Coil_Face_A4_avg | Return_Coil_Face_A4_std | Return_Coil_Face_B1_avg | Return_Coil_Face_B1_std | Return_Coil_Face_B2_avg | Return_Coil_Face_B2_std | Return_Coil_Face_B3_avg | Return_Coil_Face_B3_std | Return_Coil_Face_B4_avg | Return_Coil_Face_B4_std | Return_Coil_Face_C1_avg | Return_Coil_Face_C1_std | Return_Coil_Face_C2_avg | Return_Coil_Face_C2_std | Return_Coil_Face_C3_avg | Return_Coil_Face_C3_std | Return_Coil_Face_C4_avg | Return_Coil_Face_C4_std | Return_Coil_Face_D1_avg | Return_Coil_Face_D1_std | Return_Coil_Face_D2_avg | Return_Coil_Face_D2_std | Return_Coil_Face_D3_avg | Return_Coil_Face_D3_std | Return_Coil_Face_D4_avg | Return_Coil_Face_D4_std | Return_Coil_Face_E1_avg | Return_Coil_Face_E1_std | Return_Coil_Face_E2_avg | Return_Coil_Face_E2_std | Return_Coil_Face_E3_avg | Return_Coil_Face_E3_std | Return_Coil_Face_E4_avg | Return_Coil_Face_E4_std | Inside_Return_Duct_8_avg | Inside_Return_Duct_8_std | Inside_Return_Duct_9_avg | Inside_Return_Duct_9_std | Inside_Return_Duct_10_avg | Inside_Return_Duct_10_std | Inside_Return_Duct_11_avg | Inside_Return_Duct_11_std | Inside_Return_Duct_12_avg | Inside_Return_Duct_12_std | Inside_Return_Duct_13_avg | Inside_Return_Duct_13_std | Inside_Return_Duct_14_avg | Inside_Return_Duct_14_std | Inside_Return_Duct_15_avg | Inside_Return_Duct_15_std | Return_Coil_Face_A5_avg | Return_Coil_Face_A5_std | Return_Coil_Face_B5_avg | Return_Coil_Face_B5_std | Return_Coil_Face_C5_avg | Return_Coil_Face_C5_std | Economizer_1_avg | Economizer_1_std | Economizer_2_avg | Economizer_2_std | Economizer_3_avg | Economizer_3_std | Economizer_4_avg | Economizer_4_std | Economizer_5_avg | Economizer_5_std | Economizer_6_avg | Economizer_6_std | Return_Coil_Face_D5_avg | Return_Coil_Face_D5_std | OD_Inlet_Grid_3_avg | OD_Inlet_Grid_3_std | Return_Coil_Face_1_avg | Return_Coil_Face_1_std | Return_Coil_Face_2_avg | Return_Coil_Face_2_std | Return_Coil_Face_3_avg | Return_Coil_Face_3_std | Return_Coil_Face_4_avg | Return_Coil_Face_4_std | Return_Coil_Face_5_avg | Return_Coil_Face_5_std | Return_Coil_Face_6_avg | Return_Coil_Face_6_std | Return_Coil_Face_7_avg | Return_Coil_Face_7_std | Return_Coil_Face_8_avg | Return_Coil_Face_8_std | Return_Coil_Face_9_avg | Return_Coil_Face_9_std | Return_Coil_Face_10_avg | Return_Coil_Face_10_std | Return_Coil_Face_11_avg | Return_Coil_Face_11_std | Return_Coil_Face_12_avg | Return_Coil_Face_12_std | Return_Coil_Face_13_avg | Return_Coil_Face_13_std | Return_Coil_Face_14_avg | Return_Coil_Face_14_std | Return_Coil_Face_15_avg | Return_Coil_Face_15_std | Return_Coil_Face_16_avg | Return_Coil_Face_16_std | Economizer_grid_avg | Economizer_grid_std | Liq_Bef_FlowM_Ck1_avg | Liq_Bef_FlowM_Ck1_1std | Liq_After_FlowM_Ck1_avg | Liq_After_FlowM_Ck1_std | Liq_Bef_FlowM_Ck2_avg | Liq_Bef_FlowM_Ck2_std | Liq_After_FlowM_Ck2_avg | Liq_After_FlowM_Ck2_std | Inside_Supply_Duct_7_avg | Inside_Supply_Duct_7_std | Inside_Supply_Duct_8_avg | Inside_Supply_Duct_8_std | Comparison | ID_Inlet_Dry_Air_mean | ID_Inlet_Dry_Air_std | ID_Inlet_Wet_Air_mean | ID_Inlet_Wet_Air_std | ID_Outlet_Dry_Air_mean | ID_Outlet_Dry_Air_std | ID_Outlet_Wet_Air_mean | ID_Outlet_Wet_Air_std | OD_Inlet_Dry_Air_mean | OD_Inlet_Dry_Air_std | OD_Inlet_Wet_Air_mean | OD_Inlet_Wet_Air_std | Tot_Air_Flow_CFM_mean | Tot_Air_Flow_CFM_std | Tot_Air_Flow_SCFM_mean | Tot_Air_Flow_SCFM_std | Unit_Total_Static_mean | Unit_Total_Static_std | Unit_Inlet_Static_mean | Unit_Inlet_Static_std | B4_Nozzle_Static_mean | B4_Nozzle_Static_std | Nozzle_Delta_mean | Nozzle_Delta_std | Barometric_Pressure_mean | Barometric_Pressure_std | Total_Power_mean | Total_Power_std | ID_Blower_W_avg | ID_Blower_W_std | OA_Comp_Ratio | OA_Comp | Spec_Vol_Comp | Delta_P_Comp | Fan_Heat_DT | SA_Mass_Flow | Flow_Power | OA_Flow_Corrected | OA_Mass_Flow_Corrected | RA_Mass_Flow_Rate | MA_Hum_Ratio | MA_Enthalpy | Coil_Leaving_DB | OA_Spec_Vol | Coil_Out_Spec_Vol | OA_Hum_Ratio | OA_Enthalpy | RA_Hum_Ratio | RA_Enthalpy | Coil_Out_Hum_Ratio | SA_Enthalpy | MA_Dry_Bulb | MA_Wet_Bulb | Coil_Leaving_Enthalpy | Gross_Cooling_Capacity | Gross_Sensible_Capacity | Comp_Unit_Power | EIR | Net_Cooling_Capacity | Net_Sensible_Capacity | EER | Coil_Bypass_Factor | dh | dT | Ts | Gross_Coil_Capacity | Space_Load | Fan_Heat | OA_Load | Total load | Calibration
5 | C-55-1ER-DM | 30N0001 | C-55-1ER-DM | 1 Finger | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 6:42:49 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.2 | 0.8 | 1.7 | 0 | 7597 | 27 | 6946 | 49 | 3193 | 71 | 10793 | 82 |  | 943 |  | 12.9 |  | 109.86 | 0.01 | 0 | [31 empty] | 28.7813 | Econo 1F-open, no compressor, 55/51 ambient, 53.5% inlet 52% outlet Meriam, adjust code tester speed to match total static of run C-55-1E-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 1F: with flow meter: new filter drier: with isolation ball valves: with code | 74.996 | 0.012 | 62.002 | 0.031 | 54.994 | 0.014 | 50.997 | 0.017 | 74.36 | 0.04 | 68.97 | 0.03 | 71.69 | 0.02 | 0.006 | 0.006 | 1.1763 | 0.0064 | 7597 | 27 | 3193 | 71 | 28.827 | 0.419 | [6 empty] | 230.2 | 0.8 | 230.2 | 0.8 | 230.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.2 | 0.3 | 0.2 | 0.3 | 0.2 | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 23 |  | 397.1 | 476.6 | 477.8 | 478 | 0.9 | 0.9 | 1 | 500 | 0.64 | 12.9 | 18 | [44 empty] | -0.59 | 0.04 | 26.22 | 0.01 | -1277 | 16 | [114 empty] | 68.86 | 0.35 | 69.81 | 0.22 | 69.38 | 0.02 | 69.7 | 0.2 | 69.18 | 0.17 | 69.15 | 0.17 | [32 empty] | 56.01 | 0.02 |  |  | 55.97 | 0.25 | 55.9 | 0.21 | 55.12 | 0.17 | 55.1 | 0.12 | 54.95 | 0.07 | 54.98 | 0.07 | [8 empty] | 54.74 | 0.07 | [34 empty] | 54.83 | 0.09 | 54.57 | 0.06 | 74.4 | 0.05 | 74.42 | 0.05 | 74.38 | 0.03 | 74.49 | 0.06 | 74.45 | 0.06 | 74.53 | 0.06 | 74.49 | 0.05 | 58.54 | 0.04 | 57.71 | 0.05 | 57.21 | 0.05 | 60.23 | 0.23 | 59.32 | 0.07 | 59.98 | 0.11 | 60.99 | 0.14 | 62.25 | 0.11 | 59.85 | 0.07 | 74.25 | 0.06 | 73.45 | 0.1 | 74.55 | 0.06 | 67.72 | 0.15 | 73.95 | 0.04 | 74.48 | 0.03 | 73.35 | 0.05 | 72.46 | 0.14 | 74.15 | 0.06 | 74.31 | 0.05 | 74.42 | 0.04 | [84 empty] | Economizer test | 74.996 | 0.012 | 62.002 | 0.031 | 69.095 | 0.007 | 58.991 | 0.026 | 54.994 | 0.014 | 50.997 | 0.017 | 1177.7 | 3.2 | 1144.1 | 3.1 | 0.568 | 0.011 | -0.136 | 0.001 | 0.006 | 0.006 | 1.1763 | 0.0064 | 29.601 | 0.001 | 375 | 5 | 374.1 | 4.7 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.80253 | 5274.6772 | 76.3444 | 291.7774 | 1343.6317 | 3931.0455 | 0.0083239 | 25.8693 | 68.2925 | 13.0293 | 13.3965 | 0.0069812 | 20.776 | 0.0087829 | 27.6101 | 0.0082503 | 25.5895 | 69.9133 | 59.4191 | 25.3939
5 | C-55-2ER-DM | 30N0002 | C-55-2ER-DM | 2 Finger | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 9:20:19 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.2 | 0.8 | 1.7 | 0 | 9635 | 29 | 8894 | 53 | 4063 | 82 | 13702 | 85 |  | 942 |  | 13.8 | [35 empty] | 36.3448 | Econo 2F-open, no compressor, 55/51, 53.5% inlet 52% outlet Meriam, ambient--adjust code tester speed to match total static of run C-55-2E-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 1F: with flow meter: new filter drier: with isolation ball valves: with code | 75 | 0.014 | 62.001 | 0.029 | 55 | 0.016 | 50.998 | 0.018 | 74.37 | 0.06 | 67.58 | 0.05 | 70.69 | 0.01 | 0.025 | 0.004 | 1.2105 | 0.0047 | 9635 | 29 | 4063 | 82 | 36.343 | 0.518 | [24 empty] | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 478 | 480 | 480 | 0.9 | 0.9 | 1.1 | 510 | 0.64 | 13.8 | 18.4 | [164 empty] | 66.83 | 0.21 | 69.04 | 0.16 | 67.99 | 0.08 | 68.89 | 0.13 | 67.33 | 0.1 | 68.12 | 0.12 | [32 empty] | 56.14 | 0.03 |  |  | 55.04 | 0.18 | 55.27 | 0.19 | 54.58 | 0.11 | 54.89 | 0.12 | 54.82 | 0.1 | 54.82 | 0.09 | [44 empty] | 55.22 | 0.1 | 54.95 | 0.1 | 74.68 | 0.09 | 74.64 | 0.07 | 74.47 | 0.03 | 74.85 | 0.1 | 74.79 | 0.1 | 74.85 | 0.1 | 74.75 | 0.08 | 59.12 | 0.07 | 58.71 | 0.07 | 57.59 | 0.07 | 58.85 | 0.12 | 60.43 | 0.09 | 59.03 | 0.13 | 58.94 | 0.1 | 59.74 | 0.1 | 60.27 | 0.09 | 73.41 | 0.07 | 68.9 | 0.15 | 70.64 | 0.12 | 64.85 | 0.15 | 73.3 | 0.04 | 73.73 | 0.04 | 72.75 | 0.05 | 70.62 | 0.15 | 73.23 | 0.05 | 73.84 | 0.04 | 72.84 | 0.03 | [84 empty] | Economizer test | 75 | 0.014 | 62.001 | 0.029 | 67.639 | 0.008 | 58.203 | 0.026 | 55 | 0.016 | 50.998 | 0.018 | 1192.7 | 2.4 | 1162.9 | 2.3 | 0.538 | 0.007 | -0.108 | 0.002 | 0.025 | 0.004 | 1.2105 | 0.0047 | 29.645 | 0.001 | 377 | 5 | 376.8 | 4.9 | 0.32805 | 381.4893 | 13.029 | 0.108 | 0.8049 | 5357.0601 | 73.5004 | 381.4966 | 1756.7678 | 3600.2924 | 0.0081907 | 25.3686 | 66.8341 | 13.0295 | 13.3584 | 0.0069803 | 20.7765 | 0.0087813 | 27.6094 | 0.0081087 | 25.0803 | 68.4558 | 58.6507 | 24.8842
5 | C-55-3ER-DM | 30N0003 | C-55-3ER-DM | 3 Finger | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 16:28:28 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.2 | 0.8 | 1.7 | 0 | 13008 | 144 | 12228 | 143 | 5272 | 135 | 18284 | 260 |  | 942 |  | 14 | [35 empty] | 48.4987 | Econo 3F-open, no compressor, 55/51 ambient, 53.5% inlet 52% outlet Meriam,--adjust code tester speed to match total static of run C-55-3E-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 3F: with flow meter: new filter drier: with isolation ball valves: with code | 75.002 | 0.017 | 62.003 | 0.031 | 55 | 0.011 | 51.002 | 0.019 | 74.38 | 0.05 | 65.03 | 0.03 | 69.01 | 0.03 | 0.016 | 0.014 | 1.2053 | 0.0251 | 13008 | 144 | 5272 | 135 | 48.572 | 0.838 | [24 empty] | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 482 | 482 | 482 | 0.9 | 0.9 | 1 | 500 | 0.63 | 14 | 18.3 | [164 empty] | 64.13 | 0.23 | 66.26 | 0.17 | 65.1 | 0.08 | 66.18 | 0.16 | 64.35 | 0.13 | 65.42 | 0.13 | [32 empty] | 56.31 | 0.02 |  |  | 55.23 | 0.1 | 55.4 | 0.13 | 54.59 | 0.06 | 54.8 | 0.07 | 54.72 | 0.06 | 54.73 | 0.06 | [44 empty] | 55.11 | 0.09 | 54.67 | 0.07 | 74.43 | 0.05 | 74.43 | 0.05 | 74.4 | 0.04 | 74.49 | 0.07 | 74.45 | 0.07 | 74.53 | 0.07 | 74.53 | 0.06 | 57.27 | 0.04 | 57.09 | 0.03 | 57.1 | 0.04 | 56.92 | 0.03 | 57.04 | 0.08 | 59.98 | 0.08 | 57.19 | 0.05 | 57.04 | 0.06 | 60.89 | 0.09 | 69.3 | 0.13 | 61.55 | 0.14 | 65.53 | 0.15 | 67.15 | 0.09 | 72.69 | 0.06 | 71.5 | 0.05 | 69.75 | 0.06 | 69.75 | 0.1 | 72.47 | 0.06 | 72.67 | 0.04 | 69.27 | 0.05 | [84 empty] | Economizer test | 75.002 | 0.017 | 62.003 | 0.031 | 65.039 | 0.007 | 56.87 | 0.023 | 55 | 0.011 | 51.002 | 0.019 | 1191.7 | 12.5 | 1159 | 12.3 | 0.497 | 0.004 | -0.061 | 0.002 | 0.016 | 0.014 | 1.2053 | 0.0251 | 29.471 | 0.002 | 377 | 5 | 376.1 | 5.3 | 0.4576 | 530.3633 | 13.03 | 0.061 | 0.81507 | 5379.7007 | 67.6714 | 530.3533 | 2442.2408 | 2937.4599 | 0.0079651 | 24.5093 | 64.2239 | 13.0295 | 13.2911 | 0.0069824 | 20.7788 | 0.0087821 | 27.6108 | 0.0079184 | 24.2395 | 65.9379 | 57.3029 | 24.041
5 | C-55-CE-DM | 30N0004 | C-55-CE-DM | closed | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/12/2014 | 23:25:52 | 10 Ton | 0:30:00 | 75/62 - 55/51 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.2 | 0.5 | 1.7 | 0 | 5340 | 17 | 4796 | 44 | 2236 | 49 | 7578 | 48 |  | 942 |  | 13.8 | [35 empty] | 20.1008 | Econo closed, no compressor, 55/51 ambient, 53.5% inlet 52% outlet Meriam,--adjust code tester speed to match total static of run C-55-CE-DM-SPWCT-SS | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo fulley closed: with flow meter: new filter drier: with isolation ball valves: with code | 74.996 | 0.01 | 62 | 0.028 | 54.981 | 0.013 | 51 | 0.017 | 74.36 | 0.03 | 70.67 | 0.05 | 72.83 | 0.01 | 0.033 | 0.004 | 1.1992 | 0.0047 | 5340 | 17 | 2236 | 49 | 20.12 | 0.288 | [24 empty] | 229.9 | 0.5 | 229.9 | 0.5 | 229.9 | 0.5 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 486 | 487 | 488 | 0.9 | 0.9 | 1.1 | 510 | 0.62 | 13.8 | 18.4 | [164 empty] | 70.73 | 0.04 | 71.62 | 0.03 | 71.38 | 0.03 | 71.34 | 0.03 | 71.33 | 0.03 | 70.9 | 0.04 | [32 empty] | 55.99 | 0.03 |  |  | 54.32 | 0.1 | 54.41 | 0.11 | 54.01 | 0.08 | 54.24 | 0.09 | 54.33 | 0.07 | 54.36 | 0.07 | [8 empty] | 54.19 | 0.07 | [34 empty] | 54.67 | 0.11 | 54.29 | 0.07 | 74.5 | 0.06 | 74.52 | 0.05 | 74.45 | 0.03 | 74.61 | 0.06 | 74.58 | 0.07 | 74.63 | 0.07 | 74.57 | 0.06 | 64.16 | 0.08 | 65.54 | 0.14 | 67.94 | 0.09 | 63.66 | 0.11 | 64.15 | 0.08 | 65.01 | 0.16 | 70.92 | 0.1 | 65.15 | 0.14 | 58.35 | 0.07 | 72.28 | 0.11 | 74.93 | 0.07 | 74.91 | 0.06 | 67.61 | 0.21 | 74.78 | 0.05 | 74.87 | 0.04 | 74.28 | 0.05 | 73.84 | 0.06 | 74.28 | 0.06 | 74.38 | 0.04 | 74.5 | 0.03 | [84 empty] | Economizer test | 74.996 | 0.01 | 62 | 0.028 | 70.879 | 0.009 | 59.927 | 0.026 | 54.981 | 0.013 | 51 | 0.017 | 1190.2 | 2.4 | 1153.9 | 2.3 | 0.599 | 0.007 | -0.182 | 0.001 | 0.033 | 0.004 | 1.1992 | 0.0047 | 29.611 | 0.001 | 377 | 5 | 376.3 | 4.8 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.78975 | 5312.2157 | 81.2008 | 191.8078 | 883.2927 | 4428.923 | 0.008483 | 26.4729 | 70.0892 | 13.0291 | 13.443 | 0.0069858 | 20.7779 | 0.0087816 | 27.6087 | 0.0084154 | 26.2046 | 71.6771 | 60.3303 | 26.0121
5 | C-55-OER-DM | 30N0005 | C-55-OER-DM | Fully open | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 18:30:01 | 10 Ton | 0:30:00 | 75/62 - 55/51 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.2 | 0.6 | 1.7 | 0 | 16001 | 132 | 15186 | 132 | 6554 | 120 | 22562 | 221 |  | 943 |  | 12.1 | [35 empty] | 60.6505 | Econo fully open, no compressor, 55/51 ambient, 53.5% inlet 52% outlet Meriam,--adjust code tester speed to match total static of run C-55-OE-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo fully open: with flow meter: new filter drier: with isolation ball valves: with code | 74.998 | 0.02 | 62.005 | 0.025 | 54.998 | 0.011 | 50.999 | 0.015 | 74.36 | 0.05 | 62.31 | 0.03 | 67.26 | 0.02 | 0.01 | 0.009 | 1.1155 | 0.0178 | 16001 | 132 | 6554 | 120 | 60.729 | 0.928 | [24 empty] | 229.8 | 0.6 | 229.8 | 0.6 | 229.8 | 0.6 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 480 | 480 | 480 | 0.8 | 0.9 | 0.9 | 490 | 0.63 | 12.1 | 17.6 | [164 empty] | 62.45 | 0.21 | 62.55 | 0.14 | 62.33 | 0.05 | 62.46 | 0.13 | 62.26 | 0.14 | 61.98 | 0.11 | [32 empty] | 56.42 | 0.03 |  |  | 55.53 | 0.11 | 55.68 | 0.17 | 54.68 | 0.08 | 54.92 | 0.08 | 54.74 | 0.07 | 54.75 | 0.06 | [44 empty] | 55.15 | 0.1 | 54.77 | 0.09 | 74.37 | 0.05 | 74.38 | 0.04 | 74.37 | 0.03 | 74.43 | 0.06 | 74.41 | 0.06 | 74.47 | 0.05 | 74.48 | 0.04 | 57.19 | 0.04 | 57.07 | 0.04 | 57.32 | 0.05 | 57.17 | 0.04 | 57.12 | 0.04 | 58.78 | 0.1 | 57.75 | 0.09 | 56.51 | 0.07 | 70.09 | 0.09 | 66.39 | 0.09 | 56.32 | 0.13 | 56.24 | 0.09 | 74 | 0.05 | 72.44 | 0.05 | 62.87 | 0.09 | 63.7 | 0.13 | 72.98 | 0.05 | 71.28 | 0.07 | 65.26 | 0.07 | 64.8 | 0.1 | [84 empty] | Economizer test | 74.998 | 0.02 | 62.005 | 0.025 | 62.294 | 0.009 | 55.341 | 0.019 | 54.998 | 0.011 | 50.999 | 0.015 | 1145.1 | 9.1 | 1116.2 | 8.8 | 0.425 | 0.003 | -0.023 | 0.001 | 0.01 | 0.009 | 1.1155 | 0.0178 | 29.43 | 0.001 | 372 | 5 | 371.2 | 5.1 | 0.5922 | 661.0136 | 13.029 | 0.023 | 0.86293 | 5197.2904 | 55.7309 | 661.0251 | 3043.989 | 2153.3014 | 0.0077283 | 23.609 | 61.4311 | 13.0295 | 13.2196 | 0.0069813 | 20.7771 | 0.0087844 | 27.6123 | 0.0076693 | 23.2998 | 63.3002 | 55.8513 | 23.0898
5 | C-MF-75629575-1E3J | 30N0006 | C-MF-75629575-1E3J | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/11/2014 | 18:53:52 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 1 | 15.2 | 0 | 17856 | 38 | 16991 | 73 | -1179 | 73 | 16677 | 81 |  | 939 |  | 8.23 |  | 112.36 | 0.01 | 54.3 | [31 empty] | 4.9961 | Factory charge, 3 turns, Econo 1-F open unsealed cab, 53.5% inlet 52% outlet Meriam,--adjust code tester speed to match total static of run C-1E3J-SPWCT-SS | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 1F: with flow meter: new filter drier: with isolation ball valves: with code | 74.999 | 0.022 | 62.001 | 0.029 | 94.999 | 0.01 | 75.002 | 0.012 | 74.31 | 0.06 | 60.6 | 0.04 | 66.14 | 0.02 | 0.014 | 0.003 | 0.8123 | 0.0028 | 17856 | 38 | -1179 | 73 | 4.997 | 0.027 |  |  | 10.9338 |  |  |  | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2974.4 | 5.6 | 2974.4 | 5.6 | 2974.4 | 5.6 | 230 | 1 | 230 | 1 | 230 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 1 | 227.8 | 1 | 227.8 | 1 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2781.7 | 4.9 | [9 empty] | 228.3 | 1 | 0.7 | 0 | 169.1 | 0.9 | 23 |  | 3335.8 | 482 | 483 | 483 | 0.7 | 0.8 | 0.8 | 400 | 0.62 | 8.23 | 15.8 | [12 empty] | 264.87 | 0.17 | 182.61 | 0.04 | 121.25 | 0.05 | 61.36 | 0.05 | 244.87 | 0.22 | 103.24 | 0.04 | 115.48 | 0.07 | 12.24 | 0.07 | 78.35 | 0.04 | 65.87 | 0.07 | 46.14 | 0.02 |  |  | 79.13 | 0.02 | 69.51 | 0.06 | 46.63 | 0.01 | 22.88 | 0.06 | 525.11 | 0.53 | 40.5 | 0.01 | 36497 | 47 | 37733 | 43 | [22 empty] | 248.56 | 0.22 | 104.19 | 0.05 | 116.57 | 0.06 | 12.38 | 0.07 | 247.15 | 0.19 | 116.15 | 0.06 | 12.99 | 0.07 | 19.74 | 0.07 | [74 empty] | 60.06 | 0.06 | 61.83 | 0.05 | 61.49 | 0.08 | 61.64 | 0.04 | 60.99 | 0.07 | 61 | 0.04 | [32 empty] | 103.89 | 0.05 |  |  | 87.45 | 0.27 | 90.02 | 0.24 | 84.71 | 0.33 | 87.18 | 0.47 | 91.93 | 0.7 | 91.95 | 0.7 | [8 empty] | 93.58 | 0.34 |  |  | 103.16 | 0.05 | [30 empty] | 94.87 | 0.06 | 95.19 | 0.06 | 74.68 | 0.05 | 74.67 | 0.05 | 74.45 | 0.05 | 74.86 | 0.06 | 74.87 | 0.06 | 74.85 | 0.06 | 74.65 | 0.06 | 93.15 | 0.05 | 93.03 | 0.09 | 92.45 | 0.17 | 89.84 | 0.31 | 90.76 | 0.09 | 91.15 | 0.15 | 89.05 | 0.14 | 87.32 | 0.1 | 91.63 | 0.06 | 76.2 | 0.1 | 76.89 | 0.12 | 75.59 | 0.07 | 82.46 | 0.16 | 75.77 | 0.06 | 75.3 | 0.06 | 75.37 | 0.05 | 76.65 | 0.12 | 74.82 | 0.04 | 74.86 | 0.04 | 75.01 | 0.05 | [84 empty] | C-55-1ER-DM | 74.999 | 0.022 | 62.001 | 0.029 | 60.591 | 0.013 | 57.182 | 0.022 | 94.999 | 0.01 | 75.002 | 0.012 | 1160.9 | 2 | 1109.9 | 2 | 0.54 | 0.004 | -0.135 | 0.001 | 0.014 | 0.003 | 0.8123 | 0.0028 | 28.879 | 0.001 | 3338 | 9 | 362 | 5.6 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.78488 | 5281.5787 | 70.4114 | 302.4098 | 1286.8589 | 3994.7197 | 0.010034 | 30.1798 | 59.8061 | 14.0999 | 13.1881 | 0.013923 | 38.1591 | 0.0087815 | 27.6094 | 0.0091559 | 24.5025 | 79.9064 | 65.5272 | 24.311 | 30996.8223 | 25478.7261 | 2976 | 0.32768 | 30001.6302 | 24483.5341 | 8.9879 | 0.22534 | -5.8689 | -20.1003 | 53.959 | 30996.8223 | 16409.0926 | 1011.7524 | 13575.9773 | 30996.8223 | 100%
5 | C-MF-75629575-2E3J | 30N0007 | C-MF-75629575-2E3J | 2 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/11/2014 | 21:36:24 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.8 | 15.2 | 0 | 16314 | 38 | 15548 | 72 | -3297 | 77 | 13014 | 65 |  | 939 |  | 8.5 |  | 112.78 | 0.01 | 64.84 | [31 empty] | 3.8929 | Factory charge, 3 turns, Econo 2-F open unsealed cab, 53.5% inlet 52% outlet--Meriam, adjust code tester speed to match total static of run C-2E3J-SPWCT-SS | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 2F: with flow meter: new filter drier: with isolation ball valves: with code | 75.002 | 0.019 | 61.996 | 0.029 | 95.001 | 0.012 | 74.998 | 0.015 | 74.35 | 0.05 | 61.85 | 0.04 | 66.97 | 0.01 | 0.023 | 0.003 | 0.8243 | 0.0025 | 16314 | 38 | -3297 | 77 | 3.894 | 0.022 |  |  | 11.073 |  |  |  | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2977.9 | 6 | 2977.9 | 6 | 2977.9 | 6 | 230 | 0.8 | 230 | 0.8 | 230 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2784.7 | 5.6 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 169.4 | 0.8 | 23 |  | 3340.7 | 486 | 487 | 488 | 0.7 | 0.7 | 0.8 | 410 | 0.62 | 8.5 | 15.9 | [12 empty] | 265.78 | 0.19 | 183.77 | 0.04 | 121.52 | 0.05 | 62.25 | 0.06 | 245.68 | 0.23 | 103.04 | 0.06 | 115.74 | 0.07 | 12.7 | 0.09 | 79.34 | 0.05 | 68.53 | 0.04 | 46.81 | 0.03 |  |  | 79.96 | 0.03 | 71.36 | 0.05 | 47.2 | 0.02 | 24.16 | 0.06 | 528.88 | 0.52 | 40.44 | 0.02 | 37017 | 46 | 38259 | 42 | [22 empty] | 249.41 | 0.22 | 103.93 | 0.05 | 116.84 | 0.06 | 12.91 | 0.07 | 247.94 | 0.22 | 116.41 | 0.07 | 13.51 | 0.08 | 21.72 | 0.05 | [74 empty] | 61.5 | 0.05 | 62.89 | 0.04 | 62.76 | 0.05 | 62.65 | 0.04 | 62.45 | 0.05 | 62.11 | 0.04 | [32 empty] | 103.67 | 0.06 |  |  | 94.4 | 0.1 | 94.28 | 0.11 | 94.78 | 0.09 | 94.84 | 0.09 | 94.91 | 0.08 | 94.94 | 0.07 | [8 empty] | 94.76 | 0.08 |  |  | 102.89 | 0.06 | [30 empty] | 94.7 | 0.09 | 95.04 | 0.08 | 74.59 | 0.06 | 74.63 | 0.06 | 74.49 | 0.04 | 74.72 | 0.07 | 74.73 | 0.07 | 74.71 | 0.08 | 74.57 | 0.07 | 91.72 | 0.08 | 91.58 | 0.08 | 92.44 | 0.09 | 90.63 | 0.14 | 89.28 | 0.09 | 91.15 | 0.1 | 91.17 | 0.07 | 90.26 | 0.09 | 90.56 | 0.08 | 77.25 | 0.09 | 82.42 | 0.17 | 79.1 | 0.13 | 84.01 | 0.14 | 75.75 | 0.06 | 75.46 | 0.05 | 75.18 | 0.09 | 77.85 | 0.15 | 75.1 | 0.08 | 75.01 | 0.06 | 75.27 | 0.04 | [84 empty] | C-55-2ER-DM | 75.002 | 0.019 | 61.996 | 0.029 | 61.89 | 0.014 | 58.281 | 0.017 | 95.001 | 0.012 | 74.998 | 0.015 | 1167.7 | 1.8 | 1119.5 | 1.7 | 0.507 | 0.003 | -0.107 | 0.001 | 0.023 | 0.003 | 0.8243 | 0.0025 | 29.02 | 0.004 | 3343 | 9 | 363.6 | 5.6 | 0.32805 | 381.4893 | 13.029 | 0.108 | 0.79673 | 5298.1524 | 66.6802 | 395.0165 | 1680.9306 | 3617.2218 | 0.010409 | 30.9527 | 61.0933 | 14.0999 | 13.2239 | 0.013919 | 38.1552 | 0.0087775 | 27.6057 | 0.0095159 | 25.2115 | 81.3875 | 66.5373 | 25.0169 | 31448.7634 | 25805.2052 | 2979.4 | 0.32334 | 30435.3763 | 24791.8181 | 9.1042 | 0.2314 | -5.9358 | -20.2942 | 54.9835 | 31448.7634 | 12684.9461 | 1030.9252 | 17732.8921 | 31448.7634 | 100%
5 | C-MF-75629575-3E3J | 30N0008 | C-MF-75629575-3E3J | 3 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/12/2014 | 5:25:29 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.8 | 15.2 | 0 | 13667 | 36 | 12957 | 60 | -6980 | 61 | 6681 | 70 |  | 937 |  | 8.6 |  | 113.31 | 0.01 | 82.27 | [31 empty] | 1.9943 | . | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 3F: with flow meter: new filter drier: with isolation ball valves: with code | 75.002 | 0.013 | 62.006 | 0.017 | 94.997 | 0.011 | 75.001 | 0.014 | 74.49 | 0.05 | 64.09 | 0.03 | 68.38 | 0.01 | 0.026 | 0.003 | 0.8395 | 0.0029 | 13667 | 36 | -6980 | 61 | 1.994 | 0.022 |  |  | 11.2463 |  |  |  | 229.7 | 0.8 | 229.7 | 0.8 | 229.7 | 0.8 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2982.8 | 5.5 | 2982.8 | 5.5 | 2982.8 | 5.5 | 230 | 0.8 | 230 | 0.8 | 230 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 0.8 | 227.8 | 0.8 | 227.8 | 0.8 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2789.2 | 5.1 | [9 empty] | 228.3 | 0.8 | 0.7 | 0 | 170.3 | 0.8 | 23 |  | 3348.5 | 480 | 480 | 480 | 0.8 | 0.7 | 0.9 | 410 | 0.63 | 8.6 | 16 | [12 empty] | 266.6 | 0.2 | 185.16 | 0.03 | 121.8 | 0.06 | 63.37 | 0.05 | 246.35 | 0.23 | 102.77 | 0.04 | 115.99 | 0.07 | 13.22 | 0.07 | 80.53 | 0.05 | 71.86 | 0.04 | 47.66 | 0.03 |  |  | 81.33 | 0.03 | 73.86 | 0.05 | 48.16 | 0.02 | 25.7 | 0.05 | 533.52 | 0.58 | 40.35 | 0.01 | 37675 | 50 | 38923 | 47 | [22 empty] | 250.12 | 0.23 | 103.65 | 0.05 | 117.09 | 0.07 | 13.44 | 0.07 | 248.68 | 0.22 | 116.67 | 0.06 | 14.13 | 0.07 | 24.2 | 0.05 | [74 empty] | 63.74 | 0.16 | 65.07 | 0.06 | 64.98 | 0.11 | 64.74 | 0.08 | 64.8 | 0.16 | 64.19 | 0.1 | [32 empty] | 103.32 | 0.06 |  |  | 94.2 | 0.18 | 93.9 | 0.2 | 94.72 | 0.11 | 94.72 | 0.13 | 94.89 | 0.08 | 94.9 | 0.08 | [8 empty] | 94.79 | 0.08 |  |  | 102.55 | 0.06 | [30 empty] | 94.93 | 0.08 | 95.31 | 0.06 | 74.87 | 0.04 | 74.86 | 0.03 | 74.59 | 0.03 | 75.06 | 0.04 | 75.06 | 0.05 | 75.02 | 0.04 | 74.82 | 0.04 | 93.97 | 0.05 | 93.41 | 0.05 | 93.39 | 0.05 | 92.93 | 0.06 | 92.96 | 0.05 | 90.7 | 0.09 | 93.27 | 0.06 | 93.26 | 0.06 | 89.69 | 0.07 | 80.42 | 0.11 | 90.01 | 0.14 | 85.57 | 0.17 | 84.07 | 0.11 | 75.65 | 0.03 | 76.16 | 0.04 | 76.01 | 0.04 | 80.83 | 0.11 | 75.76 | 0.04 | 75.98 | 0.03 | 77.02 | 0.03 | [84 empty] | C-55-3ER-DM | 75.002 | 0.013 | 62.006 | 0.017 | 64.047 | 0.015 | 60.125 | 0.019 | 94.997 | 0.011 | 75.001 | 0.014 | 1173.2 | 2.1 | 1134.1 | 2 | 0.473 | 0.005 | -0.067 | 0.001 | 0.026 | 0.003 | 0.8395 | 0.0029 | 29.362 | 0.002 | 3350 | 8 | 366 | 5.4 | 0.4576 | 530.3633 | 13.03 | 0.061 | 0.81284 | 5299.164 | 63.0199 | 578.2039 | 2460.4682 | 2838.6958 | 0.01117 | 32.5092 | 63.2342 | 14.0999 | 13.2836 | 0.013922 | 38.1581 | 0.0087841 | 27.6129 | 0.010159 | 26.4389 | 84.3322 | 68.5056 | 26.2401 | 33220.8445 | 26832.5318 | 2984 | 0.30657 | 32186.7734 | 25798.4607 | 9.608 | 0.23709 | -6.2691 | -21.0981 | 56.6776 | 33220.8445 | 6221.5036 | 1053.197 | 25946.1439 | 33220.8445 | 100%
5 | C-MF-75629575-E3J | 30N0009 | C-MF-75629575-E3J | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/11/2014 | 12:31:48 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 1 | 15 | 0 | 19926 | 38 | 19005 | 79 | 1249 | 73 | 21176 | 85 |  | 939 |  | 8.25 |  | 111.82 | 0.02 | 40.88 | [31 empty] | 6.3668 | Factory charge, 3 turns, closed econo unsealed cab, return and supply Meriam's--set to same as run C-MF-NE3J-SPWCT-SS, adjust code tester speed to match--total static of run C-MF-E3J-SPWCT-SS | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: with economizer: with flow meter: new filter drier: with isolation ball valves: with code | 75.001 | 0.019 | 61.999 | 0.025 | 95 | 0.009 | 75.001 | 0.018 | 74.41 | 0.08 | 59.2 | 0.05 | 65.12 | 0.02 | 0.027 | 0.003 | 0.8139 | 0.0027 | 19926 | 38 | 1249 | 73 | 6.367 | 0.03 |  |  | 10.77 |  |  |  | 229.7 | 1 | 229.7 | 1 | 229.7 | 1 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2962 | 6.3 | 2962 | 6.3 | 2962 | 6.3 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 |  | 227.8 | 1 | 227.8 | 1 | 227.8 | 1 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2769.4 | 6 | [9 empty] | 228.3 | 1 | 0.7 | 0 | 169.3 | 0.9 | 23 |  | 3324.8 | 475 | 478 | 478 | 0.7 | 0.7 | 0.8 | 400 | 0.62 | 8.25 | 15.8 | [12 empty] | 263.3 | 0.2 | 180.58 | 0.05 | 120.82 | 0.06 | 59.77 | 0.06 | 243.42 | 0.22 | 103.44 | 0.06 | 115.06 | 0.07 | 11.62 | 0.08 | 76.92 | 0.04 | 62.46 | 0.11 | 45.26 | 0.03 |  |  | 77.53 | 0.02 | 66.74 | 0.1 | 45.64 | 0.01 | 21.09 | 0.1 | 520.11 | 0.55 | 40.57 | 0.02 | 35821 | 50 | 37060 | 46 | [22 empty] | 247.06 | 0.22 | 104.26 | 0.05 | 116.14 | 0.07 | 11.88 | 0.07 | 245.66 | 0.22 | 115.73 | 0.06 | 12.31 | 0.07 | 17.21 | 0.12 | [74 empty] | 58.28 | 0.05 | 60.34 | 0.08 | 59.66 | 0.11 | 60.21 | 0.06 | 59.05 | 0.07 | 59.54 | 0.04 | [18 empty] | 103.44 | 0.06 | [12 empty] | 104.11 | 0.06 |  |  | 94.75 | 0.07 | 94.76 | 0.06 | 94.91 | 0.05 | 94.89 | 0.07 | 94.78 | 0.08 | 94.81 | 0.07 | [12 empty] | 103.42 | 0.07 | [30 empty] | 94.83 | 0.09 | 95.13 | 0.09 | 74.61 | 0.08 | 74.62 | 0.07 | 74.46 | 0.06 | 74.72 | 0.09 | 74.71 | 0.09 | 74.71 | 0.1 | 74.59 | 0.08 | 86.86 | 0.11 | 82.29 | 0.11 | 80.52 | 0.1 | 84.64 | 0.15 | 84.1 | 0.09 | 86.45 | 0.11 | 77.54 | 0.08 | 82.79 | 0.1 | 92.09 | 0.05 | 79.24 | 0.15 | 75 | 0.07 | 74.99 | 0.07 | 82.59 | 0.18 | 74.96 | 0.06 | 74.9 | 0.06 | 74.97 | 0.06 | 76.04 | 0.09 | 74.81 | 0.05 | 74.76 | 0.06 | 74.83 | 0.05 | [84 empty] | C-55-CE-DM | 75.001 | 0.019 | 61.999 | 0.025 | 59.059 | 0.013 | 55.828 | 0.018 | 95 | 0.009 | 75.001 | 0.018 | 1158.9 | 2 | 1114.7 | 1.9 | 0.565 | 0.005 | -0.176 | 0.001 | 0.027 | 0.003 | 0.8139 | 0.0027 | 28.974 | 0.002 | 3326 | 9 | 363.1 | 5.7 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.77706 | 5289.4335 | 73.9897 | 196.218 | 834.9749 | 4454.4586 | 0.0095914 | 29.2733 | 58.2819 | 14.0999 | 13.1458 | 0.013922 | 38.1581 | 0.0087797 | 27.6079 | 0.0087157 | 23.6501 | 78.1828 | 64.3139 | 23.4606 | 30746.0385 | 25263.4643 | 2962.9 | 0.3289 | 29759.3052 | 24276.731 | 8.9475 | 0.22116 | -5.8127 | -19.9009 | 52.6309 | 30746.0385 | 20934.5464 | 1002.3497 | 8809.1423 | 30746.0385 | 100%
5 | C-MF-75629575-OE3J | 30N0011 | C-MF-75629575-OE3J | Fully open | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/12/2014 | 7:42:47 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 15.1 | 0 | 10435 | 28 | 9786 | 47 | -10648 | 115 | -223 | 126 |  | 940 |  | 7.3 |  | 111.71 | 0.1 | 93.61 | [31 empty] | -0.066727 | Factory charge, 3 turns, Econo fully open unsealed cab, 53.5% inlet 52% outlet Meriam, CT-SS--adjust code tester speed to match total static of run C-OE3J-SPWCT-SS | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo Fully open: with flow meter: new filter drier: with isolation ball valves: with code | 74.996 | 0.01 | 62.002 | 0.028 | 95 | 0.012 | 74.999 | 0.017 | 74.5 | 0.04 | 66.19 | 0.05 | 69.99 | 0.03 | 0.015 | 0.003 | 0.7771 | 0.0026 | 10435 | 28 | -10648 | 115 | 0.005 | 0.004 |  |  | 11.0805 |  |  |  | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2981.6 | 5.6 | 2981.6 | 5.6 | 2981.6 | 5.6 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2788 | 5.3 | [9 empty] | 228.3 | 0.9 | 0.8 | 0 | 170.6 | 0.8 | 23 |  | 3341 | 480 | 480 | 480 | 0.7 | 0.7 | 0.8 | 390 | 0.62 | 7.3 | 15.3 | [12 empty] | 266.79 | 0.19 | 184.19 | 0.05 | 121.86 | 0.05 | 62.33 | 0.07 | 246.5 | 0.22 | 102.57 | 0.05 | 116.05 | 0.06 | 13.47 | 0.07 | 80.82 | 0.06 | 63.15 | 0.52 | 47.87 | 0.04 |  |  | 81.44 | 0.03 | 72.95 | 0.1 | 48.26 | 0.02 | 24.69 | 0.11 | 535.73 | 0.52 | 40.29 | 0.02 | 37031 | 73 | 38260 | 72 | [22 empty] | 250.3 | 0.21 | 103.53 | 0.05 | 117.16 | 0.06 | 13.64 | 0.07 | 248.89 | 0.21 | 116.75 | 0.06 | 14.41 | 0.08 | 15.28 | 0.54 | [74 empty] | 65.8 | 0.14 | 67.49 | 0.06 | 67.14 | 0.14 | 67.12 | 0.08 | 67.06 | 0.16 | 66.41 | 0.1 | [32 empty] | 103.11 | 0.06 |  |  | 93.82 | 0.26 | 93.4 | 0.27 | 94.47 | 0.18 | 94.53 | 0.17 | 94.77 | 0.12 | 94.77 | 0.12 | [8 empty] | 94.7 | 0.12 |  |  | 102.33 | 0.07 | [30 empty] | 94.93 | 0.08 | 95.33 | 0.07 | 74.91 | 0.03 | 74.89 | 0.04 | 74.61 | 0.03 | 75.1 | 0.04 | 75.09 | 0.04 | 75.07 | 0.05 | 74.86 | 0.04 | 93.87 | 0.07 | 93.47 | 0.07 | 92.99 | 0.09 | 92.82 | 0.08 | 92.54 | 0.08 | 91.96 | 0.13 | 92.14 | 0.23 | 94.02 | 0.11 | 79.84 | 0.09 | 82.5 | 0.13 | 94.07 | 0.22 | 94.08 | 0.1 | 75.7 | 0.02 | 76.93 | 0.03 | 85.6 | 0.09 | 84.58 | 0.09 | 76.35 | 0.03 | 77.39 | 0.04 | 83.07 | 0.07 | 83.84 | 0.09 | [84 empty] | C-55-OER-DM | 74.996 | 0.01 | 62.002 | 0.028 | 66.16 | 0.014 | 62.017 | 0.022 | 95 | 0.012 | 74.999 | 0.017 | 1128.5 | 1.9 | 1090 | 1.9 | 0.413 | 0.004 | -0.028 | 0.001 | 0.015 | 0.003 | 0.7771 | 0.0026 | 29.462 | 0.002 | 3342 | 8 | 359.4 | 5.5 | 0.5922 | 661.0136 | 13.029 | 0.023 | 0.85871 | 5074.5882 | 52.8861 | 758.714 | 3228.5917 | 1845.9966 | 0.012051 | 34.3198 | 65.3013 | 14.0999 | 13.343 | 0.01392 | 38.1562 | 0.0087829 | 27.6101 | 0.010888 | 27.7509 | 87.7661 | 70.6927 | 27.5407 | 34401.1971 | 27359.9572 | 2982.6 | 0.29591 | 33355.0652 | 26313.8253 | 9.9806 | 0.23115 | -6.7791 | -22.4648 | 58.5473 | 34401.1971 | -714.4777 | 1066.8922 | 34048.7826 | 34401.1971 | 100%
5 | C-95-3+10-C | 30N0016 | C-95-3+10-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 10:38:37 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 6.1 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.1 |  | 5.5 |  | 230.3 | 0.9 | 15.4 | 0 | 20231 | 42 | 19565 | 69 | 1542 | 116 | 21774 | 123 |  | 945 |  | 12.17 | 5.9416 | 109.77 | 0.01 | 42.85 | [31 empty] | 6.3947 | Closed damper, +10% charge 95F Test, adjust code tester speed to match total--static of run C-95-FC3-EC-SPWCT-SS | R22 6.1 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75.002 | 0.018 | 62.002 | 0.04 | 94.995 | 0.008 | 74.999 | 0.014 | 74.56 | 0.06 | 58.77 | 0.04 | 65.12 | 0.02 | 0.018 | 0.003 | 1.1047 | 0.0033 | 20231 | 42 | 1542 | 116 | 6.394 | 0.039 |  |  | 11.1888 |  |  |  | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13.7 | 0 | 13.7 | 0 | 13.7 | 0 | 3036.9 | 4.9 | 3036.9 | 4.9 | 3036.9 | 4.9 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 0.9 | 227.7 | 0.9 | 227.7 | 0.9 | 13 | 0 | 13 | 0 | 13 | 0 | 2843.1 | 4.6 | [9 empty] | 228.2 | 0.9 | 0.7 | 0 | 168.9 | 0.8 | 23 |  | 3402 | 480 | 480 | 480 | 0.8 | 0.8 | 1 | 490 | 0.65 | 12.17 | 17.6 | [12 empty] | 273.51 | 0.15 | 161.58 | 0.08 | 123.66 | 0.04 | 37.92 | 0.08 | 252.77 | 0.24 | 101.43 | 0.05 | 117.81 | 0.07 | 16.38 | 0.08 | 78.8 | 0.04 | 51.81 | 0.04 | 46.46 | 0.03 |  |  | 79 | 0.04 | 51.97 | 0.05 | 46.59 | 0.03 | 5.39 | 0.04 | 563.47 | 0.45 | 39.93 | 0.01 | 38098 | 38 | 39351 | 34 | [22 empty] | 256.81 | 0.23 | 102.25 | 0.04 | 118.98 | 0.06 | 16.72 | 0.07 | 255.38 | 0.24 | 118.56 | 0.07 | 16.59 | 0.08 | 5.35 | 0.04 | [74 empty] | 57.76 | 0.04 | 60.16 | 0.05 | 59.36 | 0.1 | 59.96 | 0.04 | 58.79 | 0.07 | 59.11 | 0.04 | [32 empty] | 102.04 | 0.04 |  |  |  |  | 95.06 | 0.16 | 95.19 | 0.13 | 95.29 | 0.11 | 95.27 | 0.08 | 95.3 | 0.08 | [12 empty] | 101.98 | 0.04 | [30 empty] | 94.87 | 0.09 | 95.35 | 0.08 | 75.03 | 0.07 | 74.97 | 0.06 | 74.74 | 0.04 | 75.21 | 0.07 | 75.17 | 0.08 | 75.15 | 0.08 | 74.97 | 0.06 | 91.9 | 0.11 | 84 | 0.13 | 81.05 | 0.08 | 86.69 | 0.14 | 85.3 | 0.16 | 86.11 | 0.13 | 78.08 | 0.07 | 83.29 | 0.11 | 92.88 | 0.08 | 79.29 | 0.16 | 75.26 | 0.05 | 75.34 | 0.05 | 83.55 | 0.22 | 75.22 | 0.06 | 75.27 | 0.05 | 74.98 | 0.05 | 76.16 | 0.08 | 75.04 | 0.05 | 75.03 | 0.04 | 75.11 | 0.04 | [84 empty] | C-55-CE-DM | 75.002 | 0.018 | 62.002 | 0.04 | 58.665 | 0.012 | 55.579 | 0.017 | 94.995 | 0.008 | 74.999 | 0.014 | 1146.4 | 1.7 | 1103.2 | 1.6 | 0.569 | 0.004 | -0.177 | 0.001 | 0.018 | 0.003 | 1.1047 | 0.0033 | 28.985 | 0.001 | 3405 | 8 | 367 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.79616 | 5236.5206 | 73.7448 | 196.7737 | 837.3475 | 4399.1731 | 0.0096033 | 29.2964 | 57.8688 | 14.0998 | 13.1354 | 0.013921 | 38.1562 | 0.0087815 | 27.6101 | 0.0086636 | 23.4974 | 78.2241 | 64.3452 | 23.3032 | 31383.5159 | 25581.7505 | 3038 | 0.33039 | 30382.6361 | 24580.8707 | 8.9229 | 0.2098 | -5.9932 | -20.3552 | 52.4646 | 31383.5159 | 21536.0624 | 1016.6238 | 8830.8297 | 31383.5159 | 100%
5 | C-95-3+40-C | 30N0017 | C-95-3+40-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 5:37:43 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 7.7 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 5.5 |  | 230.3 | 1 | 15.5 | 0 | 19797 | 34 | 19133 | 74 | 910 | 104 | 20707 | 111 |  | 943 |  | 12.3 | 5.7785 | 109.8 | 0.01 | 49.29 | [31 empty] | 6.0441 | Closed Damper, +40% charge, 95F Test, adjust code tester speed to match total static--of run C-95-FC3-EC-SPWCT-SS | R22 7.7 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 74.998 | 0.012 | 62.001 | 0.04 | 95 | 0.006 | 75.002 | 0.015 | 74.53 | 0.06 | 59.05 | 0.04 | 65.34 | 0.02 | 0.019 | 0.003 | 1.1039 | 0.0038 | 19797 | 34 | 910 | 104 | 6.043 | 0.034 |  |  | 11.9183 |  |  |  | 229.7 | 1 | 229.7 | 1 | 229.7 | 1 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3058.4 | 6 | 3058.4 | 6 | 3058.4 | 6 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 1 | 227.7 | 1 | 227.7 | 1 | 13.1 | 0 | 13.1 | 0 | 13.1 | 0 | 2864.4 | 5.5 | [9 empty] | 228.2 | 1 | 0.7 | 0 | 168.9 | 0.9 | 23 |  | 3423.1 | 480 | 480 | 480 | 0.8 | 0.8 | 1 | 490 | 0.63 | 12.3 | 17.7 | [12 empty] | 281.17 | 0.18 | 140.7 | 0.08 | 125.74 | 0.05 | 14.97 | 0.07 | 260.14 | 0.18 | 99.68 | 0.04 | 119.92 | 0.05 | 20.25 | 0.06 | 79.73 | 0.04 | 52.29 | 0.04 | 47.04 | 0.03 |  |  | 79.91 | 0.05 | 52.03 | 0.05 | 47.15 | 0.03 | 4.88 | 0.04 | 597.61 | 0.49 | 39.38 | 0.01 | 40832 | 41 | 42084 | 37 | [22 empty] | 264.51 | 0.21 | 100.58 | 0.03 | 121.16 | 0.06 | 20.57 | 0.06 | 262.98 | 0.19 | 120.73 | 0.05 | 20.31 | 0.06 | 5.25 | 0.03 | [74 empty] | 58.1 | 0.05 | 60.43 | 0.05 | 59.64 | 0.12 | 60.22 | 0.04 | 59.1 | 0.09 | 59.39 | 0.04 | [32 empty] | 100.42 | 0.04 |  |  |  |  | 95.03 | 0.08 | 95.21 | 0.07 | 95.25 | 0.07 | 95.24 | 0.07 | 95.28 | 0.07 | [12 empty] | 100.42 | 0.03 | [30 empty] | 94.84 | 0.07 | 95.3 | 0.07 | 74.98 | 0.05 | 74.94 | 0.04 | 74.71 | 0.03 | 75.13 | 0.06 | 75.1 | 0.06 | 75.09 | 0.05 | 74.92 | 0.04 | 91.96 | 0.09 | 84.4 | 0.11 | 80.93 | 0.09 | 86.66 | 0.14 | 85.38 | 0.14 | 86.12 | 0.11 | 78.07 | 0.06 | 83.19 | 0.09 | 93.06 | 0.05 | 79.27 | 0.15 | 75.23 | 0.04 | 75.3 | 0.04 | 83.63 | 0.21 | 75.2 | 0.05 | 75.28 | 0.05 | 74.99 | 0.05 | 76.2 | 0.08 | 75.05 | 0.04 | 75.03 | 0.04 | 75.11 | 0.04 | [84 empty] | C-55-CE-DM | 74.998 | 0.012 | 62.001 | 0.04 | 58.981 | 0.012 | 55.906 | 0.02 | 95 | 0.006 | 75.002 | 0.015 | 1146.6 | 1.9 | 1102 | 1.9 | 0.568 | 0.005 | -0.177 | 0.001 | 0.019 | 0.003 | 1.1039 | 0.0038 | 28.968 | 0.002 | 3426 | 9 | 366.8 | 5.3 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.79659 | 5233.8818 | 73.5352 | 196.7747 | 837.3434 | 4396.5384 | 0.0096042 | 29.2972 | 58.1844 | 14.0999 | 13.1444 | 0.013923 | 38.1591 | 0.0087818 | 27.6094 | 0.0087798 | 23.7008 | 78.2231 | 64.3462 | 23.5065 | 30307.887 | 25171.2819 | 3059.2 | 0.3445 | 29306.9741 | 24170.369 | 8.5543 | 0.20763 | -5.7907 | -20.0387 | 52.9335 | 30307.887 | 20457.3196 | 1016.8724 | 8833.695 | 30307.887 | 100%
5 | C-95-3-10-C | 30N0018 | C-95-3+10-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 10:38:37 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 4.95 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.1 |  | 5.5 |  | 230.3 | 1 | 14.9 | 0 | 19376 | 34 | 18738 | 62 | 1101 | 97 | 20478 | 101 |  | 944 |  | 12.8 | 5.9037 | 112.55 | 0.01 | 41.7 | [31 empty] | 6.2395 | Closed Damper, -10% charge, 95F Test, adjust code tester speed to match total--static of run C-95-FC3-EC-SPWCT-SS | R22 4.95 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75.002 | 0.011 | 62.007 | 0.044 | 94.996 | 0.008 | 74.992 | 0.012 | 74.59 | 0.05 | 59.64 | 0.05 | 65.67 | 0.02 | 0.035 | 0.003 | 1.1374 | 0.0042 | 19376 | 34 | 1101 | 97 | 6.239 | 0.035 |  |  | 10.7023 |  |  |  | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 13.2 | 0 | 13.2 | 0 | 13.2 | 0 | 2912.7 | 5.6 | 2912.7 | 5.6 | 2912.7 | 5.6 | 230 | 1 | 230 | 1 | 230 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 1 | 227.8 | 1 | 227.8 | 1 | 12.5 | 0 | 12.5 | 0 | 12.5 | 0 | 2720.9 | 5 | [9 empty] | 228.3 | 1 | 0.7 | 0 | 168.8 | 0.9 | 23 |  | 3281.2 | 480 | 480 | 480 | 0.8 | 0.9 | 1 | 510 | 0.65 | 12.8 | 17.9 | [12 empty] | 260.05 | 0.13 | 183.21 | 0.04 | 119.89 | 0.04 | 63.31 | 0.05 | 240.38 | 0.18 | 104.21 | 0.05 | 114.15 | 0.05 | 9.94 | 0.06 | 76.16 | 0.05 | 66.29 | 0.06 | 44.76 | 0.03 |  |  | 76.01 | 0.04 | 69.26 | 0.07 | 44.66 | 0.03 | 24.6 | 0.07 | 507.13 | 0.46 | 40.81 | 0.02 | 35125 | 42 | 36383 | 37 | [22 empty] | 243.88 | 0.19 | 104.72 | 0.05 | 115.2 | 0.06 | 10.47 | 0.07 | 242.53 | 0.19 | 114.79 | 0.06 | 10.12 | 0.08 | 21.53 | 0.07 | [74 empty] | 58.68 | 0.05 | 60.83 | 0.07 | 60.05 | 0.07 | 60.69 | 0.06 | 59.47 | 0.06 | 59.96 | 0.05 | [32 empty] | 104.59 | 0.04 |  |  |  |  | 95.09 | 0.07 | 95.22 | 0.06 | 95.26 | 0.08 | 96.07 | 0.08 | 96.09 | 0.07 | [12 empty] | 104.67 | 0.05 | [30 empty] | 94.7 | 0.09 | 95.18 | 0.09 | 74.89 | 0.08 | 74.88 | 0.06 | 74.72 | 0.04 | 75 | 0.09 | 74.98 | 0.1 | 75 | 0.09 | 74.87 | 0.07 | 91.72 | 0.09 | 83.9 | 0.12 | 81.17 | 0.11 | 86.97 | 0.15 | 85.25 | 0.15 | 85.91 | 0.13 | 78.19 | 0.06 | 83.6 | 0.11 | 92.99 | 0.06 | 79.49 | 0.15 | 75.45 | 0.05 | 75.49 | 0.04 | 83.76 | 0.2 | 75.41 | 0.04 | 75.37 | 0.04 | 74.85 | 0.06 | 76.03 | 0.09 | 74.94 | 0.06 | 75.01 | 0.04 | 75.1 | 0.03 | [84 empty] | C-55-CE-DM | 75.002 | 0.011 | 62.007 | 0.044 | 59.544 | 0.018 | 56.077 | 0.03 | 94.996 | 0.008 | 74.992 | 0.012 | 1164.8 | 2.1 | 1118 | 2.1 | 0.568 | 0.004 | -0.18 | 0.001 | 0.035 | 0.003 | 1.1374 | 0.0042 | 28.944 | 0.001 | 3282 | 8 | 368.5 | 5.3 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.78667 | 5311.2975 | 74.6028 | 198.4341 | 844.4147 | 4466.8828 | 0.0096004 | 29.2887 | 58.7573 | 14.0998 | 13.1584 | 0.013915 | 38.1495 | 0.0087848 | 27.6137 | 0.008747 | 23.8024 | 78.2057 | 64.3346 | 23.6105 | 30158.4402 | 24791.0171 | 2913.5 | 0.32972 | 29155.3691 | 23787.946 | 8.8834 | 0.23837 | -5.6782 | -19.4483 | 52.6705 | 30158.4402 | 20242.8511 | 1019.0041 | 8896.585 | 30158.4402 | 100%
5 | C-95-3-40-C | 30N0019 | C-95-3+40-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 5:37:43 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 3.3 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 5.5 |  | 230.3 | 1 | 14.1 | 0 | 14400 | 27 | 13831 | 58 | -1373 | 72 | 13026 | 73 |  | 942 |  | 16.9 |  | 114.13 | 0.01 | 52.13 | [31 empty] | 4.1763 | Closed Damper, -40% charge, 95F Test, adjust code tester speed--to match total static of run C-95-FC3-EC-SPWCT-SS | R22 3.3 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 74.998 | 0.017 | 61.999 | 0.039 | 95.001 | 0.007 | 75.002 | 0.015 | 74.58 | 0.05 | 64.15 | 0.04 | 68.42 | 0.01 | 0.139 | 0.002 | 1.2959 | 0.0027 | 14400 | 27 | -1373 | 72 | 4.177 | 0.026 |  |  | 8.7252 |  |  |  | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 12.4 | 0 | 12.4 | 0 | 12.4 | 0 | 2739.1 | 6 | 2739.1 | 6 | 2739.1 | 6 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.9 | 1 | 227.9 | 1 | 227.9 | 1 | 11.7 | 0 | 11.7 | 0 | 11.7 | 0 | 2549.2 | 5.4 | [9 empty] | 228.4 | 1 | 0.7 | 0 | 169.4 | 0.9 | 23 |  | 3120.2 | 478 | 478 | 479 | 1 | 1 | 1.2 | 600 | 0.64 | 16.9 | 19.9 | [12 empty] | 239.37 | 0.14 | 196.34 | 0.09 | 113.87 | 0.04 | 82.47 | 0.09 | 222.46 | 0.24 | 108.2 | 0.06 | 108.65 | 0.08 | 0.45 | 0.09 | 61.14 | 0.06 | 70.72 | 0.03 | 34.41 | 0.04 |  |  | 60.93 | 0.05 | 73.73 | 0.03 | 34.25 | 0.04 | 39.48 | 0.05 | 395.66 | 2.38 | 42.08 | 0.02 | 27214 | 175 | 28508 | 174 | [22 empty] | 225.51 | 0.16 | 107.84 | 0.03 | 109.61 | 0.05 | 1.77 | 0.05 | 224.31 | 0.24 | 109.23 | 0.07 | 0.43 | 0.07 | 36.3 | 0.05 | [74 empty] | 63.19 | 0.06 | 65.67 | 0.07 | 64.7 | 0.07 | 65.53 | 0.06 | 63.77 | 0.05 | 64.88 | 0.05 | [32 empty] | 109 | 0.04 |  |  |  |  | 94.63 | 0.11 | 94.8 | 0.11 | 94.87 | 0.09 | 94.92 | 0.08 | 94.95 | 0.08 | [12 empty] | 108.8 | 0.03 | [30 empty] | 94.64 | 0.07 | 95.01 | 0.07 | 74.78 | 0.07 | 74.81 | 0.05 | 74.67 | 0.04 | 74.85 | 0.09 | 74.84 | 0.09 | 74.89 | 0.08 | 74.79 | 0.06 | 87.53 | 0.77 | 83.16 | 0.19 | 80.79 | 0.12 | 86.54 | 0.19 | 84.81 | 0.14 | 85.46 | 0.17 | 78.34 | 0.08 | 83.59 | 0.12 | 92.9 | 0.06 | 78.28 | 0.37 | 75.52 | 0.05 | 75.54 | 0.05 | 84.57 | 0.28 | 75.4 | 0.04 | 75.37 | 0.04 | 74.87 | 0.08 | 76.08 | 0.11 | 74.93 | 0.08 | 74.98 | 0.05 | 75.1 | 0.05 | [84 empty] | C-55-CE-DM | 74.998 | 0.017 | 61.999 | 0.039 | 64.144 | 0.013 | 58.517 | 0.029 | 95.001 | 0.007 | 75.002 | 0.015 | 1243.9 | 1.3 | 1193.1 | 1.3 | 0.541 | 0.003 | -0.195 | 0.001 | 0.139 | 0.002 | 1.2959 | 0.0027 | 29.084 | 0.002 | 3119 | 9 | 378.6 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.76578 | 5620.9013 | 75.8297 | 206.5381 | 878.8887 | 4742.0125 | 0.0095844 | 29.2577 | 63.3782 | 14.1 | 13.2779 | 0.013922 | 38.159 | 0.0087804 | 27.6079 | 0.0091272 | 25.3385 | 78.1503 | 64.2927 | 25.1516 | 23080.0246 | 19927.8442 | 2740.4 | 0.40524 | 22046.6695 | 18894.4891 | 7.0685 | 0.39476 | -4.1061 | -14.7721 | 53.7434 | 23080.0246 | 12756.2913 | 1050.4958 | 9273.2374 | 23080.0246 | 100%
5 | C-95-3-FC-C | 30N0020 | C-95-3-FC-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/17/2014 | 23:01:06 | 10 Ton | 0:30:08 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.8 | 15.1 | 0 | 19903 | 39 | 19222 | 57 | 1384 | 112 | 21288 | 117 |  | 944 |  | 12.6 | 5.9661 | 111.39 | 0.05 | 40.85 | [31 empty] | 6.3813 | Closed damper, 5.5 lbs factory charge 95F test, adjust code tester speed to match--total static of run C -95-FC3-EC-SPWCT-SS | R22 5.5 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 74.992 | 0.011 | 62.005 | 0.044 | 94.996 | 0.014 | 75 | 0.014 | 74.55 | 0.04 | 59.18 | 0.03 | 65.48 | 0.03 | 0.03 | 0.003 | 1.1258 | 0.0036 | 19903 | 39 | 1384 | 112 | 6.383 | 0.037 |  |  | 10.7902 |  |  |  | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2965.5 | 4.4 | 2965.5 | 4.4 | 2965.5 | 4.4 | 230 | 0.8 | 230 | 0.8 | 230 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 0.8 | 227.8 | 0.8 | 227.8 | 0.8 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2772.5 | 4 | [9 empty] | 228.3 | 0.8 | 0.7 | 0 | 169.3 | 0.8 | 23 |  | 3334.4 | 489 | 490 | 491 | 0.8 | 0.8 | 1 | 490 | 0.63 | 12.6 | 17.9 | [12 empty] | 264.19 | 0.15 | 178.57 | 0.07 | 121.08 | 0.04 | 57.49 | 0.07 | 244.25 | 0.21 | 103.13 | 0.02 | 115.32 | 0.06 | 12.19 | 0.06 | 77.42 | 0.05 | 60.24 | 0.29 | 45.61 | 0.03 |  |  | 77.72 | 0.05 | 64.91 | 0.18 | 45.8 | 0.03 | 19.11 | 0.17 | 525.32 | 0.43 | 40.47 | 0.01 | 35996 | 51 | 37255 | 49 | [22 empty] | 247.9 | 0.25 | 103.82 | 0.03 | 116.4 | 0.07 | 12.59 | 0.07 | 246.44 | 0.21 | 115.97 | 0.06 | 12.37 | 0.07 | 14.64 | 0.28 | [74 empty] | 58.19 | 0.04 | 60.38 | 0.05 | 59.64 | 0.07 | 60.25 | 0.04 | 59.06 | 0.05 | 59.53 | 0.04 | [32 empty] | 103.54 | 0.04 |  |  |  |  | 95.02 | 0.08 | 95.17 | 0.06 | 95.12 | 0.06 | 95.16 | 0.05 | 95.2 | 0.05 | [12 empty] | 103.61 | 0.04 | [30 empty] | 94.67 | 0.07 | 95.14 | 0.07 | 74.83 | 0.04 | 74.84 | 0.03 | 74.66 | 0.03 | 74.96 | 0.04 | 74.93 | 0.04 | 74.97 | 0.04 | 74.82 | 0.04 | 86.79 | 0.09 | 83.29 | 0.12 | 80.63 | 0.07 | 86.33 | 0.14 | 84.49 | 0.08 | 86.11 | 0.12 | 78.12 | 0.06 | 83.37 | 0.1 | 93.01 | 0.05 | 79.15 | 0.16 | 75.38 | 0.04 | 75.45 | 0.04 | 83.12 | 0.2 | 75.38 | 0.04 | 75.41 | 0.03 | 74.92 | 0.05 | 75.98 | 0.08 | 75.02 | 0.04 | 75.09 | 0.04 | 75.18 | 0.04 | [84 empty] | C-55-CE-DM | 74.992 | 0.011 | 62.005 | 0.044 | 59.083 | 0.017 | 55.793 | 0.022 | 94.996 | 0.014 | 75 | 0.014 | 1156 | 1.9 | 1115 | 1.8 | 0.571 | 0.004 | -0.18 | 0.001 | 0.03 | 0.003 | 1.1258 | 0.0036 | 29.07 | 0.001 | 3336 | 7 | 369.6 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.79437 | 5276.0352 | 74.7956 | 198.4345 | 844.4129 | 4431.6223 | 0.0096078 | 29.3 | 58.2886 | 14.0998 | 13.1462 | 0.013922 | 38.1572 | 0.0087858 | 27.6124 | 0.0086896 | 23.6275 | 78.2187 | 64.3498 | 23.4338 | 30950.3169 | 25236.4008 | 2966.4 | 0.32712 | 29944.1495 | 24230.2334 | 8.9761 | 0.22537 | -5.8662 | -19.9301 | 52.4901 | 30950.3169 | 21024.0815 | 1022.0428 | 8904.1926 | 30950.3169 | 100%
5 | C-95-3+10-1 | 30N0039 | C-95-3+10-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 11:54:44 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 6.1 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.1 |  | 5.5 |  | 230.3 | 1 | 15.5 | 0 | 18714 | 36 | 18080 | 63 | -1097 | 109 | 17616 | 120 |  | 945 |  | 13.3 | 5.4592 | 109.98 | 0.01 | 54.29 | [31 empty] | 5.1389 | 1 Finger Open, +10% charge 95F Test, adjust code tester speed to match total--static of run C-95-FC3-1F-SPWCT-SS | R22 6.1 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 74.996 | 0.016 | 61.992 | 0.041 | 95 | 0.008 | 75.003 | 0.017 | 74.64 | 0.05 | 60.27 | 0.03 | 65.98 | 0.02 | 0.032 | 0.003 | 1.1538 | 0.0036 | 18714 | 36 | -1097 | 109 | 5.139 | 0.037 |  |  | 11.2407 |  |  |  | 229.7 | 1 | 229.7 | 1 | 229.7 | 1 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3056.6 | 5.9 | 3056.6 | 5.9 | 3056.6 | 5.9 | 230 | 1 | 230 | 1 | 230 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 1 | 227.7 | 1 | 227.7 | 1 | 13.1 | 0 | 13.1 | 0 | 13.1 | 0 | 2862.5 | 5.5 | [9 empty] | 228.2 | 1 | 0.7 | 0 | 168.8 | 0.9 | 23 |  | 3424.5 | 480 | 480 | 480 | 0.9 | 0.9 | 1 | 510 | 0.65 | 13.3 | 18.2 | [12 empty] | 275.74 | 0.18 | 167.51 | 0.06 | 124.27 | 0.05 | 43.24 | 0.07 | 254.7 | 0.28 | 101.63 | 0.04 | 118.37 | 0.08 | 16.74 | 0.08 | 80.58 | 0.05 | 53.55 | 0.05 | 47.58 | 0.03 |  |  | 81.28 | 0.05 | 53.97 | 0.06 | 48.01 | 0.03 | 5.95 | 0.05 | 568.64 | 0.47 | 39.99 | 0.01 | 38533 | 40 | 39795 | 35 | [22 empty] | 258.81 | 0.27 | 102.51 | 0.04 | 119.55 | 0.08 | 17.03 | 0.08 | 257.4 | 0.28 | 119.14 | 0.08 | 17.02 | 0.08 | 5.97 | 0.04 | [74 empty] | 59.47 | 0.06 | 61.19 | 0.05 | 60.71 | 0.09 | 61.02 | 0.05 | 60.36 | 0.08 | 60.39 | 0.05 | [32 empty] | 101.98 | 0.04 |  |  |  |  | 95.16 | 0.08 | 95.27 | 0.07 | 95.34 | 0.07 | 96.18 | 0.07 | 96.18 | 0.07 | [12 empty] | 102.12 | 0.05 | [30 empty] | 94.68 | 0.07 | 95.18 | 0.07 | 74.88 | 0.06 | 74.86 | 0.05 | 74.68 | 0.03 | 74.98 | 0.06 | 74.96 | 0.07 | 75 | 0.07 | 74.85 | 0.05 | 93.22 | 0.04 | 93.33 | 0.05 | 92.22 | 0.08 | 89.16 | 0.11 | 89.17 | 0.13 | 90.94 | 0.1 | 88.52 | 0.13 | 87.49 | 0.09 | 92.22 | 0.07 | 76.22 | 0.08 | 76.54 | 0.11 | 75.78 | 0.06 | 81.73 | 0.16 | 75.82 | 0.05 | 75.48 | 0.04 | 75.72 | 0.05 | 76.83 | 0.12 | 75.03 | 0.05 | 75.05 | 0.04 | 75.13 | 0.04 | [84 empty] | C-55-1ER-DM | 74.996 | 0.016 | 61.992 | 0.041 | 60.12 | 0.01 | 56.953 | 0.022 | 95 | 0.008 | 75.003 | 0.017 | 1172.8 | 1.9 | 1125.9 | 1.8 | 0.543 | 0.004 | -0.142 | 0.001 | 0.032 | 0.003 | 1.1538 | 0.0036 | 28.983 | 0.002 | 3428 | 8 | 370.2 | 5.2 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.79427 | 5340.635 | 71.8232 | 310.1513 | 1319.7989 | 4020.8361 | 0.010048 | 30.2118 | 59.3257 | 14.0999 | 13.176 | 0.013923 | 38.16 | 0.0087763 | 27.6029 | 0.0091301 | 24.3595 | 79.9743 | 65.5696 | 24.1657 | 32290.3237 | 26466.308 | 3057.8 | 0.3232 | 31271.9637 | 25447.948 | 9.1225 | 0.20722 | -6.0462 | -20.6485 | 53.9286 | 32290.3237 | 17321.8177 | 1035.2574 | 13933.2487 | 32290.3237 | 100%
5 | C-95-3+20-1 | 30N0040 | C-95-3+20-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 8:44:20 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 6.6 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.6 |  | 5.5 |  | 230.3 | 1 | 15.7 | 0 | 18437 | 38 | 17795 | 65 | -1220 | 117 | 17216 | 116 |  | 944 |  | 12.5 | 5.3194 | 109.93 | 0.01 | 57.24 | [31 empty] | 4.9671 | 1 Finger Open, +20% charge 95F Test, adjust code tester speed to match total--static of run C-95-FC3-1F-SPWCT-SS | R22 6.6 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 74.998 | 0.02 | 62 | 0.042 | 94.999 | 0.009 | 75 | 0.019 | 74.62 | 0.06 | 60.3 | 0.03 | 66.08 | 0.01 | 0.017 | 0.003 | 1.1261 | 0.0035 | 18437 | 38 | -1220 | 117 | 4.967 | 0.035 |  |  | 11.6168 |  |  |  | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 14 | 0 | 14 | 0 | 14 | 0 | 3097 | 5.2 | 3097 | 5.2 | 3097 | 5.2 | 230 | 1 | 230 | 1 | 230 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 1 | 227.7 | 1 | 227.7 | 1 | 13.3 | 0 | 13.3 | 0 | 13.3 | 0 | 2902.5 | 4.8 | [9 empty] | 228.2 | 1 | 0.7 | 0 | 168.9 | 0.9 | 23 |  | 3462.5 | 482 | 483 | 483 | 0.8 | 0.8 | 1 | 490 | 0.65 | 12.5 | 17.9 | [12 empty] | 281.13 | 0.16 | 156.14 | 0.1 | 125.72 | 0.04 | 30.42 | 0.09 | 259.86 | 0.18 | 100.58 | 0.04 | 119.84 | 0.05 | 19.26 | 0.06 | 80.99 | 0.04 | 53.44 | 0.03 | 47.83 | 0.03 |  |  | 81.77 | 0.04 | 53.4 | 0.05 | 48.31 | 0.02 | 5.08 | 0.04 | 590.89 | 0.44 | 39.66 | 0.01 | 40264 | 37 | 41521 | 32 | [22 empty] | 264.18 | 0.2 | 101.52 | 0.04 | 121.07 | 0.06 | 19.55 | 0.07 | 262.76 | 0.18 | 120.67 | 0.05 | 19.52 | 0.08 | 5.61 | 0.04 | [74 empty] | 59.53 | 0.08 | 61.5 | 0.04 | 60.94 | 0.13 | 61.25 | 0.04 | 60.52 | 0.12 | 60.49 | 0.06 | [32 empty] | 101.21 | 0.04 |  |  |  |  | 95.09 | 0.1 | 95.3 | 0.08 | 95.36 | 0.07 | 95.41 | 0.06 | 95.42 | 0.06 | [12 empty] | 101.15 | 0.06 | [30 empty] | 94.91 | 0.06 | 95.4 | 0.07 | 75.08 | 0.04 | 75.02 | 0.03 | 74.75 | 0.04 | 75.27 | 0.04 | 75.23 | 0.04 | 75.24 | 0.04 | 75 | 0.04 | 93.56 | 0.04 | 93.43 | 0.06 | 92.43 | 0.08 | 89.58 | 0.1 | 89.3 | 0.15 | 90.49 | 0.11 | 88.4 | 0.14 | 87.6 | 0.09 | 91.98 | 0.07 | 75.88 | 0.06 | 76.59 | 0.1 | 75.75 | 0.05 | 82.48 | 0.15 | 75.92 | 0.04 | 75.5 | 0.03 | 76.19 | 0.04 | 77.18 | 0.14 | 75.23 | 0.03 | 75.13 | 0.03 | 75.26 | 0.04 | [84 empty] | C-55-1ER-DM | 74.998 | 0.02 | 62 | 0.042 | 60.157 | 0.007 | 57.019 | 0.018 | 94.999 | 0.009 | 75 | 0.019 | 1158.9 | 1.8 | 1111.9 | 1.7 | 0.541 | 0.005 | -0.137 | 0.001 | 0.017 | 0.003 | 1.1261 | 0.0035 | 28.973 | 0.001 | 3466 | 8 | 368.1 | 5.3 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.80132 | 5276.866 | 70.6689 | 304.6415 | 1296.3568 | 3980.5091 | 0.010044 | 30.2001 | 59.3557 | 14.0999 | 13.1771 | 0.013921 | 38.1571 | 0.0087811 | 27.6087 | 0.0091608 | 24.402 | 79.9462 | 65.554 | 24.2064 | 31627.7662 | 26076.8324 | 3097.9 | 0.3343 | 30612.6338 | 25061.6999 | 8.8323 | 0.20457 | -5.9937 | -20.5905 | 54.06 | 31627.7662 | 16921.1453 | 1032.034 | 13674.5869 | 31627.7662 | 100%
5 | C-95-3+20-C | 30N0041 | C-95-3+20-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 9:50:45 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 6.6 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.6 |  | 5.5 |  | 230.3 | 0.8 | 15.5 | 0 | 20098 | 40 | 19432 | 66 | 1337 | 122 | 21436 | 128 |  | 945 |  | 12.17 | 5.8578 | 109.77 | 0.01 | 45.83 | [31 empty] | 6.2477 | Closed damper, +20% charge 95F Test, adjust code tester speed to match total--static of run C-95-FC3-EC-SPWCT-SS | R22 6.6 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75.001 | 0.012 | 62.001 | 0.044 | 95 | 0.009 | 74.998 | 0.015 | 74.58 | 0.06 | 58.87 | 0.04 | 65.22 | 0.02 | 0.019 | 0.003 | 1.1035 | 0.0033 | 20098 | 40 | 1337 | 122 | 6.248 | 0.039 |  |  | 11.5331 |  |  |  | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3062.9 | 5.2 | 3062.9 | 5.2 | 3062.9 | 5.2 | 230 | 0.8 | 230 | 0.8 | 230 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 0.8 | 227.7 | 0.8 | 227.7 | 0.8 | 13.1 | 0 | 13.1 | 0 | 13.1 | 0 | 2868.8 | 5 | [9 empty] | 228.2 | 0.8 | 0.7 | 0 | 168.9 | 0.7 | 23 |  | 3427.4 | 482 | 482 | 482 | 0.8 | 0.8 | 1 | 490 | 0.64 | 12.17 | 17.7 | [12 empty] | 277.96 | 0.16 | 151.43 | 0.1 | 124.87 | 0.04 | 26.56 | 0.1 | 257.01 | 0.24 | 100.59 | 0.05 | 119.03 | 0.07 | 18.44 | 0.08 | 79.35 | 0.05 | 52.02 | 0.04 | 46.8 | 0.03 |  |  | 79.57 | 0.06 | 52.01 | 0.06 | 46.94 | 0.04 | 5.07 | 0.05 | 582.27 | 0.48 | 39.67 | 0.01 | 39570 | 41 | 40821 | 37 | [22 empty] | 261.25 | 0.22 | 101.43 | 0.04 | 120.24 | 0.06 | 18.82 | 0.07 | 259.84 | 0.23 | 119.84 | 0.07 | 18.69 | 0.17 | 5.22 | 0.04 | [74 empty] | 57.86 | 0.05 | 60.3 | 0.06 | 59.5 | 0.12 | 60.08 | 0.04 | 58.93 | 0.09 | 59.21 | 0.04 | [32 empty] | 101.29 | 0.04 |  |  |  |  | 95.08 | 0.14 | 95.25 | 0.13 | 95.33 | 0.12 | 95.31 | 0.11 | 95.33 | 0.11 | [12 empty] | 101.15 | 0.15 | [30 empty] | 94.93 | 0.06 | 95.42 | 0.08 | 75.08 | 0.04 | 75.01 | 0.03 | 74.75 | 0.03 | 75.27 | 0.04 | 75.24 | 0.04 | 75.22 | 0.04 | 75.01 | 0.04 | 92 | 0.11 | 84.05 | 0.11 | 81.07 | 0.08 | 86.65 | 0.14 | 85.35 | 0.15 | 86.07 | 0.12 | 78.01 | 0.07 | 83.16 | 0.1 | 92.81 | 0.07 | 79.2 | 0.15 | 75.2 | 0.05 | 75.27 | 0.05 | 83.51 | 0.2 | 75.15 | 0.05 | 75.19 | 0.04 | 75.03 | 0.04 | 76.22 | 0.08 | 75.08 | 0.03 | 75.05 | 0.03 | 75.12 | 0.03 | [84 empty] | C-55-CE-DM | 75.001 | 0.012 | 62.001 | 0.044 | 58.754 | 0.012 | 55.68 | 0.022 | 95 | 0.009 | 74.998 | 0.015 | 1146 | 1.7 | 1102.2 | 1.6 | 0.568 | 0.005 | -0.177 | 0.002 | 0.019 | 0.003 | 1.1035 | 0.0033 | 28.976 | 0.001 | 3431 | 8 | 366.7 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.79631 | 5233.6772 | 73.5485 | 196.7745 | 837.3442 | 4396.333 | 0.0096031 | 29.2966 | 57.9577 | 14.0999 | 13.138 | 0.013919 | 38.1552 | 0.008781 | 27.6093 | 0.0087014 | 23.5602 | 78.2258 | 64.3454 | 23.366 | 31038.9243 | 25458.3872 | 3064.3 | 0.33695 | 30038.3983 | 24457.8612 | 8.755 | 0.2084 | -5.9306 | -20.2681 | 52.6218 | 31038.9243 | 21192.0875 | 1016.3343 | 8830.5025 | 31038.9243 | 100%
5 | C-95-3+30-1 | 30N0042 | C-95-3+30-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 7:39:56 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 7.2 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.2 |  | 5.5 |  | 230.3 | 1 | 15.7 | 0 | 18262 | 41 | 17642 | 71 | -1459 | 113 | 16802 | 117 |  | 944 |  | 12.5 | 5.2704 | 109.93 | 0.01 | 59.32 | [31 empty] | 4.8491 | 1 Finger Open, +30% charge 95F Test, adjust code tester speed to match total static--of run C-95-FC3-1F-SPWCT-SS | R22 7.2 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75 | 0.016 | 61.997 | 0.039 | 95.004 | 0.008 | 75.006 | 0.023 | 74.56 | 0.05 | 60.35 | 0.03 | 66.15 | 0.02 | 0.015 | 0.004 | 1.1261 | 0.0038 | 18262 | 41 | -1459 | 113 | 4.849 | 0.035 |  |  | 11.9201 |  |  |  | 229.7 | 1 | 229.7 | 1 | 229.7 | 1 | 14 | 0 | 14 | 0 | 14 | 0 | 3095.6 | 5.4 | 3095.6 | 5.4 | 3095.6 | 5.4 | 230 | 1 | 230 | 1 | 230 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 1 | 227.7 | 1 | 227.7 | 1 | 13.3 | 0 | 13.3 | 0 | 13.3 | 0 | 2901 | 5 | [9 empty] | 228.2 | 1 | 0.7 | 0 | 168.9 | 0.9 | 23 |  | 3461 | 480 | 480 | 480 | 0.8 | 0.8 | 1 | 490 | 0.65 | 12.5 | 17.8 | [12 empty] | 284.07 | 0.17 | 147.56 | 0.09 | 126.51 | 0.04 | 21.05 | 0.09 | 262.76 | 0.18 | 99.89 | 0.03 | 120.67 | 0.05 | 20.77 | 0.06 | 81.33 | 0.05 | 53.53 | 0.03 | 48.04 | 0.03 |  |  | 81.95 | 0.04 | 53.43 | 0.05 | 48.42 | 0.03 | 5.01 | 0.04 | 603.83 | 0.49 | 39.44 | 0.01 | 41303 | 41 | 42559 | 37 | [22 empty] | 267.21 | 0.2 | 100.89 | 0.03 | 121.91 | 0.05 | 21.03 | 0.06 | 265.76 | 0.19 | 121.51 | 0.05 | 20.92 | 0.07 | 5.49 | 0.03 | [74 empty] | 59.62 | 0.1 | 61.54 | 0.04 | 60.96 | 0.18 | 61.31 | 0.04 | 60.58 | 0.16 | 60.6 | 0.07 | [32 empty] | 100.58 | 0.04 |  |  |  |  | 94.81 | 0.15 | 95.06 | 0.14 | 95.03 | 0.13 | 95.14 | 0.11 | 95.17 | 0.11 | [12 empty] | 100.59 | 0.05 | [30 empty] | 94.74 | 0.07 | 95.2 | 0.08 | 74.91 | 0.04 | 74.89 | 0.03 | 74.7 | 0.03 | 75.04 | 0.05 | 75.01 | 0.06 | 75.02 | 0.04 | 74.85 | 0.03 | 93.34 | 0.09 | 93.21 | 0.11 | 92.31 | 0.11 | 89.51 | 0.12 | 89.16 | 0.13 | 90.59 | 0.13 | 88.54 | 0.15 | 87.77 | 0.09 | 92.13 | 0.08 | 76.06 | 0.07 | 76.77 | 0.1 | 75.87 | 0.06 | 82.79 | 0.16 | 76.07 | 0.05 | 75.64 | 0.04 | 76.17 | 0.04 | 77.22 | 0.14 | 75.22 | 0.03 | 75.14 | 0.03 | 75.3 | 0.03 | [84 empty] | C-55-1ER-DM | 75 | 0.016 | 61.997 | 0.039 | 60.289 | 0.012 | 57.139 | 0.017 | 95.004 | 0.008 | 75.006 | 0.023 | 1159.2 | 2 | 1111.6 | 1.9 | 0.54 | 0.006 | -0.135 | 0.001 | 0.015 | 0.004 | 1.1261 | 0.0038 | 28.968 | 0.001 | 3465 | 8 | 368.1 | 5.3 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.80174 | 5276.7645 | 70.5192 | 302.4114 | 1286.8523 | 3989.9122 | 0.010034 | 30.1809 | 59.4873 | 14.1001 | 13.1808 | 0.013925 | 38.1629 | 0.0087786 | 27.6065 | 0.0092015 | 24.4785 | 79.9129 | 65.5287 | 24.2828 | 31122.6672 | 25867.4937 | 3096.9 | 0.33961 | 30107.0239 | 24851.8504 | 8.6889 | 0.20503 | -5.8981 | -20.4256 | 54.2193 | 31122.6672 | 16505.5358 | 1032.6298 | 13584.5016 | 31122.6672 | 100%
5 | C-95-3+30-C | 30N0043 | C-95-3+30-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 6:33:57 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 7.2 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.2 |  | 5.5 |  | 230.3 | 0.9 | 15.5 | 0 | 19903 | 34 | 19231 | 61 | 1135 | 128 | 21040 | 124 |  | 944 |  | 12.1 | 5.8196 | 109.77 | 0.01 | 47.85 | [31 empty] | 6.152 | Closed damper, +30% charge 95F Test, adjust code tester speed to match total--static of run C-95-FC3-EC-SPWCT-SS | R22 7.2 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75 | 0.014 | 62 | 0.046 | 95.003 | 0.005 | 74.998 | 0.017 | 74.56 | 0.06 | 58.96 | 0.05 | 65.26 | 0.02 | 0.013 | 0.003 | 1.0965 | 0.0031 | 19903 | 34 | 1135 | 128 | 6.153 | 0.038 |  |  | 11.7971 |  |  |  | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3052.6 | 5.6 | 3052.6 | 5.6 | 3052.6 | 5.6 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 0.9 | 227.7 | 0.9 | 227.7 | 0.9 | 13.1 | 0 | 13.1 | 0 | 13.1 | 0 | 2858.6 | 5.1 | [9 empty] | 228.2 | 0.9 | 0.7 | 0 | 168.9 | 0.8 | 23 |  | 3416.6 | 480 | 480 | 480 | 0.8 | 0.8 | 1 | 480 | 0.65 | 12.1 | 17.6 | [12 empty] | 279.92 | 0.16 | 144.4 | 0.08 | 125.4 | 0.04 | 19 | 0.08 | 258.96 | 0.17 | 100.05 | 0.05 | 119.59 | 0.05 | 19.54 | 0.07 | 79.55 | 0.04 | 52.08 | 0.05 | 46.93 | 0.03 |  |  | 79.75 | 0.05 | 51.97 | 0.04 | 47.05 | 0.03 | 4.92 | 0.03 | 591.87 | 0.44 | 39.49 | 0.01 | 40346 | 38 | 41595 | 33 | [22 empty] | 263.27 | 0.19 | 100.86 | 0.03 | 120.81 | 0.05 | 19.95 | 0.06 | 261.84 | 0.17 | 120.41 | 0.05 | 19.67 | 0.06 | 5.16 | 0.04 | [74 empty] | 57.98 | 0.05 | 60.34 | 0.04 | 59.58 | 0.08 | 60.14 | 0.04 | 59.02 | 0.07 | 59.3 | 0.04 | [32 empty] | 100.77 | 0.04 |  |  |  |  | 95.07 | 0.07 | 95.25 | 0.06 | 95.3 | 0.07 | 95.28 | 0.06 | 95.3 | 0.05 | [12 empty] | 100.73 | 0.05 | [30 empty] | 94.87 | 0.06 | 95.34 | 0.06 | 75.02 | 0.05 | 74.98 | 0.05 | 74.74 | 0.04 | 75.18 | 0.06 | 75.15 | 0.06 | 75.15 | 0.06 | 74.96 | 0.05 | 91.97 | 0.1 | 84.36 | 0.12 | 80.92 | 0.09 | 86.66 | 0.13 | 85.35 | 0.18 | 86.1 | 0.13 | 77.99 | 0.07 | 83.09 | 0.1 | 92.97 | 0.06 | 79.16 | 0.16 | 75.22 | 0.04 | 75.29 | 0.04 | 83.54 | 0.21 | 75.19 | 0.04 | 75.21 | 0.05 | 75.05 | 0.05 | 76.25 | 0.09 | 75.1 | 0.04 | 75.06 | 0.04 | 75.13 | 0.03 | [84 empty] | C-55-CE-DM | 75 | 0.014 | 62 | 0.046 | 58.85 | 0.017 | 55.78 | 0.019 | 95.003 | 0.005 | 74.998 | 0.017 | 1142.6 | 1.6 | 1098.4 | 1.5 | 0.569 | 0.004 | -0.176 | 0.001 | 0.013 | 0.003 | 1.0965 | 0.0031 | 28.966 | 0.001 | 3420 | 8 | 366.1 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.79755 | 5217.0731 | 73.424 | 196.2183 | 834.9734 | 4382.0997 | 0.0096029 | 29.2966 | 58.0524 | 14.1 | 13.1407 | 0.013918 | 38.1551 | 0.0087806 | 27.6086 | 0.0087371 | 23.6224 | 78.2265 | 64.3454 | 23.4278 | 30617.5376 | 25259.9026 | 3053.9 | 0.34042 | 29618.6343 | 24260.9993 | 8.6604 | 0.20762 | -5.8687 | -20.1741 | 52.7665 | 30617.5376 | 20796.7403 | 1014.7518 | 8806.0456 | 30617.5376 | 100%
5 | C-95-3+40-1 | 30N0044 | C-95-3+40-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 3:01:30 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 7.7 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 5.5 |  | 230.3 | 0.7 | 15.7 | 0 | 18021 | 135 | 17406 | 129 | -1789 | 112 | 16230 | 185 |  | 944 |  | 12.5 | 5.1889 | 109.94 | 0.01 | 61.21 | [31 empty] | 4.6732 | 1 Finger Open, +40% charge, 95F Test, adjust code tester speed--to match total static of run C-95-FC3-1F-SPWCT-SS | R22 7.7 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 74.996 | 0.018 | 62.001 | 0.042 | 94.998 | 0.014 | 75 | 0.015 | 74.55 | 0.05 | 60.54 | 0.04 | 66.31 | 0.02 | 0.018 | 0.011 | 1.1291 | 0.0165 | 18021 | 135 | -1789 | 112 | 4.673 | 0.053 |  |  | 12.0452 |  |  |  | 229.7 | 0.8 | 229.7 | 0.8 | 229.7 | 0.8 | 14 | 0 | 14 | 0 | 14 | 0 | 3103.1 | 5.4 | 3103.1 | 5.4 | 3103.1 | 5.4 | 230 | 0.7 | 230 | 0.7 | 230 | 0.7 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.7 | 0.8 | 227.7 | 0.8 | 227.7 | 0.8 | 13.3 | 0 | 13.3 | 0 | 13.3 | 0 | 2908.1 | 4.9 | [9 empty] | 228.2 | 0.8 | 0.7 | 0 | 169 | 0.7 | 23 |  | 3468.5 | 489 | 489 | 490 | 0.8 | 0.9 | 1.1 | 500 | 0.63 | 12.5 | 18 | [12 empty] | 285.51 | 0.2 | 143.02 | 0.1 | 126.9 | 0.05 | 16.12 | 0.08 | 264.19 | 0.21 | 99.55 | 0.04 | 121.07 | 0.06 | 21.52 | 0.06 | 81.73 | 0.08 | 53.73 | 0.05 | 48.3 | 0.05 |  |  | 82.07 | 0.08 | 53.47 | 0.06 | 48.51 | 0.05 | 4.96 | 0.06 | 610.39 | 0.53 | 39.34 | 0.01 | 41833 | 44 | 43093 | 40 | [22 empty] | 268.68 | 0.24 | 100.48 | 0.04 | 122.33 | 0.07 | 21.85 | 0.07 | 267.14 | 0.22 | 121.9 | 0.06 | 21.59 | 0.08 | 5.43 | 0.03 | [74 empty] | 59.85 | 0.08 | 61.65 | 0.09 | 61.1 | 0.15 | 61.43 | 0.07 | 60.77 | 0.12 | 60.76 | 0.06 | [32 empty] | 100.18 | 0.04 |  |  |  |  | 95.04 | 0.11 | 95.22 | 0.08 | 95.15 | 0.1 | 95.21 | 0.09 | 95.25 | 0.09 | [12 empty] | 100.3 | 0.05 | [30 empty] | 94.62 | 0.1 | 95.11 | 0.11 | 74.81 | 0.09 | 74.82 | 0.07 | 74.67 | 0.04 | 74.91 | 0.11 | 74.88 | 0.11 | 74.93 | 0.1 | 74.79 | 0.07 | 93.56 | 0.07 | 93.33 | 0.08 | 92.39 | 0.1 | 89.55 | 0.09 | 89.53 | 0.12 | 90.84 | 0.12 | 88.6 | 0.14 | 87.81 | 0.09 | 92.21 | 0.06 | 76.22 | 0.07 | 76.78 | 0.09 | 75.86 | 0.05 | 83.3 | 0.15 | 76.16 | 0.05 | 75.69 | 0.04 | 76.18 | 0.07 | 77.15 | 0.16 | 75.19 | 0.06 | 75.15 | 0.03 | 75.36 | 0.04 | [84 empty] | C-55-1ER-DM | 74.996 | 0.018 | 62.001 | 0.042 | 60.493 | 0.021 | 57.319 | 0.032 | 94.998 | 0.014 | 75 | 0.015 | 1160.3 | 8.6 | 1113.3 | 8.3 | 0.54 | 0.004 | -0.136 | 0.002 | 0.018 | 0.011 | 1.1291 | 0.0165 | 28.996 | 0.001 | 3473 | 8 | 368.4 | 5.3 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.80184 | 5279.5125 | 70.6271 | 303.5274 | 1291.618 | 3987.8944 | 0.010039 | 30.1899 | 59.6912 | 14.0999 | 13.1864 | 0.013921 | 38.1572 | 0.0087822 | 27.6094 | 0.0092615 | 24.5935 | 79.9239 | 65.5405 | 24.3978 | 30579.3998 | 25636.6073 | 3104.6 | 0.34651 | 29563.1008 | 24620.3082 | 8.5123 | 0.20622 | -5.7921 | -20.2328 | 54.4349 | 30579.3998 | 15922.3376 | 1033.4093 | 13623.653 | 30579.3998 | 100%
5 | C-95-3-10-1 | 30N0045 | C-95-3+10-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 11:54:44 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 4.95 | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.1 |  | 5.5 |  | 230.3 | 0.9 | 14.9 | 0 | 17538 | 36 | 16911 | 62 | -1648 | 100 | 15888 | 101 |  | 944 |  | 13.3 | 5.321 | 112.93 | 0.01 | 55.49 | [31 empty] | 4.8204 | 1 Finger Open, -10% charge, 95F Test, adjust code tester speed to match total--static of run C-95-FC3-1F-SPWCT-SS | R22 4.95 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 74.994 | 0.014 | 62.003 | 0.042 | 94.999 | 0.008 | 75.002 | 0.015 | 74.63 | 0.04 | 61.18 | 0.04 | 66.58 | 0.02 | 0.031 | 0.003 | 1.1604 | 0.0035 | 17538 | 36 | -1648 | 100 | 4.822 | 0.032 |  |  | 10.8313 |  |  |  | 229.7 | 0.9 | 229.7 | 0.9 | 229.7 | 0.9 | 13.2 | 0 | 13.2 | 0 | 13.2 | 0 | 2923.8 | 5.2 | 2923.8 | 5.2 | 2923.8 | 5.2 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.5 | 0 | 12.5 | 0 | 12.5 | 0 | 2731.7 | 4.8 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 168.8 | 0.8 | 23 |  | 3294.1 | 480 | 480 | 480 | 0.9 | 0.9 | 1 | 510 | 0.65 | 13.3 | 18.2 | [12 empty] | 261.29 | 0.16 | 184.46 | 0.06 | 120.25 | 0.04 | 64.21 | 0.07 | 241.52 | 0.2 | 104.04 | 0.05 | 114.49 | 0.06 | 10.45 | 0.08 | 77.25 | 0.05 | 68.73 | 0.04 | 45.47 | 0.03 |  |  | 77.14 | 0.06 | 71.48 | 0.05 | 45.39 | 0.04 | 26.09 | 0.06 | 512.15 | 0.46 | 40.75 | 0.01 | 35700 | 40 | 36965 | 37 | [22 empty] | 245.06 | 0.21 | 104.52 | 0.04 | 115.55 | 0.06 | 11.02 | 0.07 | 243.72 | 0.19 | 115.15 | 0.06 | 10.74 | 0.07 | 23.27 | 0.05 | [74 empty] | 60.55 | 0.08 | 62.25 | 0.04 | 61.87 | 0.1 | 62.06 | 0.03 | 61.42 | 0.09 | 61.43 | 0.04 | [32 empty] | 104.3 | 0.04 |  |  |  |  | 95.09 | 0.09 | 95.25 | 0.08 | 95.35 | 0.07 | 96.22 | 0.07 | 96.23 | 0.07 | [12 empty] | 104.41 | 0.04 | [30 empty] | 94.81 | 0.06 | 95.31 | 0.06 | 75.01 | 0.04 | 74.97 | 0.03 | 74.73 | 0.04 | 75.16 | 0.04 | 75.14 | 0.05 | 75.18 | 0.05 | 74.97 | 0.04 | 93.43 | 0.05 | 93.4 | 0.07 | 92.26 | 0.08 | 89.12 | 0.09 | 89.42 | 0.11 | 91.01 | 0.11 | 88.49 | 0.13 | 87.48 | 0.09 | 92.31 | 0.07 | 76.32 | 0.07 | 76.62 | 0.09 | 75.84 | 0.05 | 81.89 | 0.16 | 75.9 | 0.04 | 75.53 | 0.03 | 75.63 | 0.04 | 76.72 | 0.13 | 74.93 | 0.05 | 75 | 0.04 | 75.13 | 0.04 | [84 empty] | C-55-1ER-DM | 74.994 | 0.014 | 62.003 | 0.042 | 61.056 | 0.012 | 57.489 | 0.022 | 94.999 | 0.008 | 75.002 | 0.015 | 1177.4 | 1.8 | 1127.9 | 1.7 | 0.544 | 0.005 | -0.142 | 0.001 | 0.031 | 0.003 | 1.1604 | 0.0035 | 28.961 | 0.002 | 3296 | 8 | 370.6 | 5.2 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.79301 | 5351.625 | 72.0833 | 310.151 | 1319.8003 | 4031.8246 | 0.010051 | 30.2123 | 60.263 | 14.0999 | 13.2005 | 0.013923 | 38.1591 | 0.008784 | 27.6109 | 0.0092308 | 24.6975 | 79.9623 | 65.5699 | 24.504 | 30548.5622 | 25301.5476 | 2925.4 | 0.32684 | 29529.7247 | 24282.71 | 8.9593 | 0.23561 | -5.7083 | -19.6993 | 54.1911 | 30548.5622 | 15591.132 | 1035.9326 | 13921.4977 | 30548.5622 | 100%
5 | C-95-3-20-1 | 30N0046 | C-95-3+20-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 8:44:20 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 4.4 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.6 |  | 5.5 |  | 230.3 | 0.9 | 14.7 | 0 | 16420 | 232 | 15827 | 76 | -2510 | 113 | 13908 | 248 |  | 943 |  | 14.4 | 5.0648 | 113.54 | 0.01 | 58.73 | [31 empty] | 4.2899 | 1-Finger Open, -20% charge, 95F Test, adjust code tester speed to match total--static of run C-95-FC3-1F-SPWCT-SS | R22 4.4 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75.004 | 0.017 | 61.998 | 0.038 | 95.001 | 0.008 | 75.001 | 0.014 | 74.59 | 0.05 | 62.16 | 0.04 | 67.19 | 0.02 | 0.055 | 0.005 | 1.1989 | 0.0049 | 16420 | 232 | -2510 | 113 | 4.29 | 0.074 |  |  | 10.4025 |  |  |  | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13 | 0 | 13 | 0 | 13 | 0 | 2867.9 | 5.8 | 2867.9 | 5.8 | 2867.9 | 5.8 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.9 | 0.9 | 227.9 | 0.9 | 227.9 | 0.9 | 12.3 | 0 | 12.3 | 0 | 12.3 | 0 | 2676.6 | 5.3 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 168.7 | 0.8 | 23 |  | 3241.3 | 482 | 482 | 482 | 0.9 | 1 | 1 | 500 | 0.64 | 14.4 | 18.7 | [12 empty] | 254.62 | 0.15 | 188.27 | 0.04 | 118.34 | 0.04 | 69.93 | 0.05 | 235.4 | 0.2 | 105.67 | 0.05 | 112.64 | 0.06 | 6.97 | 0.07 | 73.66 | 0.04 | 71.05 | 0.03 | 43.11 | 0.02 |  |  | 73.25 | 0.03 | 73.81 | 0.03 | 42.84 | 0.02 | 30.97 | 0.04 | 484.29 | 0.43 | 41.27 | 0.01 | 33725 | 38 | 34998 | 34 | [22 empty] | 238.7 | 0.21 | 105.98 | 0.03 | 113.64 | 0.06 | 7.66 | 0.07 | 237.41 | 0.22 | 113.25 | 0.07 | 7.28 | 0.08 | 27.94 | 0.04 | [74 empty] | 61.46 | 0.16 | 62.98 | 0.05 | 62.6 | 0.18 | 62.83 | 0.05 | 62.24 | 0.19 | 62.37 | 0.06 | [32 empty] | 105.99 | 0.05 |  |  |  |  | 95.04 | 0.09 | 95.22 | 0.07 | 95.17 | 0.07 | 95.2 | 0.06 | 95.23 | 0.06 | [12 empty] | 105.97 | 0.05 | [30 empty] | 94.52 | 0.07 | 95.02 | 0.07 | 74.74 | 0.05 | 74.78 | 0.04 | 74.66 | 0.04 | 74.78 | 0.06 | 74.77 | 0.06 | 74.83 | 0.06 | 74.74 | 0.04 | 93.18 | 0.04 | 93.08 | 0.05 | 92.13 | 0.06 | 89.51 | 0.1 | 89.72 | 0.13 | 91.02 | 0.11 | 88.6 | 0.13 | 87.34 | 0.08 | 92.31 | 0.06 | 76.33 | 0.08 | 76.76 | 0.09 | 75.89 | 0.05 | 82.38 | 0.15 | 76.06 | 0.04 | 75.6 | 0.04 | 75.84 | 0.04 | 76.85 | 0.12 | 74.98 | 0.04 | 75.02 | 0.05 | 75.19 | 0.05 | [84 empty] | C-55-1ER-DM | 75.004 | 0.017 | 61.998 | 0.038 | 62.109 | 0.03 | 58.123 | 0.028 | 95.001 | 0.008 | 75.001 | 0.014 | 1198.5 | 2.5 | 1144.9 | 2.4 | 0.539 | 0.007 | -0.145 | 0.001 | 0.055 | 0.005 | 1.1989 | 0.0049 | 28.92 | 0.001 | 3242 | 8 | 373 | 5.2 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.78589 | 5436.0973 | 72.4972 | 313.4105 | 1333.6671 | 4102.4301 | 0.01004 | 30.1957 | 61.3231 | 14.0999 | 13.2282 | 0.013921 | 38.1581 | 0.0087784 | 27.6071 | 0.0093671 | 25.103 | 79.9446 | 65.5483 | 24.9111 | 28727.3645 | 24294.7122 | 2869 | 0.34086 | 27701.7486 | 23269.0962 | 8.5446 | 0.26447 | -5.2846 | -18.6214 | 54.6276 | 28727.3645 | 13612.8442 | 1043.0833 | 14071.437 | 28727.3645 | 100%
5 | C-95-3-20-C | 30N0047 | C-95-3+20-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 9:50:45 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 4.4 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.6 |  | 5.5 |  | 230.3 | 1 | 14.7 | 0 | 18445 | 39 | 17822 | 70 | 459 | 99 | 18904 | 102 |  | 944 |  | 12.8 | 5.707 | 113.23 | 0.01 | 43.27 | [31 empty] | 5.849 | Closed Damper, -20% charge, 95F Test, adjust code tester speed to match total--static of run C-95-FC3-EC-SPWCT-SS | R22 4.4 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75.002 | 0.017 | 61.999 | 0.043 | 94.997 | 0.005 | 74.998 | 0.013 | 74.63 | 0.05 | 60.33 | 0.04 | 66.06 | 0.01 | 0.026 | 0.003 | 1.1282 | 0.0035 | 18445 | 39 | 459 | 99 | 5.848 | 0.035 |  |  | 10.3097 |  |  |  | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 13 | 0 | 13 | 0 | 13 | 0 | 2863.3 | 5.9 | 2863.3 | 5.9 | 2863.3 | 5.9 | 230 | 1 | 230 | 1 | 230 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.9 | 1 | 227.9 | 1 | 227.9 | 1 | 12.3 | 0 | 12.3 | 0 | 12.3 | 0 | 2671.8 | 5.1 | [9 empty] | 228.3 | 1 | 0.7 | 0 | 168.8 | 0.9 | 23 |  | 3231.6 | 480 | 480 | 480 | 0.9 | 1 | 0.9 | 500 | 0.64 | 12.8 | 17.9 | [12 empty] | 253.89 | 0.14 | 187.14 | 0.04 | 118.13 | 0.04 | 69.01 | 0.05 | 234.76 | 0.2 | 105.91 | 0.04 | 112.45 | 0.06 | 6.54 | 0.07 | 72.7 | 0.06 | 69.02 | 0.03 | 42.48 | 0.04 |  |  | 72.35 | 0.05 | 71.87 | 0.03 | 42.24 | 0.03 | 29.63 | 0.04 | 481.04 | 0.44 | 41.35 | 0.01 | 33321 | 39 | 34578 | 34 | [22 empty] | 238.05 | 0.21 | 106.23 | 0.04 | 113.44 | 0.06 | 7.21 | 0.07 | 236.72 | 0.2 | 113.04 | 0.06 | 6.8 | 0.07 | 26.54 | 0.05 | [74 empty] | 59.35 | 0.05 | 61.43 | 0.08 | 60.67 | 0.11 | 61.3 | 0.06 | 60.1 | 0.08 | 60.61 | 0.04 | [32 empty] | 106.26 | 0.04 |  |  |  |  | 95.09 | 0.06 | 95.19 | 0.06 | 95.23 | 0.07 | 96.1 | 0.06 | 96.11 | 0.06 | [12 empty] | 106.24 | 0.04 | [30 empty] | 94.69 | 0.06 | 95.16 | 0.06 | 74.89 | 0.05 | 74.88 | 0.05 | 74.71 | 0.04 | 74.98 | 0.06 | 74.96 | 0.06 | 74.98 | 0.06 | 74.85 | 0.05 | 91.62 | 0.08 | 83.81 | 0.11 | 81.09 | 0.1 | 86.84 | 0.14 | 85.19 | 0.16 | 85.84 | 0.13 | 78.12 | 0.06 | 83.53 | 0.09 | 92.91 | 0.06 | 79.51 | 0.16 | 75.42 | 0.04 | 75.46 | 0.04 | 83.76 | 0.18 | 75.36 | 0.04 | 75.32 | 0.04 | 74.88 | 0.06 | 76.08 | 0.09 | 74.96 | 0.06 | 75.01 | 0.05 | 75.1 | 0.04 | [84 empty] | C-55-CE-DM | 75.002 | 0.017 | 61.999 | 0.043 | 60.195 | 0.017 | 56.519 | 0.03 | 94.997 | 0.005 | 74.998 | 0.013 | 1160.9 | 1.8 | 1112.4 | 1.8 | 0.572 | 0.005 | -0.178 | 0.002 | 0.026 | 0.003 | 1.1282 | 0.0035 | 28.922 | 0.001 | 3232 | 8 | 368 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.78861 | 5286.5496 | 74.7519 | 197.3291 | 839.7084 | 4446.8413 | 0.009596 | 29.2832 | 59.4064 | 14.0998 | 13.1757 | 0.01392 | 38.1552 | 0.0087795 | 27.6079 | 0.0088539 | 24.0774 | 78.2029 | 64.3274 | 23.885 | 28537.7267 | 23848.5313 | 2864 | 0.34252 | 27536.8709 | 22847.6755 | 8.5201 | 0.25259 | -5.3982 | -18.7965 | 53.0541 | 28537.7267 | 18664.0715 | 1016.9515 | 8856.7037 | 28537.7267 | 100%
5 | C-95-3-30-1 | 30N0048 | C-95-3+30-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 7:39:56 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 3.85 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.2 |  | 5.5 |  | 230.3 | 1 | 14.4 | 0 | 14475 | 39 | 13929 | 61 | -3287 | 92 | 11184 | 91 |  | 943 |  | 14.3 | 4.5619 | 113.93 | 0.01 | 63.68 | [31 empty] | 3.5247 | 1 Finger Open, -30% charge, 95F Test, adjust code tester speed to match total--static of run C-95-FC3-1F-SPWCT-SS | R22 3.85 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75.004 | 0.015 | 61.997 | 0.042 | 95.002 | 0.005 | 74.998 | 0.011 | 74.61 | 0.05 | 63.59 | 0.04 | 68.11 | 0.02 | 0.048 | 0.004 | 1.1908 | 0.0042 | 14475 | 39 | -3287 | 92 | 3.525 | 0.03 |  |  | 9.7041 |  |  |  | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2799.9 | 5.9 | 2799.9 | 5.9 | 2799.9 | 5.9 | 230 | 1 | 230 | 1 | 230 | 1 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.9 | 1 | 227.9 | 1 | 227.9 | 1 | 12 | 0 | 12 | 0 | 12 | 0 | 2609.5 | 5.3 | [9 empty] | 228.4 | 1 | 0.7 | 0 | 168.8 | 0.9 | 23 |  | 3173.3 | 482 | 482 | 482 | 0.9 | 1 | 1 | 530 | 0.64 | 14.3 | 18.7 | [12 empty] | 246.55 | 0.12 | 192.14 | 0.03 | 115.98 | 0.04 | 76.15 | 0.05 | 228.31 | 0.17 | 108.57 | 0.04 | 110.46 | 0.05 | 1.88 | 0.07 | 67.66 | 0.05 | 71.5 | 0.03 | 39.04 | 0.03 |  |  | 67.43 | 0.05 | 74.31 | 0.03 | 38.88 | 0.03 | 35.43 | 0.05 | 446.93 | 0.32 | 42.2 | 0.01 | 30791 | 30 | 32060 | 25 | [22 empty] | 231.31 | 0.18 | 108.12 | 0.03 | 111.39 | 0.05 | 3.27 | 0.06 | 230.03 | 0.19 | 110.99 | 0.06 | 2.22 | 0.07 | 32.46 | 0.04 | [74 empty] | 62.92 | 0.11 | 64.57 | 0.05 | 64.15 | 0.13 | 64.41 | 0.05 | 63.8 | 0.13 | 63.88 | 0.05 | [32 empty] | 109.03 | 0.04 |  |  |  |  | 95 | 0.09 | 95.18 | 0.07 | 95.16 | 0.08 | 95.19 | 0.07 | 95.22 | 0.07 | [12 empty] | 108.77 | 0.03 | [30 empty] | 94.56 | 0.07 | 95.05 | 0.08 | 74.78 | 0.06 | 74.8 | 0.04 | 74.68 | 0.04 | 74.84 | 0.07 | 74.82 | 0.07 | 74.87 | 0.06 | 74.77 | 0.04 | 93.17 | 0.04 | 93.1 | 0.05 | 92.15 | 0.08 | 89.58 | 0.1 | 89.7 | 0.14 | 90.93 | 0.12 | 88.58 | 0.15 | 87.31 | 0.09 | 92.24 | 0.08 | 76.33 | 0.07 | 76.72 | 0.09 | 75.87 | 0.06 | 82.27 | 0.15 | 76.06 | 0.04 | 75.62 | 0.04 | 75.87 | 0.05 | 76.85 | 0.13 | 74.99 | 0.06 | 75.05 | 0.05 | 75.2 | 0.04 | [84 empty] | C-55-1ER-DM | 75.004 | 0.015 | 61.997 | 0.042 | 63.556 | 0.022 | 58.885 | 0.026 | 95.002 | 0.005 | 74.998 | 0.011 | 1195.5 | 2.2 | 1139.7 | 2.1 | 0.54 | 0.006 | -0.143 | 0.001 | 0.048 | 0.004 | 1.1908 | 0.0042 | 28.917 | 0.001 | 3173 | 8 | 372 | 5.2 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.78799 | 5407.0859 | 72.3019 | 311.2416 | 1324.4374 | 4082.6484 | 0.010037 | 30.1903 | 62.768 | 14.0999 | 13.2659 | 0.013919 | 38.1552 | 0.0087777 | 27.6064 | 0.0094944 | 25.5949 | 79.9369 | 65.5412 | 25.4024 | 25888.2663 | 22280.1255 | 2801 | 0.36927 | 24865.3965 | 21257.2558 | 7.8366 | 0.31182 | -4.7878 | -17.1689 | 54.9885 | 25888.2663 | 10876.5902 | 1040.5311 | 13971.145 | 25888.2663 | 100%
5 | C-95-3-30-C | 30N0049 | C-95-3+30-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 6:33:57 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 3.85 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.2 |  | 5.5 |  | 230.3 | 0.9 | 14.4 | 0 | 16722 | 41 | 16128 | 68 | -480 | 83 | 16241 | 84 |  | 943 |  | 13.5 | 5.2817 | 113.68 | 0.01 | 46.96 | [31 empty] | 5.1298 | Closed Damper, -30% charge, 95F Test, adjust code tester speed to--match total static of run C-95-FC3-EC-SPWCT-SS | R22 3.85 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75.002 | 0.012 | 62.004 | 0.039 | 95 | 0.006 | 75.002 | 0.015 | 74.6 | 0.05 | 61.81 | 0.06 | 67.04 | 0.01 | 0.035 | 0.005 | 1.1607 | 0.006 | 16722 | 41 | -480 | 83 | 5.13 | 0.029 |  |  | 9.6725 |  |  |  | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2794.8 | 5.6 | 2794.8 | 5.6 | 2794.8 | 5.6 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.9 | 0.9 | 227.9 | 0.9 | 227.9 | 0.9 | 12 | 0 | 12 | 0 | 12 | 0 | 2604.2 | 5.2 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 169 | 0.8 | 23 |  | 3166.4 | 477 | 478 | 478 | 0.9 | 0.9 | 1 | 500 | 0.65 | 13.5 | 18.3 | [12 empty] | 246.49 | 0.12 | 190.93 | 0.04 | 115.98 | 0.04 | 74.95 | 0.05 | 228.25 | 0.16 | 108.71 | 0.07 | 110.45 | 0.05 | 1.74 | 0.09 | 67.32 | 0.04 | 70 | 0.04 | 38.83 | 0.03 |  |  | 67.13 | 0.04 | 72.89 | 0.05 | 38.7 | 0.03 | 34.18 | 0.05 | 446.34 | 0.29 | 42.25 | 0.02 | 30623 | 31 | 31886 | 25 | [22 empty] | 231.25 | 0.18 | 108.14 | 0.04 | 111.38 | 0.05 | 3.24 | 0.06 | 229.97 | 0.19 | 110.99 | 0.06 | 2.06 | 0.07 | 31.17 | 0.05 | [74 empty] | 60.91 | 0.08 | 62.83 | 0.09 | 62.2 | 0.14 | 62.69 | 0.07 | 61.68 | 0.1 | 62.14 | 0.05 | [32 empty] | 109.22 | 0.04 |  |  |  |  | 94.7 | 0.09 | 94.87 | 0.08 | 94.9 | 0.08 | 94.96 | 0.07 | 94.98 | 0.07 | [12 empty] | 108.92 | 0.05 | [30 empty] | 94.62 | 0.06 | 95.01 | 0.07 | 74.79 | 0.08 | 74.82 | 0.05 | 74.72 | 0.05 | 74.83 | 0.1 | 74.82 | 0.1 | 74.87 | 0.09 | 74.8 | 0.06 | 91.23 | 0.07 | 83.71 | 0.12 | 81.02 | 0.09 | 86.88 | 0.13 | 85.07 | 0.17 | 86.07 | 0.14 | 78.32 | 0.08 | 83.72 | 0.12 | 92.84 | 0.08 | 79.47 | 0.17 | 75.55 | 0.08 | 75.54 | 0.06 | 83.77 | 0.2 | 75.38 | 0.05 | 75.37 | 0.04 | 74.94 | 0.08 | 76.04 | 0.11 | 74.97 | 0.08 | 75 | 0.06 | 75.12 | 0.04 | [84 empty] | C-55-CE-DM | 75.002 | 0.012 | 62.004 | 0.039 | 61.741 | 0.022 | 57.389 | 0.027 | 95 | 0.006 | 75.002 | 0.015 | 1176.8 | 3 | 1128.9 | 3 | 0.574 | 0.006 | -0.177 | 0.002 | 0.035 | 0.005 | 1.1607 | 0.006 | 29.016 | 0.004 | 3166 | 8 | 370.2 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 0.78254 | 5342.5764 | 76.1259 | 196.7747 | 837.3434 | 4505.2331 | 0.0095883 | 29.2646 | 60.9585 | 14.0999 | 13.2161 | 0.013923 | 38.1591 | 0.0087828 | 27.6115 | 0.0090082 | 24.6225 | 78.161 | 64.302 | 24.4316 | 25820.8699 | 22057.387 | 2795.8 | 0.36955 | 24817.1951 | 21053.7121 | 7.8387 | 0.30164 | -4.833 | -17.2025 | 53.5283 | 25820.8699 | 15968.8362 | 1020.1024 | 8831.9314 | 25820.8699 | 100%
5 | C-95-3-40-1 | 30N0050 | C-95-3+40-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 3:01:30 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 3.3 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 5.5 |  | 230.3 | 0.8 | 14.2 | 0 | 11858 | 29 | 11385 | 52 | -3781 | 83 | 8073 | 93 |  | 943 |  | 13.7 | 3.8104 | 114.36 | 0.01 | 70.77 | [31 empty] | 2.5942 | 1 Finger Open, -40% charge, 95F Test, adjust code tester speed--to match total static of run C-95-FC3-1F-SPWCT-SS | R22 3.3 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75 | 0.018 | 61.994 | 0.047 | 94.997 | 0.011 | 75.001 | 0.015 | 74.61 | 0.05 | 65.55 | 0.05 | 69.5 | 0.01 | 0.031 | 0.004 | 1.1789 | 0.0041 | 11858 | 29 | -3781 | 83 | 2.594 | 0.031 |  |  | 8.8747 |  |  |  | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 12.5 | 0 | 12.5 | 0 | 12.5 | 0 | 2738.7 | 5.8 | 2738.7 | 5.8 | 2738.7 | 5.8 | 229.9 | 0.8 | 229.9 | 0.8 | 229.9 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 228 | 0.8 | 228 | 0.8 | 228 | 0.8 | 11.7 | 0 | 11.7 | 0 | 11.7 | 0 | 2548.4 | 5.2 | [9 empty] | 228.4 | 0.8 | 0.7 | 0 | 169.7 | 0.8 | 23 |  | 3113 | 482 | 483 | 484 | 0.9 | 0.9 | 1 | 510 | 0.64 | 13.7 | 18.4 | [12 empty] | 239.2 | 0.16 | 197 | 0.08 | 113.83 | 0.05 | 83.16 | 0.1 | 222.27 | 0.27 | 108.15 | 0.06 | 108.6 | 0.09 | 0.46 | 0.1 | 61.63 | 0.05 | 72.18 | 0.04 | 34.82 | 0.04 |  |  | 61.43 | 0.06 | 75.26 | 0.04 | 34.67 | 0.05 | 40.58 | 0.06 | 399.59 | 2.5 | 42.06 | 0.02 | 27618 | 181 | 28885 | 180 | [22 empty] | 225.29 | 0.17 | 107.71 | 0.03 | 109.56 | 0.05 | 1.85 | 0.05 | 224.1 | 0.23 | 109.18 | 0.07 | 0.45 | 0.07 | 37.37 | 0.05 | [74 empty] | 65.06 | 0.09 | 66.72 | 0.07 | 66.38 | 0.14 | 66.57 | 0.05 | 65.77 | 0.12 | 66.1 | 0.04 | [32 empty] | 108.93 | 0.05 |  |  |  |  | 94.98 | 0.09 | 95.33 | 0.06 | 95.23 | 0.08 | 95.25 | 0.07 | 95.27 | 0.06 | [12 empty] | 108.73 | 0.04 | [30 empty] | 94.62 | 0.07 | 95.1 | 0.07 | 74.86 | 0.06 | 74.88 | 0.05 | 74.73 | 0.04 | 74.95 | 0.07 | 74.93 | 0.07 | 74.99 | 0.07 | 74.85 | 0.05 | 93.47 | 0.05 | 93.37 | 0.06 | 92.51 | 0.08 | 89.72 | 0.1 | 89.68 | 0.1 | 91.08 | 0.11 | 88.9 | 0.12 | 87.7 | 0.1 | 91.93 | 0.08 | 76.32 | 0.07 | 76.97 | 0.1 | 75.98 | 0.07 | 82.82 | 0.14 | 76.2 | 0.05 | 75.71 | 0.04 | 76.13 | 0.06 | 77.02 | 0.14 | 75.12 | 0.07 | 75.08 | 0.05 | 75.3 | 0.03 | [84 empty] | C-55-1ER-DM | 75 | 0.018 | 61.994 | 0.047 | 65.569 | 0.012 | 59.741 | 0.031 | 94.997 | 0.011 | 75.001 | 0.015 | 1185.2 | 2.1 | 1138 | 2 | 0.547 | 0.005 | -0.139 | 0.001 | 0.031 | 0.004 | 1.1789 | 0.0041 | 29.204 | 0.002 | 3112 | 8 | 371.9 | 5.2 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.79545 | 5339.7675 | 73.1299 | 306.8566 | 1305.7869 | 4033.9806 | 0.010035 | 30.1851 | 64.7736 | 14.0999 | 13.3174 | 0.013922 | 38.1581 | 0.0087767 | 27.6043 | 0.0095539 | 26.1514 | 79.9246 | 65.5344 | 25.9571 | 22576.7804 | 19416.7312 | 2740.1 | 0.41423 | 21557.0779 | 18397.0287 | 6.9271 | 0.39287 | -4.228 | -15.151 | 54.9693 | 22576.7804 | 7758.2992 | 1037.4214 | 13781.0598 | 22576.7804 | 100%
5 | C-95-3-FC-1 | 30N0051 | C-95-3-FC-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/18/2014 | 0:55:24 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.8 | 15.2 | 0 | 17780 | 138 | 17152 | 128 | -1406 | 120 | 16373 | 179 |  | 944 |  | 12.6 | 5.3043 | 112.21 | 0.02 | 55.56 | [31 empty] | 4.8845 | 1 Finger Open, 5.5 lbs factory charge 95F test, adjust code tester speed to match--total static of run C -95-FC3-1F-SPWCT-SS | R22 5.5 LBS: Unsealed cab:Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. ID Pulley is 3 turns open from fully closed: with flow meter: new filter drier: with isolation ball valves: with code: | 75 | 0.023 | 62.008 | 0.045 | 95.001 | 0.011 | 75.001 | 0.019 | 74.55 | 0.05 | 60.82 | 0.04 | 66.68 | 0.05 | 0.021 | 0.011 | 1.1375 | 0.0166 | 17780 | 138 | -1406 | 120 | 4.885 | 0.052 |  |  | 10.9913 |  |  |  | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2980.9 | 4.8 | 2980.9 | 4.8 | 2980.9 | 4.8 | 230 | 0.8 | 230 | 0.8 | 230 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2787.8 | 4.4 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 169.2 | 0.8 | 23 |  | 3349.6 | 490 | 490 | 490 | 0.8 | 0.8 | 1 | 510 | 0.63 | 12.6 | 17.9 | [12 empty] | 266 | 0.16 | 181.39 | 0.07 | 121.59 | 0.05 | 59.8 | 0.08 | 245.88 | 0.21 | 103.03 | 0.03 | 115.8 | 0.06 | 12.78 | 0.06 | 79.04 | 0.07 | 65.31 | 0.11 | 46.62 | 0.04 |  |  | 79.71 | 0.07 | 68.48 | 0.1 | 47.05 | 0.04 | 21.43 | 0.11 | 530.86 | 0.46 | 40.43 | 0.01 | 36843 | 43 | 38104 | 40 | [22 empty] | 249.59 | 0.23 | 103.79 | 0.03 | 116.89 | 0.07 | 13.1 | 0.07 | 248.13 | 0.21 | 116.47 | 0.06 | 13 | 0.07 | 18.68 | 0.12 | [74 empty] | 60.19 | 0.09 | 61.96 | 0.06 | 61.47 | 0.1 | 61.76 | 0.05 | 60.99 | 0.1 | 61.07 | 0.06 | [32 empty] | 103.38 | 0.04 |  |  |  |  | 95.07 | 0.1 | 95.22 | 0.07 | 95.21 | 0.07 | 95.26 | 0.06 | 95.3 | 0.06 | [12 empty] | 103.47 | 0.05 | [30 empty] | 94.78 | 0.05 | 95.28 | 0.06 | 74.96 | 0.04 | 74.95 | 0.04 | 74.71 | 0.03 | 75.12 | 0.04 | 75.09 | 0.04 | 75.12 | 0.04 | 74.93 | 0.04 | 93.67 | 0.04 | 93.31 | 0.08 | 92.43 | 0.07 | 89.38 | 0.09 | 89.78 | 0.13 | 90.98 | 0.13 | 88.45 | 0.14 | 87.8 | 0.09 | 92.25 | 0.06 | 76.26 | 0.06 | 76.69 | 0.09 | 75.84 | 0.05 | 83.35 | 0.14 | 76.13 | 0.04 | 75.74 | 0.03 | 76.32 | 0.04 | 77.28 | 0.15 | 75.26 | 0.04 | 75.15 | 0.03 | 75.4 | 0.04 | [84 empty] | C-55-1ER-DM | 75 | 0.023 | 62.008 | 0.045 | 60.762 | 0.024 | 57.302 | 0.032 | 95.001 | 0.011 | 75.001 | 0.019 | 1164.2 | 8.6 | 1118.1 | 8.3 | 0.54 | 0.005 | -0.137 | 0.002 | 0.021 | 0.011 | 1.1375 | 0.0166 | 29.038 | 0.001 | 3352 | 8 | 369.6 | 5.3 | 0.25502 | 291.7735 | 13.029 | 0.136 | 0.80194 | 5294.7523 | 70.9316 | 304.6421 | 1296.3544 | 3998.3979 | 0.010043 | 30.1959 | 59.9601 | 14.0999 | 13.1927 | 0.013921 | 38.1581 | 0.0087859 | 27.6144 | 0.0091876 | 24.5788 | 79.9315 | 65.5483 | 24.383 | 30777.7719 | 25378.5043 | 2982.4 | 0.33072 | 29758.4165 | 24359.1489 | 8.8778 | 0.22797 | -5.8129 | -19.9714 | 54.0627 | 30777.7719 | 16073.0727 | 1036.3776 | 13668.3216 | 30777.7719 | 100%
5 | C-55-T1ER-DM | 30N0021 | C-55-T1ER-DM | 1 Finger | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 4:49:30 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 0.8 | 1.7 | 0 | 6120 | 21 | 5475 | 38 | 2578 | 46 | 8700 | 56 |  | 942 |  | 13.7 |  | 110.12 | 0.01 | 0 | [31 empty] | 23.2 | Econo 1F-open, tape around damper perimeter frame gaps, no compressor,--55/51 ambient, 53.5% inlet 52% outlet Meriam, adjust code tester speed to match--total static of run C-55-T1E-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 1F: with flow meter: new filter drier: with isolation ball valves: without code | 74.991 | 0.013 | 61.998 | 0.026 | 54.991 | 0.012 | 51.001 | 0.018 | 74.34 | 0.05 | 70.11 | 0.05 | 72.42 | 0.01 | 0.041 | 0.005 | 1.1912 | 0.0051 | 6120 | 21 | 2578 | 46 | 23.204 | 0.335 | [6 empty] | 230.2 | 0.8 | 230.2 | 0.8 | 230.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.2 | 0.3 | 0.2 | 0.3 | 0.2 | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 23 |  | 374.6 | 482 | 482 | 483 | 0.9 | 0.9 | 1.1 | 510 | 0.63 | 13.7 | 18.4 | [44 empty] | -0.6 | 0 | 26.2 | 0.01 | -1278 | 16 | [114 empty] | 69.68 | 0.24 | 71.35 | 0.14 | 70.71 | 0.04 | 71.15 | 0.14 | 70.19 | 0.14 | 70.59 | 0.12 | [32 empty] | 55.98 | 0.03 |  |  | 54.73 | 0.08 | 54.81 | 0.09 | 54.35 | 0.06 | 54.66 | 0.07 | 54.67 | 0.05 | 54.68 | 0.04 | [8 empty] | 54.49 | 0.06 | [34 empty] | 54.99 | 0.1 | 54.68 | 0.09 | 74.56 | 0.08 | 74.56 | 0.07 | 74.42 | 0.04 | 74.71 | 0.09 | 74.66 | 0.09 | 74.73 | 0.09 | 74.64 | 0.08 | 63.6 | 0.04 | 63.55 | 0.04 | 63.44 | 0.06 | 63.2 | 0.07 | 62.28 | 0.04 | 63.41 | 0.08 | 62.98 | 0.09 | 63.2 | 0.1 | 61.33 | 0.1 | 74.28 | 0.07 | 73.77 | 0.1 | 74.41 | 0.08 | 69.05 | 0.15 | 73.49 | 0.07 | 74.23 | 0.06 | 73.2 | 0.09 | 73.06 | 0.11 | 74.15 | 0.09 | 74.32 | 0.05 | 74.38 | 0.04 | [84 empty] | Economizer test | 74.991 | 0.013 | 61.998 | 0.026 | 70.259 | 0.007 | 59.6 | 0.02 | 54.991 | 0.012 | 51.001 | 0.018 | 1186.2 | 2.6 | 1150.2 | 2.5 | 0.569 | 0.008 | -0.164 | 0.001 | 0.041 | 0.005 | 1.1912 | 0.0051 | 29.59 | 0.001 | 375 | 5 | 374.6 | 4.8 | 0.1966 | 226.1293 | 13.029 | 0.164 | 0.79847 | 5300.7449 | 76.8866 | 226.1319 | 1041.339 | 4259.4059 | 0.0084283 | 26.2658 | 69.4605 | 13.0293 | 13.4268 | 0.006984 | 20.7784 | 0.0087814 | 27.6073 | 0.0083557 | 25.9882 | 71.0723 | 60.0195 | 25.7936
5 | C-55-T2ER-DM | 30N0022 | C-55-T2ER-DM | 2 Finger | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 11:45:56 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 0.8 | 1.7 | 0 | 8232 | 28 | 7564 | 44 | 3518 | 54 | 11753 | 65 |  | 943 |  | 13.55 | [35 empty] | 31.3413 | Econo 2F-open, tape around damper perimeter frame gaps, no compressor,--55/51, 53.5% inlet 52% outlet Meriam, ambient adjust code tester speed to match--otal static of run C-55-T2E-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 2F: with flow meter: new filter drier: with isolation ball valves: with code | 74.997 | 0.009 | 62.001 | 0.027 | 54.999 | 0.011 | 50.999 | 0.017 | 74.39 | 0.04 | 68.56 | 0.03 | 71.37 | 0.01 | 0.044 | 0.006 | 1.1905 | 0.0062 | 8232 | 28 | 3518 | 54 | 31.359 | 0.436 | [24 empty] | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 480 | 481 | 482 | 0.9 | 0.9 | 1 | 520 | 0.64 | 13.55 | 18.3 | [164 empty] | 68.07 | 0.35 | 69.63 | 0.23 | 68.81 | 0.06 | 69.54 | 0.21 | 68.34 | 0.16 | 68.9 | 0.19 | [32 empty] | 55.96 | 0.02 |  |  | 55.18 | 0.14 | 55.25 | 0.14 | 54.51 | 0.07 | 54.71 | 0.08 | 54.68 | 0.04 | 54.69 | 0.04 | [44 empty] | 55.18 | 0.06 | 54.92 | 0.05 | 74.64 | 0.03 | 74.62 | 0.03 | 74.46 | 0.03 | 74.78 | 0.04 | 74.71 | 0.04 | 74.77 | 0.04 | 74.7 | 0.04 | 61.33 | 0.03 | 61.56 | 0.04 | 61.31 | 0.05 | 60.53 | 0.07 | 60.26 | 0.03 | 62.43 | 0.09 | 60.77 | 0.07 | 60.94 | 0.07 | 61.59 | 0.07 | 73.82 | 0.05 | 70.33 | 0.13 | 71.36 | 0.11 | 66.42 | 0.13 | 73.38 | 0.04 | 74.02 | 0.03 | 72.92 | 0.05 | 71.37 | 0.14 | 73.01 | 0.04 | 73.93 | 0.03 | 73.2 | 0.03 | [84 empty] | Economizer test | 74.997 | 0.009 | 62.001 | 0.027 | 68.647 | 0.01 | 58.731 | 0.02 | 54.999 | 0.011 | 50.999 | 0.017 | 1183.9 | 3.1 | 1152.1 | 3 | 0.536 | 0.01 | -0.126 | 0.001 | 0.044 | 0.006 | 1.1905 | 0.0062 | 29.629 | 0.001 | 375 | 5 | 374.5 | 4.9 | 0.27703 | 319.1636 | 13.029 | 0.126 | 0.80887 | 5307.1163 | 72.5471 | 319.1694 | 1469.7574 | 3837.3589 | 0.0082832 | 25.7173 | 67.8381 | 13.0295 | 13.3847 | 0.006981 | 20.7771 | 0.008782 | 27.6094 | 0.0081951 | 25.4201 | 69.4719 | 59.1871 | 25.223
5 | C-55-T3ER-DM | 30N0023 | C-55-T3ER-DM | 3 Finger | Off | N/A |  | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 14:38:07 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.2 | 0.8 | 1.7 | 0 | 12185 | 55 | 11392 | 77 | 5034 | 101 | 17224 | 127 |  | 943 |  | 13.1 | [35 empty] | 46.1769 | Econo 3F-open, tape around damper perimeter frame gaps, no compressor,--55/51 ambient, 53.5% inlet 52% outlet Meriam, adjust code tester speed to match--match total static of run C-55-T3E-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 3F: with flow meter: new filter drier: with isolation ball valves: with code | 75.008 | 0.012 | 61.998 | 0.028 | 55.001 | 0.013 | 51.001 | 0.018 | 74.38 | 0.05 | 65.48 | 0.02 | 69.27 | 0.01 | 0.004 | 0.008 | 1.156 | 0.0094 | 12185 | 55 | 5034 | 101 | 46.184 | 0.678 | [24 empty] | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 478 | 478 | 478 | 0.9 | 0.9 | 1 | 500 | 0.63 | 13.1 | 18.1 | [164 empty] | 65.03 | 0.42 | 66.27 | 0.29 | 65.38 | 0.1 | 66.27 | 0.25 | 64.95 | 0.2 | 65.62 | 0.22 | [32 empty] | 56.21 | 0.03 |  |  | 55.39 | 0.15 | 55.69 | 0.21 | 54.66 | 0.1 | 55 | 0.12 | 54.83 | 0.07 | 54.83 | 0.07 | [44 empty] | 55.03 | 0.07 | 54.8 | 0.09 | 74.44 | 0.07 | 74.42 | 0.06 | 74.37 | 0.03 | 74.5 | 0.08 | 74.45 | 0.08 | 74.53 | 0.07 | 74.52 | 0.06 | 57.92 | 0.04 | 58.22 | 0.04 | 58.08 | 0.06 | 57.19 | 0.05 | 57.99 | 0.05 | 60.03 | 0.08 | 57.61 | 0.05 | 57.5 | 0.06 | 62.46 | 0.11 | 69.02 | 0.14 | 62.66 | 0.17 | 64.7 | 0.16 | 68.99 | 0.07 | 72.77 | 0.05 | 71.55 | 0.06 | 70.04 | 0.07 | 70.55 | 0.08 | 72.54 | 0.06 | 72.66 | 0.04 | 69.57 | 0.05 | [84 empty] | Economizer test | 75.008 | 0.012 | 61.998 | 0.028 | 65.486 | 0.012 | 57.066 | 0.021 | 55.001 | 0.013 | 51.001 | 0.018 | 1166.1 | 4.8 | 1135.8 | 4.7 | 0.491 | 0.008 | -0.063 | 0.001 | 0.004 | 0.008 | 1.156 | 0.0094 | 29.531 | 0.002 | 373 | 5 | 372.6 | 4.9 | 0.43445 | 493.446 | 13.03 | 0.063 | 0.83004 | 5259.6179 | 65.5162 | 493.4371 | 2272.2405 | 2987.3774 | 0.0080016 | 24.6569 | 64.656 | 13.0295 | 13.3025 | 0.0069816 | 20.7783 | 0.0087774 | 27.6071 | 0.0079299 | 24.3608 | 66.3807 | 57.5373 | 24.1587
5 | C-55-TCE-DM | 30N0024 | C-55-TCE-DM | closed | Off | N/A |  | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 1:56:07 | 10 Ton | 0:30:00 | 75/62 - 55/51 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 0.9 | 1.7 | 0 | 2635 | 13 | 2131 | 30 | 1266 | 35 | 3902 | 36 |  | 944 |  | 11.9 | [35 empty] | 10.6033 | Econo closed, tape around damper perimeter frame gaps, no compressor, 55/51 ambient,--53.5% inlet 52% outlet Meriam, adjust code tester speed to match total static of run C-55-TCE-DM-SPWCT-SS | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo fulley closed: with flow meter: new filter drier: with isolation ball valves: with code | 74.999 | 0.01 | 62 | 0.03 | 54.991 | 0.014 | 50.995 | 0.014 | 74.37 | 0.04 | 72.65 | 0.04 | 74.2 | 0 | 0.014 | 0.005 | 1.0892 | 0.0049 | 2635 | 13 | 1266 | 35 | 10.62 | 0.172 | [24 empty] | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 484 | 485 | 486 | 0.8 | 0.8 | 1 | 470 | 0.62 | 11.9 | 17.5 | [164 empty] | 72.64 | 0.05 | 73.72 | 0.03 | 73.51 | 0.03 | 73.43 | 0.04 | 73.25 | 0.04 | 72.99 | 0.05 | [32 empty] | 55.84 | 0.03 |  |  | 54.71 | 0.08 | 54.7 | 0.08 | 54.42 | 0.06 | 54.61 | 0.07 | 54.7 | 0.06 | 54.72 | 0.05 | [8 empty] | 54.47 | 0.08 | [34 empty] | 54.89 | 0.07 | 54.64 | 0.06 | 74.64 | 0.05 | 74.63 | 0.04 | 74.47 | 0.02 | 74.81 | 0.06 | 74.76 | 0.05 | 74.8 | 0.06 | 74.69 | 0.05 | 70.89 | 0.05 | 70.84 | 0.05 | 71.29 | 0.08 | 70.33 | 0.06 | 69.81 | 0.05 | 68.63 | 0.1 | 72.18 | 0.08 | 69.81 | 0.07 | 60.24 | 0.11 | 72.44 | 0.09 | 74.61 | 0.05 | 74.62 | 0.05 | 61.53 | 0.14 | 74.49 | 0.04 | 74.62 | 0.04 | 74.34 | 0.06 | 73.74 | 0.08 | 74.36 | 0.06 | 74.41 | 0.03 | 74.51 | 0.04 | [84 empty] | Economizer test | 74.999 | 0.01 | 62 | 0.03 | 72.866 | 0.005 | 60.908 | 0.025 | 54.991 | 0.014 | 50.995 | 0.014 | 1135.7 | 2.6 | 1097.5 | 2.5 | 0.598 | 0.009 | -0.209 | 0.002 | 0.014 | 0.005 | 1.0892 | 0.0049 | 29.601 | 0 | 368 | 5 | 367.1 | 4.9 | 0.065624 | 72.0221 | 13.029 | 0.209 | 0.81646 | 5049.5807 | 77.1029 | 72.0228 | 331.6662 | 4717.9145 | 0.0086626 | 27.1598 | 72.0495 | 13.0293 | 13.4946 | 0.0069808 | 20.7749 | 0.0087809 | 27.6087 | 0.0085726 | 26.8607 | 73.6889 | 61.347 | 26.6617
5 | C-55-TOER-DM | 30N0025 | C-55-TOER-DM | Fully open | Off | N/A |  | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/13/2014 | 20:37:37 | 10 Ton | 0:30:00 | 75/62 - 55/51 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 0.8 | 1.7 | 0 | 15988 | 116 | 15169 | 138 | 6508 | 111 | 22503 | 193 |  | 944 |  | 11.7 | [35 empty] | 60.4919 | Econo fully-open, tape around damper perimeter frame gaps, no compressor,--55/51 ambient, 53.5% inlet 52% outlet Meriam, adjust code tester speed to match--match total static of run C-55-TOE-DM-SPWCT-SSR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo fully open: with flow meter: new filter drier: with isolation ball valves: with code | 75.002 | 0.016 | 62 | 0.025 | 54.992 | 0.009 | 50.998 | 0.014 | 74.36 | 0.05 | 62.38 | 0.03 | 67.3 | 0.02 | 0.025 | 0.009 | 1.1268 | 0.0169 | 15988 | 116 | 6508 | 111 | 60.512 | 0.901 | [24 empty] | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 | [33 empty] | 481 | 481 | 481 | 0.8 | 0.8 | 1 | 470 | 0.63 | 11.7 | 17.5 | [164 empty] | 62.09 | 0.17 | 62.79 | 0.14 | 62.39 | 0.06 | 62.65 | 0.14 | 61.99 | 0.13 | 62.21 | 0.13 | [32 empty] | 56.56 | 0.02 |  |  | 55.67 | 0.11 | 55.8 | 0.17 | 54.73 | 0.09 | 54.9 | 0.08 | 54.67 | 0.07 | 54.69 | 0.07 | [44 empty] | 55.11 | 0.09 | 54.73 | 0.09 | 74.33 | 0.06 | 74.36 | 0.05 | 74.37 | 0.04 | 74.35 | 0.07 | 74.32 | 0.07 | 74.41 | 0.06 | 74.45 | 0.05 | 57.8 | 0.05 | 58.13 | 0.05 | 58.41 | 0.06 | 57.08 | 0.06 | 57.12 | 0.05 | 62.49 | 0.13 | 58.06 | 0.08 | 57.46 | 0.07 | 68.43 | 0.07 | 65.82 | 0.1 | 56.4 | 0.15 | 55.92 | 0.09 | 73.9 | 0.04 | 72.2 | 0.04 | 62 | 0.09 | 61.8 | 0.14 | 72.88 | 0.05 | 71.2 | 0.06 | 64.89 | 0.07 | 63.28 | 0.12 | [84 empty] | Economizer test | 75.002 | 0.016 | 62 | 0.025 | 62.366 | 0.019 | 55.388 | 0.022 | 54.992 | 0.009 | 50.998 | 0.014 | 1151.1 | 8.7 | 1121.6 | 8.5 | 0.416 | 0.004 | -0.024 | 0.001 | 0.025 | 0.009 | 1.1268 | 0.0169 | 29.416 | 0.001 | 372 | 5 | 371.5 | 5.2 | 0.58851 | 660.068 | 13.029 | 0.024 | 0.86187 | 5223.7705 | 54.8146 | 660.0758 | 3039.6514 | 2184.1191 | 0.0077339 | 23.6332 | 61.5041 | 13.0293 | 13.2215 | 0.0069822 | 20.7766 | 0.0087802 | 27.6086 | 0.0076795 | 23.3284 | 63.3744 | 55.8909 | 23.1187
5 | C-75629575-T1E3 | 30N0026 | C-75629575-T1E3 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/11/2014 | 16:39:59 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 15 | 0 | 19299 | 73 | 18440 | 105 | 1127 | 70 | 20427 | 101 |  | 939 |  | 7.38 |  | 112.07 | 0.01 | 43.3 | [31 empty] | 5.8025 | 1 Finger open damper, tape around damper perimiter frame gaps, unsealed cab,--53.5% inlet 52% outlet Meriam, adjust code tester speed to match total static--of run C-T1EM3-SPWCT-SR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: with economizer: with flow meter: new filter drier: with isolation ball valves: with code | 74.996 | 0.01 | 61.999 | 0.021 | 95.002 | 0.014 | 75 | 0.018 | 74.41 | 0.07 | 59.27 | 0.05 | 65.41 | 0.05 | 0.01 | 0.006 | 0.7755 | 0.0059 | 19299 | 73 | 1127 | 70 | 6.142 | 0.034 |  |  | 10.8304 |  |  |  | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2966.3 | 5.7 | 2966.3 | 5.7 | 2966.3 | 5.7 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2773.6 | 5.1 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 168.9 | 0.8 | 23 |  | 3323.7 | 484 | 485 | 484 | 0.7 | 0.7 | 0.7 | 380 | 0.62 | 7.38 | 15.3 | [12 empty] | 263.72 | 0.19 | 181.44 | 0.03 | 120.92 | 0.05 | 60.51 | 0.05 | 243.8 | 0.22 | 103.46 | 0.05 | 115.16 | 0.07 | 11.7 | 0.09 | 77.31 | 0.06 | 63.98 | 0.06 | 45.47 | 0.04 |  |  | 78.01 | 0.03 | 67.56 | 0.06 | 45.92 | 0.02 | 21.64 | 0.06 | 520.89 | 0.54 | 40.57 | 0.02 | 36022 | 46 | 37245 | 42 | [22 empty] | 247.45 | 0.23 | 104.3 | 0.04 | 116.24 | 0.07 | 11.93 | 0.07 | 246.06 | 0.21 | 115.83 | 0.06 | 12.54 | 0.07 | 18.51 | 0.07 | [74 empty] | 58.53 | 0.07 | 60.32 | 0.05 | 59.81 | 0.1 | 60.14 | 0.03 | 59.41 | 0.1 | 59.42 | 0.05 | [32 empty] | 104.07 | 0.06 |  |  | 94.69 | 0.08 | 94.63 | 0.09 | 94.85 | 0.06 | 94.9 | 0.07 | 94.89 | 0.06 | 94.91 | 0.06 | [12 empty] | 103.29 | 0.06 | [30 empty] | 94.96 | 0.08 | 95.26 | 0.08 | 74.74 | 0.05 | 74.72 | 0.04 | 74.47 | 0.05 | 74.9 | 0.06 | 74.9 | 0.06 | 74.87 | 0.05 | 74.68 | 0.05 | 87.16 | 0.04 | 86.45 | 0.04 | 86.2 | 0.06 | 85.62 | 0.07 | 86.12 | 0.05 | 86.46 | 0.07 | 86.35 | 0.08 | 86.03 | 0.08 | 89.46 | 0.06 | 75.69 | 0.08 | 75.85 | 0.07 | 75.29 | 0.05 | 81.39 | 0.16 | 75.8 | 0.05 | 75.06 | 0.05 | 75.55 | 0.04 | 76.24 | 0.09 | 74.95 | 0.04 | 74.87 | 0.04 | 74.96 | 0.05 | [84 empty] | C-55-T1ER-DM | 74.996 | 0.01 | 61.999 | 0.021 | 59.146 | 0.015 | 55.908 | 0.02 | 95.002 | 0.014 | 75 | 0.018 | 1133.5 | 4.3 | 1085.3 | 4.2 | 0.544 | 0.005 | -0.159 | 0.002 | 0.01 | 0.006 | 0.7755 | 0.0059 | 28.861 | 0.001 | 3326 | 9 | 358.2 | 5.6 | 0.1966 | 226.1293 | 13.029 | 0.164 | 0.79387 | 5172.555 | 69.3608 | 231.6258 | 985.6445 | 4186.9106 | 0.0097602 | 29.6181 | 58.3521 | 14.1 | 13.1482 | 0.01392 | 38.1571 | 0.0087809 | 27.608 | 0.008742 | 23.6998 | 78.837 | 64.7791 | 23.5062 | 31614.1312 | 25430.2075 | 2967.8 | 0.3204 | 30628.3229 | 24444.3991 | 9.2088 | 0.21942 | -6.1119 | -20.4849 | 52.5939 | 31614.1312 | 20214.9988 | 1001.458 | 10397.6744 | 31614.1312 | 100%
5 | C-75629575-T2E3-1 | 30N0027 | C-75629575-T2E3-1 | 2 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/11/2014 | 23:42:30 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 15 | 0 | 17224 | 33 | 16415 | 67 | -1803 | 74 | 15419 | 75 |  | 939 |  | 7.5 |  | 112.64 | 0.01 | 58.01 | [31 empty] | 5.1724 | Factory charge, 3 turns, Econo 2 Fingers open damper, tape around damper perimiter frame gaps, unsealed cab,--cab, 53.5% inlet 52% outlet Meriam, adjust code tester speed to match total static of run C-T2EM3-SPWCT-SR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 2F: with flow meter: new filter drier: with isolation ball valves: with code | 75.003 | 0.013 | 62 | 0.023 | 94.998 | 0.007 | 75.002 | 0.025 | 74.41 | 0.05 | 61.02 | 0.03 | 66.44 | 0.02 | 0.008 | 0.002 | 0.7908 | 0.0024 | 17224 | 33 | -1803 | 74 | 4.63 | 0.025 |  |  | 11.0282 |  |  |  | 229.7 | 0.9 | 229.7 | 0.9 | 229.7 | 0.9 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2967.8 | 5.1 | 2967.8 | 5.1 | 2967.8 | 5.1 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2774.8 | 4.6 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 169.7 | 0.8 | 23 |  | 3328.5 | 487 | 488 | 489 | 0.7 | 0.7 | 0.8 | 380 | 0.63 | 7.5 | 15.4 | [12 empty] | 264.75 | 0.17 | 182.86 | 0.04 | 121.25 | 0.05 | 61.61 | 0.06 | 244.71 | 0.22 | 103.14 | 0.04 | 115.47 | 0.07 | 12.33 | 0.08 | 78.55 | 0.04 | 67.55 | 0.04 | 46.35 | 0.03 |  |  | 79.31 | 0.02 | 70.18 | 0.04 | 46.83 | 0.01 | 23.35 | 0.04 | 525.9 | 0.51 | 40.47 | 0.01 | 36724 | 45 | 37956 | 41 | [22 empty] | 248.41 | 0.21 | 103.98 | 0.04 | 116.56 | 0.06 | 12.59 | 0.07 | 247 | 0.2 | 116.15 | 0.06 | 13.13 | 0.07 | 21.2 | 0.05 | [74 empty] | 60.61 | 0.06 | 61.97 | 0.07 | 61.76 | 0.09 | 61.74 | 0.06 | 61.49 | 0.06 | 61.12 | 0.04 | [32 empty] | 103.7 | 0.05 |  |  | 94.67 | 0.08 | 94.64 | 0.08 | 94.86 | 0.06 | 94.91 | 0.08 | 94.89 | 0.08 | 94.91 | 0.07 | [8 empty] | 94.85 | 0.07 |  |  | 103.02 | 0.05 | [30 empty] | 94.79 | 0.09 | 95.12 | 0.08 | 74.65 | 0.07 | 74.68 | 0.05 | 74.5 | 0.05 | 74.78 | 0.09 | 74.8 | 0.09 | 74.79 | 0.09 | 74.65 | 0.06 | 89.75 | 0.07 | 88.87 | 0.05 | 88.99 | 0.05 | 89.26 | 0.06 | 88.87 | 0.03 | 87.94 | 0.08 | 89.83 | 0.07 | 89.49 | 0.08 | 88.79 | 0.08 | 76.15 | 0.06 | 80.1 | 0.14 | 78.78 | 0.13 | 83.16 | 0.14 | 75.83 | 0.04 | 75.63 | 0.04 | 75.78 | 0.06 | 77.62 | 0.14 | 75.51 | 0.06 | 75.09 | 0.04 | 75.75 | 0.04 | [84 empty] | C-55-T2ER-DM | 75.003 | 0.013 | 62 | 0.023 | 60.959 | 0.007 | 57.484 | 0.012 | 94.998 | 0.007 | 75.002 | 0.025 | 1140.3 | 1.7 | 1099.8 | 1.7 | 0.516 | 0.003 | -0.12 | 0.001 | 0.008 | 0.002 | 0.7908 | 0.0024 | 29.15 | 0.003 | 3330 | 8 | 361 | 5.6 | 0.27703 | 319.1636 | 13.029 | 0.126 | 0.80719 | 5183.899 | 66.6697 | 324.0193 | 1378.8173 | 3805.0817 | 0.010148 | 30.4148 | 60.1518 | 14.0999 | 13.1982 | 0.013923 | 38.1591 | 0.0087799 | 27.6086 | 0.0092507 | 24.6956 | 80.3577 | 65.8367 | 24.4985 | 30669.4405 | 25138.925 | 2969 | 0.3304 | 29664.8912 | 24134.3757 | 8.9084 | 0.22698 | -5.9163 | -20.2059 | 54.2188 | 30669.4405 | 15100.7882 | 1021.4417 | 14547.2107 | 30669.4405 | 100%
5 | C-75629575-T3E3 | 30N0028 | C-75629575-T3E3 | 3 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/12/2014 | 2:32:39 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 15.2 | 0 | 14084 | 30 | 13373 | 60 | -6256 | 72 | 7822 | 80 |  | 939 |  | 8.3 |  | 113.19 | 0.01 | 79.15 | [31 empty] | 4.2092 | Factory charge, 3 turns, Econo 3 Fingers open damper, tape around damper perimiter frame gaps, unsealed cab,--cab, 53.5% inlet 52% outlet Meriam, adjust code tester speed to match total static of run C-T3EM3-SPWCT-SR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo open 3F: with flow meter: new filter drier: with isolation ball valves: with code | 74.994 | 0.007 | 61.999 | 0.021 | 95 | 0.008 | 75.001 | 0.012 | 74.42 | 0.05 | 63.57 | 0.05 | 68.17 | 0.02 | 0.024 | 0.005 | 0.8191 | 0.0035 | 14084 | 30 | -6256 | 72 | 2.338 | 0.025 |  |  | 11.2134 |  |  |  | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2981 | 6.4 | 2981 | 6.4 | 2981 | 6.4 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.7 | 0 | 1.7 | 0 | 1.7 | 0 |  | 227.8 | 1 | 227.8 | 1 | 227.8 | 1 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2787.8 | 6.1 | [9 empty] | 228.3 | 1 | 0.7 | 0 | 170.1 | 0.9 | 23 |  | 3344.8 | 488 | 489 | 490 | 0.8 | 0.7 | 0.9 | 410 | 0.62 | 8.3 | 15.8 | [12 empty] | 266.27 | 0.19 | 184.64 | 0.03 | 121.69 | 0.05 | 62.95 | 0.06 | 246.05 | 0.22 | 102.82 | 0.05 | 115.89 | 0.07 | 13.07 | 0.08 | 80.16 | 0.05 | 71.1 | 0.06 | 47.4 | 0.03 |  |  | 80.86 | 0.03 | 73.12 | 0.05 | 47.84 | 0.02 | 25.27 | 0.06 | 532.28 | 0.55 | 40.37 | 0.02 | 37520 | 47 | 38762 | 43 | [22 empty] | 249.83 | 0.21 | 103.73 | 0.06 | 117 | 0.06 | 13.27 | 0.06 | 248.39 | 0.22 | 116.58 | 0.06 | 13.91 | 0.07 | 23.7 | 0.07 | [74 empty] | 63.18 | 0.28 | 64.04 | 0.07 | 63.91 | 0.19 | 63.9 | 0.11 | 63.98 | 0.27 | 63.6 | 0.15 | [32 empty] | 103.3 | 0.05 |  |  | 94.38 | 0.15 | 94.19 | 0.15 | 94.72 | 0.09 | 94.64 | 0.11 | 94.79 | 0.07 | 94.82 | 0.07 | [8 empty] | 94.76 | 0.07 |  |  | 102.66 | 0.07 | [30 empty] | 94.49 | 0.07 | 94.88 | 0.07 | 74.47 | 0.05 | 74.57 | 0.03 | 74.5 | 0.03 | 74.48 | 0.06 | 74.52 | 0.06 | 74.55 | 0.05 | 74.54 | 0.04 | 92.59 | 0.04 | 92.06 | 0.04 | 91.89 | 0.05 | 92.41 | 0.05 | 91.97 | 0.04 | 90.54 | 0.09 | 93.38 | 0.06 | 93.22 | 0.07 | 88.77 | 0.11 | 80.85 | 0.12 | 90.04 | 0.13 | 86.05 | 0.19 | 82.49 | 0.09 | 75.96 | 0.04 | 76.24 | 0.04 | 75.94 | 0.04 | 79.79 | 0.09 | 75.58 | 0.03 | 75.82 | 0.03 | 76.81 | 0.04 | [84 empty] | C-55-T3ER-DM | 74.994 | 0.007 | 61.999 | 0.021 | 63.581 | 0.016 | 59.76 | 0.016 | 95 | 0.008 | 75.001 | 0.012 | 1160 | 2.5 | 1119.1 | 2.4 | 0.468 | 0.007 | -0.071 | 0.001 | 0.024 | 0.005 | 0.8191 | 0.0035 | 29.286 | 0.002 | 3346 | 9 | 363.9 | 5.5 | 0.43445 | 493.446 | 13.03 | 0.063 | 0.81965 | 5244.5849 | 61.529 | 544.9224 | 2318.8317 | 2925.7533 | 0.011054 | 32.2726 | 62.7614 | 14.0999 | 13.2708 | 0.013922 | 38.1581 | 0.0087814 | 27.608 | 0.010038 | 26.1927 | 83.8854 | 68.2118 | 25.9923 | 32937.5848 | 26588.8491 | 2982.1 | 0.30901 | 31905.5926 | 25556.8568 | 9.5354 | 0.23266 | -6.2803 | -21.124 | 56.3565 | 32937.5848 | 7422.863 | 1050.8478 | 24463.874 | 32937.5848 | 100%
5 | C-75629575-TE3 | 30N0029 | C-75629575-TE3 | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/11/2014 | 14:48:22 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 15 | 0 | 21752 | 40 | 20819 | 88 | 4239 | 61 | 25995 | 73 |  | 940 |  | 7.5 |  | 111.06 | 0.06 | 25.76 | [31 empty] | 7.8535 | Closed damper, tape around damper perimiter frame gaps, 53.5% inlet 52% outlet--Meriam, adjust code tester speed to match total static of run C-TEM3-SPWCT-SR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: with economizer: with flow meter: new filter drier: with isolation ball valves: with code | 74.994 | 0.015 | 62 | 0.024 | 95 | 0.014 | 74.999 | 0.02 | 74.35 | 0.08 | 57.32 | 0.05 | 64 | 0.02 | 0.034 | 0.003 | 0.7712 | 0.0026 | 21752 | 40 | 4239 | 61 | 7.854 | 0.029 |  |  | 10.5792 |  |  |  | 229.7 | 0.9 | 229.7 | 0.9 | 229.7 | 0.9 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2950 | 5.7 | 2950 | 5.7 | 2950 | 5.7 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 |  | 227.8 | 1 | 227.8 | 1 | 227.8 | 1 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2757.6 | 5.3 | [9 empty] | 228.3 | 1 | 0.7 | 0 | 169 | 0.9 | 23 |  | 3308.3 | 482 | 482 | 482 | 0.7 | 0.7 | 0.8 | 380 | 0.62 | 7.5 | 15.4 | [12 empty] | 261.77 | 0.19 | 178.19 | 0.04 | 120.37 | 0.06 | 57.81 | 0.07 | 242.05 | 0.23 | 103.59 | 0.06 | 114.64 | 0.07 | 11.05 | 0.09 | 75.3 | 0.05 | 57.72 | 0.3 | 44.18 | 0.03 |  |  | 75.88 | 0.02 | 63.2 | 0.15 | 44.55 | 0.02 | 18.64 | 0.15 | 514.43 | 0.54 | 40.61 | 0.02 | 35017 | 59 | 36240 | 56 | [22 empty] | 245.65 | 0.22 | 104.38 | 0.05 | 115.71 | 0.07 | 11.33 | 0.07 | 244.23 | 0.22 | 115.29 | 0.07 | 11.68 | 0.08 | 13.54 | 0.31 | [74 empty] | 56.37 | 0.05 | 58.47 | 0.09 | 57.74 | 0.11 | 58.37 | 0.07 | 57.23 | 0.08 | 57.58 | 0.04 | [18 empty] | 103.59 | 0.06 | [12 empty] | 104.33 | 0.05 |  |  | 94.65 | 0.07 | 94.66 | 0.06 | 94.78 | 0.05 | 94.79 | 0.08 | 94.7 | 0.08 | 94.73 | 0.07 | [12 empty] | 103.61 | 0.06 | [30 empty] | 94.75 | 0.08 | 95.03 | 0.07 | 74.53 | 0.09 | 74.54 | 0.07 | 74.41 | 0.08 | 74.61 | 0.1 | 74.62 | 0.1 | 74.63 | 0.09 | 74.52 | 0.09 | 78.99 | 0.07 | 78.76 | 0.06 | 78.29 | 0.08 | 78.45 | 0.1 | 78.49 | 0.06 | 80.41 | 0.09 | 76.82 | 0.09 | 78.24 | 0.09 | 91.19 | 0.08 | 78.42 | 0.1 | 75.2 | 0.1 | 75.17 | 0.1 | 88.24 | 0.21 | 75.25 | 0.09 | 75.08 | 0.08 | 74.93 | 0.09 | 76.4 | 0.15 | 74.69 | 0.08 | 74.74 | 0.07 | 74.86 | 0.07 | [84 empty] | C-55-TCE-DM | 74.994 | 0.015 | 62 | 0.024 | 57.201 | 0.011 | 54.125 | 0.02 | 95 | 0.014 | 74.999 | 0.02 | 1128.2 | 1.9 | 1085.1 | 1.8 | 0.575 | 0.005 | -0.215 | 0.002 | 0.034 | 0.003 | 0.7712 | 0.0026 | 28.884 | 0.001 | 3310 | 8 | 358.7 | 5.6 | 0.065624 | 72.0221 | 13.029 | 0.209 | 0.78488 | 5169.4834 | 73.2998 | 75.9914 | 323.3697 | 4846.1137 | 0.0091034 | 28.2685 | 56.4161 | 14.0999 | 13.0945 | 0.01392 | 38.1562 | 0.008782 | 27.6087 | 0.0081756 | 22.6102 | 76.2564 | 62.9308 | 22.4189 | 30239.2035 | 24615.3793 | 2951.3 | 0.3331 | 29265.1325 | 23641.3084 | 8.8414 | 0.21907 | -5.8496 | -19.8403 | 50.8505 | 30239.2035 | 25839.9705 | 988.5139 | 3410.7191 | 30239.2035 | 100%
5 | C-75629575-TOE3 | 30N0030 | C-75629575-TOE3 | Fully open | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/12/2014 | 10:06:20 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 15 | 0 | 10582 | 114 | 9950 | 69 | -10102 | 216 | 470 | 182 |  | 939 |  | 7.3 |  | 111.11 | 0.13 | 98.38 | [31 empty] | 3.1759 | Factory charge, 3 turns, Econo Fully open damper, tape around damper--perimiter frame gaps, unsealed cab, cab, 53.5% inlet 52% outlet Meriam,--adjust code tester speed to match total static of run C-TOEM3-SPWCT-SR | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: Econo Fully open: with flow meter: new filter drier: with isolation ball valves: with code | 75.001 | 0.015 | 62.004 | 0.033 | 95.001 | 0.015 | 75 | 0.02 | 74.51 | 0.04 | 65.93 | 0.08 | 69.74 | 0.02 | 0.001 | 0.012 | 0.7475 | 0.0169 | 10582 | 114 | -10102 | 216 | 0.149 | 0.051 |  |  | 10.9799 |  |  |  | 229.7 | 0.9 | 229.7 | 0.9 | 229.7 | 0.9 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2973.3 | 5.2 | 2973.3 | 5.2 | 2973.3 | 5.2 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2779.4 | 4.8 | [9 empty] | 228.3 | 0.9 | 0.8 | 0 | 170.9 | 0.9 | 23 |  | 3307.6 | 480 | 480 | 480 | 0.7 | 0.7 | 0.8 | 390 | 0.63 | 7.3 | 15.3 | [12 empty] | 266.03 | 0.23 | 183.28 | 0.09 | 121.67 | 0.06 | 61.61 | 0.1 | 245.84 | 0.24 | 102.54 | 0.07 | 115.87 | 0.07 | 13.33 | 0.08 | 80.18 | 0.07 | 59.7 | 0.72 | 47.51 | 0.04 |  |  | 80.88 | 0.05 | 71.79 | 0.24 | 47.95 | 0.03 | 23.84 | 0.22 | 533.73 | 0.58 | 40.28 | 0.02 | 36585 | 92 | 37805 | 94 | [22 empty] | 249.59 | 0.24 | 103.53 | 0.06 | 116.97 | 0.07 | 13.44 | 0.07 | 248.17 | 0.24 | 116.55 | 0.07 | 14.22 | 0.07 | 12.19 | 0.7 | [74 empty] | 65.24 | 0.35 | 67.26 | 0.1 | 66.45 | 0.38 | 67.02 | 0.08 | 66.36 | 0.46 | 66.42 | 0.16 | [32 empty] | 103.09 | 0.06 |  |  | 93.8 | 0.25 | 93.43 | 0.26 | 94.46 | 0.16 | 94.55 | 0.17 | 94.79 | 0.12 | 94.78 | 0.12 | [8 empty] | 94.72 | 0.11 |  |  | 102.33 | 0.07 | [30 empty] | 94.93 | 0.09 | 95.35 | 0.09 | 74.89 | 0.04 | 74.86 | 0.03 | 74.6 | 0.03 | 75.09 | 0.06 | 75.08 | 0.06 | 75.05 | 0.06 | 74.84 | 0.04 | 93.35 | 0.08 | 92.63 | 0.08 | 92.1 | 0.09 | 93 | 0.08 | 92.56 | 0.07 | 88.88 | 0.14 | 92.37 | 0.08 | 93.36 | 0.08 | 81.4 | 0.12 | 84.5 | 0.09 | 94.01 | 0.21 | 94.5 | 0.11 | 75.71 | 0.02 | 76.92 | 0.03 | 86.45 | 0.1 | 85.71 | 0.09 | 76.41 | 0.03 | 77.33 | 0.04 | 82.94 | 0.06 | 84.51 | 0.08 | [84 empty] | C-55-TOER-DM | 75.001 | 0.015 | 62.004 | 0.033 | 65.899 | 0.062 | 61.819 | 0.056 | 95.001 | 0.015 | 75 | 0.02 | 1103.9 | 12.5 | 1071.3 | 12.2 | 0.408 | 0.004 | -0.028 | 0.001 | 0.001 | 0.012 | 0.7475 | 0.0169 | 29.582 | 0.001 | 3332 | 9 | 357.3 | 5.8 | 0.58851 | 660.068 | 13.029 | 0.024 | 0.87576 | 4966.636 | 51.3495 | 741.6776 | 3156.0889 | 1810.547 | 0.012048 | 34.3128 | 65.0232 | 14.0999 | 13.3358 | 0.013921 | 38.1571 | 0.008783 | 27.6115 | 0.010819 | 27.6117 | 87.7532 | 70.6844 | 27.3973 | 34346.7336 | 27093.9909 | 2974.7 | 0.29559 | 33302.5246 | 26049.7819 | 9.9948 | 0.2274 | -6.9155 | -22.73 | 58.3332 | 34346.7336 | -0.90277 | 1064.7977 | 33282.8387 | 34346.7336 | 100%
5 | C-55-CE | 30N0052 | C-55-CE | closed | Off | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 2 | 6/17/2015 | 0:48:14 | 10 Ton | 0:10:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 1.4 | 2.2 | 0 | 5674 | 17 | 5319 | 69 | 2708 | 61 | 8385 | 69 |  | 942 | [37 empty] | 17.7273 | . | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed:installed economizer. No compressor; | 74.96 | 0.075 | 61.998 | 0.022 | 54.999 | 0.004 | 51.006 | 0.017 | 74.45 | 0.09 | 70.13 | 0.05 | 72.67 | 0.16 | 0.011 | 0.003 | 0.7915 | 0.0029 | 5674 | 17 | 2708 | 61 | 17.725 | 0.246 | [6 empty] | 230.1 | 1.4 | 230.1 | 1.4 | 230.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0.2 | -0.1 | 0.2 | -0.1 | 0.2 | 229.8 | 1.4 | 229.8 | 1.4 | 229.8 | 1.4 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | 473 | [10 empty] | 230.1 | 1.4 | 0 | 0 | 98.28 | 0.04 | 55.46 | 0.02 | 58 | 0.02 | 2.55 | 0.03 | 98.31 | 0.05 | 57.49 | 0.03 | 58.02 | 0.03 | -0.53 | 0.02 | 98.17 | 0.06 | 58.23 | 0.05 | 57.94 | 0.04 | -0.28 | 0.09 | 99.12 | 0.05 | 56.22 | 0.09 | 58.47 | 0.03 |  |  | 98.97 | 0.04 | 56.18 | 0.09 | 58.38 | 0.02 | -2.2 | 0.08 | [44 empty] | -2.23 | 0.08 | [74 empty] | 69.96 | 0.05 | 70.07 | 0.05 | 70.15 | 0.05 | 70.19 | 0.03 | 69.99 | 0.05 | 70.05 | 0.04 | [6 empty] | 56.63 | 0.06 | [78 empty] | 61.6 | 0.09 | 62.63 | 0.1 | 57.45 | 0.03 | 54.65 | 0.04 | 56.01 | 0.09 | 73.71 | 0.09 | 74.03 | 0.08 | 74.61 | 0.06 | 74.7 | 0.06 | 74.89 | 0.06 | 74.88 | 0.06 | 74.93 | 0.05 | [26 empty] | 57.71 | 0.05 | [12 empty] | 74.49 | 0.05 | [34 empty] | 54.78 | 0.05 | 59.83 | 0.22 | 67.54 | 0.39 | 72.61 | 0.04 | 62.88 | 0.18 | 68.85 | 0.11 | 72.82 | 0.12 | 74.82 | 0.04 | 74.41 | 0.03 | 74.37 | 0.07 | 65.87 | 0.23 | 75.06 | 0.04 | 74.51 | 0.06 | 68.1 | 0.3 | 59.52 | 0.15 | 74.6 | 0.05 | 64.66 | 0.41 | 54.88 | 0.09 | [12 empty] | Economizer test | 74.96 | 0.075 | 61.998 | 0.022 | 70.344 | 0.074 | 59.582 | 0.016 | 54.999 | 0.004 | 51.006 | 0.017 | 1145.3 | 2.2 | 1096.7 | 2 | 0.56 | 0.002 | -0.184 | 0.001 | 0.011 | 0.003 | 0.7915 | 0.0029 | 29.243 | 0.001 | 473 | 5 | 472.5 | 5.2 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.1122 | 5117.2507 | 72.1508 | 192.6235 | 887.0183 | 4230.2324 | 0.0084761 | 26.4245 | 69.2318 | 13.0295 | 13.4287 | 0.0069848 | 20.7812 | 0.0087888 | 27.6078 | 0.0083244 | 25.9747 | 71.5094 | 60.2572 | 25.7036
5 | C-EB10-55-CE | 30N0053 | C-EB10-55-CE | closed | Off | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 10 | CUST 2 | 6/18/2015 | 11:17:04 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.2 | 1.1 | 2.1 | 0 | 5385 | 22 | 5147 | 47 | 2454 | 70 | 7842 | 80 |  | 943 | [37 empty] | 16.6497 | 10% evaporator coil block, economizer closed (2V), no compressor, factory charge (5.5 lbs)--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley--3 turns open from fully closed, adjust code tester speed to match total st | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.;with outlet hose, with code tester, 6" evap coil blockage | 74.991 | 0.013 | 61.992 | 0.038 | 54.992 | 0.008 | 50.999 | 0.019 | 74.57 | 0.06 | 70.33 | 0.06 | 72.34 | 0.01 | 0.019 | 0.003 | 1.0687 | 0.0033 | 5385 | 22 | 2454 | 70 | 16.644 | 0.245 | [6 empty] | 230.2 | 1.1 | 230.2 | 1.1 | 230.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0.2 | 229.8 | 1.1 | 229.8 | 1.1 | 229.8 | 1.1 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | [11 empty] | 230.2 | 1.1 | 0 | 0 | 99.76 | 0.04 | 55.99 | 0.03 | 58.8 | 0.02 | 2.81 | 0.02 | 100.23 | 0.02 | 58.77 | 0.03 | 59.06 | 0.01 | -0.29 | 0.03 | 100.06 | 0.04 | 59.4 | 0.04 | 58.97 | 0.02 | -0.43 | 0.06 | 100.84 | 0.02 | 57.91 | 0.06 | 59.39 | 0.01 |  |  | 100.17 | 0.03 | 57.97 | 0.04 | 59.03 | 0.02 | -1.05 | 0.03 | [44 empty] | -1.48 | 0.05 | [74 empty] | 70.21 | 0.05 | 70.28 | 0.06 | 70.37 | 0.05 | 70.53 | 0.05 | 70.29 | 0.05 | 70.26 | 0.06 |  |  |  |  | 59.55 | 0.05 | 58.41 | 0.06 | [10 empty] | 59.4 | 0.04 | [66 empty] | 67.42 | 0.14 | 69.25 | 0.15 | 58.85 | 0.05 | 54.44 | 0.05 | 56 | 0.13 | 74.28 | 0.07 | 74.39 | 0.05 | 74.76 | 0.04 | 74.83 | 0.04 | 74.96 | 0.04 | 74.98 | 0.04 | 74.99 | 0.03 | [40 empty] | 74.51 | 0.03 | [34 empty] | 54.54 | 0.06 | 63.45 | 0.91 | 59.53 | 0.2 | 71.37 | 0.05 | 69.63 | 0.72 | 75.23 | 0.03 | 74.4 | 0.06 | 70.69 | 0.21 | 74.62 | 0.04 | 66.98 | 0.2 | 73.56 | 0.22 |  |  | 74.35 | 0.11 | 74.42 | 0.09 | 69.14 | 0.82 | 65.23 | 0.14 | 61.84 | 0.45 | 54.97 | 0.1 | [12 empty] | Economizer test | 74.991 | 0.013 | 61.992 | 0.038 | 70.548 | 0.014 | 59.706 | 0.024 | 54.992 | 0.008 | 50.999 | 0.019 | 1130.5 | 1.7 | 1082 | 1.7 | 0.555 | 0.001 | -0.195 | 0.001 | 0.019 | 0.003 | 1.0687 | 0.0033 | 29.211 | 0.001 | 471 | 5 | 470.6 | 5 | 0.16566 | 179.2423 | 13.029 | 0.195 | 1.1264 | 5049.0908 | 70.5481 | 179.2444 | 825.4208 | 4223.6699 | 0.0084841 | 26.4871 | 69.4216 | 13.0293 | 13.4341 | 0.0069827 | 20.7772 | 0.0087775 | 27.603 | 0.0083542 | 26.057 | 71.7305 | 60.3518 | 25.7824
5 | C-EB20-55-CE | 30N0054 | C-EB20-55-CE | closed | Off | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 20 | CUST 2 | 6/18/2015 | 12:58:46 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 1 | 2.1 | 0 | 5090 | 14 | 4844 | 55 | 2518 | 73 | 7611 | 72 |  | 944 | [37 empty] | 16.2976 | 20% evaporator coil block, economizer closed (2V), no compressor, factory charge (5.5 lbs)--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley--3 turns open from fully closed, adjust code tester speed to match total st | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.;with outlet duct, with code tester, 9" evap coil blockage | 74.971 | 0.023 | 61.988 | 0.026 | 54.995 | 0.005 | 51.001 | 0.02 | 74.53 | 0.04 | 70.48 | 0.05 | 72.69 | 0.05 | 0.012 | 0.002 | 1.0405 | 0.0031 | 5090 | 14 | 2518 | 73 | 16.309 | 0.23 | [6 empty] | 230.1 | 1 | 230.1 | 1 | 230.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0.2 | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | [11 empty] | 230.2 | 1 | 0 | 0 | 97.73 | 0.02 | 55.67 | 0.01 | 57.68 | 0.01 | 2.02 | 0.02 | 97.77 | 0.05 | 56.95 | 0.03 | 57.71 | 0.02 | -0.76 | 0.04 | 98.02 | 0.04 | 58.89 | 0.05 | 57.84 | 0.02 | -1.04 | 0.05 | 98.85 | 0.03 | 55.33 | 0.02 | 58.3 | 0.02 |  |  | 97.86 | 0.02 | 56.37 | 0.03 | 57.76 | 0.01 | -1.4 | 0.02 | [44 empty] | -2.98 | 0.03 | [74 empty] | 70.25 | 0.03 | 70.41 | 0.04 | 70.48 | 0.03 | 70.6 | 0.02 | 70.42 | 0.04 | 70.38 | 0.04 |  |  |  |  | 58.26 | 0.05 | 56.24 | 0.05 | [10 empty] | 58.89 | 0.05 | [66 empty] | 61 | 0.09 | 62.03 | 0.09 | 56.94 | 0.04 | 54.6 | 0.03 | 56.13 | 0.12 | 74.29 | 0.05 | 74.41 | 0.03 | 74.81 | 0.03 | 74.86 | 0.02 | 74.98 | 0.02 | 74.99 | 0.02 | 74.99 | 0.03 | [40 empty] | 74.49 | 0.03 | [34 empty] | 54.67 | 0.05 | 69.59 | 0.43 | 60.49 | 0.15 | 72.86 | 0.07 | 70.54 | 0.29 | 75.18 | 0.02 | 73.43 | 1.39 | 71.65 | 0.14 | 74.61 | 0.03 | 67.98 | 0.13 | 74.38 | 0.08 | 66.06 | 0.14 | 74.5 | 0.05 | 74.54 | 0.03 | 69.9 | 0.37 | 68.96 | 0.26 | 65.5 | 0.3 | 54.99 | 0.1 | [12 empty] | Economizer test | 74.971 | 0.023 | 61.988 | 0.026 | 70.718 | 0.02 | 59.741 | 0.013 | 54.995 | 0.005 | 51.001 | 0.02 | 1115.9 | 1.7 | 1066.9 | 1.6 | 0.541 | 0.001 | -0.19 | 0.001 | 0.012 | 0.002 | 1.0405 | 0.0031 | 29.202 | 0.001 | 467 | 5 | 466.1 | 4.9 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1365 | 4982.3397 | 67.8088 | 166.265 | 765.646 | 4216.6938 | 0.0085035 | 26.552 | 69.5815 | 13.0294 | 13.4383 | 0.006983 | 20.7783 | 0.0087796 | 27.6004 | 0.0083361 | 26.0786 | 71.9097 | 60.4485 | 25.8017
5 | C-EB35-55-CE | 30N0055 | C-EB35-55-CE | closed | Off | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 35 | CUST 2 | 6/18/2015 | 14:08:38 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 1 | 2.1 | 0 | 4900 | 13 | 4667 | 54 | 2456 | 59 | 7358 | 67 |  | 945 | [37 empty] | 15.961 | 35% evaporator coil block, economizer closed (2V), no compressor, factory charge--(5.5 lbs) unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code tester speed to match--total s | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.;with outlet duct, with code tester, 14.5" evap coil blockage | 74.958 | 0.021 | 61.993 | 0.02 | 54.974 | 0.011 | 51.005 | 0.018 | 74.45 | 0.05 | 70.44 | 0.08 | 72.46 | 0.02 | 0.018 | 0.002 | 0.9844 | 0.0023 | 4900 | 13 | 2456 | 59 | 15.967 | 0.224 | [6 empty] | 230.1 | 1 | 230.1 | 1 | 230.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0.2 | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | [11 empty] | 230.1 | 1 | 0 | 0 | 96.06 | 0.03 | 55.48 | 0.02 | 56.76 | 0.02 | 1.28 | 0.04 | 96.37 | 0.04 | 56.17 | 0.03 | 56.93 | 0.03 | -0.76 | 0.04 | 96.74 | 0.05 | 57.54 | 0.09 | 57.13 | 0.03 | -0.41 | 0.11 | 96.43 | 0.03 | 55.1 | 0.02 | 56.96 | 0.02 |  |  | 96.79 | 0.01 | 55.62 | 0.03 | 57.16 | 0.01 | -1.54 | 0.03 | [44 empty] | -1.86 | 0.03 | [74 empty] | 70.29 | 0.05 | 70.5 | 0.04 | 70.57 | 0.03 | 70.65 | 0.03 | 70.51 | 0.04 | 70.46 | 0.04 |  |  |  |  | 57.09 | 0.09 | 55.7 | 0.07 | [10 empty] | 57.54 | 0.09 | [66 empty] | 58.79 | 0.08 | 59.52 | 0.08 | 56.11 | 0.06 | 54.6 | 0.04 | 56.08 | 0.14 | 73.85 | 0.07 | 74.07 | 0.06 | 74.6 | 0.04 | 74.68 | 0.03 | 74.88 | 0.03 | 74.87 | 0.03 | 74.94 | 0.03 | [40 empty] | 74.45 | 0.05 | [34 empty] | 54.66 | 0.05 | 60.84 | 0.16 | 60.5 | 0.15 | 74.61 | 0.04 | 63.06 | 0.18 |  |  | 70.71 | 0.17 | 74.84 | 0.04 | 73.62 | 0.08 | 65.14 | 0.26 | 62.66 | 0.15 | 76.05 | 0.09 | 72.94 | 0.17 | 67.48 | 0.27 | 64.06 | 0.43 | 74.59 | 0.03 | 61.56 | 0.22 | 54.98 | 0.08 | [12 empty] | Economizer test | 74.958 | 0.021 | 61.993 | 0.02 | 70.749 | 0.02 | 59.76 | 0.014 | 54.974 | 0.011 | 51.005 | 0.018 | 1085.3 | 1.3 | 1037.5 | 1.2 | 0.511 | 0.001 | -0.181 | 0.001 | 0.018 | 0.002 | 0.9844 | 0.0023 | 29.185 | 0.001 | 461 | 5 | 460.3 | 4.9 | 0.15207 | 157.7743 | 13.029 | 0.181 | 1.1678 | 4845.4183 | 62.2837 | 157.7738 | 726.5709 | 4118.8474 | 0.0085166 | 26.581 | 69.5812 | 13.0289 | 13.4391 | 0.0069901 | 20.7809 | 0.0087859 | 27.6042 | 0.0083407 | 26.0913 | 71.9697 | 60.4912 | 25.8067
5 | C-EB5-55-CE | 30N0056 | C-EB5-55-CE | closed | Off | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 5 | CUST 2 | 6/18/2015 | 16:10:53 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 1.4 | 2.1 | 0 | 5359 | 16 | 5122 | 59 | 2652 | 54 | 8013 | 53 | [39 empty] | 16.9767 | 5% evaporator coil block, economizer closed (2V), no compressor, factory charge--(5.5 lbs) unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code tester speed to match--total st | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.;with outlet hose, with code tester, 19" evap coil blockage | 74.974 | 0.02 | 61.994 | 0.021 | 54.996 | 0.012 | 51 | 0.026 | 74.45 | 0.05 | 70.25 | 0.05 | 72.43 | 0.02 | 0.01 | 0.003 | 1.079 | 0.0028 | 5359 | 16 | 2652 | 54 | 16.991 | 0.221 | [6 empty] | 230.1 | 1.4 | 230.1 | 1.4 | 230.1 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0.2 | 229.8 | 1.4 | 229.8 | 1.4 | 229.8 | 1.4 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | [11 empty] | 230.1 | 1.4 | 0 | 0 | 95.88 | 0.06 | 55.61 | 0.02 | 56.65 | 0.03 | 1.05 | 0.04 | 95.8 | 0.07 | 55.52 | 0.01 | 56.61 | 0.04 | -1.09 | 0.04 | 95.89 | 0.07 | 59.9 | 0.05 | 56.67 | 0.04 | -3.24 | 0.07 | 95.69 | 0.02 | 55.94 | 0.01 | 56.55 | 0.01 |  |  | 95.93 | 0.03 | 55.29 | 0.01 | 56.68 | 0.02 | -1.39 | 0.02 | [44 empty] | -0.62 | 0.02 | [74 empty] | 70.2 | 0.05 | 70.29 | 0.04 | 70.37 | 0.03 | 70.55 | 0.02 | 70.37 | 0.04 | 70.27 | 0.04 |  |  |  |  | 59.66 | 0.05 | 55.66 | 0.04 | [10 empty] | 59.9 | 0.05 | [66 empty] | 57.06 | 0.05 | 57.42 | 0.05 | 55.5 | 0.03 | 54.66 | 0.09 | 55.99 | 0.11 | 74.44 | 0.05 | 74.49 | 0.04 | 74.86 | 0.05 | 74.9 | 0.04 | 75 | 0.03 | 75 | 0.03 | 74.99 | 0.04 | [40 empty] | 74.56 | 0.05 | [34 empty] | 54.69 | 0.09 | 65.16 | 0.33 | 66.03 | 0.46 | 74.84 | 0.03 | 60.03 | 0.22 | 74.86 | 0.04 | 72.95 | 0.11 | 73.75 | 0.1 | 74.45 | 0.04 | 70.26 | 0.29 | 61.32 | 0.29 | 70.74 | 0.28 | 73.65 | 0.18 | 63.97 | 0.17 | 63.45 | 0.31 | 72.23 | 0.24 | 67.61 | 0.4 | 54.96 | 0.16 | [12 empty] | Economizer test | 74.974 | 0.02 | 61.994 | 0.021 | 70.576 | 0.014 | 59.67 | 0.019 | 54.996 | 0.012 | 51 | 0.026 | 1136.7 | 1.5 | 1086.5 | 1.4 | 0.562 | 0.001 | -0.192 | 0.002 | 0.01 | 0.003 | 1.079 | 0.0028 | 29.176 | 0.001 | 472 | 5 | 471.2 | 5.2 | 0.16408 | 178.2735 | 13.029 | 0.192 | 1.1187 | 5076.6017 | 71.735 | 178.2762 | 820.9563 | 4255.6454 | 0.0084916 | 26.5007 | 69.4573 | 13.0294 | 13.4346 | 0.0069823 | 20.7777 | 0.0087828 | 27.6047 | 0.0083249 | 26.0318 | 71.7522 | 60.3716 | 25.7592
5 | C-EB50-55-CE | 30N0057 | C-EB50-55-CE | closed | Off | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 50 | CUST 2 | 6/18/2015 | 15:04:47 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 1 | 2 | 0 | 4711 | 14 | 4483 | 33 | 2359 | 58 | 7072 | 64 |  | 945 | [37 empty] | 15.7506 | 50% evaporator coil block, economizer closed (2V), no compressor, factory charge--(5.5 lbs) unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code tester speed to match--total s | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.;with code tester, with ouitlet hose, 19" evap coil blockage | 74.988 | 0.015 | 61.992 | 0.027 | 54.995 | 0.008 | 51.001 | 0.022 | 74.6 | 0.04 | 70.58 | 0.03 | 72.56 | 0.01 | 0.009 | 0.002 | 0.903 | 0.0019 | 4711 | 14 | 2359 | 58 | 15.735 | 0.23 | [6 empty] | 230.1 | 1 | 230.1 | 1 | 230.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 0.2 | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 2 | 0 | 2 | 0 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | [11 empty] | 230.2 | 1 | 0 | 0 | 96.21 | 0.04 | 55.46 | 0.01 | 56.84 | 0.02 | 1.39 | 0.03 | 96 | 0.03 | 55.69 | 0.01 | 56.73 | 0.02 | -1.04 | 0.02 | 96.24 | 0.04 | 57.29 | 0.04 | 56.86 | 0.02 | -0.42 | 0.05 | 95.95 | 0.03 | 55.24 | 0.02 | 56.7 | 0.02 |  |  | 96.28 | 0.02 | 55.36 | 0.02 | 56.88 | 0.01 | -1.52 | 0.03 | [44 empty] | -1.46 | 0.02 | [74 empty] | 70.3 | 0.02 | 70.5 | 0.02 | 70.56 | 0.02 | 70.64 | 0.02 | 70.48 | 0.02 | 70.45 | 0.02 |  |  |  |  | 57.01 | 0.04 | 55.63 | 0.03 | [10 empty] | 57.29 | 0.04 | [66 empty] | 57.86 | 0.04 | 58.41 | 0.03 | 55.77 | 0.03 | 54.76 | 0.05 | 56.07 | 0.11 | 73.56 | 0.08 | 73.89 | 0.07 | 74.63 | 0.05 | 74.71 | 0.04 | 74.94 | 0.02 | 74.92 | 0.02 | 75.01 | 0.02 | [40 empty] | 74.48 | 0.02 | [34 empty] | 54.79 | 0.06 | 60.63 | 0.13 | 59.87 | 0.15 | 74.76 | 0.02 | 65.27 | 0.25 |  |  | 71.51 | 0.15 | 74.83 | 0.03 | 73.67 | 0.08 | 66.14 | 0.21 | 65.17 | 0.25 |  |  | 73.09 | 0.14 | 70.82 | 0.24 | 67.25 | 0.3 | 73.99 | 0.09 | 61.2 | 0.22 | 54.96 | 0.1 | [12 empty] | Economizer test | 74.988 | 0.015 | 61.992 | 0.027 | 70.762 | 0.007 | 59.748 | 0.013 | 54.995 | 0.008 | 51.001 | 0.022 | 1039.3 | 1.1 | 993.2 | 1.1 | 0.464 | 0.001 | -0.164 | 0.001 | 0.009 | 0.002 | 0.903 | 0.0019 | 29.178 | 0 | 449 | 5 | 448.9 | 5 | 0.15085 | 149.827 | 13.029 | 0.164 | 1.2095 | 4639.9629 | 54.1402 | 149.8292 | 689.9598 | 3950.0031 | 0.0085113 | 26.5882 | 69.5525 | 13.0294 | 13.4393 | 0.006983 | 20.7783 | 0.0087782 | 27.603 | 0.0083301 | 26.0828 | 72.0233 | 60.5026 | 25.7881
5 | C-R100-EB0-CB0-95CE | 30N0058 | C-R100-EB0-CB0-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/22/2015 | 10:11:08 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1 | 16 | 0 | 18687 | 25 | 18192 | 41 | 451 | 83 | 19138 | 92 |  | 943 | [37 empty] | 5.4016 | Baseline 100% factory charge, 0% evaporator and condenser blockage, economizer closed (2V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns op | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Cond/Evap Coil are blocked 0"., with outlet hose, with code tester | 74.998 | 0.014 | 62.004 | 0.029 | 95.026 | 0.011 | 75.001 | 0.021 | 74.44 | 0.04 | 59.28 | 0.02 | 64.94 | 0.04 | 0.007 | 0.002 | 1.0568 | 0.0021 | 18687 | 25 | 451 | 83 | 5.402 | 0.03 | [6 empty] | 230 | 1 | 230 | 1 | 230 | 1 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3066.9 | 4.8 | 3066.9 | 4.8 | 3066.9 | 4.8 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.3 | 1 | 228.3 | 1 | 228.3 | 1 | 13 | 0 | 13 | 0 | 13 | 0 | 2846.3 | 4.1 | [9 empty] | 228.8 | 1 | 0.7 | 0 | 170.9 | 0.9 | 13 | 0.2 | 3506 | [10 empty] | 230.3 | 1 | 0 | 0 | 257.3 | 0.21 | 102.69 | 0.04 | 119.17 | 0.06 | 16.48 | 0.04 | 273.87 | 0.2 | 179.46 | 0.03 | 123.81 | 0.05 | 55.65 | 0.05 | 256.67 | 0.2 | 102.39 | 0.03 | 118.99 | 0.06 | 16.6 | 0.05 | 78.3 | 0.03 | 66.31 | 0.08 | 46.26 | 0.02 |  |  | 77.19 | 0.02 | 63.07 | 0.16 | 45.55 | 0.02 | 17.52 | 0.16 | [44 empty] | 20.06 | 0.09 | [74 empty] | 58.47 | 0.04 | 58.79 | 0.03 | 58.84 | 0.03 | 58.78 | 0.02 | 58.63 | 0.03 | 58.72 | 0.03 |  |  |  |  | 54.96 | 0.21 | 58.09 | 0.16 | [10 empty] | 102.39 | 0.03 | [66 empty] | 148.82 | 0.05 | 87.21 | 0.09 | 181.75 | 0.07 | 95.23 | 0.09 | 94.25 | 0.07 | 75.16 | 0.03 | 75.08 | 0.03 | 74.92 | 0.04 | 74.96 | 0.04 | 74.9 | 0.03 | 74.95 | 0.03 | 75.02 | 0.04 | [40 empty] | 74.58 | 0.04 | [34 empty] | 95.08 | 0.1 | 85.13 | 0.25 | 85.23 | 0.27 | 74.81 | 0.03 | 90.65 | 0.32 | 75.67 | 0.04 | 76.95 | 0.09 | 76.26 | 0.07 | 75.11 | 0.04 | 79.1 | 0.29 | 87.12 | 0.29 | 77.29 | 0.13 | 75.28 | 0.05 | 81.89 | 0.41 | 90.21 | 0.26 | 80.28 | 0.14 | 83.52 | 0.29 | 95.21 | 0.1 | [12 empty] | C-55-CE | 74.998 | 0.014 | 62.004 | 0.029 | 59.432 | 0.01 | 56.171 | 0.008 | 95.026 | 0.011 | 75.001 | 0.021 | 1113.8 | 1.1 | 1085.8 | 1.1 | 0.566 | 0.001 | -0.201 | 0.001 | 0.007 | 0.002 | 1.0568 | 0.0021 | 29.356 | 0 | 3543 | 8 | 475.8 | 5.3 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.1296 | 5079.5948 | 72.199 | 209.4364 | 891.1851 | 4188.4097 | 0.0096841 | 29.4618 | 58.3024 | 14.1005 | 13.1562 | 0.013915 | 38.1576 | 0.0087837 | 27.6116 | 0.0088288 | 23.864 | 78.5388 | 64.5687 | 23.5885 | 29834.2006 | 24670.2597 | 3067.2 | 0.35088 | 28456.7105 | 23292.7695 | 8.0318 | 0.20548 | -5.8733 | -20.2364 | 53.0688 | 29834.2006 | 19036.1217 | 1399.5788 | 9398.5001 | 29834.2006 | 100%
5 | C-R100-EB20-CB30-95CE | 30N0059 | C-R100-EB20-CB30-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 30 | 20 | CUST 2 | 6/22/2015 | 11:14:56 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1.3 | 17.2 | 0 | 17323 | 29 | 16852 | 63 | -378 | 86 | 16945 | 94 |  | 943 | [37 empty] | 4.4312 | Baseline 100% factory charge, 20% evaporator blockage, 30% condenser blockage,--economizer closed (2V), factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 9", Cond coil block 33", with outlet hose, with code tester | 75.025 | 0.018 | 61.998 | 0.034 | 94.996 | 0.009 | 75.007 | 0.025 | 74.5 | 0.05 | 60.16 | 0.03 | 65.51 | 0.02 | 0.01 | 0.002 | 1.0176 | 0.0024 | 17323 | 29 | -378 | 86 | 4.431 | 0.027 | [6 empty] | 230 | 1.3 | 230 | 1.3 | 230 | 1.3 | 15.1 | 0 | 15.1 | 0 | 15.1 | 0 | 3354 | 4.9 | 3354 | 4.9 | 3354 | 4.9 | 229.9 | 1.3 | 229.9 | 1.3 | 229.9 | 1.3 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.1 | 1.3 | 228.1 | 1.3 | 228.1 | 1.3 | 14.2 | 0 | 14.2 | 0 | 14.2 | 0 | 3121.9 | 4 | [9 empty] | 228.7 | 1.3 | 0.8 | 0 | 176 | 1.1 | 13 | 0.2 | 3781.2 | [10 empty] | 230.3 | 1.3 | 0 | 0 | 285.3 | 0.19 | 109.87 | 0.06 | 126.89 | 0.05 | 17.02 | 0.04 | 302.11 | 0.19 | 170.33 | 0.04 | 131.28 | 0.05 | 39.06 | 0.07 | 284.66 | 0.19 | 109.28 | 0.04 | 126.72 | 0.05 | 17.44 | 0.04 | 78.16 | 0.02 | 58.89 | 0.04 | 46.17 | 0.02 |  |  | 77.17 | 0.02 | 53.16 | 0.03 | 45.54 | 0.01 | 7.62 | 0.02 | [44 empty] | 12.72 | 0.04 | [74 empty] | 59.39 | 0.03 | 59.68 | 0.03 | 59.74 | 0.03 | 59.71 | 0.03 | 59.5 | 0.02 | 59.59 | 0.02 |  |  |  |  | 51.38 | 0.06 | 49.06 | 0.04 | [10 empty] | 109.28 | 0.04 | [66 empty] | 140.17 | 0.05 | 65.17 | 0.2 | 172.65 | 0.09 | 95.24 | 0.09 | 94.42 | 0.08 | 75.43 | 0.05 | 75.29 | 0.05 | 75.09 | 0.05 | 75.11 | 0.05 | 75.01 | 0.05 | 75.05 | 0.05 | 75.06 | 0.05 | [40 empty] | 74.59 | 0.05 | [34 empty] | 95.16 | 0.08 | 87.92 | 0.37 | 89.72 | 0.25 | 74.85 | 0.04 | 89.63 | 0.16 | 76.48 | 0.07 | 77.84 | 0.13 | 75.44 | 0.05 | 75.27 | 0.06 | 82.89 | 0.31 | 88.54 | 0.14 | 75.83 | 0.06 | 75.59 | 0.06 | 81.71 | 0.33 | 85.9 | 0.24 | 78.92 | 0.24 | 88.37 | 0.28 | 95 | 0.07 | [12 empty] | C-EB20-55-CE | 75.025 | 0.018 | 61.998 | 0.034 | 60.294 | 0.007 | 56.757 | 0.011 | 94.996 | 0.009 | 75.007 | 0.025 | 1093.2 | 1.3 | 1064.7 | 1.3 | 0.535 | 0.001 | -0.192 | 0.001 | 0.01 | 0.002 | 1.0176 | 0.0024 | 29.366 | 0.001 | 3824 | 8 | 470.3 | 5.5 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1523 | 4976.9582 | 66.9185 | 173.8682 | 739.8715 | 4237.0868 | 0.0095397 | 29.1762 | 59.1417 | 14.0999 | 13.1791 | 0.013928 | 38.164 | 0.0087734 | 27.6068 | 0.0089719 | 24.2299 | 78.0176 | 64.1825 | 23.9488 | 26016.8808 | 22546.5981 | 3353.7 | 0.43995 | 24640.1398 | 21169.857 | 6.4436 | 0.22433 | -5.2275 | -18.8758 | 53.6828 | 26016.8808 | 16806.7755 | 1399.1821 | 7810.9232 | 26016.8808 | 100%
5 | C-R120-EB0-CB0-95CE | 30N0060 | C-R120-EB0-CB0-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/22/2015 | 18:43:02 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 16.2 | 0 | 18671 | 42 | 18313 | 65 | 574 | 46 | 19246 | 50 |  | 943 | [37 empty] | 5.3476 | Baseline 120% factory charge, 0% evaporator and condenser blockage, economizer closed (2V),--120% factory charge (6.6 lbs), 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 tu | R22 6.6 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 0 in. with outlet hose, with code tester, added 35.2 oz of R2 | 75.022 | 0.022 | 61.997 | 0.019 | 95.007 | 0.01 | 74.998 | 0.026 | 74.6 | 0.05 | 58.92 | 0.05 | 64.25 | 0.04 | -0.058 | 0.002 | 1.0015 | 0.0031 | 18671 | 42 | 574 | 46 | 5.348 | 0.018 | [6 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 14.1 | 0 | 14.1 | 0 | 14.1 | 0 | 3131.6 | 4.6 | 3131.6 | 4.6 | 3131.6 | 4.6 | 229.8 | 1.1 | 229.8 | 1.1 | 229.8 | 1.1 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.1 | 1.1 | 228.1 | 1.1 | 228.1 | 1.1 | 13.3 | 0 | 13.3 | 0 | 13.3 | 0 | 2910.8 | 3.8 | [9 empty] | 228.6 | 1.1 | 0.7 | 0 | 169.2 | 1 | 0.1 | 0.2 | 3547 | [10 empty] | 230.1 | 1.1 | 0 | 0 | 265.94 | 0.2 | 100.6 | 0.05 | 121.6 | 0.06 | 21.01 | 0.05 | 283.32 | 0.17 | 150.99 | 0.05 | 126.35 | 0.05 | 24.63 | 0.06 | 265.24 | 0.26 | 100.13 | 0.06 | 121.41 | 0.07 | 21.28 | 0.06 | 79.86 | 0.03 | 50.03 | 0.03 | 47.22 | 0.02 |  |  | 79.82 | 0.03 | 51.85 | 0.04 | 47.2 | 0.02 | 4.65 | 0.04 | [44 empty] | 2.81 | 0.02 | [74 empty] | 58 | 0.03 | 58.4 | 0.03 | 58.51 | 0.03 | 58.51 | 0.02 | 58.26 | 0.03 | 58.33 | 0.03 | [86 empty] | 129.98 | 0.09 | 59.78 | 0.08 | 152.62 | 0.07 | 95.56 | 0.09 | 94.64 | 0.07 | 75.65 | 0.05 | 75.51 | 0.04 | 75.63 | 0.04 | 75.55 | 0.04 | 75.35 | 0.04 | 75.35 | 0.04 | 75.3 | 0.04 | [40 empty] | 74.64 | 0.04 | [34 empty] | 95.24 | 0.08 | 85.84 | 0.21 | 84.84 | 0.39 | 75.09 | 0.04 | 90.94 | 0.3 | 75.84 | 0.04 | 77.18 | 0.09 | 75.75 | 0.06 | 75.23 | 0.05 | 80.16 | 0.29 | 88.12 | 0.27 | 76.49 | 0.11 | 75.47 | 0.07 | 82.94 | 0.35 | 90.3 | 0.27 | 78.7 | 0.25 | 84.05 | 0.31 | 95.06 | 0.11 | [12 empty] | C-55-CE | 75.022 | 0.022 | 61.997 | 0.019 | 59.04 | 0.011 | 55.965 | 0.012 | 95.007 | 0.01 | 74.998 | 0.026 | 1084.7 | 1.6 | 1056.2 | 1.6 | 0.581 | 0.001 | -0.188 | 0.001 | -0.058 | 0.002 | 1.0015 | 0.0031 | 29.29 | 0.001 | 3599 | 8 | 467 | 5.3 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.134 | 4950.7032 | 72.0921 | 202.547 | 861.8982 | 4088.8049 | 0.009669 | 29.4427 | 57.906 | 14.1001 | 13.146 | 0.013917 | 38.1551 | 0.0087734 | 27.6062 | 0.0088005 | 23.7376 | 78.5282 | 64.5435 | 23.461 | 29613.6483 | 24502.6679 | 3132 | 0.36097 | 28265.8275 | 23154.8471 | 7.8538 | 0.1912 | -5.9817 | -20.6222 | 53.0308 | 29613.6483 | 19152.1955 | 1369.3631 | 9092.0897 | 29613.6483 | 100%
5 | C-R120-EB0-CB30-95CE | 30N0061 | C-R120-EB0-CB30-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 30 | 0 | CUST 2 | 6/22/2015 | 19:50:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1 | 17.5 | 0 | 17996 | 25 | 17630 | 55 | -981 | 77 | 17014 | 84 |  | 943 | [37 empty] | 4.3952 | Baseline 120% factory charge, 0% evaporator blockage, 30% condenser blockage,--economizer closed (2V), 120% factory charge (6.6 lbs), 95F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID | R22 6.6 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 0", Cond coil block 33", with outlet hose, with code tester, added 35.2 | 75.013 | 0.01 | 61.998 | 0.026 | 95.001 | 0.007 | 75.003 | 0.023 | 74.57 | 0.03 | 59.91 | 0.03 | 64.69 | 0.03 | -0.001 | 0.002 | 1.0673 | 0.0026 | 17996 | 25 | -981 | 77 | 4.395 | 0.022 | [6 empty] | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 15.3 | 0 | 15.3 | 0 | 15.3 | 0 | 3397.4 | 4.3 | 3397.4 | 4.3 | 3397.4 | 4.3 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228 | 1 | 228 | 1 | 228 | 1 | 14.4 | 0 | 14.4 | 0 | 14.4 | 0 | 3164.9 | 3.7 | [9 empty] | 228.6 | 1 | 0.8 | 0 | 174.5 | 0.9 | 0 | 0.2 | 3339.4 | [10 empty] | 230.2 | 1 | 0 | 0 | 294.47 | 0.16 | 108.29 | 0.03 | 129.3 | 0.04 | 21.01 | 0.04 | 311.77 | 0.12 | 152.49 | 0.06 | 133.71 | 0.03 | 18.78 | 0.05 | 293.63 | 0.14 | 107.63 | 0.03 | 129.08 | 0.04 | 21.45 | 0.04 | 81.97 | 0.02 | 51.77 | 0.02 | 48.53 | 0.01 |  |  | 81.93 | 0.02 | 54.39 | 0.05 | 48.51 | 0.01 | 5.88 | 0.05 | [44 empty] | 3.24 | 0.02 | [74 empty] | 59.02 | 0.02 | 59.41 | 0.03 | 59.53 | 0.03 | 59.55 | 0.02 | 59.3 | 0.02 | 59.38 | 0.03 | [86 empty] | 133.87 | 0.03 | 64.13 | 0.19 | 153.76 | 0.12 | 95.54 | 0.07 | 94.86 | 0.05 | 75.63 | 0.04 | 75.49 | 0.03 | 75.62 | 0.04 | 75.54 | 0.03 | 75.33 | 0.02 | 75.34 | 0.02 | 75.28 | 0.03 | [40 empty] | 74.6 | 0.03 | [34 empty] | 95.39 | 0.05 | 85.62 | 0.26 | 84.62 | 0.42 | 75.06 | 0.04 | 90.69 | 0.3 | 75.78 | 0.03 | 77.09 | 0.07 | 75.72 | 0.06 | 75.18 | 0.03 | 79.99 | 0.29 | 87.8 | 0.29 | 76.49 | 0.12 | 75.41 | 0.06 | 82.9 | 0.37 | 90.32 | 0.25 | 78.71 | 0.25 | 83.88 | 0.34 | 94.9 | 0.08 | [12 empty] | C-55-CE | 75.013 | 0.01 | 61.998 | 0.026 | 60.051 | 0.005 | 56.868 | 0.008 | 95.001 | 0.007 | 75.003 | 0.023 | 1120.2 | 1.4 | 1089.9 | 1.3 | 0.56 | 0.001 | -0.199 | 0.001 | -0.001 | 0.002 | 1.0673 | 0.0026 | 29.299 | 0 | 3871 | 8 | 473.9 | 5.3 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.1207 | 5101.8895 | 71.7034 | 208.3876 | 886.7582 | 4215.1313 | 0.0096708 | 29.4412 | 58.9303 | 14.1 | 13.1739 | 0.013923 | 38.16 | 0.0087762 | 27.607 | 0.0090956 | 24.3052 | 78.514 | 64.5413 | 24.0317 | 27598.8281 | 23979.3298 | 3397.1 | 0.4201 | 26226.1311 | 22606.6328 | 6.775 | 0.19703 | -5.4095 | -19.5837 | 54.125 | 27598.8281 | 16845.4808 | 1395.3862 | 9357.9611 | 27598.8281 | 100%
5 | C-R120-EB20-CB0-95CE | 30N0062 | C-R120-EB20-CB0-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 20 | CUST 2 | 6/22/2015 | 21:38:53 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 16.1 | 0 | 17953 | 39 | 17612 | 63 | 427 | 52 | 18379 | 80 |  | 944 | [37 empty] | 5.1612 | Baseline 120% factory charge, 20% evaporator blockage, 0% condenser blockage,--economizer closed (2V), 120% factory charge (6.6 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75"--ID | R22 6.6 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 9", Cond coil block 0", with outlet hose, with code tester, added 35.2 | 75.016 | 0.02 | 61.993 | 0.027 | 95.005 | 0.008 | 75.001 | 0.021 | 74.61 | 0.06 | 59.58 | 0.06 | 64.42 | 0.02 | -0.001 | 0.002 | 1.0083 | 0.003 | 17953 | 39 | 427 | 52 | 5.162 | 0.024 | [6 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 14 | 0 | 14 | 0 | 14 | 0 | 3093.4 | 5.4 | 3093.4 | 5.4 | 3093.4 | 5.4 | 229.8 | 1.1 | 229.8 | 1.1 | 229.8 | 1.1 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.2 | 1.1 | 228.2 | 1.1 | 228.2 | 1.1 | 13.1 | 0 | 13.1 | 0 | 13.1 | 0 | 2873.5 | 4.5 | [9 empty] | 228.7 | 1.1 | 0.7 | 0 | 169.5 | 1 | 0 | 0.2 | 3510.1 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 262.97 | 0.22 | 100.59 | 0.04 | 120.77 | 0.06 | 20.18 | 0.04 | 280.14 | 0.19 | 147.52 | 0.06 | 125.51 | 0.05 | 22.02 | 0.07 | 262.2 | 0.2 | 100.16 | 0.07 | 120.56 | 0.06 | 20.39 | 0.07 | 78.2 | 0.03 | 48.76 | 0.03 | 46.18 | 0.02 |  |  | 77.94 | 0.04 | 50.81 | 0.05 | 46.01 | 0.02 | 4.79 | 0.06 | [44 empty] | 2.58 | 0.03 | [74 empty] | 58.68 | 0.03 | 59.1 | 0.03 | 59.19 | 0.03 | 59.16 | 0.03 | 58.92 | 0.03 | 59.04 | 0.02 | [86 empty] | 127.73 | 0.1 | 55.53 | 0.1 | 148.86 | 0.09 | 95.56 | 0.09 | 94.69 | 0.05 | 75.74 | 0.05 | 75.55 | 0.04 | 75.65 | 0.04 | 75.57 | 0.04 | 75.36 | 0.03 | 75.37 | 0.03 | 75.29 | 0.04 | [40 empty] | 74.64 | 0.04 | [34 empty] | 95.26 | 0.08 | 89.11 | 0.23 | 89.91 | 0.14 | 75.15 | 0.04 | 89.81 | 0.18 | 76.02 | 0.06 | 77.1 | 0.1 | 75.61 | 0.05 | 75.32 | 0.05 | 82.72 | 0.36 | 88.3 | 0.2 | 76.01 | 0.08 | 75.65 | 0.07 | 83.24 | 0.24 | 87.71 | 0.27 | 78.39 | 0.15 | 88.27 | 0.13 | 95.03 | 0.09 | [12 empty] | C-EB20-55-CE | 75.016 | 0.02 | 61.993 | 0.027 | 59.704 | 0.008 | 56.265 | 0.014 | 95.005 | 0.008 | 75.001 | 0.021 | 1088 | 1.7 | 1060.2 | 1.6 | 0.525 | 0.001 | -0.189 | 0.001 | -0.001 | 0.002 | 1.0083 | 0.003 | 29.318 | 0.001 | 3561 | 9 | 467.1 | 5.4 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1516 | 4959.3591 | 65.3901 | 172.5055 | 734.0641 | 4225.295 | 0.0095342 | 29.1656 | 58.5524 | 14.1 | 13.163 | 0.01392 | 38.158 | 0.0087722 | 27.6034 | 0.0088198 | 23.9206 | 77.9983 | 64.168 | 23.6397 | 27404.838 | 23145.3338 | 3093.9 | 0.38531 | 26033.8022 | 21774.298 | 7.3108 | 0.21876 | -5.5259 | -19.4458 | 53.1073 | 27404.838 | 18264.0518 | 1392.9983 | 7747.7879 | 27404.838 | 100%
5 | C-R120-EB20-CB30-95CE | 30N0063 | C-R120-EB20-CB30-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 30 | 20 | CUST 2 | 6/22/2015 | 20:47:48 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 17.2 | 0 | 17104 | 24 | 16745 | 36 | -484 | 52 | 16620 | 58 |  | 944 | [37 empty] | 4.3519 | Baseline 120% factory charge, 20% evaporator blockage, 30% condenser blockage,--economizer closed (2V), 120% factory charge (6.6 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75"--ID | R22 6.6 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 9", Cond coil block 33", with outlet hose, with code tester, added 35.2 | 75.009 | 0.012 | 61.997 | 0.017 | 94.994 | 0.004 | 74.995 | 0.029 | 74.57 | 0.06 | 60.13 | 0.04 | 65.02 | 0.03 | -0.013 | 0.002 | 0.9919 | 0.0026 | 17104 | 24 | -484 | 52 | 4.352 | 0.018 | [6 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 15.1 | 0 | 15.1 | 0 | 15.1 | 0 | 3353.4 | 4.5 | 3353.4 | 4.5 | 3353.4 | 4.5 | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228 | 1.1 | 228 | 1.1 | 228 | 1.1 | 14.2 | 0 | 14.2 | 0 | 14.2 | 0 | 3121.9 | 3.9 | [9 empty] | 228.6 | 1.1 | 0.8 | 0 | 174.6 | 1 | 0.1 | 0.2 | 3761.9 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 290.29 | 0.15 | 108.33 | 0.03 | 128.21 | 0.04 | 19.88 | 0.03 | 307.36 | 0.14 | 150.28 | 0.05 | 132.6 | 0.04 | 17.68 | 0.04 | 289.47 | 0.16 | 107.7 | 0.04 | 127.99 | 0.04 | 20.3 | 0.05 | 80.11 | 0.02 | 50.41 | 0.03 | 47.38 | 0.01 |  |  | 79.79 | 0.03 | 53.28 | 0.04 | 47.18 | 0.02 | 6.1 | 0.04 | [44 empty] | 3.03 | 0.03 | [74 empty] | 59.27 | 0.02 | 59.71 | 0.03 | 59.78 | 0.03 | 59.75 | 0.03 | 59.53 | 0.02 | 59.63 | 0.02 | [86 empty] | 132.2 | 0.03 | 61.41 | 0.57 | 151.33 | 0.13 | 95.51 | 0.05 | 94.85 | 0.06 | 75.69 | 0.03 | 75.52 | 0.03 | 75.59 | 0.02 | 75.51 | 0.03 | 75.32 | 0.03 | 75.32 | 0.03 | 75.25 | 0.03 | [40 empty] | 74.63 | 0.03 | [34 empty] | 95.35 | 0.06 | 89.15 | 0.17 | 89.94 | 0.14 | 75.17 | 0.03 | 89.76 | 0.18 | 75.98 | 0.06 | 77.04 | 0.1 | 75.58 | 0.07 | 75.31 | 0.05 | 82.65 | 0.35 | 88.21 | 0.2 | 75.95 | 0.1 | 75.61 | 0.08 | 83.22 | 0.24 | 87.68 | 0.23 | 78.31 | 0.16 | 88.24 | 0.16 | 94.89 | 0.07 | [12 empty] | C-EB20-55-CE | 75.009 | 0.012 | 61.997 | 0.017 | 60.266 | 0.005 | 56.796 | 0.01 | 94.994 | 0.004 | 74.995 | 0.029 | 1079.9 | 1.4 | 1050.4 | 1.4 | 0.527 | 0.001 | -0.186 | 0.001 | -0.013 | 0.002 | 0.9919 | 0.0026 | 29.307 | 0 | 3819 | 8 | 465.4 | 5.3 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1577 | 4916.5855 | 65.0325 | 171.1291 | 728.2227 | 4188.3629 | 0.009538 | 29.1684 | 59.1083 | 14.0997 | 13.1787 | 0.013918 | 38.1524 | 0.0087765 | 27.6063 | 0.0090018 | 24.2556 | 77.9927 | 64.1716 | 23.9731 | 25543.0383 | 22283.1645 | 3353.6 | 0.4481 | 24176.584 | 20916.7102 | 6.3306 | 0.21892 | -5.1953 | -18.8843 | 53.8156 | 25543.0383 | 16474.3583 | 1388.8031 | 7679.8769 | 25543.0383 | 100%
5 | C-R80-EB0-CB0-95CE | 30N0064 | C-R80-EB0-CB0-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/22/2015 | 17:25:26 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1 | 15.4 | 0 | 16724 | 47 | 16318 | 83 | -861 | 78 | 15862 | 60 |  | 943 | [37 empty] | 4.6694 | Baseline 80% factory charge, 0% evaporator and condenser blockage, economizer closed (2V),--80% factory charge (4.4 lbs), 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turn | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 0", Cond coil block 0", with outlet hose, with code tester, removed 17. | 74.911 | 0.032 | 61.976 | 0.023 | 95.005 | 0.008 | 74.997 | 0.029 | 74.44 | 0.06 | 60.96 | 0.03 | 66.32 | 0.03 | 0.011 | 0.002 | 1.0845 | 0.0031 | 16724 | 47 | -861 | 78 | 4.67 | 0.021 | [6 empty] | 230 | 1 | 230 | 1 | 230 | 1 | 13.2 | 0 | 13.2 | 0 | 13.2 | 0 | 2920.8 | 4.4 | 2920.8 | 4.4 | 2920.8 | 4.4 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.4 | 1 | 228.4 | 1 | 228.4 | 1 | 12.4 | 0 | 12.4 | 0 | 12.4 | 0 | 2704.7 | 3.5 | [9 empty] | 228.8 | 1 | 0.7 | 0 | 169.4 | 0.9 | 13 | 0.2 | 3362.7 | [10 empty] | 230.2 | 1 | 0 | 0 | 242.24 | 0.13 | 105.55 | 0.04 | 114.76 | 0.04 | 9.21 | 0.03 | 258.14 | 0.13 | 190.46 | 0.03 | 119.4 | 0.04 | 71.06 | 0.04 | 241.66 | 0.14 | 105.81 | 0.04 | 114.58 | 0.04 | 8.77 | 0.05 | 71.72 | 0.02 | 72.3 | 0.05 | 41.94 | 0.01 |  |  | 72.42 | 0.02 | 72.58 | 0.02 | 42.4 | 0.01 | 30.17 | 0.03 | [44 empty] | 30.35 | 0.05 | [74 empty] | 60.16 | 0.02 | 60.51 | 0.02 | 60.62 | 0.02 | 60.63 | 0.03 | 60.36 | 0.02 | 60.49 | 0.02 |  |  |  |  | 69.88 | 0.04 | 68.95 | 0.04 | [10 empty] | 105.81 | 0.04 | [66 empty] | 156.75 | 0.06 | 97.83 | 0.07 | 193.83 | 0.04 | 95.51 | 0.06 | 94.57 | 0.05 | 75.51 | 0.05 | 75.38 | 0.05 | 75.42 | 0.05 | 75.36 | 0.04 | 75.21 | 0.04 | 75.22 | 0.05 | 75.16 | 0.05 | [40 empty] | 74.51 | 0.04 | [34 empty] | 95.22 | 0.06 | 85.24 | 0.27 | 84.09 | 0.4 | 74.94 | 0.05 | 91.02 | 0.3 | 75.65 | 0.05 | 76.96 | 0.1 | 75.68 | 0.07 | 75.04 | 0.04 | 79.9 | 0.31 | 88.02 | 0.27 | 76.56 | 0.14 | 75.29 | 0.07 | 82.74 | 0.35 | 89.88 | 0.24 | 78.94 | 0.25 | 83.49 | 0.36 | 95.05 | 0.07 | [12 empty] | C-55-CE | 74.911 | 0.032 | 61.976 | 0.023 | 61.094 | 0.011 | 57.242 | 0.012 | 95.005 | 0.008 | 74.997 | 0.029 | 1131.2 | 1.6 | 1096.9 | 1.6 | 0.573 | 0.001 | -0.202 | 0.001 | 0.011 | 0.002 | 1.0845 | 0.0031 | 29.289 | 0.001 | 3397 | 8 | 475.6 | 5.3 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.1108 | 5141.7394 | 73.8392 | 209.9528 | 893.4157 | 4248.3236 | 0.0096774 | 29.4278 | 59.9832 | 14.1 | 13.2002 | 0.013917 | 38.1541 | 0.0087858 | 27.5926 | 0.0090728 | 24.535 | 78.4294 | 64.5219 | 24.2639 | 26551.3979 | 22762.9762 | 2921.4 | 0.37553 | 25180.1882 | 21391.7665 | 7.4125 | 0.24866 | -5.1639 | -18.4462 | 53.8782 | 26551.3979 | 15721.7664 | 1393.8167 | 9435.8148 | 26551.3979 | 100%
5 | C-R80-EB0-CB30-95CE | 30N0065 | C-R80-EB0-CB30-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 30 | CUST 2 | 6/22/2015 | 15:04:33 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 16.6 | 0 | 16831 | 27 | 16366 | 75 | -1230 | 98 | 15600 | 92 |  | 943 | [37 empty] | 4.2311 | Baseline 80% factory charge, 0% evaporator and 30% condenser blockage, economizer closed (2V),--80% factory charge (4.4 lbs), 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3- | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 0", Cond coil block 33", with outlet hose, with code tester, removed 17 | 75.009 | 0.02 | 61.992 | 0.033 | 94.999 | 0.009 | 75.002 | 0.033 | 74.53 | 0.07 | 61.04 | 0.04 | 66.17 | 0.03 | 0.02 | 0.003 | 1.0898 | 0.0039 | 16831 | 27 | -1230 | 98 | 4.232 | 0.027 | [6 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 14.4 | 0 | 14.4 | 0 | 14.4 | 0 | 3210.4 | 4.1 | 3210.4 | 4.1 | 3210.4 | 4.1 | 229.8 | 1.1 | 229.8 | 1.1 | 229.8 | 1.1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.1 | 1.1 | 228.1 | 1.1 | 228.1 | 1.1 | 13.6 | 0 | 13.6 | 0 | 13.6 | 0 | 2983 | 3.2 | [9 empty] | 228.6 | 1.1 | 0.8 | 0 | 174.5 | 1 | 13 | 0.2 | 3646.5 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 270.61 | 0.13 | 113.55 | 0.03 | 122.91 | 0.04 | 9.36 | 0.03 | 286.88 | 0.11 | 196.37 | 0.03 | 127.31 | 0.03 | 69.06 | 0.04 | 270.05 | 0.12 | 113.44 | 0.05 | 122.75 | 0.03 | 9.31 | 0.06 | 75.41 | 0.02 | 74.94 | 0.05 | 44.39 | 0.02 |  |  | 76.05 | 0.02 | 74.32 | 0.03 | 44.81 | 0.02 | 29.51 | 0.03 | [44 empty] | 30.55 | 0.05 | [74 empty] | 60.2 | 0.04 | 60.54 | 0.04 | 60.63 | 0.04 | 60.62 | 0.03 | 60.39 | 0.04 | 60.51 | 0.03 |  |  |  |  | 68.79 | 0.04 | 69.13 | 0.04 | [10 empty] | 113.44 | 0.05 | [66 empty] | 158.75 | 0.05 | 99.12 | 0.04 | 200.52 | 0.04 | 95.47 | 0.08 | 94.75 | 0.05 | 75.49 | 0.04 | 75.34 | 0.04 | 75.39 | 0.04 | 75.37 | 0.04 | 75.22 | 0.05 | 75.23 | 0.05 | 75.16 | 0.04 | [40 empty] | 74.55 | 0.07 | [34 empty] | 95.34 | 0.06 | 84.78 | 0.3 | 83.83 | 0.31 | 74.91 | 0.04 | 90.86 | 0.27 | 75.72 | 0.05 | 77.08 | 0.1 | 75.9 | 0.07 | 75.09 | 0.04 | 80.05 | 0.27 | 87.84 | 0.26 | 76.76 | 0.11 | 75.32 | 0.06 | 82.52 | 0.4 | 90.03 | 0.28 | 79.49 | 0.24 | 83.54 | 0.31 | 94.93 | 0.07 | [12 empty] | C-55-CE | 75.009 | 0.02 | 61.992 | 0.033 | 61.139 | 0.012 | 57.351 | 0.02 | 94.999 | 0.009 | 75.002 | 0.033 | 1133.1 | 2 | 1100.3 | 2 | 0.569 | 0.001 | -0.203 | 0.001 | 0.02 | 0.003 | 1.0898 | 0.0039 | 29.324 | 0.001 | 3687 | 8 | 476 | 5.2 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.111 | 5149.7625 | 73.551 | 210.4711 | 895.6277 | 4254.1348 | 0.0096688 | 29.4387 | 60.028 | 14.0999 | 13.2018 | 0.013923 | 38.1591 | 0.0087732 | 27.6027 | 0.0091278 | 24.6058 | 78.5125 | 64.5379 | 24.3346 | 26284.5995 | 22845.7704 | 3211 | 0.41694 | 24911.041 | 21472.2119 | 6.7565 | 0.24202 | -5.104 | -18.4845 | 54.1259 | 26284.5995 | 15433.7037 | 1396.3438 | 9454.5519 | 26284.5995 | 100%
5 | C-R80-EB20-CB0-95CE | 30N0066 | C-R80-EB20-CB0-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 20 | CUST 2 | 6/22/2015 | 16:27:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.2 | 15.2 | 0 | 16105 | 32 | 15655 | 48 | -441 | 74 | 15664 | 83 |  | 943 | [37 empty] | 4.6329 | Baseline 80% factory charge, 20% evaporator blockage, 0% condenser blockage, economizer closed (2V),--80% factory charge (4.4 lbs), 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pul | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 9", Cond coil block 0", with outlet hose, with code tester, removed 17. | 74.992 | 0.011 | 62.002 | 0.034 | 95.005 | 0.005 | 75.001 | 0.017 | 74.5 | 0.06 | 61.32 | 0.06 | 66.31 | 0.02 | 0.014 | 0.003 | 1.0421 | 0.0033 | 16105 | 32 | -441 | 74 | 4.633 | 0.028 | [6 empty] | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 13.1 | 0 | 13.1 | 0 | 13.1 | 0 | 2910.4 | 5.5 | 2910.4 | 5.5 | 2910.4 | 5.5 | 229.8 | 1.2 | 229.8 | 1.2 | 229.8 | 1.2 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.3 | 1.2 | 228.3 | 1.2 | 228.3 | 1.2 | 12.3 | 0 | 12.3 | 0 | 12.3 | 0 | 2694.3 | 4.4 | [9 empty] | 228.8 | 1.2 | 0.7 | 0 | 169.5 | 1.1 | 0.1 | 0.2 | [11 empty] | 230.2 | 1.2 | 0 | 0 | 241.13 | 0.16 | 105.59 | 0.04 | 114.43 | 0.05 | 8.84 | 0.03 | 256.91 | 0.16 | 188.92 | 0.04 | 119.05 | 0.05 | 69.87 | 0.05 | 240.54 | 0.17 | 105.95 | 0.05 | 114.25 | 0.05 | 8.3 | 0.07 | 70.61 | 0.02 | 69.98 | 0.06 | 41.2 | 0.01 |  |  | 70.85 | 0.02 | 70.23 | 0.05 | 41.36 | 0.01 | 28.87 | 0.06 | [44 empty] | 28.79 | 0.06 | [74 empty] | 60.59 | 0.04 | 60.87 | 0.04 | 60.94 | 0.04 | 60.93 | 0.03 | 60.66 | 0.03 | 60.82 | 0.04 |  |  |  |  | 67.17 | 0.05 | 66.22 | 0.04 | [10 empty] | 105.95 | 0.05 | [66 empty] | 155.51 | 0.09 | 96.3 | 0.05 | 192.23 | 0.05 | 95.55 | 0.08 | 94.62 | 0.06 | 75.64 | 0.05 | 75.46 | 0.04 | 75.49 | 0.03 | 75.44 | 0.03 | 75.24 | 0.05 | 75.25 | 0.04 | 75.17 | 0.04 | [40 empty] | 74.54 | 0.04 | [34 empty] | 95.27 | 0.08 | 86.33 | 1.25 | 88.36 | 0.45 | 74.92 | 0.03 | 90.86 | 0.54 | 75.91 | 0.06 | 77.83 | 0.13 | 75.6 | 0.07 | 75.18 | 0.05 | 83.2 | 0.38 | 89.38 | 0.43 | 76.72 | 0.08 | 75.37 | 0.08 | 82.58 | 0.91 | 86.09 | 0.42 | 79.78 | 0.16 | 86.91 | 0.53 | 95.07 | 0.09 | [12 empty] | C-EB20-55-CE | 74.992 | 0.011 | 62.002 | 0.034 | 61.432 | 0.017 | 57.236 | 0.021 | 95.005 | 0.005 | 75.001 | 0.017 | 1108.5 | 1.8 | 1075.4 | 1.7 | 0.543 | 0.001 | -0.195 | 0.001 | 0.014 | 0.003 | 1.0421 | 0.0033 | 29.301 | 0.001 | 3381 | 9 | 470.6 | 5.5 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1349 | 5035.5409 | 68.6017 | 175.2223 | 745.6249 | 4289.9161 | 0.0095444 | 29.172 | 60.2971 | 14.1 | 13.2081 | 0.01392 | 38.158 | 0.0087838 | 27.6102 | 0.0089892 | 24.5264 | 77.9789 | 64.1761 | 24.2495 | 24787.4824 | 21369.0984 | 2910.4 | 0.40073 | 23415.4623 | 19997.0783 | 6.9256 | 0.27489 | -4.9225 | -17.6819 | 53.5937 | 24787.4824 | 15528.3504 | 1394.4283 | 7864.7038 | 24787.4824 | 100%
5 | C-R80-EB20-CB30-95CE | 30N0067 | C-R80-EB20-CB30-95CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 30 | 20 | CUST 2 | 6/22/2015 | 13:44:41 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 0.9 | 16.4 | 0 | 15937 | 39 | 15533 | 55 | -702 | 59 | 15234 | 79 |  | 944 | [37 empty] | 4.1634 | Baseline 80% factory charge, 20% evaporator blockage, 30% condenser blockage,--economizer closed (2V), 80% factory charge (4.4 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pu | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Evap coil block 9", Cond coil block 33", with outlet hose, with code tester, removed 17 | 75.012 | 0.02 | 61.989 | 0.028 | 94.998 | 0.01 | 75.005 | 0.023 | 74.64 | 0.05 | 61.53 | 0.05 | 66.61 | 0.04 | 0.011 | 0.002 | 1.0372 | 0.0032 | 15937 | 39 | -702 | 59 | 4.164 | 0.023 | [6 empty] | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 14.3 | 0 | 14.3 | 0 | 14.3 | 0 | 3187.5 | 4.7 | 3187.5 | 4.7 | 3187.5 | 4.7 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.2 | 1 | 228.2 | 1 | 228.2 | 1 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2960.3 | 4.1 | [9 empty] | 228.7 | 1 | 0.8 | 0 | 174.8 | 0.9 | 13 | 0.2 | 3619.2 | [10 empty] | 230.2 | 0.9 | 0 | 0 | 268.19 | 0.18 | 113.31 | 0.05 | 122.24 | 0.05 | 8.93 | 0.03 | 284.23 | 0.18 | 194.8 | 0.06 | 126.61 | 0.05 | 68.2 | 0.05 | 267.62 | 0.19 | 113.4 | 0.05 | 122.08 | 0.05 | 8.68 | 0.04 | 73.73 | 0.03 | 73.28 | 0.05 | 43.29 | 0.02 |  |  | 74.62 | 0.08 | 71.61 | 0.03 | 43.88 | 0.05 | 27.73 | 0.06 | [44 empty] | 29.99 | 0.06 | [74 empty] | 60.63 | 0.03 | 60.9 | 0.03 | 61 | 0.03 | 61.05 | 0.03 | 60.74 | 0.03 | 60.85 | 0.03 |  |  |  |  | 65.68 | 0.07 | 66.36 | 0.05 | [10 empty] | 113.4 | 0.05 | [66 empty] | 157.33 | 0.06 | 97.33 | 0.04 | 198.86 | 0.06 | 95.52 | 0.07 | 94.74 | 0.06 | 75.71 | 0.04 | 75.51 | 0.04 | 75.49 | 0.04 | 75.46 | 0.04 | 75.3 | 0.03 | 75.32 | 0.03 | 75.22 | 0.04 | [40 empty] | 74.55 | 0.04 | [34 empty] | 95.35 | 0.07 | 87.38 | 0.53 | 89.51 | 0.28 | 74.94 | 0.03 | 89.69 | 0.21 | 76.49 | 0.05 | 77.87 | 0.12 | 75.49 | 0.05 | 75.3 | 0.05 | 82.97 | 0.35 | 88.63 | 0.17 | 75.92 | 0.06 | 75.6 | 0.06 | 81.91 | 0.39 | 86.07 | 0.32 | 79.2 | 0.26 | 88.1 | 0.35 | 94.98 | 0.07 | [12 empty] | C-EB20-55-CE | 75.012 | 0.02 | 61.989 | 0.028 | 61.56 | 0.01 | 57.343 | 0.019 | 94.998 | 0.01 | 75.005 | 0.023 | 1105.4 | 1.7 | 1073.3 | 1.7 | 0.545 | 0.002 | -0.195 | 0.001 | 0.011 | 0.002 | 1.0372 | 0.0032 | 29.341 | 0.001 | 3659 | 8 | 471.1 | 5.2 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1395 | 5020.1239 | 68.7199 | 175.2215 | 745.6284 | 4274.4954 | 0.0095362 | 29.1692 | 60.4205 | 14.0999 | 13.2116 | 0.013926 | 38.162 | 0.0087705 | 27.6005 | 0.0090233 | 24.5948 | 78.0042 | 64.1729 | 24.3168 | 24359.8949 | 21185.3409 | 3187.9 | 0.44665 | 22986.5717 | 19812.0177 | 6.2822 | 0.27516 | -4.8524 | -17.5837 | 53.7454 | 24359.8949 | 15089.1246 | 1395.8392 | 7874.9311 | 24359.8949 | 100%
5 | C-CB0-115-CE | 30N0076 | C-CB0-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/20/2015 | 1:44:08 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.2 | 19.2 | 0 | 14018 | 45 | 13706 | 76 | -3334 | 91 | 10681 | 69 |  | 944 | [37 empty] | 2.4938 | Baseline no condenser coil blockage, economizer closed (2.8V),--factory charge (5.5 lbs) 115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjus | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. | 74.918 | 0.03 | 61.977 | 0.032 | 114.99 | 0.018 | 79.996 | 0.024 | 74.39 | 0.06 | 62.9 | 0.02 | 67.27 | 0.02 | 0.003 | 0.002 | 1.0684 | 0.0034 | 14018 | 45 | -3334 | 91 | 2.494 | 0.017 | [6 empty] | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 17 | 0.1 | 17 | 0.1 | 17 | 0.1 | 3809.9 | 4.6 | 3809.9 | 4.6 | 3809.9 | 4.6 | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.9 | 1.2 | 227.9 | 1.2 | 227.9 | 1.2 | 16.3 | 0.1 | 16.3 | 0.1 | 16.3 | 0.1 | 3583.1 | 4.2 | [9 empty] | 228.6 | 1.2 | 0.7 | 0 | 167.4 | 1 | 0.1 | 0.2 | 4223.4 | [10 empty] | 230.3 | 1.2 | 0 | 0 | 331.78 | 0.31 | 124.53 | 0.07 | 138.59 | 0.07 | 14.06 | 0.04 | 347.67 | 0.3 | 190.72 | 0.05 | 142.33 | 0.07 | 48.39 | 0.08 | 331.1 | 0.32 | 123.95 | 0.05 | 138.43 | 0.08 | 14.48 | 0.06 | 84.64 | 0.03 | 53.34 | 0.03 | 50.15 | 0.02 |  |  | 84.12 | 0.03 | 55.79 | 0.03 | 49.83 | 0.02 | 5.96 | 0.03 | [44 empty] | 3.2 | 0.03 | [74 empty] | 62.29 | 0.03 | 62.6 | 0.04 | 62.64 | 0.03 | 62.59 | 0.03 | 62.45 | 0.03 | 62.51 | 0.03 | [86 empty] | 159.8 | 0.07 | 68.99 | 0.13 | 193.35 | 0.06 | 114.9 | 0.11 | 113.72 | 0.17 | 75.73 | 0.07 | 75.6 | 0.07 | 75.18 | 0.06 | 75.23 | 0.06 | 75.06 | 0.05 | 75.11 | 0.05 | 75.12 | 0.04 | [40 empty] | 74.78 | 0.05 | [34 empty] | 115.11 | 0.07 | 94.72 | 0.58 | 94.32 | 0.46 | 74.94 | 0.05 | 105.5 | 0.51 | 76.16 | 0.07 | 78.94 | 0.17 | 77.1 | 0.11 | 75.55 | 0.05 | 83.59 | 0.62 | 98.9 | 0.58 | 78.79 | 0.23 | 75.76 | 0.07 | 89.84 | 0.54 | 102.77 | 0.56 | 85.08 | 0.32 | 91.36 | 0.62 | 113.67 | 0.29 | [12 empty] | C-55-CE-DM | 74.918 | 0.03 | 61.977 | 0.032 | 63.163 | 0.006 | 58.801 | 0.016 | 114.99 | 0.018 | 79.996 | 0.024 | 1125.1 | 1.8 | 1085.8 | 1.7 | 0.569 | 0.001 | -0.201 | 0.001 | 0.003 | 0.002 | 1.0684 | 0.0034 | 29.228 | 0.001 | 4283 | 8 | 472.9 | 5.4 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1176 | 5092.3774 | 72.5817 | 213.4267 | 876.6916 | 4215.6858 | 0.0096423 | 30.2294 | 62.0454 | 14.6067 | 13.2563 | 0.013766 | 42.9057 | 0.0087848 | 27.5932 | 0.0095353 | 25.5435 | 81.8684 | 65.6299 | 25.2706 | 25252.2354 | 24227.0768 | 3810.1 | 0.51496 | 23885.9491 | 22860.7905 | 5.5769 | 0.24185 | -4.9588 | -19.823 | 55.7219 | 25252.2354 | 10437.9972 | 1389.9807 | 13424.2575 | 25252.2354 | 100%
5 | C-CB10-115-CE | 30N0077 | C-CB10-115-CE | closed | on | N/A |  | unsealed | unsealed |  |  | horizontal | 10 | 0 | CUST 2 | 6/20/2015 | 0:21:45 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1 | 19.8 | 0 | 13681 | 39 | 13435 | 51 | -3962 | 52 | 9716 | 55 |  | 944 | [37 empty] | 2.2057 | . | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 12`.; | 74.976 | 0.027 | 61.978 | 0.015 | 114.984 | 0.018 | 80.005 | 0.025 | 74.47 | 0.03 | 63.23 | 0.03 | 67.23 | 0.02 | 0 | 0.002 | 1.0771 | 0.003 | 13681 | 39 | -3962 | 52 | 2.206 | 0.014 | [6 empty] | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 17.6 | 0.1 | 17.6 | 0.1 | 17.6 | 0.1 | 3930.7 | 4.5 | 3930.7 | 4.5 | 3930.7 | 4.5 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.7 | 1 | 227.7 | 1 | 227.7 | 1 | 16.8 | 0.1 | 16.8 | 0.1 | 16.8 | 0.1 | 3700.6 | 4.3 | [9 empty] | 228.5 | 1 | 0.7 | 0 | 167.6 | 0.9 | 0.1 | 0.2 | 4342 | [10 empty] | 230.2 | 1 | 0 | 0 | 343.32 | 0.32 | 126.65 | 0.06 | 141.32 | 0.07 | 14.67 | 0.03 | 359.25 | 0.31 | 190.47 | 0.06 | 144.98 | 0.07 | 45.5 | 0.1 | 342.57 | 0.31 | 126.36 | 0.06 | 141.15 | 0.07 | 14.78 | 0.07 | 85.56 | 0.04 | 54.15 | 0.05 | 50.7 | 0.02 |  |  | 84.87 | 0.04 | 56.52 | 0.04 | 50.29 | 0.02 | 6.23 | 0.05 | [44 empty] | 3.45 | 0.04 | [74 empty] | 62.71 | 0.04 | 63.01 | 0.04 | 63.04 | 0.03 | 63 | 0.03 | 62.86 | 0.04 | 62.92 | 0.04 | [86 empty] | 157.08 | 0.05 | 69.04 | 0.07 | 193.57 | 0.08 | 115.2 | 0.13 | 113.78 | 0.1 | 75.85 | 0.05 | 75.71 | 0.05 | 75.25 | 0.04 | 75.29 | 0.04 | 75.13 | 0.04 | 75.2 | 0.03 | 75.25 | 0.03 | [40 empty] | 74.89 | 0.05 | [34 empty] | 115.33 | 0.08 | 96.26 | 1.65 | 95.34 | 0.92 | 75.07 | 0.04 | 106.12 | 0.68 | 76.27 | 0.05 | 79.15 | 0.16 | 77.26 | 0.12 | 75.67 | 0.05 | 83.97 | 0.57 | 99.59 | 0.75 | 79.07 | 0.25 | 75.91 | 0.09 | 90.4 | 0.6 | 102.82 | 0.94 | 85.54 | 0.38 | 92.69 | 1.42 | 114.92 | 0.14 | [12 empty] | C-55-CE-DM | 74.976 | 0.027 | 61.978 | 0.015 | 63.534 | 0.007 | 59.105 | 0.011 | 114.984 | 0.018 | 80.005 | 0.025 | 1129.5 | 1.6 | 1090.3 | 1.6 | 0.57 | 0.001 | -0.206 | 0.001 | 0 | 0.002 | 1.0771 | 0.003 | 29.237 | 0 | 4405 | 7 | 473.8 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1154 | 5108.3605 | 73.0106 | 216.0645 | 887.5307 | 4220.8298 | 0.0096412 | 30.2552 | 62.4186 | 14.6067 | 13.2665 | 0.013776 | 42.9155 | 0.0087718 | 27.5931 | 0.0096367 | 25.7445 | 81.9793 | 65.6651 | 25.472 | 24434.3447 | 23981.5007 | 3931.2 | 0.54911 | 23066.4505 | 22613.6065 | 5.2364 | 0.24409 | -4.7832 | -19.5607 | 56.1022 | 24434.3447 | 9443.357 | 1391.8729 | 13599.1148 | 24434.3447 | 100%
5 | C-CB20-115-CE | 30N0078 | C-CB20-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 20 | 0 | CUST 2 | 6/19/2015 | 23:33:22 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 20.2 | 0 | 13363 | 35 | 13131 | 59 | -4351 | 65 | 9009 | 47 |  | 944 | [37 empty] | 1.9967 | 20% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 24`.; | 74.928 | 0.033 | 61.966 | 0.008 | 114.993 | 0.006 | 79.998 | 0.037 | 74.42 | 0.04 | 63.45 | 0.02 | 67.43 | 0.02 | 0 | 0.002 | 1.0827 | 0.0025 | [12 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 18 | 0.1 | 18 | 0.1 | 18 | 0.1 | 4037.2 | 2.9 | 4037.2 | 2.9 | 4037.2 | 2.9 | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.6 | 1.1 | 227.6 | 1.1 | 227.6 | 1.1 | 17.3 | 0.1 | 17.3 | 0.1 | 17.3 | 0.1 | 3803.5 | 2.6 | [9 empty] | 228.5 | 1.1 | 0.7 | 0 | 168.3 | 1 | 0.1 | 0.2 | 4446.1 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 353.16 | 0.17 | 129.3 | 0.03 | 143.59 | 0.04 | 14.3 | 0.03 | 369.15 | 0.15 | 191.25 | 0.05 | 147.19 | 0.03 | 44.06 | 0.07 | 352.42 | 0.15 | 128.78 | 0.03 | 143.42 | 0.03 | 14.65 | 0.04 | 86.4 | 0.03 | 54.91 | 0.04 | 51.21 | 0.02 |  |  | 85.79 | 0.03 | 57.84 | 0.03 | 50.84 | 0.02 | 7.01 | 0.04 | [44 empty] | 3.7 | 0.05 | [74 empty] | 62.95 | 0.03 | 63.27 | 0.04 | 63.29 | 0.03 | 63.23 | 0.03 | 63.13 | 0.03 | 63.2 | 0.04 | [86 empty] | 159.11 | 0.02 | 67.46 | 0.13 | 194.23 | 0.07 | 115.24 | 0.11 | 113.85 | 0.09 | 75.87 | 0.07 | 75.72 | 0.06 | 75.28 | 0.03 | 75.32 | 0.04 | 75.14 | 0.03 | 75.19 | 0.04 | 75.22 | 0.05 | [40 empty] | 74.87 | 0.05 | [34 empty] | 115.36 | 0.06 | 95.77 | 0.65 | 95.05 | 0.52 | 75.04 | 0.04 | 106.4 | 0.55 | 76.26 | 0.05 | 79.18 | 0.2 | 77.2 | 0.1 | 75.65 | 0.06 | 84.23 | 0.6 | 99.95 | 0.65 | 78.86 | 0.2 | 75.89 | 0.1 | 90.7 | 0.77 | 103.51 | 0.56 | 85.22 | 0.26 | 92.13 | 0.6 | 114.67 | 0.29 | [12 empty] | C-55-CE-DM | 74.928 | 0.033 | 61.966 | 0.008 | 63.768 | 0.009 | 59.309 | 0.01 | 114.993 | 0.006 | 79.998 | 0.037 | 1132.6 | 1.3 | 1093 | 1.3 | 0.57 | 0.001 | -0.203 | 0.001 | 0 | 0.002 | 1.0827 | 0.0025 | 29.242 | 0 | 4512 | 6 | 474.3 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1138 | 5119.8717 | 73.1914 | 214.4865 | 881.0398 | 4238.8319 | 0.0096342 | 30.2219 | 62.6542 | 14.6068 | 13.273 | 0.013767 | 42.9078 | 0.0087752 | 27.5852 | 0.0097089 | 25.8803 | 81.8743 | 65.6204 | 25.6082 | 23621.564 | 23617.0079 | 4037.7 | 0.58339 | 22252.5804 | 22248.0243 | 4.9319 | 0.24617 | -4.6137 | -19.2201 | 56.3778 | 23621.564 | 8728.5808 | 1393.1642 | 13499.819 | 23621.564 | 100%
5 | C-CB30-115-CE | 30N0079 | C-CB30-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 30 | 0 | CUST 2 | 6/19/2015 | 22:56:28 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.2 | 21 | 0 | 13005 | 26 | 12690 | 37 | -4673 | 48 | 8328 | 57 |  | 944 | [37 empty] | 1.7791 | 30% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 115F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 33" | 75.005 | 0.013 | 62.003 | 0.021 | 115.024 | 0.011 | 79.989 | 0.026 | 74.42 | 0.02 | 63.75 | 0.01 | 67.59 | 0.02 | -0.003 | 0.003 | 1.0723 | 0.003 | 13005 | 26 | -4673 | 48 | 1.779 | 0.013 | [6 empty] | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 18.8 | 0.1 | 18.8 | 0.1 | 18.8 | 0.1 | 4207.8 | 3.8 | 4207.8 | 3.8 | 4207.8 | 3.8 | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.5 | 1.2 | 227.5 | 1.2 | 227.5 | 1.2 | 18 | 0.1 | 18 | 0.1 | 18 | 0.1 | 3965.4 | 3.6 | [9 empty] | 228.4 | 1.2 | 0.8 | 0 | 172.2 | 1.1 | 0.1 | 0.2 | 4610.4 | [10 empty] | 230.2 | 1.2 | 0 | 0 | 368.4 | 0.18 | 132.39 | 0.04 | 147.02 | 0.04 | 14.63 | 0.03 | 384.32 | 0.18 | 192.87 | 0.05 | 150.5 | 0.04 | 42.37 | 0.06 | 367.63 | 0.19 | 131.81 | 0.02 | 146.85 | 0.04 | 15.04 | 0.04 | 87.42 | 0.03 | 55.4 | 0.02 | 51.81 | 0.02 |  |  | 86.87 | 0.04 | 59.02 | 0.03 | 51.48 | 0.03 | 7.54 | 0.03 | [44 empty] | 3.58 | 0.03 | [74 empty] | 63.24 | 0.04 | 63.57 | 0.04 | 63.6 | 0.04 | 63.51 | 0.03 | 63.44 | 0.03 | 63.49 | 0.03 | [86 empty] | 162.65 | 0.04 | 74.79 | 0.21 | 195.99 | 0.07 | 115.33 | 0.11 | 113.9 | 0.09 | 75.88 | 0.05 | 75.75 | 0.05 | 75.29 | 0.04 | 75.34 | 0.04 | 75.15 | 0.03 | 75.21 | 0.03 | 75.23 | 0.02 | [40 empty] | 74.86 | 0.02 | [34 empty] | 115.47 | 0.07 | 95.9 | 0.46 | 95.09 | 0.57 | 75.03 | 0.03 | 106.54 | 0.51 | 76.26 | 0.06 | 79.15 | 0.17 | 77.13 | 0.12 | 75.65 | 0.05 | 84.33 | 0.62 | 100.1 | 0.6 | 78.7 | 0.2 | 75.91 | 0.1 | 90.77 | 0.72 | 103.46 | 0.49 | 85.1 | 0.31 | 92.26 | 0.63 | 114.7 | 0.31 | [12 empty] | C-55-CE-DM | 75.005 | 0.013 | 62.003 | 0.021 | 64.076 | 0.009 | 59.54 | 0.012 | 115.024 | 0.011 | 79.989 | 0.026 | 1127.4 | 1.6 | 1087.2 | 1.5 | 0.571 | 0.001 | -0.204 | 0.002 | -0.003 | 0.003 | 1.0723 | 0.003 | 29.234 | 0.001 | 4681 | 7 | 472.8 | 5.3 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1162 | 5093.1504 | 72.9307 | 215.019 | 883.1875 | 4209.9629 | 0.0096431 | 30.2615 | 62.9598 | 14.6075 | 13.2814 | 0.013751 | 42.8974 | 0.0087814 | 27.6107 | 0.0097811 | 26.0342 | 81.9964 | 65.6735 | 25.7615 | 22919.4647 | 23269.4401 | 4208.2 | 0.62665 | 21554.7109 | 21904.6863 | 4.6047 | 0.24927 | -4.5001 | -19.0365 | 56.6389 | 22919.4647 | 8029.4177 | 1389.0418 | 13501.0051 | 22919.4647 | 100%
5 | C-CB40-115-CE | 30N0080 | C-CB40-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 40 | 0 | CUST 2 | 6/19/2015 | 21:38:33 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.8 | 1.1 | 21.6 | 0 | 12809 | 19 | 12512 | 43 | -4846 | 51 | 7958 | 50 |  | 944 | [37 empty] | 1.6517 | 40% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 115F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 37`.; | 75.004 | 0.011 | 61.987 | 0.016 | 115.011 | 0.011 | 80.01 | 0.022 | 74.42 | 0.03 | 63.88 | 0.02 | 67.65 | 0.01 | -0.007 | 0.003 | 1.0694 | 0.0031 | 12809 | 19 | -4846 | 51 | 1.652 | 0.011 | [6 empty] | 229.8 | 1.1 | 229.8 | 1.1 | 229.8 | 1.1 | 19.4 | 0.1 | 19.4 | 0.1 | 19.4 | 0.1 | 4345.3 | 3.6 | 4345.3 | 3.6 | 4345.3 | 3.6 | 229.8 | 1.1 | 229.8 | 1.1 | 229.8 | 1.1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.4 | 1.1 | 227.4 | 1.1 | 227.4 | 1.1 | 18.6 | 0.1 | 18.6 | 0.1 | 18.6 | 0.1 | 4095.3 | 3.7 | [9 empty] | 228.3 | 1.1 | 0.8 | 0 | 175.8 | 1 | 0.1 | 0.2 | 4743.8 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 379.85 | 0.19 | 134.88 | 0.04 | 149.53 | 0.04 | 14.66 | 0.03 | 395.78 | 0.19 | 194.02 | 0.04 | 152.94 | 0.04 | 41.09 | 0.06 | 379.09 | 0.2 | 134.38 | 0.03 | 149.37 | 0.04 | 14.99 | 0.04 | 88.2 | 0.03 | 55.84 | 0.03 | 52.27 | 0.02 |  |  | 87.85 | 0.04 | 59.01 | 0.04 | 52.06 | 0.03 | 6.95 | 0.05 | [44 empty] | 3.58 | 0.03 | [74 empty] | 63.37 | 0.03 | 63.73 | 0.03 | 63.74 | 0.03 | 63.66 | 0.03 | 63.6 | 0.03 | 63.66 | 0.03 | [86 empty] | 162.76 | 0.15 | 77.05 | 0.53 | 197.13 | 0.1 | 115.28 | 0.08 | 113.74 | 0.09 | 75.84 | 0.06 | 75.69 | 0.04 | 75.27 | 0.04 | 75.3 | 0.04 | 75.14 | 0.03 | 75.2 | 0.03 | 75.22 | 0.03 | [40 empty] | 74.88 | 0.02 | [34 empty] | 115.33 | 0.06 | 96.09 | 0.43 | 95.15 | 0.46 | 75.07 | 0.03 | 106.38 | 0.5 | 76.26 | 0.05 | 79.11 | 0.2 | 77.1 | 0.09 | 75.64 | 0.04 | 84.2 | 0.62 | 99.76 | 0.65 | 78.6 | 0.16 | 75.88 | 0.1 | 90.63 | 0.61 | 103.77 | 0.51 | 85.02 | 0.27 | 92.36 | 0.6 | 114.64 | 0.24 | [12 empty] | C-55-CE-DM | 75.004 | 0.011 | 61.987 | 0.016 | 64.214 | 0.006 | 59.629 | 0.01 | 115.011 | 0.011 | 80.01 | 0.022 | 1126.4 | 1.6 | 1085.2 | 1.6 | 0.572 | 0.001 | -0.204 | 0.001 | -0.007 | 0.003 | 1.0694 | 0.0031 | 29.21 | 0 | 4818 | 6 | 472.7 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1172 | 5087.2218 | 72.9241 | 215.018 | 883.1914 | 4204.0304 | 0.0096397 | 30.2591 | 63.0968 | 14.6073 | 13.2851 | 0.013774 | 42.9204 | 0.0087711 | 27.5992 | 0.0098045 | 26.0934 | 82.0018 | 65.6705 | 25.8204 | 22580.5274 | 23081.7531 | 4345.3 | 0.65678 | 21216.0921 | 21717.3179 | 4.4035 | 0.25191 | -4.4387 | -18.905 | 56.7307 | 22580.5274 | 7660.1566 | 1388.7767 | 13531.5941 | 22580.5274 | 100%
5 | C-CB5-115-CE | 30N0081 | C-CB5-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 5 | 0 | CUST 2 | 6/20/2015 | 1:08:12 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.2 | 19.5 | 0 | 13791 | 56 | 13545 | 74 | -3664 | 114 | 10124 | 93 |  | 944 | [37 empty] | 2.3258 | 5% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 115F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 7.`.; | 74.925 | 0.039 | 61.972 | 0.019 | 115.011 | 0.053 | 80.014 | 0.044 | 74.45 | 0.05 | 63.07 | 0.02 | 67.22 | 0.02 | -0.002 | 0.003 | 1.0663 | 0.0035 | 13791 | 56 | -3664 | 114 | 2.325 | 0.025 | [6 empty] | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 17.3 | 0.1 | 17.3 | 0.1 | 17.3 | 0.1 | 3880.3 | 7.7 | 3880.3 | 7.7 | 3880.3 | 7.7 | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.8 | 1.2 | 227.8 | 1.2 | 227.8 | 1.2 | 16.6 | 0.1 | 16.6 | 0.1 | 16.6 | 0.1 | 3650.9 | 7.3 | [9 empty] | 228.6 | 1.2 | 0.7 | 0 | 168.2 | 1 | 0.1 | 0.2 | 4291.9 | [10 empty] | 230.2 | 1.2 | 0 | 0 | 338.51 | 0.62 | 125.72 | 0.11 | 140.19 | 0.15 | 14.48 | 0.07 | 354.44 | 0.62 | 190.02 | 0.07 | 143.89 | 0.14 | 46.14 | 0.1 | 337.8 | 0.63 | 125.08 | 0.1 | 140.03 | 0.15 | 14.94 | 0.1 | 85.13 | 0.05 | 54.01 | 0.03 | 50.44 | 0.03 |  |  | 84.42 | 0.05 | 55.93 | 0.04 | 50.01 | 0.03 | 5.92 | 0.04 | [44 empty] | 3.56 | 0.02 | [74 empty] | 62.48 | 0.04 | 62.8 | 0.03 | 62.81 | 0.03 | 62.77 | 0.03 | 62.64 | 0.04 | 62.71 | 0.04 | [86 empty] | 158.57 | 0.05 | 68.83 | 0.06 | 193.21 | 0.11 | 115.15 | 0.22 | 113.85 | 0.14 | 75.8 | 0.07 | 75.67 | 0.05 | 75.22 | 0.05 | 75.25 | 0.06 | 75.09 | 0.06 | 75.15 | 0.06 | 75.19 | 0.04 | [40 empty] | 74.84 | 0.06 | [34 empty] | 115.11 | 0.13 | 95.26 | 0.52 | 94.84 | 0.41 | 75.01 | 0.05 | 106.2 | 0.53 | 76.18 | 0.05 | 78.99 | 0.16 | 77.16 | 0.12 | 75.59 | 0.05 | 83.94 | 0.55 | 99.63 | 0.6 | 78.89 | 0.2 | 75.8 | 0.11 | 89.99 | 0.74 | 103.32 | 0.54 | 85.29 | 0.27 | 92 | 0.49 | 114.64 | 0.28 | [12 empty] | C-55-CE-DM | 74.925 | 0.039 | 61.972 | 0.019 | 63.341 | 0.01 | 58.961 | 0.014 | 115.011 | 0.053 | 80.014 | 0.044 | 1123.8 | 1.8 | 1084.9 | 1.8 | 0.571 | 0.002 | -0.204 | 0.001 | -0.002 | 0.003 | 1.0663 | 0.0035 | 29.235 | 0 | 4353 | 10 | 472.8 | 5.3 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1185 | 5084.5896 | 72.7765 | 215.0183 | 883.1904 | 4201.3992 | 0.0096481 | 30.2533 | 62.2225 | 14.6074 | 13.2612 | 0.013778 | 42.9248 | 0.0087799 | 27.5895 | 0.0095926 | 25.6494 | 81.9402 | 65.6619 | 25.3762 | 24797.9398 | 24061.4922 | 3880.2 | 0.53404 | 23432.6595 | 22696.2119 | 5.3831 | 0.24188 | -4.8771 | -19.7177 | 55.9316 | 24797.9398 | 9864.8908 | 1389.102 | 13543.9471 | 24797.9398 | 100%
5 | C-CB50-115-CE | 30N0082 | C-CB50-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 50 | 0 | CUST 2 | 6/19/2015 | 20:30:46 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 0.9 | 22.4 | 0 | 12397 | 37 | 12097 | 24 | -5106 | 70 | 7286 | 62 |  | 943 | [37 empty] | 1.4578 | 50% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 43.75". | 75.016 | 0.016 | 62.016 | 0.019 | 115.011 | 0.017 | 79.994 | 0.028 | 74.46 | 0.04 | 64.27 | 0.03 | 67.95 | 0.02 | -0.008 | 0.003 | 1.0728 | 0.0043 | 12397 | 37 | -5106 | 70 | 1.458 | 0.013 | [6 empty] | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 20.2 | 0.1 | 20.2 | 0.1 | 20.2 | 0.1 | 4524.8 | 6 | 4524.8 | 6 | 4524.8 | 6 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.3 | 0.9 | 227.3 | 0.9 | 227.3 | 0.9 | 19.4 | 0.1 | 19.4 | 0.1 | 19.4 | 0.1 | 4273.7 | 5.7 | [9 empty] | 228.3 | 0.9 | 0.8 | 0 | 171.5 | 1 | 0.1 | 0.2 | 4918.8 | [10 empty] | 230.2 | 0.9 | 0 | 0 | 393.45 | 0.25 | 138.1 | 0.05 | 152.44 | 0.05 | 14.34 | 0.04 | 409.24 | 0.25 | 196.98 | 0.05 | 155.73 | 0.05 | 41.24 | 0.06 | 392.67 | 0.25 | 137.53 | 0.04 | 152.28 | 0.05 | 14.75 | 0.06 | 89.39 | 0.03 | 56.49 | 0.03 | 52.96 | 0.02 |  |  | 89.24 | 0.03 | 58.83 | 0.02 | 52.87 | 0.01 | 5.96 | 0.02 | [44 empty] | 3.53 | 0.03 | [74 empty] | 63.58 | 0.05 | 63.98 | 0.04 | 63.99 | 0.03 | 63.91 | 0.03 | 63.84 | 0.04 | 63.93 | 0.04 | [86 empty] | 165.77 | 0.04 | 74.47 | 0.15 | 199.39 | 0.1 | 115.18 | 0.1 | 113.61 | 0.1 | 75.84 | 0.07 | 75.72 | 0.05 | 75.26 | 0.06 | 75.29 | 0.05 | 75.1 | 0.05 | 75.17 | 0.04 | 75.24 | 0.02 | [40 empty] | 74.81 | 0.04 | [34 empty] | 115.64 | 0.06 | 95.9 | 0.39 | 94.93 | 0.45 | 75.07 | 0.03 | 106.21 | 0.57 | 76.28 | 0.05 | 79.15 | 0.18 | 77.04 | 0.1 | 75.68 | 0.05 | 84.35 | 0.6 | 99.92 | 0.54 | 78.53 | 0.19 | 75.91 | 0.11 | 90.86 | 0.52 | 103.51 | 0.51 | 84.85 | 0.29 | 92.19 | 0.58 | 114.47 | 0.2 | [12 empty] | C-55-CE-DM | 75.016 | 0.016 | 62.016 | 0.019 | 64.575 | 0.007 | 59.863 | 0.007 | 115.011 | 0.017 | 79.994 | 0.028 | 1128.9 | 2.3 | 1086.3 | 2.2 | 0.575 | 0.001 | -0.203 | 0.001 | -0.008 | 0.003 | 1.0728 | 0.0043 | 29.197 | 0 | 4998 | 8 | 473.6 | 5 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1168 | 5094.8133 | 73.3808 | 214.4894 | 881.0281 | 4213.7852 | 0.009647 | 30.2628 | 63.4582 | 14.6072 | 13.2947 | 0.013759 | 42.9031 | 0.0087874 | 27.62 | 0.0098669 | 26.2497 | 81.9839 | 65.6749 | 25.9768 | 21836.5345 | 22652.345 | 4524.4 | 0.70715 | 20470.5866 | 21286.397 | 4.0958 | 0.2596 | -4.286 | -18.5257 | 56.9629 | 21836.5345 | 6981.1917 | 1390.4742 | 13464.8687 | 21836.5345 | 100%
5 | C-CB60-115-CE | 30N0083 | C-CB60-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 60 | 0 | CUST 2 | 6/19/2015 | 19:39:59 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.8 | 1.2 | 22.7 | 0 | 12167 | 24 | 11853 | 37 | -5428 | 52 | 6734 | 58 |  | 943 | [37 empty] | 1.3303 | 60% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 115F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet--52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code tester | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 43".; | 74.987 | 0.01 | 61.776 | 0.026 | 114.989 | 0.01 | 80.007 | 0.023 | 74.45 | 0.02 | 64.38 | 0.04 | 68.12 | 0.02 | -0.024 | 0.002 | 1.0587 | 0.003 | 12167 | 24 | -5428 | 52 | 1.33 | 0.012 | [6 empty] | 229.8 | 1.2 | 229.8 | 1.2 | 229.8 | 1.2 | 20.5 | 0.1 | 20.5 | 0.1 | 20.5 | 0.1 | 4589.4 | 4.6 | 4589.4 | 4.6 | 4589.4 | 4.6 | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.2 | 1.2 | 227.2 | 1.2 | 227.2 | 1.2 | 19.7 | 0.1 | 19.7 | 0.1 | 19.7 | 0.1 | 4337.7 | 4.6 | [9 empty] | 228.2 | 1.2 | 0.7 | 0 | 170.1 | 1.1 | 0.1 | 0.2 | 4980.6 | [10 empty] | 230.2 | 1.2 | 0 | 0 | 396.17 | 0.17 | 138.74 | 0.03 | 153.02 | 0.04 | 14.28 | 0.03 | 411.91 | 0.16 | 197.61 | 0.04 | 156.28 | 0.03 | 41.34 | 0.04 | 395.4 | 0.16 | 138.18 | 0.04 | 152.85 | 0.03 | 14.67 | 0.05 | 89.62 | 0.03 | 56.86 | 0.06 | 53.09 | 0.02 |  |  | 89.12 | 0.02 | 59.11 | 0.04 | 52.8 | 0.01 | 6.31 | 0.03 | [44 empty] | 3.77 | 0.05 | [74 empty] | 63.49 | 0.04 | 63.93 | 0.04 | 63.99 | 0.04 | 63.91 | 0.03 | 63.78 | 0.04 | 63.89 | 0.04 | [86 empty] | 165.86 | 0.05 | 72.19 | 0.07 | 200.2 | 0.09 | 115.43 | 0.04 | 114.07 | 0.16 | 75.98 | 0.05 | 75.73 | 0.05 | 75.52 | 0.03 | 75.49 | 0.03 | 75.27 | 0.03 | 75.29 | 0.03 | 75.21 | 0.02 | [40 empty] | 74.66 | 0.04 | [34 empty] | 115.63 | 0.06 | 95.87 | 0.47 | 95.07 | 0.5 | 75.07 | 0.02 | 105.9 | 0.51 | 76.11 | 0.04 | 78.92 | 0.19 | 76.92 | 0.12 | 75.46 | 0.05 | 83.79 | 0.59 | 99.42 | 0.58 | 78.46 | 0.19 | 75.7 | 0.08 | 90.15 | 0.82 | 103.8 | 0.49 | 84.78 | 0.24 | 92.35 | 0.66 | 114.42 | 0.1 | [12 empty] | C-55-CE-DM | 74.987 | 0.01 | 61.776 | 0.026 | 64.656 | 0.014 | 59.764 | 0.016 | 114.989 | 0.01 | 80.007 | 0.023 | 1121.6 | 1.6 | 1078.8 | 1.5 | 0.582 | 0.001 | -0.201 | 0.001 | -0.024 | 0.002 | 1.0587 | 0.003 | 29.189 | 0 | 5062 | 6 | 472.8 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1209 | 5061.3316 | 73.7614 | 213.4272 | 876.6895 | 4184.6421 | 0.0095267 | 30.1272 | 63.5351 | 14.6068 | 13.2961 | 0.013777 | 42.9176 | 0.0086364 | 27.4476 | 0.009785 | 26.1802 | 81.9694 | 65.5007 | 25.9063 | 21363.386 | 22392.4549 | 4589.2 | 0.73317 | 20001.4672 | 21030.5361 | 3.9513 | 0.268 | -4.2209 | -18.4343 | 56.7858 | 21363.386 | 6414.8189 | 1386.1662 | 13562.4008 | 21363.386 | 100%
5 | C-CB0-82-CE | 30N0086 | C-CB0-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/20/2015 | 8:23:36 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 1 | 14.2 | 0 | 22594 | 33 | 22110 | 91 | 5225 | 67 | 27824 | 85 |  | 944 | [37 empty] | 8.9208 | Baseline no condenser coil blockage, economizer closed (2.8V), factory charge (5.5 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 0 in. | 75.025 | 0.009 | 61.988 | 0.027 | 81.957 | 0.021 | 68 | 0.032 | 74.57 | 0.07 | 56.2 | 0.02 | 62.72 | 0.03 | -0.016 | 0.002 | 1.0481 | 0.0029 | 22594 | 33 | 5225 | 67 | 8.922 | 0.034 | [6 empty] | 230 | 1 | 230 | 1 | 230 | 1 | 12 | 0 | 12 | 0 | 12 | 0 | 2644.7 | 5.2 | 2644.7 | 5.2 | 2644.7 | 5.2 | 229.8 | 1 | 229.8 | 1 | 229.8 | 1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.5 | 1 | 228.5 | 1 | 228.5 | 1 | 11.2 | 0 | 11.2 | 0 | 11.2 | 0 | 2433.6 | 4.1 | [9 empty] | 228.8 | 1 | 0.7 | 0 | 170.7 | 0.9 | 0.1 | 0.2 | 3078.2 | [10 empty] | 230.2 | 1 | 0 | 0 | 213.98 | 0.19 | 88.03 | 0.05 | 105.95 | 0.06 | 17.92 | 0.03 | 230.59 | 0.2 | 167.62 | 0.03 | 111.22 | 0.06 | 56.41 | 0.05 | 213.26 | 0.19 | 87.9 | 0.04 | 105.72 | 0.06 | 17.81 | 0.04 | 72.56 | 0.03 | 60.67 | 0.04 | 42.5 | 0.02 |  |  | 73.21 | 0.04 | 62.58 | 0.04 | 42.93 | 0.02 | 19.65 | 0.03 | [44 empty] | 18.18 | 0.04 | [74 empty] | 55.23 | 0.03 | 55.56 | 0.03 | 55.65 | 0.03 | 55.66 | 0.04 | 55.39 | 0.04 | 55.5 | 0.03 | [86 empty] | 137.18 | 0.06 | 85.1 | 0.03 | 169.82 | 0.05 | 82.11 | 0.06 | 82.19 | 0.05 | 75.22 | 0.05 | 75.13 | 0.04 | 75.37 | 0.04 | 75.33 | 0.05 | 75.21 | 0.06 | 75.22 | 0.06 | 75.17 | 0.06 | [40 empty] | 74.55 | 0.06 | [34 empty] | 81.91 | 0.08 | 78.5 | 0.07 | 78.46 | 0.09 | 74.94 | 0.05 | 80.71 | 0.12 | 75.38 | 0.05 | 75.78 | 0.06 | 75.34 | 0.06 | 74.85 | 0.05 | 76.69 | 0.1 | 79.41 | 0.1 | 75.71 | 0.07 | 75.04 | 0.06 | 77.28 | 0.12 | 80.23 | 0.1 | 76.73 | 0.06 | 77.96 | 0.1 | 81.7 | 0.07 | [12 empty] | C-55-CE-DM | 75.025 | 0.009 | 61.988 | 0.027 | 56.252 | 0.007 | 53.276 | 0.018 | 81.957 | 0.021 | 68 | 0.032 | 1108.3 | 1.5 | 1083.2 | 1.5 | 0.577 | 0.002 | -0.197 | 0.001 | -0.016 | 0.002 | 1.0481 | 0.0029 | 29.266 | 0.001 | 3119 | 8 | 473.9 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1189 | 5088.4047 | 73.4259 | 204.9842 | 894.634 | 4193.7707 | 0.0092216 | 28.396 | 55.1331 | 13.7476 | 13.0685 | 0.011354 | 32.129 | 0.0087668 | 27.5996 | 0.0079236 | 22.1053 | 76.2485 | 63.1034 | 21.8328 | 33395.9856 | 25786.4832 | 2645.1 | 0.27032 | 32029.1676 | 24419.6652 | 10.2691 | 0.20301 | -6.5632 | -21.1154 | 49.7547 | 33395.9856 | 27957.4211 | 1386.4472 | 4052.1172 | 33395.9856 | 100%
5 | C-CB10-82-CE | 30N0087 | C-CB10-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 10 | 0 | CUST 2 | 6/20/2015 | 7:20:35 | 10 Ton | 0:10:00 | 75/68 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 68 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 0.6 | 14.5 | 0 | 22899 | 53 | 22377 | 82 | 5113 | 134 | 28017 | 121 |  | 944 | [37 empty] | 8.7335 | 10% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 82F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 12 in. | 75.014 | 0.038 | 61.982 | 0.043 | 82.013 | 0.008 | 68.004 | 0.017 | 74.53 | 0.07 | 56.21 | 0.03 | 62.85 | 0.06 | 0.016 | 0.002 | 1.0804 | 0.0029 | [12 empty] | 230 | 0.6 | 230 | 0.6 | 230 | 0.6 | 12.3 | 0 | 12.3 | 0 | 12.3 | 0 | 2731.3 | 3.3 | 2731.3 | 3.3 | 2731.3 | 3.3 | 229.9 | 0.6 | 229.9 | 0.6 | 229.9 | 0.6 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.5 | 0.6 | 228.5 | 0.6 | 228.5 | 0.6 | 11.6 | 0 | 11.6 | 0 | 11.6 | 0 | 2518.7 | 2.7 | [9 empty] | 228.8 | 0.6 | 0.7 | 0 | 170.8 | 0.7 | 0.1 | 0.2 | 3166 | [10 empty] | 230.2 | 0.6 | 0 | 0 | 222.85 | 0.09 | 90.06 | 0.03 | 108.79 | 0.03 | 18.73 | 0.03 | 239.9 | 0.09 | 166.98 | 0.03 | 114.05 | 0.03 | 52.93 | 0.04 | 222.18 | 0.11 | 89.9 | 0.03 | 108.58 | 0.04 | 18.68 | 0.04 | 74 | 0.03 | 59.08 | 0.07 | 43.44 | 0.02 |  |  | 74.93 | 0.03 | 61.24 | 0.05 | 44.05 | 0.02 | 17.19 | 0.04 | [44 empty] | 15.63 | 0.07 | [74 empty] | 55.26 | 0.04 | 55.58 | 0.03 | 55.64 | 0.03 | 55.68 | 0.03 | 55.41 | 0.03 | 55.53 | 0.03 | [86 empty] | 134.13 | 0.04 | 84.47 | 0.03 | 169.89 | 0.04 | 82.1 | 0.07 | 82.06 | 0.04 | 75.22 | 0.05 | 75.12 | 0.05 | 75.29 | 0.06 | 75.26 | 0.05 | 75.17 | 0.06 | 75.19 | 0.06 | 75.11 | 0.06 | [40 empty] | 74.57 | 0.06 | [34 empty] | 82.01 | 0.06 | 78.54 | 0.09 | 78.45 | 0.11 | 74.95 | 0.06 | 80.62 | 0.13 | 75.4 | 0.06 | 75.78 | 0.07 | 75.39 | 0.08 | 74.88 | 0.06 | 76.71 | 0.11 | 79.39 | 0.11 | 75.76 | 0.09 | 75.08 | 0.07 | 77.33 | 0.11 | 80.36 | 0.09 | 76.75 | 0.08 | 78 | 0.1 | 81.76 | 0.06 | [12 empty] | C-55-CE-DM | 75.014 | 0.038 | 61.982 | 0.043 | 56.261 | 0.009 | 53.346 | 0.02 | 82.013 | 0.008 | 68.004 | 0.017 | 1125.8 | 1.5 | 1099.3 | 1.5 | 0.567 | 0.001 | -0.204 | 0.001 | 0.016 | 0.002 | 1.0804 | 0.0029 | 29.247 | 0 | 3208 | 7 | 476.5 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1093 | 5168.5469 | 73.2258 | 208.6044 | 910.3455 | 4258.2014 | 0.0092195 | 28.3944 | 55.1517 | 13.7489 | 13.0691 | 0.011343 | 32.1314 | 0.0087655 | 27.5954 | 0.0079604 | 22.1474 | 76.2515 | 63.1013 | 21.8773 | 33683.7167 | 26173.2229 | 2731.5 | 0.27677 | 32307.342 | 24796.8482 | 10.0709 | 0.1977 | -6.5171 | -21.0998 | 49.9526 | 33683.7167 | 28158.2331 | 1396.2349 | 4129.2486 | 33683.7167 | 100%
5 | C-CB20-82-CE | 30N0088 | C-CB20-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 20 | 0 | CUST 2 | 6/20/2015 | 6:51:27 | 10 Ton | 0:10:07 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 229.9 | 1.2 | 14.9 | 0 | 22559 | 169 | 22166 | 249 | 5166 | 258 | 27730 | 136 |  | 944 | [37 empty] | 8.4183 | 20% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 82F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 24 in. | 74.863 | 0.159 | 61.991 | 0.062 | 81.986 | 0.011 | 67.99 | 0.026 | 74.46 | 0.22 | 56.22 | 0.04 | 62.88 | 0.06 | 0.007 | 0.002 | 1.0688 | 0.0024 | 22559 | 169 | 5166 | 258 | 8.419 | 0.046 | [6 empty] | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2818.5 | 5.6 | 2818.5 | 5.6 | 2818.5 | 5.6 | 229.8 | 1.2 | 229.8 | 1.2 | 229.8 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.3 | 1.2 | 228.3 | 1.2 | 228.3 | 1.2 | 11.9 | 0 | 11.9 | 0 | 11.9 | 0 | 2604.8 | 4.3 | [9 empty] | 228.7 | 1.2 | 0.7 | 0 | 170.7 | 1 | 0.1 | 0.2 | 3250.5 | [10 empty] | 230.1 | 1.2 | 0 | 0 | 231.9 | 0.19 | 92.94 | 0.05 | 111.62 | 0.06 | 18.68 | 0.07 | 249.19 | 0.19 | 167.61 | 0.06 | 116.81 | 0.06 | 50.8 | 0.08 | 231.24 | 0.21 | 92.17 | 0.05 | 111.41 | 0.06 | 19.25 | 0.09 | 75.02 | 0.05 | 57.15 | 0.15 | 44.11 | 0.03 |  |  | 76 | 0.05 | 59.8 | 0.13 | 44.75 | 0.04 | 15.06 | 0.11 | [44 empty] | 13.04 | 0.14 | [74 empty] | 55.27 | 0.06 | 55.59 | 0.06 | 55.65 | 0.05 | 55.67 | 0.05 | 55.46 | 0.06 | 55.55 | 0.05 | [86 empty] | 134.97 | 0.05 | 82.17 | 0.06 | 170.23 | 0.08 | 82.02 | 0.08 | 82.01 | 0.04 | 75.17 | 0.17 | 75.06 | 0.17 | 75.2 | 0.17 | 75.19 | 0.17 | 75.13 | 0.18 | 75.14 | 0.18 | 75.07 | 0.19 | [40 empty] | 74.59 | 0.19 | [34 empty] | 81.94 | 0.07 | 78.61 | 0.1 | 78.52 | 0.14 | 74.92 | 0.19 | 80.87 | 0.14 | 75.49 | 0.18 | 75.87 | 0.17 | 75.44 | 0.18 | 74.92 | 0.19 | 76.86 | 0.2 | 79.57 | 0.15 | 75.8 | 0.17 | 75.13 | 0.19 | 77.44 | 0.16 | 80.54 | 0.1 | 76.78 | 0.14 | 78.11 | 0.15 | 81.96 | 0.08 | [12 empty] | C-55-CE-DM | 74.863 | 0.159 | 61.991 | 0.062 | 56.29 | 0.026 | 53.403 | 0.033 | 81.986 | 0.011 | 67.99 | 0.026 | 1120 | 1.3 | 1093.2 | 1.2 | 0.568 | 0.001 | -0.203 | 0.002 | 0.007 | 0.002 | 1.0688 | 0.0024 | 29.238 | 0 | 3294 | 9 | 475 | 5.4 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1117 | 5141.5538 | 72.9479 | 208.0871 | 908.1352 | 4233.4186 | 0.0092543 | 28.4018 | 55.1783 | 13.7482 | 13.07 | 0.011339 | 32.1203 | 0.0088071 | 27.6042 | 0.0079853 | 22.1816 | 76.1259 | 63.1088 | 21.9108 | 33373.8375 | 25848.7431 | 2819 | 0.28829 | 32001.6338 | 24476.5394 | 9.7151 | 0.19719 | -6.491 | -20.9476 | 50.033 | 33373.8375 | 27880.5294 | 1392.0669 | 4101.2411 | 33373.8375 | 100%
5 | C-CB30-82-CE | 30N0089 | C-CB30-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 30 | 0 | CUST 2 | 6/20/2015 | 6:20:53 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 1.3 | 15.4 | 0 | 22488 | 56 | 21970 | 74 | 4803 | 102 | 27296 | 93 |  | 944 | [37 empty] | 8.0235 | 30% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 33 in. | 74.932 | 0.034 | 61.972 | 0.025 | 81.947 | 0.017 | 68.017 | 0.021 | 74.47 | 0.05 | 56.42 | 0.04 | 62.77 | 0.06 | 0.01 | 0.003 | 1.0748 | 0.0033 | 22488 | 56 | 4803 | 102 | 8.022 | 0.034 | [6 empty] | 230 | 1.3 | 230 | 1.3 | 230 | 1.3 | 13.2 | 0 | 13.2 | 0 | 13.2 | 0 | 2926.6 | 5.6 | 2926.6 | 5.6 | 2926.6 | 5.6 | 229.8 | 1.3 | 229.8 | 1.3 | 229.8 | 1.3 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.3 | 1.3 | 228.3 | 1.3 | 228.3 | 1.3 | 12.4 | 0 | 12.4 | 0 | 12.4 | 0 | 2705.4 | 4.1 | [9 empty] | 228.7 | 1.3 | 0.8 | 0 | 176.2 | 1.1 | 0.1 | 0.2 | 3357.2 | [10 empty] | 230.2 | 1.3 | 0 | 0 | 242.41 | 0.18 | 95.74 | 0.05 | 114.8 | 0.05 | 19.06 | 0.03 | 259.8 | 0.17 | 167.48 | 0.04 | 119.87 | 0.05 | 47.61 | 0.05 | 241.79 | 0.18 | 95.14 | 0.03 | 114.62 | 0.05 | 19.48 | 0.05 | 75.95 | 0.02 | 53.37 | 0.51 | 44.71 | 0.02 |  |  | 76.86 | 0.02 | 54.3 | 0.32 | 45.3 | 0.02 | 9 | 0.32 | [44 empty] | 8.66 | 0.51 | [74 empty] | 55.33 | 0.03 | 55.67 | 0.04 | 55.76 | 0.03 | 55.77 | 0.02 | 55.55 | 0.03 | 55.62 | 0.04 | [86 empty] | 135.73 | 0.03 | 80.27 | 0.1 | 169.88 | 0.04 | 82.01 | 0.1 | 82.13 | 0.04 | 75.16 | 0.04 | 75.09 | 0.04 | 75.23 | 0.04 | 75.22 | 0.04 | 75.13 | 0.05 | 75.14 | 0.05 | 75.09 | 0.04 | [40 empty] | 74.5 | 0.05 | [34 empty] | 81.88 | 0.09 | 78.45 | 0.12 | 78.37 | 0.12 | 74.87 | 0.04 | 80.71 | 0.14 | 75.46 | 0.05 | 75.86 | 0.05 | 75.41 | 0.05 | 74.89 | 0.05 | 76.79 | 0.12 | 79.47 | 0.11 | 75.77 | 0.05 | 75.11 | 0.05 | 77.34 | 0.16 | 80.39 | 0.12 | 76.76 | 0.06 | 78 | 0.12 | 81.7 | 0.1 | [12 empty] | C-55-CE-DM | 74.932 | 0.034 | 61.972 | 0.025 | 56.461 | 0.01 | 53.552 | 0.011 | 81.947 | 0.017 | 68.017 | 0.021 | 1123.1 | 1.7 | 1096.2 | 1.7 | 0.567 | 0.001 | -0.203 | 0.002 | 0.01 | 0.003 | 1.0748 | 0.0033 | 29.235 | 0 | 3402 | 9 | 475.6 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1105 | 5153.9454 | 73.0193 | 208.0814 | 908.16 | 4245.7854 | 0.0092347 | 28.3918 | 55.3505 | 13.7474 | 13.0746 | 0.011369 | 32.1431 | 0.0087782 | 27.5894 | 0.0080281 | 22.2697 | 76.1729 | 63.0963 | 21.9992 | 32947.0188 | 25756.1642 | 2926.4 | 0.30315 | 31573.0111 | 24382.1564 | 9.2807 | 0.19735 | -6.3926 | -20.8224 | 50.231 | 32947.0188 | 27417.5179 | 1394.006 | 4135.4949 | 32947.0188 | 100%
5 | C-CB40-82-CE | 30N0090 | C-CB40-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 40 | 0 | CUST 2 | 6/20/2015 | 5:45:58 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 15.8 | 0 | 22353 | 51 | 21936 | 76 | 4633 | 75 | 26989 | 80 |  | 945 | [37 empty] | 7.6979 | 40% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 37 in. | 74.955 | 0.024 | 61.981 | 0.022 | 82.002 | 0.012 | 67.993 | 0.028 | 74.61 | 0.06 | 56.55 | 0.04 | 62.55 | 0.03 | 0.003 | 0.002 | 1.0698 | 0.0027 | 22353 | 51 | 4633 | 75 | 7.698 | 0.028 | [6 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 13.6 | 0 | 13.6 | 0 | 13.6 | 0 | 3030.4 | 4.7 | 3030.4 | 4.7 | 3030.4 | 4.7 | 229.8 | 1.1 | 229.8 | 1.1 | 229.8 | 1.1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 1.1 | 228.2 | 1.1 | 228.2 | 1.1 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2803.8 | 3.6 | [9 empty] | 228.7 | 1.1 | 0.8 | 0 | 179.8 | 1 | 0.1 | 0.2 | 3459.1 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 252.42 | 0.13 | 98.3 | 0.03 | 117.74 | 0.04 | 19.44 | 0.03 | 270.05 | 0.11 | 165.77 | 0.05 | 122.74 | 0.03 | 43.03 | 0.05 | 251.79 | 0.11 | 97.8 | 0.04 | 117.56 | 0.03 | 19.77 | 0.04 | 76.54 | 0.02 | 48.19 | 0.03 | 45.1 | 0.01 |  |  | 77.48 | 0.02 | 50.15 | 0.06 | 45.69 | 0.01 | 4.45 | 0.06 | [44 empty] | 3.1 | 0.03 | [74 empty] | 55.43 | 0.02 | 55.76 | 0.02 | 55.85 | 0.02 | 55.85 | 0.02 | 55.65 | 0.02 | 55.71 | 0.02 | [86 empty] | 133.9 | 0.04 | 76.76 | 0.06 | 168.12 | 0.08 | 82.25 | 0.08 | 82.06 | 0.06 | 75.24 | 0.03 | 75.15 | 0.04 | 75.31 | 0.04 | 75.3 | 0.04 | 75.24 | 0.04 | 75.25 | 0.04 | 75.18 | 0.05 | [40 empty] | 74.58 | 0.05 | [34 empty] | 82.05 | 0.06 | 78.51 | 0.07 | 78.44 | 0.08 | 74.91 | 0.04 | 80.66 | 0.1 | 75.51 | 0.04 | 75.89 | 0.05 | 75.47 | 0.05 | 74.96 | 0.04 | 76.79 | 0.11 | 79.45 | 0.1 | 75.81 | 0.05 | 75.19 | 0.04 | 77.39 | 0.11 | 80.47 | 0.11 | 76.79 | 0.07 | 78.1 | 0.08 | 81.75 | 0.08 | [12 empty] | C-55-CE-DM | 74.955 | 0.024 | 61.981 | 0.022 | 56.553 | 0.007 | 53.646 | 0.011 | 82.002 | 0.012 | 67.993 | 0.028 | 1120.3 | 1.4 | 1093.8 | 1.4 | 0.567 | 0.001 | -0.202 | 0.001 | 0.003 | 0.002 | 1.0698 | 0.0027 | 29.232 | 0 | 3506 | 8 | 475.5 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1136 | 5140.0853 | 72.8595 | 207.5769 | 905.8827 | 4234.2026 | 0.0092297 | 28.3934 | 55.4394 | 13.7486 | 13.0772 | 0.011338 | 32.1225 | 0.0087787 | 27.5956 | 0.008059 | 22.3257 | 76.2017 | 63.099 | 22.0544 | 32582.933 | 25612.8691 | 3030.5 | 0.31744 | 31208.7209 | 24238.657 | 8.9015 | 0.19614 | -6.339 | -20.7624 | 50.3735 | 32582.933 | 27087.8132 | 1394.2918 | 4100.828 | 32582.933 | 100%
5 | C-CB5-82-CE | 30N0091 | C-CB5-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 5 | 0 | CUST 2 | 6/20/2015 | 7:47:34 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 1.2 | 14.4 | 0 | 22762 | 36 | 22342 | 88 | 5160 | 98 | 27927 | 114 |  | 944 | [37 empty] | 8.8126 | 5% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code tester | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 7 in. | 74.954 | 0.023 | 61.981 | 0.027 | 81.998 | 0.016 | 67.992 | 0.019 | 74.55 | 0.08 | 56.27 | 0.03 | 62.93 | 0.07 | 0.012 | 0.002 | 1.0827 | 0.0032 | 22762 | 36 | 5160 | 98 | 8.812 | 0.045 | [6 empty] | 230 | 1.2 | 230 | 1.2 | 230 | 1.2 | 12.2 | 0 | 12.2 | 0 | 12.2 | 0 | 2691.9 | 6 | 2691.9 | 6 | 2691.9 | 6 | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.5 | 1.2 | 228.5 | 1.2 | 228.5 | 1.2 | 11.4 | 0 | 11.4 | 0 | 11.4 | 0 | 2479.4 | 4.6 | [9 empty] | 228.9 | 1.2 | 0.8 | 0 | 171.4 | 1.1 | 0.1 | 0.2 | 3127.8 | [10 empty] | 230.3 | 1.2 | 0 | 0 | 218.56 | 0.22 | 89.2 | 0.06 | 107.43 | 0.07 | 18.23 | 0.04 | 235.48 | 0.21 | 166.98 | 0.05 | 112.71 | 0.06 | 54.26 | 0.04 | 217.89 | 0.23 | 88.52 | 0.05 | 107.21 | 0.07 | 18.7 | 0.05 | 73.42 | 0.03 | 60.29 | 0.05 | 43.07 | 0.02 |  |  | 74.3 | 0.02 | 61.91 | 0.04 | 43.64 | 0.02 | 18.26 | 0.04 | [44 empty] | 17.23 | 0.04 | [74 empty] | 55.32 | 0.03 | 55.64 | 0.03 | 55.75 | 0.02 | 55.74 | 0.03 | 55.46 | 0.03 | 55.58 | 0.03 | [86 empty] | 135.49 | 0.03 | 85 | 0.03 | 169.82 | 0.05 | 82.16 | 0.09 | 82.09 | 0.06 | 75.26 | 0.06 | 75.14 | 0.06 | 75.36 | 0.06 | 75.32 | 0.05 | 75.23 | 0.06 | 75.24 | 0.06 | 75.14 | 0.07 | [40 empty] | 74.56 | 0.06 | [34 empty] | 81.99 | 0.08 | 78.55 | 0.1 | 78.52 | 0.09 | 74.96 | 0.06 | 80.75 | 0.13 | 75.4 | 0.06 | 75.8 | 0.06 | 75.37 | 0.07 | 74.87 | 0.06 | 76.76 | 0.09 | 79.47 | 0.11 | 75.74 | 0.07 | 75.06 | 0.07 | 77.33 | 0.12 | 80.36 | 0.1 | 76.75 | 0.07 | 78.01 | 0.1 | 81.83 | 0.07 | [12 empty] | C-55-CE-DM | 74.954 | 0.023 | 61.981 | 0.027 | 56.338 | 0.01 | 53.385 | 0.011 | 81.998 | 0.016 | 67.992 | 0.019 | 1126.9 | 1.6 | 1100.6 | 1.7 | 0.568 | 0.001 | -0.203 | 0.001 | 0.012 | 0.002 | 1.0827 | 0.0032 | 29.254 | 0 | 3169 | 9 | 477 | 5.3 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1091 | 5172.814 | 73.4417 | 208.0893 | 908.1255 | 4264.6885 | 0.0092282 | 28.3902 | 55.2289 | 13.7485 | 13.071 | 0.011338 | 32.1217 | 0.008779 | 27.5956 | 0.0079639 | 22.1701 | 76.1954 | 63.0945 | 21.9 | 33572.807 | 26029.3779 | 2692 | 0.27367 | 32195.4627 | 24652.0336 | 10.1595 | 0.20164 | -6.4902 | -20.9665 | 49.9334 | 33572.807 | 28065.301 | 1397.2276 | 4110.2784 | 33572.807 | 100%
5 | C-CB50-82-CE | 30N0092 | C-CB50-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 50 | 0 | CUST 2 | 6/20/2015 | 5:01:57 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 229.9 | 1 | 16.3 | 0 | 22208 | 44 | 21671 | 63 | 4304 | 117 | 26517 | 98 |  | 944 | [37 empty] | 7.3597 | 50% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 41.75` | 75.038 | 0.017 | 61.998 | 0.045 | 81.994 | 0.008 | 68 | 0.017 | 74.67 | 0.04 | 56.78 | 0.03 | 62.48 | 0.02 | 0 | 0.003 | 1.0644 | 0.0041 | 22208 | 44 | 4304 | 117 | 7.359 | 0.031 | [6 empty] | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 14.1 | 0 | 14.1 | 0 | 14.1 | 0 | 3128.3 | 4.4 | 3128.3 | 4.4 | 3128.3 | 4.4 | 229.9 | 1 | 229.9 | 1 | 229.9 | 1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 1 | 228.2 | 1 | 228.2 | 1 | 13.3 | 0 | 13.3 | 0 | 13.3 | 0 | 2904.8 | 3.4 | [9 empty] | 228.7 | 1 | 0.8 | 0 | 174.6 | 1.1 | 0.1 | 0.2 | 3554.2 | [10 empty] | 230.2 | 1 | 0 | 0 | 262.82 | 0.13 | 101.06 | 0.03 | 120.72 | 0.04 | 19.66 | 0.03 | 280.45 | 0.13 | 165.06 | 0.07 | 125.58 | 0.04 | 39.48 | 0.06 | 262.18 | 0.14 | 100.91 | 0.02 | 120.54 | 0.04 | 19.63 | 0.05 | 77.08 | 0.03 | 48.22 | 0.04 | 45.44 | 0.02 |  |  | 77.85 | 0.03 | 49.84 | 0.04 | 45.93 | 0.02 | 3.91 | 0.03 | [44 empty] | 2.78 | 0.03 | [74 empty] | 55.58 | 0.04 | 55.91 | 0.04 | 56 | 0.04 | 56.02 | 0.03 | 55.77 | 0.04 | 55.86 | 0.04 | [86 empty] | 133.52 | 0.05 | 66.98 | 0.38 | 167.41 | 0.08 | 81.87 | 0.07 | 82.1 | 0.07 | 75.22 | 0.02 | 75.14 | 0.04 | 75.25 | 0.03 | 75.26 | 0.03 | 75.2 | 0.03 | 75.22 | 0.03 | 75.17 | 0.05 | [40 empty] | 74.55 | 0.05 | [34 empty] | 81.6 | 0.05 | 78.58 | 0.13 | 78.43 | 0.1 | 74.88 | 0.05 | 80.88 | 0.12 | 75.55 | 0.05 | 75.93 | 0.05 | 75.52 | 0.03 | 74.98 | 0.05 | 76.88 | 0.11 | 79.62 | 0.09 | 75.87 | 0.05 | 75.24 | 0.05 | 77.55 | 0.13 | 80.56 | 0.11 | 76.82 | 0.06 | 78.08 | 0.12 | 82.09 | 0.14 | [12 empty] | C-55-CE-DM | 75.038 | 0.017 | 61.998 | 0.045 | 56.701 | 0.01 | 53.8 | 0.017 | 81.994 | 0.008 | 68 | 0.017 | 1117.5 | 2.2 | 1090.9 | 2.2 | 0.568 | 0.002 | -0.203 | 0.001 | 0 | 0.003 | 1.0644 | 0.0041 | 29.227 | 0 | 3603 | 8 | 474.8 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.115 | 5125.6121 | 72.7945 | 208.0889 | 908.127 | 4217.485 | 0.0092265 | 28.4078 | 55.586 | 13.7484 | 13.0814 | 0.011345 | 32.1284 | 0.0087703 | 27.6066 | 0.0081104 | 22.4176 | 76.2752 | 63.1199 | 22.146 | 32095.4904 | 25450.7516 | 3128.2 | 0.33265 | 30723.4455 | 24078.7067 | 8.5272 | 0.19406 | -6.2618 | -20.6892 | 50.6044 | 32095.4904 | 26596.9576 | 1392.2235 | 4106.3093 | 32095.4904 | 100%
5 | C-CB60-82-CE | 30N0093 | C-CB60-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 60 | 0 | CUST 2 | 6/20/2015 | 4:14:36 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 0.9 | 16.3 | 0 | 21746 | 53 | 21463 | 93 | 4495 | 146 | 26245 | 128 |  | 944 | [37 empty] | 7.254 | 60% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 43` | 74.884 | 0.059 | 61.974 | 0.05 | 81.971 | 0.007 | 67.991 | 0.02 | 74.48 | 0.09 | 56.46 | 0.02 | 62.44 | 0.03 | -0.033 | 0.003 | 1.0295 | 0.0035 | 21746 | 53 | 4495 | 146 | 7.254 | 0.039 | [6 empty] | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 14.1 | 0 | 14.1 | 0 | 14.1 | 0 | 3145.9 | 4 | 3145.9 | 4 | 3145.9 | 4 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 0.9 | 228.2 | 0.9 | 228.2 | 0.9 | 13.3 | 0 | 13.3 | 0 | 13.3 | 0 | 2923 | 3.3 | [9 empty] | 228.7 | 0.9 | 0.8 | 0 | 173.8 | 0.9 | 0.1 | 0.2 | 3568.9 | [10 empty] | 230.2 | 0.9 | 0 | 0 | 264.64 | 0.17 | 101.72 | 0.03 | 121.23 | 0.05 | 19.51 | 0.04 | 282.16 | 0.16 | 164.82 | 0.06 | 126.04 | 0.04 | 38.78 | 0.07 | 263.95 | 0.16 | 101.36 | 0.04 | 121.03 | 0.04 | 19.68 | 0.04 | 77.04 | 0.04 | 48.1 | 0.04 | 45.42 | 0.02 |  |  | 77.6 | 0.04 | 49.25 | 0.04 | 45.77 | 0.03 | 3.48 | 0.03 | [44 empty] | 2.68 | 0.03 | [74 empty] | 55.61 | 0.03 | 55.92 | 0.03 | 55.96 | 0.03 | 55.92 | 0.03 | 55.79 | 0.03 | 55.83 | 0.02 | [86 empty] | 132.64 | 0.05 | 64.68 | 0.31 | 166.99 | 0.09 | 81.45 | 0.09 | 82 | 0.07 | 74.99 | 0.08 | 74.99 | 0.06 | 74.84 | 0.09 | 74.91 | 0.09 | 74.92 | 0.08 | 75 | 0.08 | 75.08 | 0.06 | [40 empty] | 74.76 | 0.07 | [34 empty] | 81.48 | 0.07 | 78.59 | 0.09 | 78.46 | 0.1 | 74.92 | 0.08 | 81.09 | 0.12 | 75.75 | 0.05 | 76.1 | 0.06 | 75.73 | 0.05 | 75.2 | 0.05 | 77.12 | 0.12 | 79.73 | 0.11 | 76.06 | 0.06 | 75.42 | 0.06 | 77.66 | 0.17 | 80.6 | 0.09 | 76.9 | 0.07 | 78.16 | 0.1 | 81.99 | 0.09 | [12 empty] | C-55-CE-DM | 74.884 | 0.059 | 61.974 | 0.05 | 56.633 | 0.011 | 53.717 | 0.018 | 81.971 | 0.007 | 67.991 | 0.02 | 1098.9 | 1.9 | 1072.8 | 1.8 | 0.576 | 0.001 | -0.195 | 0.001 | -0.033 | 0.003 | 1.0295 | 0.0035 | 29.225 | 0.001 | 3618 | 7 | 472.1 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1267 | 5041.0553 | 72.5949 | 203.943 | 890.0723 | 4150.983 | 0.0092416 | 28.3914 | 55.5063 | 13.7479 | 13.0794 | 0.011343 | 32.1213 | 0.0087909 | 27.5916 | 0.0080799 | 22.3679 | 76.1401 | 63.095 | 22.0934 | 31748.2829 | 24963.8374 | 3145.9 | 0.33819 | 30384.7721 | 23600.3266 | 8.3982 | 0.19692 | -6.2979 | -20.6338 | 50.4469 | 31748.2829 | 26332.9918 | 1383.4868 | 4031.8043 | 31748.2829 | 100%
5 | C-CB70-82-CE | 30N0094 | C-CB70-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 70 | 0 | CUST 2 | 6/20/2015 | 3:43:38 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 0.6 | 16.7 | 0 | 21826 | 34 | 21412 | 69 | 3843 | 84 | 25672 | 103 |  | 944 | [37 empty] | 6.9215 | 70% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 82F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 46` | 75.024 | 0.04 | 61.992 | 0.033 | 81.973 | 0.012 | 68.013 | 0.027 | 74.48 | 0.05 | 56.86 | 0.02 | 62.6 | 0.03 | 0.001 | 0.003 | 1.0724 | 0.0043 | 21826 | 34 | 3843 | 84 | 6.921 | 0.029 | [6 empty] | 230 | 0.6 | 230 | 0.6 | 230 | 0.6 | 14.5 | 0 | 14.5 | 0 | 14.5 | 0 | 3233.4 | 3.5 | 3233.4 | 3.5 | 3233.4 | 3.5 | 229.9 | 0.6 | 229.9 | 0.6 | 229.9 | 0.6 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 0.6 | 228.2 | 0.6 | 228.2 | 0.6 | 13.7 | 0 | 13.7 | 0 | 13.7 | 0 | 3011.4 | 3.1 | [9 empty] | 228.8 | 0.6 | 0.8 | 0 | 171.4 | 0.7 | 0 | 0.2 | 3658.6 | [10 empty] | 230.3 | 0.6 | 0 | 0 | 273.71 | 0.22 | 104.21 | 0.05 | 123.75 | 0.06 | 19.53 | 0.04 | 291.27 | 0.22 | 165.77 | 0.05 | 128.45 | 0.06 | 37.31 | 0.05 | 273.1 | 0.22 | 103.85 | 0.04 | 123.58 | 0.06 | 19.73 | 0.06 | 77.72 | 0.04 | 48.18 | 0.03 | 45.84 | 0.03 |  |  | 78.04 | 0.04 | 49.55 | 0.04 | 46.05 | 0.03 | 3.5 | 0.03 | [44 empty] | 2.34 | 0.02 | [74 empty] | 56.15 | 0.03 | 56.47 | 0.03 | 56.5 | 0.03 | 56.43 | 0.03 | 56.36 | 0.03 | 56.39 | 0.04 | [86 empty] | 133.83 | 0.05 | 61.68 | 0.09 | 168.05 | 0.07 | 81.59 | 0.17 | 81.93 | 0.13 | 75.13 | 0.05 | 75.11 | 0.04 | 75 | 0.05 | 75.07 | 0.05 | 75.06 | 0.05 | 75.11 | 0.05 | 75.16 | 0.05 | [40 empty] | 74.87 | 0.05 | [34 empty] | 81 | 0.11 | 79.2 | 0.11 | 79 | 0.12 | 75.01 | 0.04 | 81.7 | 0.13 | 75.81 | 0.04 | 76.23 | 0.05 | 75.78 | 0.04 | 75.24 | 0.05 | 77.26 | 0.12 | 80.21 | 0.11 | 76.14 | 0.05 | 75.47 | 0.05 | 78.04 | 0.15 | 81.32 | 0.15 | 77.11 | 0.06 | 78.52 | 0.11 | 83.01 | 0.16 | [12 empty] | C-55-CE-DM | 75.024 | 0.04 | 61.992 | 0.033 | 57.057 | 0.014 | 54.106 | 0.019 | 81.973 | 0.012 | 68.013 | 0.027 | 1121.9 | 2.2 | 1094.7 | 2.2 | 0.565 | 0.001 | -0.202 | 0.001 | 0.001 | 0.003 | 1.0724 | 0.0043 | 29.224 | 0 | 3709 | 6 | 475.8 | 4.9 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1146 | 5141.9778 | 72.6622 | 207.5726 | 905.9011 | 4236.0767 | 0.009226 | 28.4018 | 55.9424 | 13.748 | 13.0911 | 0.01136 | 32.1394 | 0.0087697 | 27.6025 | 0.0081988 | 22.6003 | 76.253 | 63.1114 | 22.3288 | 31227.4313 | 25064.8147 | 3233.2 | 0.35337 | 29851.5221 | 23688.9055 | 8.0484 | 0.19716 | -6.073 | -20.3106 | 50.9547 | 31227.4313 | 25721.0691 | 1396.3695 | 4109.9927 | 31227.4313 | 100%
5 | C-CB80-82-CE | 30N0095 | C-CB80-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 80 | 0 | CUST 2 | 6/20/2015 | 3:01:00 | 10 Ton | 0:10:00 | 75/68 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 68 | 82 | 68 | 5.5 |  | 5.5 |  | 229.9 | 1.3 | 17.2 | 0 | 21296 | 25 | 20852 | 51 | 3564 | 94 | 24864 | 93 |  | 944 | [37 empty] | 6.5174 | 80% condenser coil block, economizer closed (2.8V), factory charge (5.5 lbs) 82F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 51` | 75.022 | 0.017 | 62.004 | 0.031 | 81.955 | 0.013 | 67.994 | 0.023 | 74.5 | 0.04 | 57.1 | 0.03 | 63.59 | 0.04 | -0.007 | 0.002 | 1.0472 | 0.0025 | 21296 | 25 | 3564 | 94 | 6.517 | 0.027 | [6 empty] | 229.9 | 1.3 | 229.9 | 1.3 | 229.9 | 1.3 | 15 | 0 | 15 | 0 | 15 | 0 | 3342.1 | 4.6 | 3342.1 | 4.6 | 3342.1 | 4.6 | 229.8 | 1.3 | 229.8 | 1.3 | 229.8 | 1.3 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228 | 1.3 | 228 | 1.3 | 228 | 1.3 | 14.2 | 0 | 14.2 | 0 | 14.2 | 0 | 3119 | 3.7 | [9 empty] | 228.6 | 1.3 | 0.8 | 0 | 170.9 | 1.1 | 0 | 0.2 | 3763 | [10 empty] | 230.2 | 1.3 | 0 | 0 | 285.04 | 0.18 | 107.67 | 0.05 | 126.8 | 0.05 | 19.14 | 0.03 | 302.39 | 0.17 | 166.76 | 0.03 | 131.33 | 0.05 | 35.43 | 0.05 | 284.45 | 0.18 | 107.63 | 0.04 | 126.65 | 0.05 | 19.02 | 0.05 | 78.39 | 0.02 | 48.53 | 0.03 | 46.27 | 0.02 |  |  | 78.05 | 0.02 | 50.12 | 0.03 | 46.05 | 0.02 | 4.06 | 0.03 | [44 empty] | 2.26 | 0.02 | [74 empty] | 56.33 | 0.03 | 56.65 | 0.03 | 56.65 | 0.02 | 56.63 | 0.02 | 56.53 | 0.02 | 56.57 | 0.02 | [86 empty] | 134.95 | 0.03 | 60.94 | 0.06 | 168.88 | 0.06 | 81.65 | 0.14 | 82.08 | 0.13 | 75.18 | 0.03 | 75.15 | 0.03 | 75.04 | 0.04 | 75.11 | 0.04 | 75.09 | 0.04 | 75.15 | 0.04 | 75.18 | 0.04 | [40 empty] | 74.89 | 0.05 | [34 empty] | 80.83 | 0.07 | 78.93 | 0.09 | 78.79 | 0.1 | 75.03 | 0.04 | 81.55 | 0.14 | 75.83 | 0.04 | 76.24 | 0.05 | 75.81 | 0.04 | 75.25 | 0.05 | 77.27 | 0.11 | 80.11 | 0.13 | 76.18 | 0.05 | 75.47 | 0.04 | 77.89 | 0.15 | 81.02 | 0.11 | 77.11 | 0.06 | 78.36 | 0.12 | 82.52 | 0.12 | [12 empty] | C-55-CE-DM | 75.022 | 0.017 | 62.004 | 0.031 | 57.259 | 0.01 | 54.281 | 0.01 | 81.955 | 0.013 | 67.994 | 0.023 | 1109.6 | 1.3 | 1080.5 | 1.3 | 0.57 | 0.001 | -0.199 | 0.001 | -0.007 | 0.002 | 1.0472 | 0.0025 | 29.221 | 0.001 | 3815 | 8 | 473.1 | 5.4 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1207 | 5083.4608 | 72.3544 | 206.0215 | 899.1665 | 4184.2943 | 0.0092329 | 28.4094 | 56.1383 | 13.7475 | 13.0966 | 0.01135 | 32.1241 | 0.0087781 | 27.6112 | 0.0082502 | 22.7054 | 76.253 | 63.1217 | 22.4323 | 30384.6168 | 24540.649 | 3341.9 | 0.37538 | 29016.8719 | 23172.9041 | 7.606 | 0.1986 | -5.9772 | -20.1148 | 51.1534 | 30384.6168 | 24938.5915 | 1388.2137 | 4057.8115 | 30384.6168 | 100%
5 | C-CB0-95-CE | 30N0096 | C-CB0-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/18/2015 | 20:12:22 | 10 Ton | 0:10:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1.1 | 16 | 0 | 18411 | 27 | 18034 | 50 | 587 | 90 | 18999 | 88 |  | 944 | [37 empty] | 5.3685 | Baseline no condenser coil blockage, economizer closed (2.8V), factory charge (5.5 lbs) 95F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 74.99 | 0.006 | 61.949 | 0.038 | 94.989 | 0.007 | 74.988 | 0.03 | 74.65 | 0.04 | 59.58 | 0.03 | 64.37 | 0.02 | -0.014 | 0.003 | 1.0549 | 0.003 | 18411 | 27 | 587 | 90 | 5.369 | 0.027 | [6 empty] | 230 | 1.1 | 230 | 1.1 | 230 | 1.1 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3064 | 5.7 | 3064 | 5.7 | 3064 | 5.7 | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.3 | 1.1 | 228.3 | 1.1 | 228.3 | 1.1 | 13 | 0 | 13 | 0 | 13 | 0 | 2842.6 | 4.8 | [9 empty] | 228.7 | 1.1 | 0.7 | 0 | 169.5 | 0.9 | 0.1 | 0.2 | 3487.1 | [10 empty] | 230.3 | 1.1 | 0 | 0 | 256.79 | 0.23 | 102.59 | 0.04 | 118.99 | 0.07 | 16.41 | 0.04 | 273.42 | 0.2 | 178.98 | 0.06 | 123.65 | 0.05 | 55.33 | 0.04 | 256.05 | 0.22 | 102.15 | 0.05 | 118.78 | 0.06 | 16.63 | 0.05 | 77.94 | 0.04 | 59.95 | 0.16 | 45.97 | 0.03 |  |  | 78.4 | 0.05 | 60.56 | 0.41 | 46.26 | 0.03 | 14.31 | 0.4 | [44 empty] | 13.98 | 0.14 | [74 empty] | 58.42 | 0.03 | 58.78 | 0.03 | 58.89 | 0.04 | 58.93 | 0.04 | 58.62 | 0.03 | 58.73 | 0.03 | [86 empty] | 149.79 | 0.05 | 87.61 | 0.07 | 180.51 | 0.08 | 95.81 | 0.08 | 94.56 | 0.12 | 75.54 | 0.04 | 75.38 | 0.04 | 75.51 | 0.04 | 75.46 | 0.03 | 75.33 | 0.03 | 75.33 | 0.03 | 75.24 | 0.03 | [40 empty] | 74.52 | 0.03 | [34 empty] | 95.3 | 0.08 | 84.81 | 0.3 | 85.08 | 0.25 | 74.94 | 0.03 | 90.33 | 0.31 | 75.59 | 0.03 | 76.86 | 0.1 | 76.03 | 0.06 | 75.05 | 0.03 | 79.07 | 0.25 | 86.97 | 0.26 | 77.05 | 0.11 | 75.26 | 0.05 | 81.82 | 0.3 | 90.07 | 0.33 | 80.26 | 0.14 | 83.4 | 0.31 | 95.12 | 0.15 | [12 empty] | C-55-CE-DM | 74.99 | 0.006 | 61.949 | 0.038 | 59.601 | 0.014 | 56.16 | 0.02 | 94.989 | 0.007 | 74.988 | 0.03 | 1115.9 | 1.6 | 1081.7 | 1.5 | 0.57 | 0.002 | -0.197 | 0.001 | -0.014 | 0.003 | 1.0549 | 0.003 | 29.162 | 0 | 3539 | 9 | 474.9 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1246 | 5087.6561 | 72.4347 | 207.5918 | 883.3963 | 4204.2598 | 0.0096459 | 29.408 | 58.4764 | 14.0996 | 13.1601 | 0.013913 | 38.1457 | 0.0087494 | 27.572 | 0.0087823 | 23.8547 | 78.4895 | 64.4972 | 23.5804 | 29648.6728 | 24436.7315 | 3064.1 | 0.35272 | 28275.0588 | 23063.1175 | 7.9896 | 0.21919 | -5.8276 | -20.0131 | 52.8583 | 29648.6728 | 18912.3687 | 1395.5225 | 9340.7816 | 29648.6728 | 100%
5 | C-CB10-95-CE | 30N0097 | C-CB10-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 10 | 0 | CUST 2 | 6/19/2015 | 6:07:04 | 10 Ton | 0:10:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 0.9 | 16.4 | 0 | 18584 | 23 | 18304 | 36 | 395 | 91 | 18979 | 89 |  | 943 | [37 empty] | 5.2255 | 10% condenser coil block(~10 psig DP above C-CB0-95-CE), economizer closed (2.8V)--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from f | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 12`.; | 74.989 | 0.004 | 61.999 | 0.032 | 94.991 | 0.01 | 75.001 | 0.026 | 74.59 | 0.04 | 59.41 | 0.05 | 64.35 | 0.02 | -0.007 | 0.002 | 1.068 | 0.0026 | 18584 | 23 | 395 | 91 | 5.225 | 0.025 | [6 empty] | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 14.2 | 0 | 14.2 | 0 | 14.2 | 0 | 3157.1 | 5.2 | 3157.1 | 5.2 | 3157.1 | 5.2 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 0.9 | 228.2 | 0.9 | 228.2 | 0.9 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2933 | 4.6 | [9 empty] | 228.7 | 0.9 | 0.7 | 0 | 170.2 | 0.9 | 0.1 | 0.2 | 3578.3 | [10 empty] | 230.3 | 0.9 | 0 | 0 | 266.61 | 0.23 | 104.23 | 0.05 | 121.78 | 0.07 | 17.55 | 0.04 | 283.53 | 0.23 | 176.01 | 0.04 | 126.4 | 0.06 | 49.6 | 0.06 | 265.94 | 0.23 | 103.68 | 0.05 | 121.6 | 0.06 | 17.92 | 0.08 | 78.96 | 0.04 | 50.89 | 0.16 | 46.64 | 0.02 |  |  | 79.84 | 0.02 | 52.74 | 0.1 | 47.19 | 0.01 | 5.54 | 0.1 | [44 empty] | 4.25 | 0.17 | [74 empty] | 58.6 | 0.02 | 58.94 | 0.02 | 59 | 0.02 | 59.02 | 0.02 | 58.82 | 0.02 | 58.91 | 0.02 | [86 empty] | 144.16 | 0.07 | 82.05 | 0.04 | 178.44 | 0.06 | 95.53 | 0.06 | 94.37 | 0.08 | 75.57 | 0.03 | 75.45 | 0.02 | 75.48 | 0.03 | 75.45 | 0.02 | 75.3 | 0.03 | 75.3 | 0.03 | 75.28 | 0.03 | [40 empty] | 74.71 | 0.02 | [34 empty] | 95.11 | 0.1 | 85.16 | 0.22 | 85.16 | 0.26 | 75.1 | 0.02 | 90.63 | 0.31 | 75.78 | 0.04 | 77.08 | 0.1 | 76.22 | 0.07 | 75.21 | 0.04 | 79.4 | 0.32 | 87.26 | 0.32 | 77.19 | 0.13 | 75.43 | 0.05 | 82.19 | 0.4 | 90.22 | 0.24 | 80.41 | 0.14 | 83.6 | 0.29 | 95.16 | 0.06 | [12 empty] | C-55-CE-DM | 74.989 | 0.004 | 61.999 | 0.032 | 59.572 | 0.007 | 56.257 | 0.014 | 94.991 | 0.01 | 75.001 | 0.026 | 1121.1 | 1.3 | 1090.2 | 1.3 | 0.567 | 0.002 | -0.199 | 0.001 | -0.007 | 0.002 | 1.068 | 0.0026 | 29.253 | 0 | 3632 | 8 | 475.1 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1194 | 5111.4553 | 72.6197 | 208.6439 | 887.8648 | 4223.5905 | 0.0096756 | 29.4407 | 58.4526 | 14.0997 | 13.1599 | 0.013924 | 38.1583 | 0.0087826 | 27.6081 | 0.0088463 | 23.9172 | 78.4902 | 64.5401 | 23.6442 | 29628.4475 | 24581.1419 | 3156.9 | 0.36365 | 28254.7822 | 23207.4765 | 7.7794 | 0.21003 | -5.7965 | -20.0376 | 53.1253 | 29628.4475 | 18865.5813 | 1395.7373 | 9367.1289 | 29628.4475 | 100%
5 | C-CB20-95-CE | 30N0098 | C-CB20-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 20 | 0 | CUST 2 | 6/19/2015 | 7:29:25 | 10 Ton | 0:10:00 | 75/62 - 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 0.9 | 16.9 | 0 | 18421 | 33 | 18009 | 45 | 102 | 97 | 18523 | 114 |  | 943 | [37 empty] | 4.9633 | 20% condenser coil block(~30 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from f | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 12`.; | 75.014 | 0.008 | 62.013 | 0.036 | 95.014 | 0.006 | 74.997 | 0.027 | 74.65 | 0.06 | 59.76 | 0.05 | 64.89 | 0.03 | 0.003 | 0.002 | 1.0759 | 0.003 | 18421 | 33 | 102 | 97 | 4.964 | 0.033 | [6 empty] | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 14.7 | 0 | 14.7 | 0 | 14.7 | 0 | 3256 | 4.3 | 3256 | 4.3 | 3256 | 4.3 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 0.9 | 228.2 | 0.9 | 228.2 | 0.9 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3030.1 | 4 | [9 empty] | 228.7 | 0.9 | 0.7 | 0 | 169.6 | 0.8 | 0.1 | 0.2 | 3675.3 | [10 empty] | 230.3 | 0.9 | 0 | 0 | 276.16 | 0.2 | 107.1 | 0.05 | 124.42 | 0.05 | 17.32 | 0.03 | 293.24 | 0.18 | 175.64 | 0.05 | 128.97 | 0.05 | 46.66 | 0.09 | 275.51 | 0.17 | 106.3 | 0.08 | 124.25 | 0.05 | 17.94 | 0.07 | 79.63 | 0.03 | 50.63 | 0.04 | 47.07 | 0.02 |  |  | 80.92 | 0.02 | 52.61 | 0.04 | 47.88 | 0.02 | 4.73 | 0.04 | [44 empty] | 3.56 | 0.04 | [74 empty] | 58.74 | 0.04 | 59.08 | 0.03 | 59.16 | 0.04 | 59.21 | 0.03 | 58.93 | 0.03 | 59.04 | 0.03 | [86 empty] | 143.41 | 0.05 | 80.84 | 0.09 | 177.97 | 0.09 | 95.63 | 0.08 | 94.53 | 0.07 | 75.62 | 0.04 | 75.45 | 0.03 | 75.54 | 0.04 | 75.51 | 0.04 | 75.36 | 0.03 | 75.36 | 0.04 | 75.27 | 0.04 | [40 empty] | 74.6 | 0.04 | [34 empty] | 95.29 | 0.09 | 85.12 | 0.29 | 85.12 | 0.29 | 75 | 0.04 | 90.72 | 0.31 | 75.77 | 0.03 | 77.08 | 0.09 | 76.19 | 0.06 | 75.22 | 0.04 | 79.38 | 0.31 | 87.33 | 0.25 | 77.17 | 0.11 | 75.42 | 0.06 | 82.29 | 0.31 | 90.26 | 0.28 | 80.44 | 0.12 | 83.71 | 0.3 | 95.17 | 0.1 | [12 empty] | C-55-CE-DM | 75.014 | 0.008 | 62.013 | 0.036 | 59.777 | 0.006 | 56.434 | 0.018 | 95.014 | 0.006 | 74.997 | 0.027 | 1125.4 | 1.6 | 1093.9 | 1.6 | 0.568 | 0.002 | -0.197 | 0.001 | 0.003 | 0.002 | 1.0759 | 0.003 | 29.272 | 0 | 3732 | 7 | 475.6 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.116 | 5128.8646 | 72.9947 | 207.5966 | 883.3759 | 4245.4886 | 0.0096693 | 29.4325 | 58.661 | 14.1002 | 13.1655 | 0.013915 | 38.154 | 0.0087859 | 27.6178 | 0.0089024 | 24.0282 | 78.4853 | 64.5293 | 23.756 | 29114.1947 | 24402.2544 | 3256.4 | 0.38174 | 27740.1027 | 23028.1624 | 7.433 | 0.2115 | -5.6765 | -19.8243 | 53.3435 | 29114.1947 | 18410.4935 | 1396.3134 | 9307.3878 | 29114.1947 | 100%
5 | C-CB30-95-CE | 30N0099 | C-CB30-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 30 | 0 | CUST 2 | 6/19/2015 | 8:33:12 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 0.9 | 17.3 | 0 | 18207 | 45 | 17841 | 60 | -188 | 54 | 18019 | 66 |  | 943 | [37 empty] | 4.7022 | 30% condenser coil block(~30 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open--from | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 33".with outlet duct, with code tester. | 74.99 | 0.028 | 61.985 | 0.025 | 95 | 0.005 | 75.002 | 0.025 | 74.48 | 0.04 | 59.67 | 0.02 | 65.24 | 0.04 | 0.004 | 0.003 | 1.0699 | 0.0032 | 18207 | 45 | -188 | 54 | 4.703 | 0.02 | [6 empty] | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 15.1 | 0 | 15.1 | 0 | 15.1 | 0 | 3356.6 | 4.6 | 3356.6 | 4.6 | 3356.6 | 4.6 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.1 | 0.9 | 228.1 | 0.9 | 228.1 | 0.9 | 14.2 | 0 | 14.2 | 0 | 14.2 | 0 | 3123.9 | 4.5 | [9 empty] | 228.6 | 0.9 | 0.8 | 0 | 173.9 | 0.8 | 13 | 0.2 | 3785.8 | [10 empty] | 230.2 | 0.9 | 0 | 0 | 285.63 | 0.15 | 109.19 | 0.04 | 126.97 | 0.04 | 17.78 | 0.03 | 302.65 | 0.15 | 175.06 | 0.04 | 131.4 | 0.04 | 43.66 | 0.05 | 284.95 | 0.16 | 108.57 | 0.05 | 126.79 | 0.04 | 18.21 | 0.04 | 80.21 | 0.03 | 50.72 | 0.03 | 47.44 | 0.02 |  |  | 81.46 | 0.02 | 52.99 | 0.05 | 48.21 | 0.01 | 4.78 | 0.05 | [44 empty] | 3.28 | 0.03 | [74 empty] | 58.98 | 0.03 | 59.27 | 0.03 | 59.31 | 0.03 | 59.27 | 0.02 | 59.14 | 0.03 | 59.2 | 0.03 |  |  |  |  | 51.8 | 0.07 | 50.41 | 0.02 | [10 empty] | 108.57 | 0.05 | [66 empty] | 143.35 | 0.04 | 71.69 | 0.25 | 177.26 | 0.06 | 94.88 | 0.07 | 94.26 | 0.07 | 75.27 | 0.05 | 75.25 | 0.03 | 74.9 | 0.04 | 74.97 | 0.04 | 74.91 | 0.05 | 75.01 | 0.04 | 75.12 | 0.04 | [40 empty] | 74.76 | 0.04 | [34 empty] | 94.97 | 0.07 | 84.99 | 0.26 | 85.12 | 0.23 | 74.96 | 0.04 | 90.87 | 0.3 | 76.01 | 0.04 | 77.28 | 0.09 | 76.44 | 0.06 | 75.45 | 0.05 | 79.72 | 0.27 | 87.39 | 0.29 | 77.4 | 0.1 | 75.63 | 0.05 | 82.5 | 0.3 | 90.08 | 0.26 | 80.36 | 0.14 | 83.53 | 0.29 | 94.88 | 0.1 | [12 empty] | C-55-CE-DM | 74.99 | 0.028 | 61.985 | 0.025 | 59.879 | 0.012 | 56.544 | 0.018 | 95 | 0.005 | 75.002 | 0.025 | 1122.5 | 1.7 | 1090.6 | 1.6 | 0.567 | 0.001 | -0.197 | 0.001 | 0.004 | 0.003 | 1.0699 | 0.0032 | 29.281 | 0 | 3832 | 7 | 475 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1184 | 5114.5192 | 72.6463 | 207.5944 | 883.3851 | 4231.1341 | 0.0096625 | 29.4221 | 58.7606 | 14.0999 | 13.1684 | 0.013923 | 38.1591 | 0.0087731 | 27.598 | 0.0089435 | 24.0978 | 78.4729 | 64.5154 | 23.8249 | 28626.9379 | 24196.5662 | 3357 | 0.40023 | 27253.7048 | 22823.3331 | 7.1121 | 0.21024 | -5.5972 | -19.7123 | 53.5129 | 28626.9379 | 17901.8795 | 1395.5448 | 9329.5137 | 28626.9379 | 100%
5 | C-CB40-95-CE | 30N0100 | C-CB40-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 40 | 0 | CUST 2 | 6/19/2015 | 4:56:54 | 10 Ton | 0:10:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1 | 17.7 | 0 | 17828 | 32 | 17569 | 38 | -155 | 41 | 17673 | 52 |  | 943 | [37 empty] | 4.4867 | 40% condenser coil block(~40 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from f | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 37`.; | 74.988 | 0.011 | 62.002 | 0.016 | 95.002 | 0.011 | 74.994 | 0.018 | 74.62 | 0.04 | 59.71 | 0.05 | 64.51 | 0.03 | -0.039 | 0.002 | 1.0233 | 0.0029 | 17828 | 32 | -155 | 41 | 4.487 | 0.016 | [6 empty] | 230 | 1 | 230 | 1 | 230 | 1 | 15.6 | 0 | 15.6 | 0 | 15.6 | 0 | 3467.3 | 4.6 | 3467.3 | 4.6 | 3467.3 | 4.6 | 230 | 1 | 230 | 1 | 230 | 1 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.1 | 1 | 228.1 | 1 | 228.1 | 1 | 14.7 | 0 | 14.7 | 0 | 14.7 | 0 | 3228.4 | 4 | [9 empty] | 228.6 | 0.9 | 0.8 | 0 | 177.1 | 0.9 | 0.1 | 0.2 | 3876.6 | [10 empty] | 230.3 | 1 | 0 | 0 | 296.41 | 0.19 | 111.65 | 0.04 | 129.79 | 0.05 | 18.15 | 0.04 | 313.52 | 0.18 | 173.78 | 0.06 | 134.14 | 0.04 | 39.64 | 0.07 | 295.69 | 0.18 | 111.29 | 0.04 | 129.61 | 0.05 | 18.32 | 0.05 | 80.6 | 0.03 | 50.94 | 0.03 | 47.67 | 0.02 |  |  | 81.61 | 0.02 | 53.07 | 0.07 | 48.3 | 0.01 | 4.77 | 0.07 | [44 empty] | 3.27 | 0.02 | [74 empty] | 58.84 | 0.03 | 59.17 | 0.03 | 59.28 | 0.03 | 59.31 | 0.03 | 59.05 | 0.02 | 59.13 | 0.02 | [86 empty] | 141.13 | 0.07 | 64.71 | 0.12 | 175.94 | 0.06 | 95.43 | 0.06 | 94.7 | 0.08 | 75.66 | 0.03 | 75.49 | 0.02 | 75.58 | 0.02 | 75.54 | 0.02 | 75.38 | 0.02 | 75.38 | 0.02 | 75.3 | 0.03 | [40 empty] | 74.71 | 0.03 | [34 empty] | 95.39 | 0.07 | 85.02 | 0.29 | 85.05 | 0.29 | 75.14 | 0.02 | 90.54 | 0.24 | 75.82 | 0.02 | 77.09 | 0.08 | 76.21 | 0.06 | 75.26 | 0.04 | 79.39 | 0.29 | 87.18 | 0.26 | 77.15 | 0.12 | 75.46 | 0.05 | 82.22 | 0.33 | 89.96 | 0.32 | 80.33 | 0.14 | 83.48 | 0.31 | 94.91 | 0.08 | [12 empty] | C-55-CE-DM | 74.988 | 0.011 | 62.002 | 0.016 | 59.859 | 0.009 | 56.551 | 0.007 | 95.002 | 0.011 | 74.994 | 0.018 | 1097.6 | 1.6 | 1066.4 | 1.5 | 0.576 | 0.002 | -0.191 | 0.001 | -0.039 | 0.002 | 1.0233 | 0.0029 | 29.244 | 0 | 3939 | 8 | 471.1 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.134 | 5001.2318 | 72.1619 | 204.4086 | 869.8288 | 4131.403 | 0.009677 | 29.4436 | 58.725 | 14.0999 | 13.168 | 0.013915 | 38.1513 | 0.0087848 | 27.6103 | 0.0089524 | 24.1025 | 78.4957 | 64.544 | 23.8259 | 28095.5225 | 23730.7322 | 3467.9 | 0.42128 | 26733.9466 | 22369.1563 | 6.787 | 0.20762 | -5.6177 | -19.7707 | 53.5447 | 28095.5225 | 17542.9099 | 1383.7206 | 9168.892 | 28095.5225 | 100%
5 | C-CB5-95-CE | 30N0101 | C-CB5-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 5 | 0 | CUST 2 | 6/18/2015 | 22:22:03 | 10 Ton | 0:10:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1.2 | 16.2 | 0 | 18453 | 29 | 18139 | 52 | 478 | 105 | 18931 | 113 |  | 943 | [37 empty] | 5.2836 | 5% condenser coil block(~5 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from ful | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. 7" condenser coil blockage. | 74.987 | 0.014 | 62.005 | 0.031 | 95.006 | 0.012 | 74.996 | 0.03 | 74.58 | 0.05 | 59.55 | 0.02 | 64.54 | 0.03 | -0.001 | 0.002 | 1.0723 | 0.0029 | 18453 | 29 | 478 | 105 | 5.284 | 0.035 | [6 empty] | 230 | 1.2 | 230 | 1.2 | 230 | 1.2 | 14 | 0 | 14 | 0 | 14 | 0 | 3107.4 | 5.8 | 3107.4 | 5.8 | 3107.4 | 5.8 | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 1.2 | 228.2 | 1.2 | 228.2 | 1.2 | 13.2 | 0 | 13.2 | 0 | 13.2 | 0 | 2884 | 4.9 | [9 empty] | 228.7 | 1.2 | 0.7 | 0 | 170.4 | 1 | 0.1 | 0.2 | 3530 | [10 empty] | 230.2 | 1.2 | 0 | 0 | 261.1 | 0.23 | 103.54 | 0.06 | 120.23 | 0.07 | 16.69 | 0.03 | 277.88 | 0.23 | 178.19 | 0.04 | 124.88 | 0.06 | 53.31 | 0.06 | 260.36 | 0.25 | 102.77 | 0.04 | 120.02 | 0.07 | 17.25 | 0.05 | 78.48 | 0.03 | 58.57 | 0.42 | 46.33 | 0.02 |  |  | 79.39 | 0.03 | 56.89 | 0.45 | 46.9 | 0.02 | 9.99 | 0.46 | [44 empty] | 12.25 | 0.42 | [74 empty] | 58.59 | 0.02 | 58.97 | 0.02 | 59.09 | 0.02 | 59.14 | 0.03 | 58.82 | 0.02 | 58.92 | 0.03 | [86 empty] | 146.73 | 0.05 | 85.47 | 0.11 | 179.7 | 0.09 | 95.7 | 0.1 | 94.62 | 0.08 | 75.62 | 0.03 | 75.48 | 0.03 | 75.6 | 0.03 | 75.53 | 0.03 | 75.38 | 0.03 | 75.38 | 0.03 | 75.29 | 0.04 | [40 empty] | 74.61 | 0.05 | [34 empty] | 95.23 | 0.08 | 85.07 | 0.27 | 85.31 | 0.26 | 75.1 | 0.02 | 90.32 | 0.36 | 75.65 | 0.05 | 76.94 | 0.09 | 76.08 | 0.07 | 75.1 | 0.05 | 79.11 | 0.32 | 87.03 | 0.3 | 77.1 | 0.12 | 75.29 | 0.06 | 81.81 | 0.34 | 90.34 | 0.24 | 80.31 | 0.12 | 83.58 | 0.35 | 95.15 | 0.08 | [12 empty] | C-55-CE-DM | 74.987 | 0.014 | 62.005 | 0.031 | 59.697 | 0.009 | 56.292 | 0.015 | 95.006 | 0.012 | 74.996 | 0.03 | 1124.4 | 1.6 | 1091.4 | 1.5 | 0.567 | 0.001 | -0.2 | 0.001 | -0.001 | 0.002 | 1.0723 | 0.0029 | 29.209 | 0.001 | 3583 | 9 | 475.5 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1173 | 5125.2944 | 72.6996 | 209.1698 | 890.0829 | 4235.2115 | 0.0096777 | 29.443 | 58.5797 | 14.1 | 13.163 | 0.013916 | 38.1531 | 0.008787 | 27.6124 | 0.0088374 | 23.938 | 78.4904 | 64.5431 | 23.6655 | 29611.3695 | 24491.5319 | 3107.5 | 0.35817 | 28236.6118 | 23116.7742 | 7.8807 | 0.21709 | -5.7775 | -19.9107 | 53.0587 | 29611.3695 | 18832.4374 | 1396.8246 | 9382.1076 | 29611.3695 | 100%
5 | C-CB50-95-CE | 30N0102 | C-CB50-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 50 | 0 | CUST 2 | 6/19/2015 | 10:27:05 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.3 | 18.2 | 0 | 17793 | 51 | 17423 | 50 | -859 | 74 | 16934 | 77 |  | 943 | [37 empty] | 4.1957 | 50% condenser coil block(~50 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam--set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from f | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 41.75", with outlet duct, with code tester | 75.009 | 0.028 | 61.996 | 0.023 | 94.988 | 0.011 | 75.006 | 0.016 | 74.62 | 0.08 | 60.15 | 0.06 | 65.57 | 0.03 | 0.013 | 0.003 | 1.0718 | 0.0041 | 17793 | 51 | -859 | 74 | 4.196 | 0.021 | [6 empty] | 229.9 | 1.3 | 229.9 | 1.3 | 229.9 | 1.3 | 16 | 0.1 | 16 | 0.1 | 16 | 0.1 | 3559.9 | 6.3 | 3559.9 | 6.3 | 3559.9 | 6.3 | 229.8 | 1.3 | 229.8 | 1.3 | 229.8 | 1.3 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.9 | 1.3 | 227.9 | 1.3 | 227.9 | 1.3 | 15.1 | 0.1 | 15.1 | 0.1 | 15.1 | 0.1 | 3323.8 | 5.7 | [9 empty] | 228.5 | 1.3 | 0.8 | 0 | 173.3 | 1.3 | 13 | 0.2 | 3985.9 | [10 empty] | 230.2 | 1.3 | 0 | 0 | 306.04 | 0.31 | 114.05 | 0.08 | 132.26 | 0.08 | 18.22 | 0.04 | 323.25 | 0.32 | 174.24 | 0.07 | 136.54 | 0.08 | 37.7 | 0.08 | 305.34 | 0.33 | 113.71 | 0.08 | 132.09 | 0.08 | 18.37 | 0.1 | 81.56 | 0.04 | 51.43 | 0.03 | 48.28 | 0.02 |  |  | 82.69 | 0.03 | 53.52 | 0.05 | 48.97 | 0.02 | 4.54 | 0.04 | [44 empty] | 3.15 | 0.02 | [74 empty] | 59.25 | 0.05 | 59.58 | 0.04 | 59.64 | 0.04 | 59.63 | 0.03 | 59.45 | 0.04 | 59.53 | 0.04 |  |  |  |  | 52.97 | 0.08 | 50.92 | 0.05 | [10 empty] | 113.71 | 0.08 | [66 empty] | 143.55 | 0.06 | 65.67 | 0.15 | 176.57 | 0.09 | 95.16 | 0.07 | 94.74 | 0.1 | 75.55 | 0.05 | 75.42 | 0.04 | 75.37 | 0.05 | 75.38 | 0.05 | 75.27 | 0.04 | 75.29 | 0.04 | 75.22 | 0.04 | [40 empty] | 74.69 | 0.05 | [34 empty] | 95.32 | 0.09 | 85.01 | 0.23 | 85.03 | 0.23 | 74.99 | 0.04 | 90.57 | 0.33 | 75.81 | 0.04 | 77.07 | 0.09 | 76.2 | 0.08 | 75.24 | 0.04 | 79.43 | 0.24 | 87.17 | 0.29 | 77.19 | 0.12 | 75.45 | 0.07 | 82.28 | 0.37 | 90.01 | 0.22 | 80.34 | 0.12 | 83.57 | 0.26 | 94.74 | 0.08 | [12 empty] | C-55-CE-DM | 75.009 | 0.028 | 61.996 | 0.023 | 60.233 | 0.012 | 56.9 | 0.014 | 94.988 | 0.011 | 75.006 | 0.016 | 1123.9 | 2.1 | 1091 | 2.1 | 0.564 | 0.001 | -0.199 | 0.001 | 0.013 | 0.003 | 1.0718 | 0.0041 | 29.279 | 0 | 4036 | 9 | 475.8 | 5.3 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1211 | 5117.0219 | 72.2885 | 208.6437 | 887.8659 | 4229.156 | 0.00967 | 29.4375 | 59.1119 | 14.0997 | 13.1784 | 0.013929 | 38.1631 | 0.0087759 | 27.6056 | 0.0090716 | 24.3235 | 78.5024 | 64.5361 | 24.05 | 27568.058 | 23813.2042 | 3560.2 | 0.44076 | 26190.8731 | 22436.0193 | 6.4893 | 0.20852 | -5.3875 | -19.3905 | 54.0034 | 27568.058 | 16794.508 | 1399.8873 | 9373.6627 | 27568.058 | 100%
5 | C-CB60-95-CE | 30N0103 | C-CB60-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 60 | 0 | CUST 2 | 6/19/2015 | 12:09:14 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 18.6 | 0 | 17193 | 61 | 16848 | 92 | -910 | 50 | 16282 | 54 |  | 643 | [37 empty] | 3.9519 | 60% condenser coil block(~60 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet--Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from f | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 43", with outlet duct, with code tester | 74.873 | 0.044 | 61.968 | 0.013 | 95.002 | 0.009 | 75.008 | 0.022 | 74.55 | 0.09 | 60.28 | 0.05 | 66 | 0.09 | -0.021 | 0.002 | 1.0312 | 0.0032 | 17193 | 61 | -910 | 50 | 3.952 | 0.015 | [6 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 16.4 | 0.1 | 16.4 | 0.1 | 16.4 | 0.1 | 3648.1 | 5 | 3648.1 | 5 | 3648.1 | 5 | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.9 | 1.1 | 227.9 | 1.1 | 227.9 | 1.1 | 15.5 | 0.1 | 15.5 | 0.1 | 15.5 | 0.1 | 3411.5 | 4.5 | [9 empty] | 228.5 | 1.1 | 0.8 | 0 | 171.9 | 1 | 0 | 0.2 | 4068.3 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 315.08 | 0.17 | 116.98 | 0.06 | 134.53 | 0.04 | 17.56 | 0.04 | 332.06 | 0.17 | 175.68 | 0.05 | 138.66 | 0.04 | 37.02 | 0.05 | 314.39 | 0.18 | 116.55 | 0.07 | 134.36 | 0.04 | 17.81 | 0.06 | 81.88 | 0.02 | 51.56 | 0.04 | 48.47 | 0.01 |  |  | 82.95 | 0.02 | 53.96 | 0.04 | 49.13 | 0.01 | 4.83 | 0.03 | [44 empty] | 3.09 | 0.03 | [74 empty] | 59.22 | 0.03 | 59.57 | 0.03 | 59.65 | 0.03 | 59.65 | 0.03 | 59.42 | 0.03 | 59.52 | 0.03 |  |  |  |  | 53.13 | 0.05 | 51.07 | 0.04 | [10 empty] | 116.55 | 0.07 | [66 empty] | 145.27 | 0.05 | 64.91 | 0.05 | 177.95 | 0.07 | 95.17 | 0.08 | 94.81 | 0.12 | 75.5 | 0.05 | 75.38 | 0.05 | 75.35 | 0.06 | 75.35 | 0.05 | 75.2 | 0.05 | 75.23 | 0.05 | 75.16 | 0.05 | [40 empty] | 74.56 | 0.05 | [34 empty] | 95.35 | 0.07 | 85 | 0.27 | 85.02 | 0.24 | 74.92 | 0.05 | 90.62 | 0.34 | 75.71 | 0.05 | 76.99 | 0.09 | 76.09 | 0.08 | 75.14 | 0.06 | 79.33 | 0.27 | 87.22 | 0.29 | 77.03 | 0.11 | 75.37 | 0.07 | 82.21 | 0.38 | 89.85 | 0.27 | 80.23 | 0.15 | 83.44 | 0.32 | 94.86 | 0.07 | [12 empty] | C-55-CE-DM | 74.873 | 0.044 | 61.968 | 0.013 | 60.307 | 0.015 | 56.973 | 0.012 | 95.002 | 0.009 | 75.008 | 0.022 | 1102.8 | 1.7 | 1069.4 | 1.7 | 0.576 | 0.001 | -0.195 | 0.001 | -0.021 | 0.002 | 1.0312 | 0.0032 | 29.274 | 0 | 4120 | 8 | 471.9 | 5.2 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1314 | 5020.1629 | 72.3649 | 206.5386 | 878.8866 | 4141.2763 | 0.009689 | 29.4392 | 59.1756 | 14.1 | 13.1804 | 0.013927 | 38.1648 | 0.0087895 | 27.5874 | 0.0090978 | 24.37 | 78.4242 | 64.5368 | 24.0939 | 26834.3561 | 23191.4715 | 3648.1 | 0.46399 | 25470.7427 | 21827.858 | 6.1822 | 0.20913 | -5.3453 | -19.2486 | 54.0856 | 26834.3561 | 16151.8554 | 1386.158 | 9296.3428 | 26834.3561 | 100%
5 | C-CB70-95-CE | 30N0104 | C-CB70-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 70 | 0 | CUST 2 | 6/19/2015 | 15:33:54 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.2 | 19.1 | 0 | 17233 | 43 | 16889 | 66 | -1425 | 80 | 15807 | 76 |  | 943 | [37 empty] | 3.7333 | 70% condenser coil block(~70 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from f | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 46", with outlet duct, with code tester | 74.996 | 0.027 | 61.989 | 0.02 | 95.002 | 0.013 | 74.997 | 0.028 | 74.59 | 0.04 | 60.42 | 0.04 | 65.73 | 0.03 | -0.003 | 0.002 | 1.0554 | 0.003 | 17233 | 43 | -1425 | 80 | 3.734 | 0.019 | [6 empty] | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 16.9 | 0.1 | 16.9 | 0.1 | 16.9 | 0.1 | 3759.7 | 5 | 3759.7 | 5 | 3759.7 | 5 | 229.9 | 1.2 | 229.9 | 1.2 | 229.9 | 1.2 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.8 | 1.2 | 227.8 | 1.2 | 227.8 | 1.2 | 16 | 0.1 | 16 | 0.1 | 16 | 0.1 | 3522 | 4.4 | [9 empty] | 228.5 | 1.2 | 0.7 | 0 | 169.3 | 1.2 | 13 | 0.2 | 4178.2 | [10 empty] | 230.2 | 1.2 | 0 | 0 | 326.34 | 0.22 | 120.05 | 0.06 | 137.28 | 0.05 | 17.24 | 0.04 | 343.17 | 0.21 | 177.22 | 0.04 | 141.28 | 0.05 | 35.94 | 0.06 | 325.62 | 0.21 | 119.58 | 0.07 | 137.11 | 0.05 | 17.53 | 0.06 | 82.74 | 0.02 | 51.82 | 0.03 | 48.99 | 0.01 |  |  | 83.55 | 0.02 | 53.63 | 0.06 | 49.48 | 0.01 | 4.15 | 0.06 | [44 empty] | 2.84 | 0.02 | [74 empty] | 59.49 | 0.03 | 59.85 | 0.03 | 59.91 | 0.03 | 59.94 | 0.03 | 59.73 | 0.03 | 59.81 | 0.03 |  |  |  |  | 53.52 | 0.05 | 51.31 | 0.03 | [10 empty] | 119.58 | 0.07 | [66 empty] | 146.74 | 0.04 | 66.11 | 0.13 | 179.88 | 0.07 | 95.26 | 0.09 | 95.51 | 0.14 | 75.56 | 0.05 | 75.42 | 0.04 | 75.49 | 0.04 | 75.45 | 0.04 | 75.29 | 0.04 | 75.31 | 0.04 | 75.22 | 0.05 | [40 empty] | 74.61 | 0.05 | [34 empty] | 95.04 | 0.06 | 85.17 | 0.28 | 85.14 | 0.28 | 75.02 | 0.05 | 90.48 | 0.29 | 75.63 | 0.04 | 76.95 | 0.1 | 76.09 | 0.07 | 75.09 | 0.05 | 79.21 | 0.31 | 87.02 | 0.3 | 77.06 | 0.12 | 75.31 | 0.06 | 82.2 | 0.39 | 90.07 | 0.27 | 80.33 | 0.15 | 83.56 | 0.34 | 95.01 | 0.12 | [12 empty] | C-55-CE-DM | 74.996 | 0.027 | 61.989 | 0.02 | 60.542 | 0.007 | 57.207 | 0.008 | 95.002 | 0.013 | 74.997 | 0.028 | 1116.6 | 1.6 | 1081.1 | 1.5 | 0.57 | 0.001 | -0.197 | 0.001 | -0.003 | 0.002 | 1.0554 | 0.003 | 29.219 | 0.001 | 4234 | 8 | 473.9 | 5.3 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1235 | 5080.4316 | 72.3945 | 207.5945 | 883.3848 | 4197.0468 | 0.0096686 | 29.4358 | 59.4185 | 14.0999 | 13.1871 | 0.013918 | 38.1542 | 0.0087743 | 27.6008 | 0.0091825 | 24.5195 | 78.5015 | 64.5339 | 24.2453 | 26369.9124 | 23268.0249 | 3760.1 | 0.48666 | 24999.5743 | 21897.6868 | 5.9045 | 0.20739 | -5.1905 | -19.083 | 54.4252 | 26369.9124 | 15653.9673 | 1393.2086 | 9322.7365 | 26369.9124 | 100%
5 | C-CB80-95-CE | 30N0105 | C-CB80-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 80 | 0 | CUST 2 | 6/19/2015 | 2:29:19 | 10 Ton | 0:10:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.1 | 19.6 | 0 | 16940 | 34 | 16637 | 54 | -1948 | 92 | 14990 | 85 |  | 943 | [37 empty] | 3.4389 | 80% condenser coil block(~80 psig DP above C-CB0-95-CE), economizer closed (2.8V),--factory charge (5.5 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from f | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Condenser Coil is blocked 51`.; | 75.001 | 0.017 | 61.988 | 0.026 | 95.005 | 0.014 | 74.995 | 0.029 | 74.62 | 0.06 | 60.7 | 0.03 | 65.33 | 0.02 | -0.007 | 0.002 | 1.0622 | 0.0026 | 16940 | 34 | -1948 | 92 | 3.439 | 0.021 | [6 empty] | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 17.4 | 0.1 | 17.4 | 0.1 | 17.4 | 0.1 | 3883.8 | 5.1 | 3883.8 | 5.1 | 3883.8 | 5.1 | 229.9 | 1.1 | 229.9 | 1.1 | 229.9 | 1.1 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.7 | 1.1 | 227.7 | 1.1 | 227.7 | 1.1 | 16.5 | 0.1 | 16.5 | 0.1 | 16.5 | 0.1 | 3639.9 | 4.7 | [9 empty] | 228.4 | 1.1 | 0.7 | 0 | 170.1 | 1 | 0 | 0.2 | 4284.8 | [10 empty] | 230.2 | 1.1 | 0 | 0 | 337.8 | 0.23 | 122.45 | 0.05 | 140.02 | 0.05 | 17.58 | 0.03 | 354.45 | 0.23 | 178.9 | 0.05 | 143.88 | 0.05 | 35.02 | 0.07 | 337.07 | 0.24 | 122.57 | 0.05 | 139.85 | 0.06 | 17.28 | 0.06 | 83.35 | 0.03 | 52.25 | 0.03 | 49.37 | 0.02 |  |  | 84.52 | 0.02 | 54.54 | 0.04 | 50.07 | 0.01 | 4.46 | 0.03 | [44 empty] | 2.89 | 0.02 | [74 empty] | 59.82 | 0.03 | 60.2 | 0.02 | 60.3 | 0.03 | 60.37 | 0.03 | 60.1 | 0.03 | 60.17 | 0.02 | [86 empty] | 146.58 | 0.04 | 66.85 | 0.1 | 180.75 | 0.06 | 95.53 | 0.1 | 95.45 | 0.18 | 75.64 | 0.03 | 75.5 | 0.04 | 75.6 | 0.03 | 75.54 | 0.03 | 75.37 | 0.03 | 75.37 | 0.03 | 75.33 | 0.05 | [40 empty] | 74.65 | 0.05 | [34 empty] | 94.97 | 0.07 | 85.14 | 0.26 | 85.15 | 0.24 | 75.13 | 0.04 | 90.79 | 0.32 | 75.81 | 0.06 | 77.09 | 0.14 | 76.23 | 0.09 | 75.22 | 0.06 | 79.47 | 0.25 | 87.32 | 0.31 | 77.18 | 0.14 | 75.43 | 0.06 | 82.37 | 0.37 | 89.98 | 0.22 | 80.29 | 0.15 | 83.53 | 0.28 | 95.02 | 0.16 | [12 empty] | C-55-CE-DM | 75.001 | 0.017 | 61.988 | 0.026 | 60.835 | 0.009 | 57.479 | 0.008 | 95.005 | 0.014 | 74.995 | 0.029 | 1119.6 | 1.4 | 1085.2 | 1.3 | 0.565 | 0.001 | -0.198 | 0.002 | -0.007 | 0.002 | 1.0622 | 0.0026 | 29.235 | 0 | 4359 | 7 | 474.8 | 5.1 | 0.16623 | 191.8074 | 13.029 | 0.182 | 1.1248 | 5090.928 | 72.0316 | 208.1211 | 885.6223 | 4205.3057 | 0.0096671 | 29.4356 | 59.7102 | 14.1 | 13.1952 | 0.013915 | 38.1522 | 0.0087725 | 27.6 | 0.0092771 | 24.694 | 78.5078 | 64.5338 | 24.4194 | 25537.3101 | 22967.2512 | 3884.2 | 0.51911 | 24162.6617 | 21592.6028 | 5.5432 | 0.20786 | -5.0162 | -18.7975 | 54.7777 | 25537.3101 | 14794.1853 | 1397.8313 | 9345.2935 | 25537.3101 | 100%
5 | C-EB0-115-CE | 30N0106 | C-EB0-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 2 | 6/17/2015 | 18:52:41 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.6 | 19.4 | 0 | 13615 | 60 | 13420 | 82 | -3993 | 151 | 9618 | 199 |  | 943 | [37 empty] | 2.229 | . | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75.01 | 0.027 | 61.989 | 0.024 | 115.013 | 0.016 | 80.4 | 0.17 | 74.56 | 0.05 | 63.1 | 0.09 | 67.36 | 0.04 | -0.006 | 0.003 | 1.043 | 0.0034 | 13615 | 60 | -3993 | 151 | 2.229 | 0.047 | [6 empty] | 229.9 | 1.6 | 229.9 | 1.6 | 229.9 | 1.6 | 17.2 | 0.1 | 17.2 | 0.1 | 17.2 | 0.1 | 3841.9 | 4.8 | 3841.9 | 4.8 | 3841.9 | 4.8 | 229.8 | 1.6 | 229.8 | 1.6 | 229.8 | 1.6 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.7 | 1.7 | 227.7 | 1.7 | 227.7 | 1.7 | 16.4 | 0.1 | 16.4 | 0.1 | 16.4 | 0.1 | 3606.3 | 4.5 | [9 empty] | 228.5 | 1.6 | 0.7 | 0 | 167 | 1.4 | 0.1 | 0.2 | 4246.2 | [10 empty] | 230.2 | 1.6 | 0 | 0 | 332.23 | 0.22 | 124.76 | 0.03 | 138.67 | 0.05 | 13.91 | 0.05 | 348.09 | 0.21 | 192.58 | 0.09 | 142.4 | 0.05 | 50.19 | 0.08 | 331.51 | 0.24 | 123.84 | 0.05 | 138.5 | 0.06 | 14.65 | 0.06 | 84.9 | 0.07 | 53.84 | 0.07 | 50.23 | 0.04 |  |  | 85.96 | 0.07 | 56.25 | 0.04 | 50.86 | 0.04 | 5.39 | 0.05 | [44 empty] | 3.61 | 0.05 | [74 empty] | 62.42 | 0.07 | 62.78 | 0.06 | 62.83 | 0.06 | 62.81 | 0.07 | 62.67 | 0.07 | 62.74 | 0.06 | [6 empty] | 53.42 | 0.08 | [78 empty] | 161.74 | 0.09 | 73.04 | 0.36 | 194.08 | 0.17 | 115.61 | 0.1 | 113.75 | 0.14 | 76.72 | 0.11 | 76.36 | 0.11 | 75.73 | 0.1 | 75.7 | 0.09 | 75.38 | 0.06 | 75.46 | 0.05 | 75.39 | 0.04 | [40 empty] | 74.87 | 0.03 | [34 empty] | 115.07 | 0.1 | 95.02 | 1.14 | 104.21 | 0.29 | 79.25 | 0.13 | 101.03 | 0.45 | 76.58 | 0.08 | 83.57 | 0.38 | 82.25 | 0.23 | 75.71 | 0.04 | 81.38 | 0.37 | 99.63 | 0.6 | 83.25 | 0.63 | 75.88 | 0.05 | 85.9 | 0.97 | 96.93 | 0.25 | 80.77 | 0.48 | 102.34 | 0.94 | 115.15 | 0.12 | [12 empty] | C-55-CE | 75.01 | 0.027 | 61.989 | 0.024 | 63.385 | 0.037 | 59.103 | 0.053 | 115.013 | 0.016 | 80.4 | 0.17 | 1116.7 | 1.8 | 1067.6 | 1.8 | 0.557 | 0.001 | -0.198 | 0.002 | -0.006 | 0.003 | 1.043 | 0.0034 | 28.971 | 0.002 | 4315 | 8 | 472.8 | 5.5 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.1339 | 5051.8069 | 69.86 | 211.5943 | 868.9307 | 4182.8761 | 0.0096973 | 30.3088 | 62.2511 | 14.6107 | 13.263 | 0.014156 | 43.3458 | 0.008771 | 27.6006 | 0.0096708 | 25.7452 | 81.9464 | 65.733 | 25.4682 | 24453.6597 | 23879.337 | 3842.2 | 0.53626 | 23078.4257 | 22504.1029 | 5.3484 | 0.23565 | -4.8406 | -19.6954 | 56.1789 | 24453.6597 | 9372.7031 | 1399.4281 | 13681.5285 | 24453.6597 | 100%
5 | C-EB10-115-CE | 30N0107 | C-EB10-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 10 | CUST 2 | 6/17/2015 | 21:16:41 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 230 | 1.5 | 19.2 | 0 | 13187 | 19 | 12905 | 36 | -2954 | 45 | 10231 | 54 |  | 943 | [37 empty] | 2.3927 | 10% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 115F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley--3 turns open from fully closed, adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 74.998 | 0.013 | 62.014 | 0.014 | 114.978 | 0.021 | 80.011 | 0.024 | 74.44 | 0.03 | 63.27 | 0.04 | 67.36 | 0.02 | -0.002 | 0.002 | 1.0093 | 0.0021 | 13187 | 19 | -2954 | 45 | 2.393 | 0.013 | [6 empty] | 230 | 1.5 | 230 | 1.5 | 230 | 1.5 | 17.1 | 0.1 | 17.1 | 0.1 | 17.1 | 0.1 | 3806.4 | 6.4 | 3806.4 | 6.4 | 3806.4 | 6.4 | 230 | 1.5 | 230 | 1.5 | 230 | 1.5 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 227.9 | 1.5 | 227.9 | 1.5 | 227.9 | 1.5 | 16.2 | 0.1 | 16.2 | 0.1 | 16.2 | 0.1 | 3571.8 | 5.8 | [9 empty] | 228.7 | 1.5 | 0.7 | 0 | 167.3 | 1.3 | 0.1 | 0.2 | 4208.3 | [10 empty] | 230.3 | 1.5 | 0 | 0 | 329.82 | 0.24 | 124.62 | 0.05 | 138.1 | 0.06 | 13.48 | 0.03 | 345.52 | 0.25 | 187.44 | 0.07 | 141.81 | 0.06 | 45.64 | 0.08 | 329.12 | 0.26 | 123.8 | 0.05 | 137.93 | 0.06 | 14.13 | 0.05 | 82.77 | 0.03 | 52.62 | 0.03 | 48.94 | 0.02 |  |  | 83.8 | 0.03 | 54.71 | 0.06 | 49.57 | 0.02 | 5.14 | 0.06 | [44 empty] | 3.68 | 0.02 | [74 empty] | 62.71 | 0.03 | 63.03 | 0.02 | 63.09 | 0.03 | 63.02 | 0.03 | 62.84 | 0.03 | 62.95 | 0.03 | [86 empty] | 158.92 | 0.06 | 67.2 | 0.07 | 188.78 | 0.09 | 115.38 | 0.12 | 113.87 | 0.16 | 76.9 | 0.11 | 76.41 | 0.09 | 75.66 | 0.07 | 75.63 | 0.06 | 75.27 | 0.05 | 75.36 | 0.04 | 75.24 | 0.02 | [40 empty] | 74.77 | 0.03 | [34 empty] | 114.95 | 0.09 | 98.87 | 0.76 | 104.11 | 0.52 | 77.21 | 0.16 | 98.13 | 0.41 | 76.84 | 0.12 | 81.1 | 0.33 | 78.83 | 0.22 | 75.64 | 0.04 | 79.16 | 0.24 | 99.05 | 0.39 |  |  | 75.78 | 0.06 | 86.42 | 0.76 | 91.63 | 0.38 | 79.11 | 0.54 | 101.99 | 0.65 | 115.03 | 0.21 | [12 empty] | C-EB10-55-CE | 74.998 | 0.013 | 62.014 | 0.014 | 63.585 | 0.01 | 58.893 | 0.01 | 114.978 | 0.021 | 80.011 | 0.024 | 1097.4 | 1.1 | 1051.3 | 1.1 | 0.535 | 0.001 | -0.194 | 0.001 | -0.002 | 0.002 | 1.0093 | 0.0021 | 29.021 | 0.001 | 4276 | 9 | 469.1 | 5.4 | 0.16566 | 179.2423 | 13.029 | 0.195 | 1.1544 | 4963.1232 | 66.0763 | 189.2966 | 777.5806 | 4185.5427 | 0.0095725 | 30.0164 | 62.4306 | 14.6066 | 13.2666 | 0.013783 | 42.9222 | 0.0087903 | 27.6188 | 0.0094925 | 25.5999 | 81.3097 | 65.345 | 25.318 | 23318.8698 | 22487.854 | 3806.9 | 0.55719 | 21943.3498 | 21112.334 | 5.1317 | 0.26526 | -4.6984 | -18.8791 | 55.6147 | 23318.8698 | 10019.9844 | 1399.2654 | 11899.62 | 23318.8698 | 100%
5 | C-EB20-115-CE | 30N0108 | C-EB20-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 20 | CUST 2 | 6/17/2015 | 22:24:39 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.8 | 1.9 | 19.1 | 0 | 12714 | 25 | 12448 | 45 | -3032 | 47 | 9679 | 55 |  | 943 | [37 empty] | 2.2769 | 20% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 115F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 74.995 | 0.005 | 61.942 | 0.007 | 115.015 | 0.019 | 79.989 | 0.016 | 74.45 | 0.05 | 63.48 | 0.06 | 67.42 | 0.01 | -0.005 | 0.002 | 0.9733 | 0.0029 | 12714 | 25 | -3032 | 47 | 2.277 | 0.015 | [6 empty] | 229.8 | 1.9 | 229.8 | 1.9 | 229.8 | 1.9 | 17 | 0.1 | 17 | 0.1 | 17 | 0.1 | 3786.8 | 5.3 | 3786.8 | 5.3 | 3786.8 | 5.3 | 229.8 | 1.9 | 229.8 | 1.9 | 229.8 | 1.9 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 227.8 | 1.9 | 227.8 | 1.9 | 227.8 | 1.9 | 16.1 | 0.1 | 16.1 | 0.1 | 16.1 | 0.1 | 3552.7 | 4.9 | [9 empty] | 228.5 | 1.9 | 0.7 | 0 | 167.4 | 1.6 | 0.1 | 0.2 | 4184.1 | [10 empty] | 230.2 | 1.9 | 0 | 0 | 328.48 | 0.23 | 124.61 | 0.05 | 137.78 | 0.06 | 13.17 | 0.03 | 344.08 | 0.23 | 184.3 | 0.04 | 141.47 | 0.05 | 42.82 | 0.07 | 327.77 | 0.23 | 123.79 | 0.07 | 137.61 | 0.05 | 13.82 | 0.07 | 81.46 | 0.03 | 51.8 | 0.03 | 48.14 | 0.02 |  |  | 82.45 | 0.03 | 53.83 | 0.07 | 48.75 | 0.02 | 5.08 | 0.07 | [44 empty] | 3.66 | 0.03 | [74 empty] | 62.99 | 0.04 | 63.3 | 0.03 | 63.34 | 0.04 | 63.28 | 0.04 | 63.1 | 0.03 | 63.21 | 0.04 | [86 empty] | 156.64 | 0.07 | 65.76 | 0.15 | 185.43 | 0.07 | 115.29 | 0.1 | 113.96 | 0.11 | 77.11 | 0.13 | 76.59 | 0.12 | 75.77 | 0.07 | 75.72 | 0.06 | 75.33 | 0.03 | 75.42 | 0.04 | 75.26 | 0.02 | [40 empty] | 74.84 | 0.03 | [34 empty] | 115.01 | 0.1 | 100.13 | 0.52 | 104.1 | 0.44 | 76.69 | 0.13 | 92.27 | 0.41 | 77.17 | 0.19 | 87.58 | 0.42 | 78.51 | 0.17 | 75.56 | 0.04 | 78.88 | 0.2 | 91.7 | 0.39 |  |  | 75.74 | 0.05 | 79.5 | 0.38 | 88.79 | 0.36 | 77.81 | 0.25 | 105.08 | 0.48 | 114.83 | 0.2 | [12 empty] | C-EB20-55-CE | 74.995 | 0.005 | 61.942 | 0.007 | 63.787 | 0.011 | 58.93 | 0.018 | 115.015 | 0.019 | 79.989 | 0.016 | 1077.1 | 1.6 | 1032.6 | 1.6 | 0.515 | 0.001 | -0.187 | 0.001 | -0.005 | 0.002 | 0.9733 | 0.0029 | 29.042 | 0.001 | 4251 | 9 | 463.9 | 5.8 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.172 | 4869.506 | 62.4747 | 174.6494 | 717.3806 | 4152.1255 | 0.0094815 | 29.8254 | 62.615 | 14.6073 | 13.2716 | 0.013753 | 42.8976 | 0.0087436 | 27.5669 | 0.0094676 | 25.6221 | 80.9366 | 65.0907 | 25.3359 | 21861.5906 | 21412.0483 | 3787.1 | 0.59124 | 20491.5262 | 20041.9838 | 4.8204 | 0.27654 | -4.4895 | -18.3215 | 55.6117 | 21861.5906 | 9469.9961 | 1393.6527 | 10997.9418 | 21861.5906 | 100%
5 | C-EB35-115-CE | 30N0109 | C-EB35-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 35 | CUST 2 | 6/17/2015 | 23:09:27 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.9 | 19 | 0 | 11925 | 42 | 11769 | 66 | -2205 | 44 | 9717 | 41 |  | 946 | [37 empty] | 2.3037 | 35% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 115F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 74.96 | 0.032 | 61.969 | 0.019 | 115.004 | 0.013 | 79.997 | 0.019 | 74.6 | 0.06 | 63.66 | 0.06 | 67.81 | 0.03 | -0.018 | 0.002 | 0.8733 | 0.0031 | 11925 | 42 | -2205 | 44 | 2.304 | 0.011 | [6 empty] | 229.9 | 1.9 | 229.9 | 1.9 | 229.9 | 1.9 | 16.9 | 0.1 | 16.9 | 0.1 | 16.9 | 0.1 | 3763.4 | 5.9 | 3763.4 | 5.9 | 3763.4 | 5.9 | 229.8 | 1.9 | 229.8 | 1.9 | 229.8 | 1.9 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 227.8 | 1.9 | 227.8 | 1.9 | 227.8 | 1.9 | 16 | 0.1 | 16 | 0.1 | 16 | 0.1 | 3529.8 | 5.3 | [9 empty] | 228.5 | 1.9 | 0.7 | 0 | 167.4 | 1.6 | 0.1 | 0.2 | 4151.5 | [10 empty] | 230.2 | 1.9 | 0 | 0 | 326.35 | 0.27 | 124.79 | 0.05 | 137.27 | 0.07 | 12.48 | 0.03 | 341.84 | 0.26 | 181.02 | 0.07 | 140.95 | 0.06 | 40.06 | 0.06 | 325.65 | 0.28 | 124.01 | 0.07 | 137.1 | 0.07 | 13.09 | 0.07 | 79.78 | 0.03 | 50.72 | 0.03 | 47.1 | 0.02 |  |  | 80.87 | 0.03 | 52.48 | 0.05 | 47.79 | 0.02 | 4.69 | 0.04 | [44 empty] | 3.62 | 0.03 | [74 empty] | 62.98 | 0.04 | 63.36 | 0.03 | 63.37 | 0.03 | 63.34 | 0.03 | 63.17 | 0.04 | 63.26 | 0.03 | [86 empty] | 154.67 | 0.07 | 64.54 | 0.08 | 182.11 | 0.07 | 115.42 | 0.09 | 114.09 | 0.1 | 78.1 | 0.14 | 77.25 | 0.16 | 76.27 | 0.09 | 76.16 | 0.08 | 75.6 | 0.06 | 75.69 | 0.06 | 75.38 | 0.05 | [40 empty] | 74.9 | 0.04 | [34 empty] | 115.09 | 0.08 | 101.8 | 0.23 | 102.15 | 0.41 | 77.16 | 0.14 | 92.04 | 0.35 | 78.44 | 0.25 | 91.35 | 0.35 | 76.66 | 0.06 | 75.78 | 0.05 | 78.47 | 0.16 | 89.01 | 0.4 |  |  | 76.42 | 0.1 | 81.3 | 0.41 | 90.07 | 0.4 | 76.4 | 0.09 | 103.55 | 0.44 | 114.81 | 0.14 | [12 empty] | C-EB35-55-CE | 74.96 | 0.032 | 61.969 | 0.019 | 63.881 | 0.015 | 58.775 | 0.02 | 115.004 | 0.013 | 79.997 | 0.019 | 1019.7 | 1.8 | 978 | 1.7 | 0.469 | 0.001 | -0.167 | 0.001 | -0.018 | 0.002 | 0.8733 | 0.0031 | 29.07 | 0.001 | 4218 | 10 | 454.2 | 5.9 | 0.15207 | 157.7743 | 13.029 | 0.181 | 1.2347 | 4609.5004 | 53.8861 | 160.4654 | 659.1275 | 3950.3729 | 0.0094837 | 29.7775 | 62.6463 | 14.6071 | 13.273 | 0.013763 | 42.9065 | 0.0087696 | 27.5869 | 0.009349 | 25.5159 | 80.7306 | 65.0244 | 25.2145 | 21032.9707 | 20006.2196 | 3763.8 | 0.61075 | 19666.6994 | 18639.9483 | 4.6626 | 0.29378 | -4.563 | -18.0842 | 55.1234 | 21032.9707 | 9545.9 | 1389.4947 | 10097.576 | 21032.9707 | 100%
5 | C-EB5-115-CE | 30N0110 | C-EB5-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 5 | CUST 2 | 6/17/2015 | 20:01:36 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.5 | 19.3 | 0 | 13471 | 25 | 13203 | 44 | -3204 | 87 | 10265 | 89 |  | 943 | [37 empty] | 2.3911 | . | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75 | 0.011 | 62.011 | 0.029 | 114.998 | 0.013 | 79.99 | 0.028 | 74.53 | 0.06 | 63.16 | 0.07 | 67.12 | 0.02 | -0.009 | 0.002 | 1.0204 | 0.0029 | 13471 | 25 | -3204 | 87 | 2.391 | 0.021 | [6 empty] | 229.9 | 1.5 | 229.9 | 1.5 | 229.9 | 1.5 | 17.1 | 0.1 | 17.1 | 0.1 | 17.1 | 0.1 | 3822.1 | 5.4 | 3822.1 | 5.4 | 3822.1 | 5.4 | 229.9 | 1.5 | 229.9 | 1.5 | 229.9 | 1.5 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.8 | 1.6 | 227.8 | 1.6 | 227.8 | 1.6 | 16.3 | 0.1 | 16.3 | 0.1 | 16.3 | 0.1 | 3587.2 | 4.8 | [9 empty] | 228.6 | 1.6 | 0.7 | 0 | 167.1 | 1.4 | 0.1 | 0.2 | 4225.3 | [10 empty] | 230.2 | 1.5 | 0 | 0 | 331.13 | 0.21 | 124.74 | 0.05 | 138.41 | 0.05 | 13.67 | 0.04 | 346.89 | 0.21 | 189.34 | 0.05 | 142.12 | 0.05 | 47.22 | 0.06 | 330.42 | 0.22 | 123.91 | 0.07 | 138.24 | 0.05 | 14.34 | 0.06 | 83.68 | 0.03 | 53.01 | 0.04 | 49.5 | 0.02 |  |  | 84.76 | 0.03 | 55.15 | 0.07 | 50.15 | 0.02 | 5 | 0.06 | [44 empty] | 3.52 | 0.03 | [74 empty] | 62.47 | 0.04 | 62.8 | 0.03 | 62.86 | 0.03 | 62.84 | 0.03 | 62.61 | 0.03 | 62.73 | 0.04 | [6 empty] | 52.64 | 0.07 | [78 empty] | 159.37 | 0.1 | 68.04 | 0.09 | 190.47 | 0.1 | 115.53 | 0.11 | 113.93 | 0.15 | 76.87 | 0.1 | 76.39 | 0.11 | 75.7 | 0.08 | 75.66 | 0.07 | 75.32 | 0.05 | 75.4 | 0.04 | 75.24 | 0.03 | [40 empty] | 74.72 | 0.04 | [34 empty] | 115.08 | 0.13 | 95.63 | 1.22 | 104.94 | 0.75 | 76.09 | 0.09 | 100.44 | 0.54 | 76.49 | 0.06 | 81.22 | 0.34 | 79.41 | 0.27 | 75.58 | 0.04 | 80.14 | 0.38 | 100.94 | 0.56 | 83.41 | 0.85 | 75.9 | 0.09 | 88.33 | 0.87 | 93.01 | 0.38 | 79.85 | 0.64 | 101.03 | 1.1 | 115 | 0.2 | [12 empty] | C-EB5-55-CE | 75 | 0.011 | 62.011 | 0.029 | 63.399 | 0.008 | 58.895 | 0.012 | 114.998 | 0.013 | 79.99 | 0.028 | 1103.4 | 1.6 | 1057.1 | 1.5 | 0.546 | 0.001 | -0.195 | 0.001 | -0.009 | 0.002 | 1.0204 | 0.0029 | 29.011 | 0.001 | 4293 | 9 | 470.9 | 5.4 | 0.16408 | 178.2735 | 13.029 | 0.192 | 1.148 | 4991.8993 | 67.8069 | 190.2289 | 781.3947 | 4210.5046 | 0.0095658 | 30.0088 | 62.251 | 14.6069 | 13.2623 | 0.013758 | 42.899 | 0.0087879 | 27.6166 | 0.0095378 | 25.6038 | 81.3087 | 65.3352 | 25.3235 | 23388.6186 | 22832.1727 | 3822.1 | 0.55774 | 22012.8618 | 21456.4159 | 5.1276 | 0.2529 | -4.6853 | -19.0577 | 55.7996 | 23388.6186 | 10047.4003 | 1399.6217 | 11941.5966 | 23388.6186 | 100%
5 | C-EB50-115-CE | 30N0111 | C-EB50-115-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 50 | CUST 2 | 6/18/2015 | 0:38:55 | 10 Ton | 0:10:00 | 75/62 115/80 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 115 | 80 | 5.5 |  | 5.5 |  | 229.9 | 1.6 | 18.8 | 0 | 11167 | 442 | 10952 | 51 | -1279 | 79 | 9889 | 399 |  | 947 | [37 empty] | 2.3669 | 50% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 115F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75.015 | 0.018 | 61.989 | 0.034 | 114.991 | 0.02 | 80.001 | 0.02 | 74.6 | 0.04 | 63.7 | 0.06 | 68.1 | 0.03 | -0.023 | 0.002 | 0.7576 | 0.0022 | 11167 | 442 | -1279 | 79 | 2.367 | 0.093 | [6 empty] | 229.9 | 1.6 | 229.9 | 1.6 | 229.9 | 1.6 | 16.8 | 0.1 | 16.8 | 0.1 | 16.8 | 0.1 | 3732.6 | 5.3 | 3732.6 | 5.3 | 3732.6 | 5.3 | 229.9 | 1.6 | 229.9 | 1.6 | 229.9 | 1.6 | 2 | 0 | 2 | 0 | 2 | 0 |  | 227.8 | 1.6 | 227.8 | 1.6 | 227.8 | 1.6 | 15.9 | 0.1 | 15.9 | 0.1 | 15.9 | 0.1 | 3499.5 | 4.8 | [9 empty] | 228.5 | 1.6 | 0.7 | 0 | 167.5 | 1.4 | 0.1 | 0.2 | 4111.9 | [10 empty] | 230.2 | 1.6 | 0 | 0 | 323.54 | 0.23 | 124.95 | 0.06 | 136.59 | 0.06 | 11.64 | 0.05 | 338.92 | 0.22 | 177.14 | 0.04 | 140.27 | 0.05 | 36.87 | 0.06 | 322.87 | 0.22 | 124.25 | 0.08 | 136.42 | 0.05 | 12.17 | 0.07 | 77.46 | 0.03 | 49.26 | 0.03 | 45.64 | 0.02 |  |  | 78.39 | 0.03 | 51.02 | 0.07 | 46.23 | 0.02 | 4.79 | 0.07 | [44 empty] | 3.62 | 0.02 | [74 empty] | 62.9 | 0.04 | 63.4 | 0.03 | 63.43 | 0.03 | 63.14 | 0.04 | 63.12 | 0.03 | 63.32 | 0.03 | [86 empty] | 152.19 | 0.06 | 63.29 | 0.2 | 178.15 | 0.11 | 115.37 | 0.11 | 114.12 | 0.15 | 78.67 | 0.21 | 77.63 | 0.15 | 76.42 | 0.09 | 76.25 | 0.07 | 75.64 | 0.04 | 75.76 | 0.05 | 75.37 | 0.02 | [40 empty] | 74.89 | 0.03 | [34 empty] | 115.01 | 0.1 | 99.94 | 0.24 | 104.58 | 0.33 | 75.81 | 0.07 | 94.68 | 0.46 | 78.9 | 0.19 | 88.05 | 0.32 | 76.02 | 0.04 | 76.11 | 0.07 | 78.04 | 0.13 | 90.69 | 0.29 |  |  | 77.63 | 0.14 | 83.23 | 0.34 | 94.71 | 0.46 | 76.27 | 0.12 | 100.07 | 0.29 | 114.94 | 0.13 | [12 empty] | C-EB50-55-CE | 75.015 | 0.018 | 61.989 | 0.034 | 63.867 | 0.008 | 58.482 | 0.014 | 114.991 | 0.02 | 80.001 | 0.02 | 949.1 | 1.4 | 910.8 | 1.4 | 0.406 | 0.002 | -0.144 | 0.001 | -0.023 | 0.002 | 0.7576 | 0.0022 | 29.093 | 0.001 | 4178 | 9 | 444.8 | 5.7 | 0.15085 | 149.827 | 13.029 | 0.164 | 1.3298 | 4290.9242 | 43.4424 | 148.6522 | 610.6151 | 3680.3091 | 0.0094814 | 29.7792 | 62.5372 | 14.6068 | 13.2713 | 0.01377 | 42.9111 | 0.0087698 | 27.6005 | 0.0091712 | 25.3188 | 80.7481 | 65.027 | 24.9943 | 20531.8825 | 18753.9541 | 3733.2 | 0.62057 | 19162.0492 | 17384.1207 | 4.5864 | 0.31001 | -4.785 | -18.2109 | 54.3552 | 20531.8825 | 9790.3452 | 1392.6669 | 9348.8705 | 20531.8825 | 100%
5 | C-EB0-82-CE | 30N0112 | C-EB0-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/18/2015 | 2:14:04 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 1.5 | 14.2 | 0 | 22303 | 42 | 21966 | 46 | 5113 | 84 | 27420 | 110 |  | 943 | [37 empty] | 8.7941 | Baseline no evaporator coil blockage, economizer closed damper, factory charge (5.5 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75 | 0.013 | 62.008 | 0.033 | 81.974 | 0.01 | 67.984 | 0.027 | 74.95 | 0.03 | 56.83 | 0.04 | 62.02 | 0.04 | -0.001 | 0.003 | 1.0678 | 0.0034 | 22303 | 42 | 5113 | 84 | 8.794 | 0.045 | [6 empty] | 230 | 1.5 | 230 | 1.5 | 230 | 1.5 | 12 | 0 | 12 | 0 | 12 | 0 | 2639.5 | 7.7 | 2639.5 | 7.7 | 2639.5 | 7.7 | 229.8 | 1.5 | 229.8 | 1.5 | 229.8 | 1.5 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.5 | 1.6 | 228.5 | 1.6 | 228.5 | 1.6 | 11.2 | 0 | 11.2 | 0 | 11.2 | 0 | 2427.8 | 6.6 | [9 empty] | 228.9 | 1.6 | 0.7 | 0 | 170.7 | 1.3 | 0.2 | 0.3 | 3077.2 | [10 empty] | 230.2 | 1.5 | 0 | 0 | 213.17 | 0.15 | 87.98 | 0.04 | 105.66 | 0.05 | 17.69 | 0.03 | 229.75 | 0.16 | 168.31 | 0.02 | 110.93 | 0.05 | 57.38 | 0.05 | 212.62 | 0.16 | 87.95 | 0.03 | 105.48 | 0.05 | 17.53 | 0.04 | 72.4 | 0.03 | 61.63 | 0.04 | 42.34 | 0.02 |  |  | 73.57 | 0.02 | 63.84 | 0.04 | 43.11 | 0.02 | 20.72 | 0.04 | [44 empty] | 19.29 | 0.04 | [74 empty] | 55.59 | 0.04 | 55.95 | 0.04 | 56.02 | 0.02 | 55.96 | 0.03 | 55.8 | 0.04 | 55.9 | 0.04 | [86 empty] | 140.18 | 0.07 | 87.09 | 0.03 | 170.42 | 0.03 | 81.89 | 0.06 | 82.52 | 0.07 | 75.56 | 0.03 | 75.43 | 0.03 | 75.52 | 0.03 | 75.55 | 0.03 | 75.47 | 0.04 | 75.48 | 0.04 | 75.39 | 0.03 | [40 empty] | 74.78 | 0.04 | [34 empty] | 81.95 | 0.09 | 76.15 | 0.08 | 77.45 | 0.15 | 76.04 | 0.04 | 79.89 | 0.11 | 75.62 | 0.03 | 76.35 | 0.06 | 77.06 | 0.07 | 75.1 | 0.03 | 78.14 | 0.1 | 79.45 | 0.1 |  |  | 75.48 | 0.04 | 77.22 | 0.1 | 78.51 | 0.06 | 78.08 | 0.09 | 76.39 | 0.12 | 81.71 | 0.05 | [12 empty] | C-55-CE | 75 | 0.013 | 62.008 | 0.033 | 56.605 | 0.015 | 53.537 | 0.018 | 81.974 | 0.01 | 67.984 | 0.027 | 1121 | 1.8 | 1091 | 1.7 | 0.563 | 0.002 | -0.199 | 0.001 | -0.001 | 0.003 | 1.0678 | 0.0034 | 29.11 | 0.001 | 3118 | 11 | 478.5 | 5.6 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.1232 | 5143.0032 | 72.1603 | 205.7694 | 898.0412 | 4244.962 | 0.0092315 | 28.4004 | 55.4818 | 13.7479 | 13.078 | 0.011338 | 32.1155 | 0.0087859 | 27.6144 | 0.0079858 | 22.2588 | 76.2224 | 63.1088 | 21.9852 | 32993.0234 | 25600.6251 | 2639.5 | 0.27305 | 31606.1859 | 24213.7876 | 10.1367 | 0.21004 | -6.4151 | -20.7407 | 49.967 | 32993.0234 | 27543.9319 | 1406.9138 | 4042.1777 | 32993.0234 | 100%
5 | C-EB10-82-CE | 30N0113 | C-EB10-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 10 | CUST 2 | 6/18/2015 | 4:18:58 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 1.3 | 14.2 | 0 | 21849 | 33 | 21544 | 52 | 5240 | 88 | 27093 | 104 |  | 944 | [37 empty] | 8.7144 | 10% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 82F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 74.989 | 0.008 | 62.003 | 0.03 | 81.988 | 0.011 | 68.006 | 0.018 | 74.73 | 0.03 | 56.78 | 0.03 | 61.72 | 0.03 | 0.006 | 0.002 | 1.0454 | 0.0033 | 21849 | 33 | 5240 | 88 | 8.715 | 0.043 | [6 empty] | 230 | 1.3 | 230 | 1.3 | 230 | 1.3 | 12 | 0 | 12 | 0 | 12 | 0 | 2633.2 | 7 | 2633.2 | 7 | 2633.2 | 7 | 229.9 | 1.3 | 229.9 | 1.3 | 229.9 | 1.3 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.6 | 1.3 | 228.6 | 1.3 | 228.6 | 1.3 | 11.2 | 0 | 11.2 | 0 | 11.2 | 0 | 2421 | 6 | [9 empty] | 228.9 | 1.3 | 0.7 | 0 | 170.8 | 1.1 | 0.2 | 0.3 | 3067.4 | [10 empty] | 230.2 | 1.3 | 0 | 0 | 212.43 | 0.15 | 88.12 | 0.04 | 105.42 | 0.05 | 17.3 | 0.03 | 228.9 | 0.13 | 166.44 | 0.03 | 110.67 | 0.04 | 55.77 | 0.05 | 211.87 | 0.14 | 87.82 | 0.05 | 105.24 | 0.05 | 17.41 | 0.04 | 71.19 | 0.02 | 58.86 | 0.04 | 41.53 | 0.02 |  |  | 72.44 | 0.02 | 61.19 | 0.04 | 42.37 | 0.02 | 18.82 | 0.05 | [44 empty] | 17.33 | 0.05 | [74 empty] | 55.79 | 0.02 | 56.14 | 0.02 | 56.24 | 0.02 | 56.22 | 0.02 | 55.95 | 0.02 | 56.08 | 0.02 | [86 empty] | 138.24 | 0.09 | 84.95 | 0.05 | 168.42 | 0.04 | 82.13 | 0.06 | 82.44 | 0.07 | 75.51 | 0.03 | 75.37 | 0.03 | 75.51 | 0.02 | 75.49 | 0.03 | 75.4 | 0.03 | 75.41 | 0.03 | 75.35 | 0.03 | [40 empty] | 74.68 | 0.03 | [34 empty] | 82.07 | 0.09 | 76.78 | 0.4 | 79.17 | 0.42 | 75.36 | 0.04 | 80.18 | 0.13 | 75.62 | 0.04 | 76.55 | 0.07 | 76.57 | 0.11 | 75.04 | 0.04 | 77.38 | 0.24 | 79.68 | 0.11 | 78.21 | 0.19 | 75.32 | 0.08 | 77.52 | 0.37 | 78.35 | 0.12 | 77.26 | 0.27 | 78.17 | 0.64 | 81.79 | 0.06 | [12 empty] | C-EB10-55-CE | 74.989 | 0.008 | 62.003 | 0.03 | 56.79 | 0.007 | 53.547 | 0.008 | 81.988 | 0.011 | 68.006 | 0.018 | 1108.7 | 1.7 | 1080 | 1.7 | 0.544 | 0.001 | -0.196 | 0.001 | 0.006 | 0.002 | 1.0454 | 0.0033 | 29.116 | 0.001 | 3109 | 10 | 475.4 | 5.2 | 0.16566 | 179.2423 | 13.029 | 0.195 | 1.1362 | 5084.8655 | 69.022 | 184.5954 | 805.6041 | 4279.2614 | 0.0091917 | 28.3275 | 55.6538 | 13.7483 | 13.0824 | 0.011351 | 32.1334 | 0.0087852 | 27.611 | 0.0079477 | 22.2625 | 76.1022 | 63.0077 | 21.9858 | 32246.314 | 24954.57 | 2633.6 | 0.27874 | 30859.346 | 23567.602 | 9.9258 | 0.22446 | -6.3416 | -20.4484 | 49.7356 | 32246.314 | 27196.061 | 1406.9486 | 3643.3043 | 32246.314 | 100%
5 | C-EB20-82-CE | 30N0114 | C-EB20-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 20 | CUST 2 | 6/18/2015 | 5:16:31 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 1.8 | 14.1 | 0 | 21567 | 47 | 21266 | 64 | 5350 | 66 | 26922 | 82 |  | 944 | [37 empty] | 8.6901 | 20% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 82F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75.043 | 0.02 | 61.996 | 0.028 | 82.036 | 0.024 | 68.012 | 0.01 | 74.76 | 0.07 | 56.66 | 0.06 | 62.49 | 0.02 | -0.004 | 0.003 | 1.0018 | 0.0036 | 21567 | 47 | 5350 | 66 | 8.692 | 0.043 | [6 empty] | 230 | 1.8 | 230 | 1.8 | 230 | 1.8 | 12 | 0 | 12 | 0 | 12 | 0 | 2627.8 | 8.5 | 2627.8 | 8.5 | 2627.8 | 8.5 | 229.8 | 1.8 | 229.8 | 1.8 | 229.8 | 1.8 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.5 | 1.8 | 228.5 | 1.8 | 228.5 | 1.8 | 11.1 | 0 | 11.1 | 0 | 11.1 | 0 | 2415.1 | 6.9 | [9 empty] | 228.9 | 1.8 | 0.7 | 0 | 170.8 | 1.5 | 0.2 | 0.3 | 3055.4 | [10 empty] | 230.2 | 1.8 | 0 | 0 | 211.81 | 0.19 | 88.19 | 0.05 | 105.22 | 0.06 | 17.03 | 0.05 | 228.22 | 0.16 | 165.77 | 0.03 | 110.46 | 0.05 | 55.3 | 0.05 | 211.24 | 0.16 | 87.89 | 0.07 | 105.04 | 0.05 | 17.14 | 0.09 | 70.57 | 0.03 | 57.82 | 0.05 | 41.11 | 0.02 |  |  | 71.78 | 0.03 | 59.99 | 0.04 | 41.93 | 0.02 | 18.06 | 0.04 | [44 empty] | 16.71 | 0.04 | [74 empty] | 55.73 | 0.03 | 56.04 | 0.03 | 56.15 | 0.02 | 56.16 | 0.03 | 55.87 | 0.02 | 55.98 | 0.03 | [86 empty] | 137.61 | 0.03 | 84.27 | 0.05 | 167.61 | 0.05 | 82.24 | 0.07 | 82.46 | 0.05 | 75.65 | 0.03 | 75.47 | 0.02 | 75.65 | 0.03 | 75.6 | 0.03 | 75.49 | 0.04 | 75.5 | 0.04 | 75.39 | 0.04 | [40 empty] | 74.79 | 0.05 | [34 empty] | 82.14 | 0.08 | 79.08 | 0.13 | 80.45 | 0.06 | 75.77 | 0.04 | 79.26 | 0.09 | 75.91 | 0.06 | 77.79 | 0.1 | 76.21 | 0.06 | 75.15 | 0.05 | 76.57 | 0.09 | 78.7 | 0.1 | 77.55 | 0.15 | 75.39 | 0.06 | 75.98 | 0.1 | 77.94 | 0.08 | 76.47 | 0.13 | 80.31 | 0.1 | 81.91 | 0.08 | [12 empty] | C-EB20-55-CE | 75.043 | 0.02 | 61.996 | 0.028 | 56.686 | 0.007 | 53.392 | 0.016 | 82.036 | 0.024 | 68.012 | 0.01 | 1085.7 | 1.9 | 1056.6 | 1.9 | 0.528 | 0.002 | -0.189 | 0.001 | -0.004 | 0.003 | 1.0018 | 0.0036 | 29.13 | 0 | 3098 | 12 | 469.5 | 5.7 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1531 | 4980.5665 | 65.5405 | 170.3477 | 743.3624 | 4237.2041 | 0.0091523 | 28.2816 | 55.5329 | 13.7495 | 13.0792 | 0.011344 | 32.1376 | 0.0087678 | 27.6051 | 0.0078858 | 22.1699 | 76.0909 | 62.9452 | 21.8891 | 31838.0615 | 24573.6658 | 2628.5 | 0.28177 | 30459.3477 | 23194.9519 | 9.8319 | 0.22765 | -6.3925 | -20.558 | 49.4735 | 31838.0615 | 27070.3841 | 1398.4176 | 3369.2598 | 31838.0615 | 100%
5 | C-EB35-82-CE | 30N0115 | C-EB35-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 35 | CUST 2 | 6/18/2015 | 6:34:18 | 10 Ton | 0:10:00 | 75/62 - 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 229.9 | 1.8 | 14 | 0 | 20677 | 48 | 20385 | 70 | 5792 | 74 | 26475 | 87 |  | 945 | [37 empty] | 8.6182 | 35% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 82F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 74.996 | 0.013 | 62.001 | 0.026 | 81.993 | 0.007 | 67.999 | 0.029 | 74.65 | 0.04 | 56.38 | 0.03 | 62.25 | 0.02 | -0.009 | 0.002 | 0.9007 | 0.0033 | 20677 | 48 | 5792 | 74 | 8.62 | 0.044 | [6 empty] | 229.9 | 1.8 | 229.9 | 1.8 | 229.9 | 1.8 | 11.9 | 0 | 11.9 | 0 | 11.9 | 0 | 2612.3 | 8 | 2612.3 | 8 | 2612.3 | 8 | 229.8 | 1.8 | 229.8 | 1.8 | 229.8 | 1.8 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.5 | 1.7 | 228.5 | 1.7 | 228.5 | 1.7 | 11.1 | 0 | 11.1 | 0 | 11.1 | 0 | 2400 | 6.6 | [9 empty] | 228.9 | 1.7 | 0.7 | 0 | 170.8 | 1.4 | 0.2 | 0.3 | 3029.7 | [10 empty] | 230.2 | 1.8 | 0 | 0 | 209.85 | 0.2 | 88.21 | 0.05 | 104.58 | 0.07 | 16.37 | 0.04 | 226.16 | 0.2 | 162.97 | 0.04 | 109.82 | 0.06 | 53.15 | 0.06 | 209.31 | 0.21 | 87.91 | 0.05 | 104.4 | 0.07 | 16.48 | 0.05 | 68.79 | 0.03 | 53.86 | 0.06 | 39.9 | 0.02 |  |  | 69.97 | 0.03 | 56.25 | 0.06 | 40.71 | 0.02 | 15.54 | 0.06 | [44 empty] | 13.96 | 0.07 | [74 empty] | 55.36 | 0.02 | 55.77 | 0.03 | 55.83 | 0.03 | 55.9 | 0.02 | 55.65 | 0.03 | 55.67 | 0.02 | [86 empty] | 135.23 | 0.04 | 81.11 | 0.06 | 164.42 | 0.16 | 82.15 | 0.06 | 82.36 | 0.08 | 75.63 | 0.02 | 75.42 | 0.03 | 75.56 | 0.02 | 75.49 | 0.03 | 75.36 | 0.03 | 75.37 | 0.02 | 75.26 | 0.03 | [40 empty] | 74.64 | 0.03 | [34 empty] | 82.04 | 0.09 | 79.54 | 0.06 | 79.91 | 0.07 | 75.46 | 0.04 | 78.3 | 0.08 | 75.79 | 0.05 | 77.84 | 0.12 | 75.64 | 0.05 | 75.01 | 0.04 | 76.26 | 0.08 | 77.52 | 0.07 | 76.66 | 0.15 | 75.31 | 0.05 | 75.77 | 0.06 | 77.67 | 0.05 | 75.57 | 0.08 | 80.15 | 0.05 | 81.82 | 0.06 | [12 empty] | C-EB35-55-CE | 74.996 | 0.013 | 62.001 | 0.026 | 56.456 | 0.005 | 53.052 | 0.013 | 81.993 | 0.007 | 67.999 | 0.029 | 1028.8 | 1.9 | 1002 | 1.9 | 0.476 | 0.001 | -0.171 | 0.001 | -0.009 | 0.002 | 0.9007 | 0.0033 | 29.132 | 0.001 | 3072 | 12 | 458.9 | 5.7 | 0.15207 | 157.7743 | 13.029 | 0.181 | 1.2129 | 4722.0235 | 56.0325 | 157.531 | 687.487 | 4034.5365 | 0.0091552 | 28.2672 | 55.2431 | 13.7484 | 13.0724 | 0.011344 | 32.1276 | 0.0087822 | 27.6094 | 0.0077512 | 21.9678 | 76.0188 | 62.9242 | 21.6725 | 31140.2619 | 23544.7804 | 2613.1 | 0.2864 | 29765.275 | 22169.7935 | 9.6892 | 0.23764 | -6.5947 | -20.7757 | 48.7671 | 31140.2619 | 26639.7992 | 1394.2953 | 3106.1674 | 31140.2619 | 100%
5 | C-EB5-82-CE | 30N0116 | C-EB5-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 5 | CUST 2 | 6/18/2015 | 3:04:36 | 10 Ton | 0:10:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 230 | 1.8 | 14.2 | 0 | 22058 | 43 | 21730 | 70 | 5233 | 48 | 27297 | 63 |  | 944 | [37 empty] | 8.7659 | 5% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 82F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust code tester | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75.011 | 0.01 | 62.014 | 0.026 | 82.015 | 0.015 | 67.998 | 0.026 | 74.64 | 0.04 | 56.57 | 0.04 | 62.21 | 0.02 | 0.002 | 0.003 | 1.0512 | 0.0036 | 22058 | 43 | 5233 | 48 | 8.767 | 0.042 | [6 empty] | 230 | 1.8 | 230 | 1.8 | 230 | 1.8 | 12 | 0 | 12 | 0 | 12 | 0 | 2637 | 8.8 | 2637 | 8.8 | 2637 | 8.8 | 229.9 | 1.8 | 229.9 | 1.8 | 229.9 | 1.8 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.6 | 1.8 | 228.6 | 1.8 | 228.6 | 1.8 | 11.2 | 0 | 11.2 | 0 | 11.2 | 0 | 2424.6 | 7.2 | [9 empty] | 228.9 | 1.8 | 0.7 | 0 | 170.8 | 1.5 | 0.2 | 0.3 | 3072.1 | [10 empty] | 230.2 | 1.8 | 0 | 0 | 212.86 | 0.12 | 88.07 | 0.05 | 105.56 | 0.04 | 17.49 | 0.05 | 229.41 | 0.16 | 167.25 | 0.04 | 110.83 | 0.05 | 56.42 | 0.04 | 212.32 | 0.15 | 87.72 | 0.05 | 105.38 | 0.05 | 17.66 | 0.05 | 71.64 | 0.03 | 60.01 | 0.05 | 41.83 | 0.02 |  |  | 72.91 | 0.03 | 62.15 | 0.06 | 42.67 | 0.02 | 19.47 | 0.05 | [44 empty] | 18.18 | 0.05 | [74 empty] | 55.68 | 0.04 | 56.05 | 0.04 | 56.12 | 0.03 | 56.11 | 0.03 | 55.87 | 0.03 | 55.98 | 0.03 | [86 empty] | 138.84 | 0.04 | 85.73 | 0.05 | 169.16 | 0.04 | 82.08 | 0.07 | 82.46 | 0.07 | 75.49 | 0.03 | 75.34 | 0.03 | 75.52 | 0.03 | 75.49 | 0.03 | 75.4 | 0.04 | 75.41 | 0.03 | 75.3 | 0.04 | [40 empty] | 74.7 | 0.05 | [34 empty] | 82.03 | 0.09 | 76.03 | 0.06 | 77.77 | 0.14 | 75.24 | 0.04 | 80.27 | 0.08 | 75.55 | 0.04 | 76.36 | 0.07 | 76.76 | 0.05 | 75.01 | 0.04 | 77.99 | 0.11 | 79.71 | 0.08 | 78.43 | 0.06 | 75.38 | 0.06 | 77.58 | 0.1 | 78.35 | 0.04 | 77.74 | 0.09 | 76.37 | 0.1 | 81.75 | 0.06 | [12 empty] | C-EB5-55-CE | 75.011 | 0.01 | 62.014 | 0.026 | 56.674 | 0.007 | 53.512 | 0.02 | 82.015 | 0.015 | 67.998 | 0.026 | 1112.5 | 1.9 | 1082.3 | 1.9 | 0.55 | 0.001 | -0.196 | 0.001 | 0.002 | 0.003 | 1.0512 | 0.0036 | 29.105 | 0.001 | 3114 | 13 | 476.5 | 5.6 | 0.16408 | 178.2735 | 13.029 | 0.192 | 1.1326 | 5103.4161 | 69.9319 | 185.0303 | 807.4681 | 4295.9479 | 0.0091909 | 28.3318 | 55.5414 | 13.7489 | 13.0795 | 0.011338 | 32.1264 | 0.0087873 | 27.6186 | 0.0079555 | 22.2428 | 76.1235 | 63.014 | 21.9669 | 32482.5783 | 25209.3557 | 2637.5 | 0.27713 | 31094.9614 | 23821.7389 | 9.9855 | 0.21749 | -6.3649 | -20.5821 | 49.8208 | 32482.5783 | 27435.0427 | 1407.6269 | 3639.9087 | 32482.5783 | 100%
5 | C-EB50-82-CE | 30N0117 | C-EB50-82-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 50 | CUST 2 | 6/18/2015 | 7:59:38 | 10 Ton | 0:10:00 | 75/62 - 82/68 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 82 | 68 | 5.5 |  | 5.5 |  | 229.9 | 1.9 | 14 | 0 | 19891 | 51 | 19546 | 67 | 6073 | 62 | 25970 | 75 |  | 946 | [37 empty] | 8.498 | 50% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 82F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code teste | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75.011 | 0.012 | 62 | 0.032 | 82.008 | 0.016 | 67.992 | 0.024 | 74.66 | 0.09 | 56.26 | 0.07 | 62.8 | 0.05 | -0.006 | 0.003 | 0.8157 | 0.0037 | 19891 | 51 | 6073 | 62 | 8.498 | 0.043 | [6 empty] | 229.9 | 1.9 | 229.9 | 1.9 | 229.9 | 1.9 | 11.9 | 0 | 11.9 | 0 | 11.9 | 0 | 2602.8 | 8.6 | 2602.8 | 8.6 | 2602.8 | 8.6 | 229.8 | 1.9 | 229.8 | 1.9 | 229.8 | 1.9 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.4 | 1.9 | 228.4 | 1.9 | 228.4 | 1.9 | 11 | 0 | 11 | 0 | 11 | 0 | 2390.8 | 6.8 | [9 empty] | 228.8 | 1.9 | 0.7 | 0 | 170.8 | 1.6 | 0.2 | 0.3 | 3014.4 | [10 empty] | 230.1 | 1.9 | 0 | 0 | 208.79 | 0.18 | 88.33 | 0.06 | 104.23 | 0.06 | 15.89 | 0.06 | 224.93 | 0.15 | 160.26 | 0.03 | 109.44 | 0.05 | 50.82 | 0.05 | 208.23 | 0.14 | 88.02 | 0.1 | 104.05 | 0.05 | 16.03 | 0.1 | 67.56 | 0.03 | 49.81 | 0.2 | 39.05 | 0.02 |  |  | 68.25 | 0.03 | 51.9 | 0.26 | 39.53 | 0.02 | 12.36 | 0.27 | [44 empty] | 10.76 | 0.21 | [74 empty] | 55.25 | 0.05 | 55.69 | 0.05 | 55.72 | 0.04 | 55.49 | 0.03 | 55.45 | 0.05 | 55.6 | 0.04 | [86 empty] | 132.79 | 0.05 | 77.14 | 0.06 | 161.14 | 0.15 | 81.91 | 0.13 | 82.16 | 0.12 | 75.67 | 0.08 | 75.5 | 0.06 | 75.32 | 0.1 | 75.34 | 0.09 | 75.25 | 0.09 | 75.3 | 0.07 | 75.27 | 0.04 | [40 empty] | 74.84 | 0.05 | [34 empty] | 81.94 | 0.12 | 79.98 | 0.04 | 80.68 | 0.04 | 75.6 | 0.04 | 78.1 | 0.09 | 76.66 | 0.05 | 78.05 | 0.06 | 75.72 | 0.03 | 75.23 | 0.04 | 78.01 | 0.09 | 77.8 | 0.07 | 77.55 | 0.1 | 75.75 | 0.04 | 75.77 | 0.05 | 77.08 | 0.13 | 76.54 | 0.1 | 79.97 | 0.09 | 81.95 | 0.06 | [12 empty] | C-EB50-55-CE | 75.011 | 0.012 | 62 | 0.032 | 56.283 | 0.011 | 52.739 | 0.023 | 82.008 | 0.016 | 67.992 | 0.024 | 978.5 | 2.2 | 953.4 | 2.1 | 0.42 | 0.002 | -0.154 | 0.001 | -0.006 | 0.003 | 0.8157 | 0.0037 | 29.166 | 0.001 | 3056 | 13 | 452.8 | 6 | 0.15085 | 149.827 | 13.029 | 0.164 | 1.2839 | 4493.0136 | 47.0424 | 149.1435 | 650.8681 | 3842.1455 | 0.0091485 | 28.2623 | 54.9991 | 13.7487 | 13.067 | 0.011335 | 32.1216 | 0.008778 | 27.6085 | 0.0076194 | 21.7825 | 76.0286 | 62.9177 | 21.47 | 30517.6007 | 22676.6212 | 2603.2 | 0.29113 | 29132.7501 | 21291.7705 | 9.533 | 0.24879 | -6.7922 | -21.0295 | 48.0345 | 30517.6007 | 26176.222 | 1403.9599 | 2937.4189 | 30517.6007 | 100%
5 | C-EB0-95-CE | 30N0118 | C-EB0-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/17/2015 | 4:55:00 | 10 Ton | 0:10:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1.8 | 16.1 | 0 | 18320 | 29 | 18019 | 56 | 34 | 82 | 18354 | 91 |  | 943 | [37 empty] | 5.1716 | Baseline no evaporator coil blockage, economizer closed damper, factory charge (5.5 lbs) 95F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%: Outlet @ 52% Horiz airflow.--4.75" ID pulley 3 turns open from fully closed, adjust | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; | 75.028 | 0.009 | 61.986 | 0.033 | 95.023 | 0.009 | 75.028 | 0.011 | 74.67 | 0.05 | 59.71 | 0.05 | 64.31 | 0.08 | 0.002 | 0.002 | 0.7727 | 0.0017 | 18320 | 29 | 34 | 82 | 5.172 | 0.031 | [6 empty] | 230 | 1.8 | 230 | 1.8 | 230 | 1.8 | 13.9 | 0 | 13.9 | 0 | 13.9 | 0 | 3071.6 | 7.5 | 3071.6 | 7.5 | 3071.6 | 7.5 | 229.9 | 1.8 | 229.9 | 1.8 | 229.9 | 1.8 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.2 | 1.8 | 228.2 | 1.8 | 228.2 | 1.8 | 13 | 0 | 13 | 0 | 13 | 0 | 2850.8 | 6.2 | [9 empty] | 228.7 | 1.8 | 0.7 | 0 | 169.6 | 1.5 | 0.1 | 0.2 | 3497.3 | [10 empty] | 230.2 | 1.8 | 0 | 0 | 257.19 | 0.24 | 102.63 | 0.04 | 119.11 | 0.07 | 16.48 | 0.05 | 273.65 | 0.2 | 178.08 | 0.04 | 123.72 | 0.06 | 54.36 | 0.06 | 256.55 | 0.23 | 102.47 | 0.06 | 118.93 | 0.07 | 16.45 | 0.07 | 77.9 | 0.04 | 60.37 | 0.47 | 45.94 | 0.02 |  |  | 78.05 | 0.02 | 56.19 | 0.35 | 46.04 | 0.01 | 10.15 | 0.35 | [44 empty] | 14.42 | 0.47 | [74 empty] | 58.7 | 0.04 | 59.05 | 0.04 | 59.17 | 0.05 | 59.21 | 0.05 | 58.92 | 0.04 | 59.02 | 0.04 | [86 empty] | 147.01 | 0.08 | 84.65 | 0.09 | 179.43 | 0.07 | 95.85 | 0.05 | 94.83 | 0.13 | 76.36 | 0.06 | 76.01 | 0.07 | 75.9 | 0.05 | 75.79 | 0.04 | 75.47 | 0.05 | 75.49 | 0.04 | 75.35 | 0.04 | [40 empty] | 74.67 | 0.05 | [34 empty] | 95.21 | 0.06 | 87.66 | 0.17 | 80.32 | 0.31 | 76.77 | 0.06 | 87.86 | 0.12 | 82.45 | 0.12 | 77.48 | 0.09 | 75.44 | 0.05 | 75.24 | 0.04 | 76.56 | 0.08 | 85.68 | 0.2 | 75.99 | 0.04 | 75.65 | 0.06 | 82.97 | 0.4 | 91.26 | 0.08 | 75.48 | 0.04 | 81.99 | 0.33 | 95.07 | 0.08 | [12 empty] | C-55-CE | 75.028 | 0.009 | 61.986 | 0.033 | 59.825 | 0.013 | 56.451 | 0.025 | 95.023 | 0.009 | 75.028 | 0.011 | 1124.2 | 1.3 | 1090.3 | 1.2 | 0.556 | 0.001 | -0.195 | 0.001 | 0.002 | 0.002 | 0.7727 | 0.0017 | 29.177 | 0 | 3549 | 11 | 476.9 | 5.8 | 0.17564 | 192.6271 | 13.03 | 0.184 | 1.1258 | 5122.9263 | 71.2174 | 206.2877 | 877.7791 | 4245.1471 | 0.0096515 | 29.4119 | 58.6992 | 14.1007 | 13.1667 | 0.01394 | 38.1838 | 0.0087648 | 27.5981 | 0.0089011 | 24.0385 | 78.4807 | 64.5022 | 23.7639 | 28934.3938 | 24321.4307 | 3072.1 | 0.36237 | 27549.799 | 22936.8359 | 7.7627 | 0.21292 | -5.648 | -19.7815 | 53.3479 | 28934.3938 | 18235.536 | 1406.9827 | 9291.8751 | 28934.3938 | 100%
5 | C-EB10-95-CE | 30N0119 | C-EB10-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 10 | CUST 2 | 6/17/2015 | 9:39:10 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.8 | 16 | 0 | 17970 | 33 | 17478 | 79 | 556 | 91 | 18527 | 88 |  | 943 | [37 empty] | 5.2425 | 10% evaporator coil block, economizer closed damper, factory charge (5.5 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed, adjust--code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.; with outlet hose, with code tester, 6" cardboard evap blockage, 98% | 75.033 | 0.024 | 62.005 | 0.032 | 95.005 | 0.007 | 74.998 | 0.018 | 74.46 | 0.08 | 59.66 | 0.06 | 65.34 | 0.03 | 0.009 | 0.001 | 0.7443 | 0.0009 | 17970 | 33 | 556 | 91 | 5.243 | 0.03 | [6 empty] | 229.9 | 1.8 | 229.9 | 1.8 | 229.9 | 1.8 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3060.4 | 7.6 | 3060.4 | 7.6 | 3060.4 | 7.6 | 229.8 | 1.8 | 229.8 | 1.8 | 229.8 | 1.8 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.3 | 1.8 | 228.3 | 1.8 | 228.3 | 1.8 | 13 | 0 | 13 | 0 | 13 | 0 | 2840.7 | 5.9 | [9 empty] | 228.7 | 1.8 | 0.7 | 0 | 169.7 | 1.5 | 13 | 0.2 | 3496.8 | [10 empty] | 230.2 | 1.8 | 0 | 0 | 256.06 | 0.13 | 102.8 | 0.03 | 118.78 | 0.04 | 15.98 | 0.03 | 272.41 | 0.11 | 175.37 | 0.07 | 123.37 | 0.03 | 51.99 | 0.09 | 255.39 | 0.12 | 102.38 | 0.05 | 118.59 | 0.04 | 16.21 | 0.06 | 76.5 | 0.03 | 51.5 | 0.63 | 45.03 | 0.02 |  |  | 77.65 | 0.02 | 52.74 | 0.28 | 45.77 | 0.01 | 6.97 | 0.27 | [44 empty] | 6.47 | 0.63 | [74 empty] | 58.96 | 0.03 | 59.22 | 0.04 | 59.27 | 0.03 | 59.3 | 0.03 | 59.1 | 0.03 | 59.17 | 0.03 |  |  |  |  | 51.29 | 0.09 | 50.2 | 0.33 | [10 empty] | 102.38 | 0.05 | [66 empty] | 141.51 | 0.08 | 82.64 | 0.15 | 176.77 | 0.15 | 95.32 | 0.06 | 94.73 | 0.07 | 76.14 | 0.07 | 75.82 | 0.08 | 75.47 | 0.06 | 75.44 | 0.05 | 75.22 | 0.05 | 75.27 | 0.05 | 75.14 | 0.06 | [40 empty] | 74.73 | 0.06 | [34 empty] | 94.82 | 0.06 | 88.71 | 0.18 | 84.77 | 0.44 | 76.55 | 0.06 | 87.94 | 0.12 | 80.81 | 0.12 | 77.73 | 0.36 | 75.47 | 0.05 | 75.23 | 0.06 | 77.51 | 0.15 | 86.46 | 0.16 | 75.76 | 0.06 | 75.8 | 0.07 | 82.52 | 0.27 | 89.21 | 0.17 | 75.28 | 0.06 | 86.75 | 0.34 | 94.98 | 0.06 | [12 empty] | C-EB10-55-CE | 75.033 | 0.024 | 62.005 | 0.032 | 59.822 | 0.006 | 56.303 | 0.011 | 95.005 | 0.007 | 74.998 | 0.018 | 1105.3 | 0.7 | 1068 | 0.6 | 0.544 | 0.001 | -0.193 | 0.001 | 0.009 | 0.001 | 0.7443 | 0.0009 | 29.122 | 0.001 | 3534 | 11 | 473.4 | 5.6 | 0.16566 | 179.2423 | 13.029 | 0.195 | 1.1435 | 5037.0886 | 68.2551 | 185.5052 | 789.3828 | 4247.7057 | 0.0095819 | 29.2641 | 58.6785 | 14.1 | 13.1659 | 0.013918 | 38.1551 | 0.0087761 | 27.6118 | 0.0088143 | 23.9434 | 78.1876 | 64.3018 | 23.6645 | 28205.384 | 23584.5067 | 3060.6 | 0.37035 | 26822.6246 | 22201.7472 | 7.5899 | 0.22484 | -5.5995 | -19.509 | 53.0198 | 28205.384 | 18477.7587 | 1404.8957 | 8322.7296 | 28205.384 | 100%
5 | C-EB20-95-CE | 30N0120 | C-EB20-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 20 | CUST 2 | 6/17/2015 | 11:03:55 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.1 | 1.8 | 15.8 | 0 | 17647 | 15 | 17131 | 63 | 904 | 70 | 18552 | 72 |  | 944 | [37 empty] | 5.287 | 20% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 95F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed, adjust--code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.;, with outlet duct, with code tester, 9" coil blockage | 74.999 | 0.012 | 61.994 | 0.026 | 94.992 | 0.006 | 74.999 | 0.015 | 74.37 | 0.08 | 59.59 | 0.07 | 65.13 | 0.03 | 0.007 | 0.001 | 0.7161 | 0.0009 | 17647 | 15 | 904 | 70 | 5.287 | 0.027 | [6 empty] | 230.1 | 1.8 | 230.1 | 1.8 | 230.1 | 1.8 | 13.7 | 0 | 13.7 | 0 | 13.7 | 0 | 3040.6 | 7.2 | 3040.6 | 7.2 | 3040.6 | 7.2 | 230 | 1.8 | 230 | 1.8 | 230 | 1.8 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.4 | 1.8 | 228.4 | 1.8 | 228.4 | 1.8 | 12.9 | 0 | 12.9 | 0 | 12.9 | 0 | 2821.2 | 6.3 | [9 empty] | 228.9 | 1.8 | 0.7 | 0 | 169.4 | 1.5 | 13 | 0.2 | 3471.5 | [10 empty] | 230.3 | 1.8 | 0 | 0 | 253.85 | 0.12 | 102.38 | 0.03 | 118.14 | 0.04 | 15.76 | 0.03 | 270.18 | 0.1 | 173.25 | 0.05 | 122.76 | 0.03 | 50.49 | 0.06 | 253.19 | 0.14 | 101.89 | 0.07 | 117.95 | 0.04 | 16.06 | 0.07 | 75.21 | 0.02 | 48.33 | 0.07 | 44.18 | 0.02 |  |  | 75.95 | 0.01 | 50.15 | 0.11 | 44.66 | 0.01 | 5.48 | 0.11 | [44 empty] | 4.14 | 0.06 | [74 empty] | 58.87 | 0.03 | 59.15 | 0.02 | 59.22 | 0.02 | 59.19 | 0.03 | 59.01 | 0.02 | 59.09 | 0.02 |  |  |  |  | 49.71 | 0.1 | 47.53 | 0.09 | [10 empty] | 101.89 | 0.07 | [66 empty] | 144.97 | 0.08 | 81.24 | 0.1 | 174.1 | 0.11 | 95.23 | 0.06 | 94.53 | 0.07 | 76.09 | 0.07 | 75.75 | 0.07 | 75.34 | 0.08 | 75.31 | 0.07 | 75.08 | 0.06 | 75.14 | 0.06 | 75.03 | 0.05 | [40 empty] | 74.6 | 0.05 | [34 empty] | 94.81 | 0.07 | 89.12 | 0.13 | 82.84 | 0.68 | 75.43 | 0.04 | 87.88 | 0.1 | 82.36 | 0.12 | 78.51 | 0.21 | 75.43 | 0.05 | 75.18 | 0.05 | 77.93 | 0.14 | 86.36 | 0.16 | 75.62 | 0.05 | 75.8 | 0.07 | 80.45 | 0.2 | 88.36 | 0.2 | 75.2 | 0.06 | 86.95 | 0.36 | 94.96 | 0.05 | [12 empty] | C-EB20-55-CE | 74.999 | 0.012 | 61.994 | 0.026 | 59.772 | 0.011 | 56.167 | 0.011 | 94.992 | 0.006 | 74.999 | 0.015 | 1084.3 | 0.7 | 1047 | 0.7 | 0.524 | 0.001 | -0.185 | 0.001 | 0.007 | 0.001 | 0.7161 | 0.0009 | 29.088 | 0.001 | 3509 | 11 | 467.9 | 5.6 | 0.15584 | 166.2625 | 13.029 | 0.19 | 1.1606 | 4942.0634 | 64.453 | 170.6684 | 726.2629 | 4215.8005 | 0.009533 | 29.155 | 58.6114 | 14.0997 | 13.1641 | 0.013922 | 38.1563 | 0.0087769 | 27.6043 | 0.008746 | 23.8569 | 77.9605 | 64.1532 | 23.5739 | 27582.3009 | 22949.879 | 3041.1 | 0.3763 | 26205.3363 | 21572.9143 | 7.468 | 0.23222 | -5.5811 | -19.3491 | 52.7592 | 27582.3009 | 18519.9574 | 1398.8341 | 7663.5094 | 27582.3009 | 100%
5 | C-EB35-95-CE | 30N0121 | C-EB35-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 35 | CUST 2 | 6/17/2015 | 12:59:49 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.7 | 15.8 | 0 | 16669 | 60 | 16201 | 112 | 1391 | 83 | 18061 | 84 |  | 945 | [37 empty] | 5.178 | 35% evaporator coil block, economizer closed damper, factory charge (5.5 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set--@ 53.5%: Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code test | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer.;, with outlet duct, with code tester, 14.5" evap coil blockage | 74.869 | 0.038 | 61.979 | 0.024 | 95.004 | 0.006 | 75.004 | 0.025 | 74.24 | 0.1 | 59.67 | 0.05 | 65.8 | 0.07 | 0.009 | 0.003 | 0.6603 | 0.0023 | 16669 | 60 | 1391 | 83 | 5.178 | 0.029 | [6 empty] | 229.9 | 1.7 | 229.9 | 1.7 | 229.9 | 1.7 | 13.7 | 0 | 13.7 | 0 | 13.7 | 0 | 3028.7 | 8.1 | 3028.7 | 8.1 | 3028.7 | 8.1 | 229.9 | 1.7 | 229.9 | 1.7 | 229.9 | 1.7 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.3 | 1.7 | 228.3 | 1.7 | 228.3 | 1.7 | 12.9 | 0 | 12.9 | 0 | 12.9 | 0 | 2809.6 | 7.2 | [9 empty] | 228.8 | 1.7 | 0.7 | 0 | 169.2 | 1.4 | 13 | 0.2 | 3451 | [10 empty] | 230.2 | 1.7 | 0 | 0 | 252.39 | 0.12 | 102.4 | 0.03 | 117.71 | 0.03 | 15.31 | 0.04 | 268.61 | 0.09 | 168.16 | 0.06 | 122.31 | 0.02 | 45.85 | 0.06 | 251.78 | 0.11 | 101.86 | 0.06 | 117.53 | 0.03 | 15.67 | 0.06 | 73.26 | 0.02 | 46.67 | 0.04 | 42.89 | 0.02 |  |  | 74.09 | 0.02 | 47.99 | 0.06 | 43.44 | 0.01 | 4.56 | 0.06 | [44 empty] | 3.77 | 0.04 | [74 empty] | 58.8 | 0.03 | 59.24 | 0.03 | 59.22 | 0.02 | 59.23 | 0.03 | 59.14 | 0.03 | 59.1 | 0.02 |  |  |  |  | 48.42 | 0.07 | 45.65 | 0.04 | [10 empty] | 101.86 | 0.06 | [66 empty] | 139.73 | 0.08 | 74.05 | 0.22 | 168.83 | 0.1 | 94.95 | 0.08 | 94.29 | 0.09 | 76.2 | 0.09 | 75.84 | 0.09 | 75.14 | 0.09 | 75.12 | 0.09 | 74.89 | 0.08 | 75.04 | 0.07 | 75.04 | 0.06 | [40 empty] | 74.56 | 0.06 | [34 empty] | 94.61 | 0.09 | 88.15 | 0.08 | 88.04 | 0.2 | 75.35 | 0.05 | 87.79 | 0.13 | 80.66 | 0.15 | 78.44 | 0.13 | 75.58 | 0.06 | 75.45 | 0.05 | 79.53 | 0.19 | 86.15 | 0.16 | 75.96 | 0.06 | 76.2 | 0.1 | 79.49 | 0.17 | 87.12 | 0.2 | 75.25 | 0.07 | 87.22 | 0.21 | 95.02 | 0.05 | [12 empty] | C-EB35-55-CE | 74.869 | 0.038 | 61.979 | 0.024 | 59.885 | 0.01 | 56.064 | 0.014 | 95.004 | 0.006 | 75.004 | 0.025 | 1042.2 | 1.8 | 1003.8 | 1.7 | 0.475 | 0.002 | -0.171 | 0.002 | 0.009 | 0.003 | 0.6603 | 0.0023 | 29.048 | 0.001 | 3488 | 11 | 459.2 | 5.7 | 0.15207 | 157.7743 | 13.029 | 0.181 | 1.2069 | 4749.3915 | 56.0152 | 159.5327 | 678.8608 | 4070.5307 | 0.0095304 | 29.1056 | 58.6781 | 14.1 | 13.1663 | 0.013923 | 38.1609 | 0.0087977 | 27.5954 | 0.0086587 | 23.7896 | 77.77 | 64.084 | 23.4953 | 26645.7049 | 21761.9643 | 3028.8 | 0.38795 | 25269.6351 | 20385.8946 | 7.2447 | 0.24986 | -5.6103 | -19.0919 | 52.3189 | 26645.7049 | 18075.4893 | 1397.7029 | 7172.5127 | 26645.7049 | 100%
5 | C-EB5-95-CE | 30N0122 | C-EB5-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 5 | CUST 2 | 6/17/2015 | 7:04:27 | 10 Ton | 0:10:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230 | 1.7 | 16 | 0 | 18061 | 33 | 17805 | 56 | 448 | 118 | 18509 | 111 |  | 943 | [37 empty] | 5.2389 | 5% evaporator coil block, economizer closed damper, factory charge (5.5 lbs) 95F OD,--75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed,--adjust code tester | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: installed economizer. Coil is blocked 4.5" | 74.982 | 0.011 | 62.006 | 0.053 | 94.996 | 0.005 | 75.003 | 0.021 | 74.49 | 0.09 | 59.56 | 0.09 | 64.25 | 0.02 | 0.002 | 0.003 | 0.7562 | 0.002 | 18061 | 33 | 448 | 118 | 5.239 | 0.034 | [6 empty] | 230 | 1.7 | 230 | 1.7 | 230 | 1.7 | 13.8 | 0 | 13.8 | 0 | 13.8 | 0 | 3058.3 | 6.9 | 3058.3 | 6.9 | 3058.3 | 6.9 | 229.9 | 1.7 | 229.9 | 1.7 | 229.9 | 1.7 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 228.4 | 1.7 | 228.4 | 1.7 | 228.4 | 1.7 | 13 | 0 | 13 | 0 | 13 | 0 | 2838.3 | 5.7 | [9 empty] | 228.8 | 1.7 | 0.7 | 0 | 169.7 | 1.4 | 0.1 | 0.2 | 3483.2 | [10 empty] | 230.3 | 1.7 | 0 | 0 | 255.86 | 0.17 | 102.48 | 0.03 | 118.73 | 0.05 | 16.24 | 0.03 | 272.28 | 0.14 | 175.98 | 0.08 | 123.35 | 0.04 | 52.64 | 0.06 | 255.18 | 0.19 | 102.2 | 0.1 | 118.53 | 0.05 | 16.33 | 0.09 | 76.89 | 0.05 | 54.4 | 0.84 | 45.3 | 0.03 |  |  | 78.02 | 0.04 | 53.57 | 0.39 | 46.01 | 0.03 | 7.56 | 0.37 | [44 empty] | 9.11 | 0.82 | [74 empty] | 58.98 | 0.03 | 59.28 | 0.03 | 59.31 | 0.03 | 59.33 | 0.04 | 59.17 | 0.03 | 59.23 | 0.03 | [86 empty] | 143.82 | 0.08 | 82.12 | 0.08 | 177.71 | 0.11 | 95.37 | 0.08 | 94.65 | 0.09 | 76.25 | 0.08 | 75.93 | 0.07 | 75.57 | 0.07 | 75.53 | 0.06 | 75.31 | 0.07 | 75.36 | 0.06 | 75.28 | 0.06 | [40 empty] | 74.84 | 0.04 | [34 empty] | 94.86 | 0.09 | 88.88 | 0.23 | 82.25 | 0.45 | 76.8 | 0.05 | 88.07 | 0.1 | 80.76 | 0.15 | 77.89 | 0.15 | 75.58 | 0.04 | 75.35 | 0.04 | 77.1 | 0.1 | 86.35 | 0.14 | 75.86 | 0.05 | 75.87 | 0.07 | 82.78 | 0.24 | 90.02 | 0.16 | 75.4 | 0.05 | 84.34 | 0.43 | 95 | 0.06 | [12 empty] | C-EB5-55-CE | 74.982 | 0.011 | 62.006 | 0.053 | 59.837 | 0.012 | 56.361 | 0.026 | 94.996 | 0.005 | 75.003 | 0.021 | 1112.4 | 1.5 | 1078.3 | 1.5 | 0.546 | 0.002 | -0.194 | 0.001 | 0.002 | 0.003 | 0.7562 | 0.002 | 29.157 | 0.002 | 3533 | 10 | 475.1 | 5.5 | 0.16408 | 178.2735 | 13.029 | 0.192 | 1.1384 | 5069.206 | 69.1667 | 186.4183 | 793.2782 | 4275.9278 | 0.0095925 | 29.2637 | 58.6986 | 14.0998 | 13.1666 | 0.013924 | 38.1601 | 0.0087888 | 27.6132 | 0.0088451 | 23.9805 | 78.1386 | 64.3004 | 23.7028 | 28189.4932 | 23650.9988 | 3057.9 | 0.37023 | 26804.043 | 22265.5486 | 7.5868 | 0.22227 | -5.5609 | -19.4401 | 53.1428 | 28189.4932 | 18415.1871 | 1407.7082 | 8366.5979 | 28189.4932 | 100%
5 | C-EB50-95-CE | 30N0123 | C-EB50-95-CE | closed | on | N/A | 3 turns | unsealed | unsealed |  | 4.75 | horizontal | 0 | 50 | CUST 2 | 6/17/2015 | 16:25:41 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 229.9 | 1.4 | 15.8 | 0 | 16316 | 43 | 15978 | 63 | 1926 | 93 | 18244 | 86 | [39 empty] | 5.2471 | 50% evaporator coil block, economizer closed damper, factory charge (5.5 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 53.5%:--Outlet @ 52% Horiz airflow. 4.75" ID pulley 3 turns open from fully closed, adjust | . | 75.005 | 0.033 | 62.001 | 0.033 | 95.003 | 0.007 | 74.995 | 0.023 | 74.49 | 0.07 | 59.4 | 0.05 | 65.41 | 0.03 | 0.003 | 0.002 | 0.8295 | 0.0024 | 16316 | 43 | 1926 | 93 | 5.247 | 0.028 | [6 empty] | 229.9 | 1.4 | 229.9 | 1.4 | 229.9 | 1.4 | 13.7 | 0 | 13.7 | 0 | 13.7 | 0 | 3026 | 6.4 | 3026 | 6.4 | 3026 | 6.4 | 229.8 | 1.4 | 229.8 | 1.4 | 229.8 | 1.4 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 228.2 | 1.5 | 228.2 | 1.5 | 228.2 | 1.5 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2807.3 | 5.9 | [9 empty] | 228.7 | 1.5 | 0.7 | 0 | 168.9 | 1.3 | 13 | 0.2 | 3440.4 | [10 empty] | 230.1 | 1.4 | 0 | 0 | 252.12 | 0.13 | 102.39 | 0.03 | 117.62 | 0.04 | 15.22 | 0.03 | 268.29 | 0.13 | 164.36 | 0.06 | 122.21 | 0.04 | 42.15 | 0.04 | 251.5 | 0.17 | 101.69 | 0.03 | 117.44 | 0.05 | 15.75 | 0.06 | 72.25 | 0.04 | 45.33 | 0.04 | 42.18 | 0.03 |  |  | 73.41 | 0.04 | 47.08 | 0.04 | 42.96 | 0.02 | 4.12 | 0.03 | [44 empty] | 3.15 | 0.03 | [74 empty] | 58.55 | 0.03 | 59.01 | 0.04 | 58.98 | 0.03 | 58.86 | 0.04 | 58.87 | 0.03 | 58.87 | 0.03 |  |  |  |  | 47.61 | 0.05 | 44.82 | 0.04 | [10 empty] | 101.69 | 0.03 | [66 empty] | 135.67 | 0.04 | 59.87 | 0.1 | 164.95 | 0.05 | 95.13 | 0.06 | 94.51 | 0.06 | 76.74 | 0.1 | 76.23 | 0.09 | 75.64 | 0.08 | 75.59 | 0.07 | 75.28 | 0.07 | 75.36 | 0.06 | 75.23 | 0.05 | [40 empty] | 74.81 | 0.04 | [34 empty] | 94.76 | 0.06 | 87.82 | 0.08 | 90.91 | 0.06 | 75.14 | 0.05 | 86.97 | 0.15 | 78.47 | 0.13 | 82.55 | 0.15 | 75.95 | 0.05 | 75.89 | 0.06 | 77.26 | 0.08 | 85.35 | 0.26 | 77.95 | 0.1 | 78.45 | 0.11 | 79.34 | 0.18 | 86.98 | 0.12 | 76.91 | 0.11 | 89.08 | 0.11 | 94.96 | 0.06 | [12 empty] | C-EB50-55-CE | 75.005 | 0.033 | 62.001 | 0.033 | 59.595 | 0.011 | 55.712 | 0.017 | 95.003 | 0.007 | 74.995 | 0.023 | 993.2 | 1.4 | 954.3 | 1.4 | 0.431 | 0.002 | -0.157 | 0.001 | 0.003 | 0.002 | 0.8295 | 0.0024 | 28.949 | 0.001 | 3477 | 10 | 451.2 | 5.4 | 0.15085 | 149.827 | 13.029 | 0.164 | 1.2647 | 4528.9922 | 48.32 | 152.5005 | 648.9406 | 3880.0516 | 0.009516 | 29.1199 | 58.3303 | 14.0999 | 13.1579 | 0.013916 | 38.1522 | 0.0087801 | 27.6093 | 0.0085213 | 23.5694 | 77.8934 | 64.1055 | 23.2611 | 26534.7355 | 21264.1672 | 3025.8 | 0.38919 | 25159.7062 | 19889.1379 | 7.236 | 0.25216 | -5.8589 | -19.563 | 51.734 | 26534.7355 | 18296.691 | 1396.2966 | 6841.748 | 26534.7355 | 100%
5 | C-55-NE | 30N0069 | C-55-NE | None | off | N/A | 3 turns | sealed | unsealed |  |  | horizontal | 0 | 0 | CUST 2 | 6/16/2015 | 22:54:25 | 10 Ton | 0:10:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230 | 1.8 | 2.1 | 0 | 557 | 15 | 314 | 42 | 439 | 35 | 996 | 26 |  | 944 | [37 empty] | 2.2084 | . | R22 5.5 LBS. sealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: no economizer. No compressor; | 74.987 | 0.028 | 62.016 | 0.016 | 54.994 | 0.007 | 51.008 | 0.007 | 74.38 | 0.06 | 74.11 | 0.06 | 75.1 | 0.02 | 0.014 | 0.002 | 0.6839 | 0.0018 | 557 | 15 | 439 | 35 | 2.211 | 0.064 | [6 empty] | 230 | 1.8 | 230 | 1.8 | 230 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0.2 | -0.1 | 0.2 | -0.1 | 0.2 | 229.7 | 1.8 | 229.7 | 1.8 | 229.7 | 1.8 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | 451 | [10 empty] | 230.1 | 1.8 | 0 | 0 | 100.48 | 0.05 | 55.72 | 0.02 | 59.21 | 0.03 | 3.5 | 0.02 | 100.12 | 0.04 | 59.37 | 0.05 | 59.01 | 0.02 | 0.36 | 0.05 | 101.13 | 0.03 | 62.17 | 0.06 | 59.56 | 0.02 | -2.61 | 0.07 | 101 | 0.03 | 58.31 | 0.03 | 59.49 | 0.02 |  |  | 100.55 | 0.02 | 58.75 | 0.09 | 59.25 | 0.01 | -0.5 | 0.08 | [44 empty] | -1.18 | 0.02 | [74 empty] | 74.44 | 0.03 | 74.48 | 0.03 | 74.55 | 0.02 | 74.63 | 0.03 | 74.46 | 0.02 | 74.49 | 0.03 | [6 empty] | 58.69 | 0.04 | [78 empty] | 70.54 | 0.18 | 72.76 | 0.21 | 59.31 | 0.05 | 54.17 | 0.06 | 55.91 | 0.11 | 74.56 | 0.06 | 74.56 | 0.05 | 74.71 | 0.04 | 74.77 | 0.04 | 74.86 | 0.03 | 74.91 | 0.03 | 74.87 | 0.03 | [40 empty] | 74.57 | 0.02 | [34 empty] | 54.51 | 0.09 | 73.96 | 0.06 | 73.07 | 0.04 | 74.71 | 0.04 | 74.63 | 0.12 | 74.99 | 0.03 | 74.52 | 0.15 | 73.91 | 0.19 | 74.64 | 0.03 | 75.13 | 0.08 | 74.62 | 0.14 | 73.13 | 0.08 | 74.61 | 0.09 | 74.54 | 0.08 | 74.24 | 0.11 | 73.05 | 0.15 | 73.25 | 0.07 | [14 empty] | No Economizer | 74.987 | 0.028 | 62.016 | 0.016 | 74.504 | 0.015 | 61.739 | 0.011 | 54.994 | 0.007 | 51.008 | 0.007 | 1065.9 | 1.4 | 1016.4 | 1.4 | 0.599 | 0.001 | -0.29 | 0.002 | 0.014 | 0.002 | 0.6839 | 0.0018 | 29.272 | 0 | 451 | 6 | 450.2 | 5.7 |  | 0 |  |  | 1.1395 | 4724.2704 | 71.5248 | 0 | 0 | 4724.2704 | 0.0087942 | 27.6204 | 73.3645 | 13.0294 | 13.5373 | 0.006987 | 20.7824 | 0.0087942 | 27.6204 | 0.0087262 | 27.4281 | 74.987 | 62.016 | 27.1502 | 2221.3462 | 1839.6773 | 0.8 | 0.0012292 | 928.9277 | 547.2588 | 2.0597 | 0.93428 | -0.4702 | -1.6225 | 50.2998 | 2221.3462 | 908.4485 | 1312.8977 | 0 | 2221.3462 | 100%
5 | C-55-NES | 30N0070 | C-55-NES | None | off | N/A | 3 turns | sealed | unsealed |  | 4.75 | horizontal | 0 | 0 | CUST 2 | 6/16/2015 | 22:17:42 | 10 Ton | 0:10:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/1 | TU3 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 5.5 |  | 5.5 |  | 230.1 | 1.3 | 2 | 0 | 45 | 12 | -153 | 46 | -54 | 23 | -8 | 24 |  | 944 | 445.6 | [36 empty] | -0.017937 | . | R22 5.5 LBS. sealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: no economizer. No compressor; | 75.02 | 0.015 | 61.977 | 0.021 | 54.961 | 0.031 | 51.01 | 0.021 | 74.47 | 0.06 | 74.61 | 0.08 | 75.26 | 0.02 | 0.005 | 0.002 | 0.6506 | 0.0017 | 45 | 12 | -54 | 23 | 0.036 | 0.026 | [6 empty] | 230.1 | 1.3 | 230.1 | 1.3 | 230.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0.2 | -0.1 | 0.2 | -0.1 | 0.2 | 229.8 | 1.3 | 229.8 | 1.3 | 229.8 | 1.3 | 2 | 0 | 2 | 0 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.3 | 446 | [10 empty] | 230.1 | 1.3 | 0 | 0 | 100.87 | 0.07 | 56.82 | 0.08 | 59.41 | 0.04 | 2.59 | 0.06 | 100.42 | 0.09 | 60.6 | 0.07 | 59.18 | 0.05 | 1.42 | 0.04 | 101.44 | 0.04 | 62.15 | 0.08 | 59.73 | 0.02 | -2.42 | 0.09 | 101.42 | 0.06 | 58.56 | 0.04 | 59.71 | 0.03 |  |  | 100.69 | 0.06 | 60.91 | 0.07 | 59.33 | 0.03 | 1.58 | 0.05 | [44 empty] | -1.15 | 0.03 | [74 empty] | 75.09 | 0.02 | 75.1 | 0.03 | 75.18 | 0.03 | 75.29 | 0.02 | 75.1 | 0.02 | 75.11 | 0.03 | [6 empty] | 59.22 | 0.07 | [78 empty] | 76.11 | 0.23 | 79.02 | 0.27 | 61.1 | 0.07 | 53.84 | 0.15 | 55.78 | 0.13 | 74.59 | 0.05 | 74.6 | 0.03 | 74.7 | 0.07 | 74.77 | 0.06 | 74.87 | 0.06 | 74.94 | 0.05 | 74.97 | 0.04 | [40 empty] | 74.65 | 0.02 | [34 empty] | 54.23 | 0.16 | 74.6 | 0.03 | 74.27 | 0.03 | 74.75 | 0.02 | 75.16 | 0.06 | 75.24 | 0.04 | 74.8 | 0.04 | 74.83 | 0.06 | 74.76 | 0.05 | 75.22 | 0.05 | 75 | 0.04 | 74.38 | 0.05 | 75 | 0.03 | 74.67 | 0.05 | 74.64 | 0.02 | 74.24 | 0.04 | 74.42 | 0.02 | [14 empty] | No Economizer | 75.02 | 0.015 | 61.977 | 0.021 | 74.977 | 0.015 | 62.007 | 0.021 | 54.961 | 0.031 | 51.01 | 0.021 | 1039.6 | 1.3 | 990.9 | 1.3 | 0.599 | 0.002 | -0.298 | 0.002 | 0.005 | 0.002 | 0.6506 | 0.0017 | 29.274 | 0.001 | 446 | 5 | 445.6 | 5.3 |  | 0 |  |  | 1.1608 | 4603.451 | 69.7303 | 0 | 0 | 4603.451 | 0.0087607 | 27.5918 | 73.8162 | 13.0286 | 13.5498 | 0.0069958 | 20.7839 | 0.0087607 | 27.5918 | 0.0087907 | 27.614 | 75.02 | 61.977 | 27.3309 | 1200.7907 | 1329.9749 | 0.4 | 0.0011369 | -82.0525 | 47.1317 | -0.18397 | 0.93977 | -0.26085 | -1.2038 | 55.0339 | 1200.7907 | -102.5331 | 1303.3237 | 0 | 1200.7907 | 100%
5 | C-MF-75629575-NE3J | 30N0010 | C-MF-75629575-NE3J | None | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 3/11/2014 | 9:58:39 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 LBS | 208/230/1 | TU1 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 14.9 | 0 | 23656 | 44 | 22676 | 87 | 6572 | 87 | 30234 | 92 |  | 940 |  | 6.9 |  | 109.99 | 0.03 | 11.32 | [31 empty] | 9.1953 | Factory charge, 3 turns, no econo unsealed cab, return and supply Meriam's set--to same as run C-MF-NE3J-SPWCT-SS, adjust code tester speed to match total--static of run C-MF-NE3J-SPWCT-SS | R22 5.5 LBS. unsealed cab:Inlet Meriam set @ 53.5%: Outlet Meriam set @ 52% manually: Horiz airflow. ID Pulley is 3 turns open from fully closed: no economizer: with flow meter: new filter drier: with isolation ball valves: with code | 74.993 | 0.03 | 62 | 0.027 | 95 | 0.009 | 74.997 | 0.014 | 74.4 | 0.08 | 55.75 | 0.03 | 62.8 | 0.02 | 0.028 | 0.003 | 0.7517 | 0.0023 | 23656 | 44 | 6572 | 87 | 9.195 | 0.038 |  |  | 10.3689 |  |  |  | 229.7 | 0.9 | 229.7 | 0.9 | 229.7 | 0.9 | 13.3 | 0 | 13.3 | 0 | 13.3 | 0 | 2934 | 6.1 | 2934 | 6.1 | 2934 | 6.1 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.6 | 0 | 12.6 | 0 | 12.6 | 0 | 2741.5 | 5.7 | [9 empty] | 228.3 | 0.9 | 0.7 | 0 | 169.5 | 0.8 | 23 |  | 3287.1 | 475 | 475 | 475 | 0.7 | 0.7 | 0.8 | 380 | 0.62 | 15.2 | [13 empty] | 260.21 | 0.18 | 176.07 | 0.06 | 119.95 | 0.05 | 56.11 | 0.08 | 240.63 | 0.22 | 103.9 | 0.05 | 114.24 | 0.07 | 10.34 | 0.08 | 73.96 | 0.06 | 51.39 | 0.17 | 43.35 | 0.04 |  |  | 74.38 | 0.03 | 60.08 | 0.2 | 43.63 | 0.02 | 16.45 | 0.19 | 509.5 | 0.52 | 40.71 | 0.02 | 34093 | 47 | 35298 | 43 | [22 empty] | 244.19 | 0.22 | 104.72 | 0.05 | 115.3 | 0.07 | 10.58 | 0.07 | 242.77 | 0.22 | 114.88 | 0.07 | 11.29 | 0.08 | 8.04 | 0.16 | [74 empty] | 54.86 | 0.06 | 56.22 | 0.07 | 55.59 | 0.12 | 56.28 | 0.05 | 55.45 | 0.09 | 55.65 | 0.06 | [32 empty] | 104.5 | 0.05 | [26 empty] | 103.59 | 0.07 | [30 empty] | 94.73 | 0.05 | 94.96 | 0.07 | 74.45 | 0.08 | 74.45 | 0.07 | 74.4 | 0.08 | 74.46 | 0.08 | 74.47 | 0.08 | 74.53 | 0.07 | 74.51 | 0.08 | 75.9 | 0.11 | 76.31 | 0.1 | 77.06 | 0.08 | 75.51 | 0.06 | 75.1 | 0.08 | 76.22 | 0.11 | 77.19 | 0.1 | 76.38 | 0.1 | 74.89 | 0.1 | 75.08 | 0.08 | 75.2 | 0.1 | 75.16 | 0.1 | 74.79 | 0.1 | 74.73 | 0.09 | 74.83 | 0.07 | 74.73 | 0.08 | 74.68 | 0.07 | 74.66 | 0.07 | 74.68 | 0.07 | 74.75 | 0.07 | [84 empty] | No Economizer | 74.993 | 0.03 | 62 | 0.027 | 55.535 | 0.019 | 52.607 | 0.019 | 95 | 0.009 | 74.997 | 0.014 | 1109.2 | 1.7 | 1076.1 | 1.7 | 0.608 | 0.004 | -0.259 | 0.002 | 0.028 | 0.003 | 0.7517 | 0.0023 | 29.046 | 0.001 | 3288 | 9 | 353.1 | 5.6 |  | 0 |  |  | 0.77 | 5100.2327 | 76.8637 | 0 | 0 | 5100.2327 | 0.0087823 | 27.6087 | 54.765 | 14.0999 | 13.0488 | 0.013918 | 38.1542 | 0.0087823 | 27.6087 | 0.0077231 | 21.7131 | 74.993 | 62 | 21.5256 | 31025.3464 | 24760.1972 | 2934.9 | 0.32286 | 30082.5519 | 23817.4027 | 9.1492 | 0.216 | -6.0831 | -20.228 | 49.192 | 31025.3464 | 30069.3617 | 955.9847 | 0 | 31025.3464 | 100%
5 | C-22A-ONE | 30N0012 | C-22A-ONE | None | on | N/A | 5.5 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 2/24/2014 | 17:57:57 | 10 Ton | 0:30:00 | 80/67 - 95/70 | ENG 1 | TECH 2 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 | TU1 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 5.5 |  | 5.5 |  | 230.3 | 1 | 14.8 | 0 | 26268 | 52 | 25410 | 130 | 9371 | 85 | 35648 | 110 | 10.8882 | 757 |  | 13.6 | [36 empty] | . | R22 5.5 lbs manuf. Unsealed cab: Meriam set @ 100%: Horiz airflow. ID Pulley is 5.5 turns open from fully closed for 1200 scfm @ 0.15 esp. | 80 | 0.02 | 67.15 | 0.023 | 94.851 | 0.018 | 69.943 | 0.032 | 79.68 | 0.1 | 62.28 | 0.04 | 67.94 | 0.02 | 0.079 | 0.002 | 1.0813 | 0.004 | 26268 | 52 | 9371 | 85 | 10.889 | 0.039 | [6 empty] | 229.7 | 1 | 229.7 | 1 | 229.7 | 1 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2977.4 | 4.8 | 2977.4 | 4.8 | 2977.4 | 4.8 | 230 | 1 | 230 | 1 | 230 | 1 | 1.4 | 0 | 1.4 | 0 | 1.4 | 0 |  | 227.8 | 1 | 227.8 | 1 | 227.8 | 1 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2782.5 | 4.2 | [9 empty] | 228.2 | 1 | 0.8 | 0 | 173.7 | 0.9 | 23 |  | 3274.7 | [22 empty] | 265.34 | 0.24 | 185.54 | 0.05 | 121.45 | 0.07 | 64.09 | 0.08 |  |  | 103.38 | 0.04 | [6 empty] | 71.15 | 0.06 |  |  |  |  | 80 | 0.05 | 72.41 | 0.06 | 47.34 | 0.03 | 25.08 | 0.07 | [120 empty] | 61.57 | 0.05 | 62.7 | 0.05 | 62.27 | 0.06 | 62.74 | 0.05 | 61.94 | 0.06 | 62.43 | 0.04 | [32 empty] | 103.23 | 0.07 | [22 empty] | 103.65 | 0.05 | [34 empty] | 94.64 | 0.09 | 94.69 | 0.1 | 79.52 | 0.1 | 79.57 | 0.09 | 79.55 | 0.08 | 79.48 | 0.1 | 79.48 | 0.1 | 79.51 | 0.1 | 79.48 | 0.09 | 80.46 | 0.08 | 80.38 | 0.08 | 80.13 | 0.08 | 79.9 | 0.07 | 80.61 | 0.06 | 79.81 | 0.08 | 79.58 | 0.09 | 79.74 | 0.08 | 80.25 | 0.07 | 79.98 | 0.08 | 79.34 | 0.1 | 79.4 | 0.1 | 79.62 | 0.09 | 79.81 | 0.08 | 79.97 | 0.08 | 79.85 | 0.09 | 80.09 | 0.07 | 79.86 | 0.08 | 79.99 | 0.08 | 79.94 | 0.07 | [84 empty] | No Economizer | 80 | 0.02 | 67.15 | 0.023 | 62.014 | 0.022 | 58.843 | 0.02 | 94.851 | 0.018 | 69.943 | 0.032 | 1331.6 | 2.5 | 1290.1 | 2.4 | 0.15 | 0.001 | -0.102 | 0.001 | 0.079 | 0.002 | 1.0813 | 0.004 | 29.383 | 0.001 | 3274 | 7 | 295.5 | 3.5 |  | 0 |  |  | 0.6421 | 6039.2339 | 22.7342 | 0 | 0 | 6039.2339 | 0.011187 | 31.4667 | 61.3719 | 14.0618 | 13.2295 | 0.0097792 | 33.5518 | 0.011187 | 31.4667 | 0.009834 | 25.588 | 80 | 67.15 | 25.4311 | 36450.381 | 26999.8754 | 2978.5 | 0.27889 | 35519.4313 | 26068.9257 | 10.8489 | 0.24191 | -6.0356 | -18.6281 | 55.4275 | 36450.381 | 35502.7724 | 947.6085 | 0 | 36450.381 | 100%
5 | C-ONE-5TA-OB | 30N0013 | C-ONE-5TA-OB | None | on | N/A | 5.5 turns | unsealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/24/2014 | 21:58:13 | 10 Ton | 0:30:00 | 80/67 - 95/70 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.16 lbs | 208/230/1 | TU1 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 5.16 |  | 5.5 |  | 230.3 | 1 | 14.8 | 0 | 25697 | 56 | 24856 | 130 | 9095 | 77 | 34801 | 95 | 10.7146 | 756 |  | 13.6 | [36 empty] | Out-of-box refrigerant charge, unsealed cab, no econo, low fan speed, 760 rpm, repaired air leak | R22 5.16 lbs manuf. Unsealed cab: Meriam set @ 100%: Horiz airflow. ID Pulley is 5.5 turns open from fully closed for 1200 scfm @ 0.15 esp. | 80 | 0.016 | 67.152 | 0.024 | 94.847 | 0.018 | 69.988 | 0.037 | 79.62 | 0.1 | 62.62 | 0.05 | 68.23 | 0.02 | 0.074 | 0.002 | 1.084 | 0.0045 | 25697 | 56 | 9095 | 77 | 10.715 | 0.036 | [6 empty] | 229.7 | 1 | 229.7 | 1 | 229.7 | 1 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2954 | 5.4 | 2954 | 5.4 | 2954 | 5.4 | 230 | 1 | 230 | 1 | 230 | 1 | 1.4 | 0 | 1.4 | 0 | 1.4 | 0 |  | 227.8 | 1 | 227.8 | 1 | 227.8 | 1 | 12.6 | 0 | 12.6 | 0 | 12.6 | 0 | 2758.3 | 5 | [9 empty] | 228.2 | 1 | 0.8 | 0 | 173.8 | 0.9 | 23 |  | 3248 | [22 empty] | 261.47 | 0.21 | 187.46 | 0.08 | 120.36 | 0.06 | 67.1 | 0.08 |  |  | 103.85 | 0.05 | [6 empty] | 72.46 | 0.07 |  |  |  |  | 78.7 | 0.01 | 73.86 | 0.06 | 46.52 | 0.01 | 27.34 | 0.06 | [120 empty] | 61.94 | 0.06 | 63.13 | 0.1 | 62.68 | 0.09 | 63.13 | 0.08 | 62.39 | 0.07 | 62.87 | 0.06 | [32 empty] | 103.66 | 0.05 | [22 empty] | 104.08 | 0.05 | [34 empty] | 94.69 | 0.11 | 94.68 | 0.12 | 79.54 | 0.11 | 79.6 | 0.1 | 79.58 | 0.09 | 79.53 | 0.13 | 79.51 | 0.12 | 79.54 | 0.12 | 79.5 | 0.1 | 80.52 | 0.1 | 80.44 | 0.1 | 80.18 | 0.09 | 79.97 | 0.08 | 80.65 | 0.06 | 80 | 0.1 | 79.74 | 0.1 | 79.89 | 0.09 | 80.38 | 0.07 | 80.08 | 0.08 | 79.61 | 0.12 | 79.66 | 0.11 | 79.82 | 0.08 | 79.94 | 0.08 | 80.12 | 0.09 | 79.94 | 0.08 | 80.18 | 0.07 | 79.94 | 0.08 | 80.05 | 0.09 | 80.06 | 0.08 | [84 empty] | No Economizer | 80 | 0.016 | 67.152 | 0.024 | 62.42 | 0.02 | 59.066 | 0.024 | 94.847 | 0.018 | 69.988 | 0.037 | 1333.4 | 2.8 | 1291.5 | 2.7 | 0.155 | 0.001 | -0.103 | 0.001 | 0.074 | 0.002 | 1.084 | 0.0045 | 29.396 | 0.002 | 3248 | 7 | 292.9 | 3.8 |  | 0 |  |  | 0.63379 | 6042.5421 | 23.5175 | 0 | 0 | 6042.5421 | 0.011188 | 31.4683 | 61.7862 | 14.062 | 13.2401 | 0.0098152 | 33.5905 | 0.011188 | 31.4683 | 0.0098766 | 25.7336 | 80 | 67.152 | 25.5787 | 35587.9166 | 26413.8266 | 2955.1 | 0.2834 | 34668.5141 | 25494.4242 | 10.6738 | 0.257 | -5.8896 | -18.2138 | 55.4861 | 35587.9166 | 34651.9894 | 935.9272 | 0 | 35587.9166 | 100%
5 | C-22A | 30N0014 | C-22A | None | on | N/A | 5.5 turns | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/24/2014 | 23:49:29 | 10 Ton | 0:30:00 | 80/67 - 95/70 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 | TU1 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 5.5 |  | 5.5 |  | 230.3 | 0.9 | 14.9 | 0 | 26354 | 69 | 25489 | 154 | 9625 | 105 | 35987 | 123 | 10.975 | 756 |  | 13.3 | [36 empty] | A test factory chg, low speed fan 760 rpm, sealed cab, no econo | R22 5.5 lbs manuf. Sealed cab: Meriam set @ 100%: Horiz airflow. ID Pulley is 5.5 turns open from fully closed for 1200 scfm @ 0.15 esp. | 79.894 | 0.035 | 67.152 | 0.029 | 94.848 | 0.015 | 70.007 | 0.022 | 79.49 | 0.14 | 61.95 | 0.06 | 67.71 | 0.02 | 0.073 | 0.002 | 1.0677 | 0.0036 | 26354 | 69 | 9625 | 105 | 10.975 | 0.044 | [6 empty] | 229.7 | 0.9 | 229.7 | 0.9 | 229.7 | 0.9 | 13.5 | 0 | 13.5 | 0 | 13.5 | 0 | 2986.2 | 5.5 | 2986.2 | 5.5 | 2986.2 | 5.5 | 230 | 0.9 | 230 | 0.9 | 230 | 0.9 | 1.4 | 0 | 1.4 | 0 | 1.4 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.8 | 0 | 12.8 | 0 | 12.8 | 0 | 2789.8 | 5.1 | [9 empty] | 228.2 | 0.9 | 0.8 | 0 | 173.7 | 0.9 | 23 |  | 3278.3 | [22 empty] | 265.78 | 0.18 | 184.73 | 0.05 | 121.57 | 0.05 | 63.15 | 0.07 |  |  | 103.15 | 0.05 | [6 empty] | 70.31 | 0.07 |  |  |  |  | 80.18 | 0.07 | 71.63 | 0.08 | 47.46 | 0.04 | 24.18 | 0.09 | [120 empty] | 61.41 | 0.06 | 62.29 | 0.08 | 61.97 | 0.09 | 62.34 | 0.07 | 61.69 | 0.07 | 62.09 | 0.06 | [32 empty] | 103.03 | 0.06 | [22 empty] | 103.44 | 0.05 | [34 empty] | 94.61 | 0.09 | 94.61 | 0.09 | 79.4 | 0.13 | 79.46 | 0.12 | 79.46 | 0.1 | 79.37 | 0.13 | 79.37 | 0.13 | 79.41 | 0.13 | 79.39 | 0.12 | 80.01 | 0.11 | 79.96 | 0.11 | 79.79 | 0.11 | 79.61 | 0.09 | 80.16 | 0.07 | 79.84 | 0.12 | 79.68 | 0.13 | 79.76 | 0.11 | 80.1 | 0.1 | 79.98 | 0.11 | 79.62 | 0.14 | 79.64 | 0.13 | 79.76 | 0.11 | 79.87 | 0.11 | 80.02 | 0.1 | 79.86 | 0.11 | 79.98 | 0.09 | 79.85 | 0.1 | 79.94 | 0.1 | 79.94 | 0.09 | [84 empty] | No Economizer | 79.894 | 0.035 | 67.152 | 0.029 | 61.749 | 0.02 | 58.704 | 0.029 | 94.848 | 0.015 | 70.007 | 0.022 | 1322.4 | 2.2 | 1282.5 | 2.2 | 0.154 | 0.001 | -0.103 | 0.001 | 0.073 | 0.002 | 1.0677 | 0.0036 | 29.399 | 0.001 | 3279 | 7 | 291.8 | 3.7 |  | 0 |  |  | 0.63636 | 6000.6404 | 23.2029 | 0 | 0 | 6000.6404 | 0.011214 | 31.47 | 61.1126 | 14.0621 | 13.2226 | 0.0098297 | 33.6068 | 0.011214 | 31.47 | 0.0098105 | 25.4977 | 79.894 | 67.152 | 25.3422 | 36770.5121 | 27048.0417 | 2987.2 | 0.27727 | 35853.7904 | 26131.32 | 10.9344 | 0.23424 | -6.1278 | -18.7814 | 55.3676 | 36770.5121 | 35837.4259 | 933.0863 | 0 | 36770.5121 | 100%
5 | C-22B | 30N0015 | C-22B | None | on | N/A | 5.5 turns | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/25/2014 | 1:35:38 | 10 Ton | 0:30:00 | 80/67 - 82 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 | TU1 | AHRI 210/240 2008 | 80 | 67 | 82 |  | 5.5 |  | 5.5 |  | 230.3 | 0.8 | 13.2 | 0 | 26890 | 66 | 26023 | 145 | 10423 | 102 | 37323 | 119 | 12.9594 | 757 |  | 13.11 | [36 empty] | B test factory chg, low speed fan 760 rpm, sealed cab, no econo | R22 5.5 lbs manuf. Sealed cab: Meriam set @ 100%: Horiz airflow. ID Pulley is 5.5 turns open from fully closed for 1200 scfm @ 0.15 esp. | 79.901 | 0.026 | 67.149 | 0.03 | 81.787 | 0.012 | 64.1 | 0.031 | 79.43 | 0.11 | 61.64 | 0.05 | 67.52 | 0.02 | 0.074 | 0.003 | 1.0797 | 0.0052 | 26890 | 66 | 10423 | 102 | 12.959 | 0.048 | [6 empty] | 229.8 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 11.8 | 0 | 11.8 | 0 | 11.8 | 0 | 2586.5 | 4.7 | 2586.5 | 4.7 | 2586.5 | 4.7 | 230 | 0.8 | 230 | 0.8 | 230 | 0.8 | 1.4 | 0 | 1.4 | 0 | 1.4 | 0 |  | 228.1 | 0.8 | 228.1 | 0.8 | 228.1 | 0.8 | 11 | 0 | 11 | 0 | 11 | 0 | 2393.7 | 4.3 | [9 empty] | 228.5 | 0.8 | 0.8 | 0 | 175.5 | 0.8 | 23 |  | 2884.8 | [22 empty] | 224.97 | 0.14 | 171.79 | 0.07 | 109.49 | 0.05 | 62.3 | 0.07 |  |  | 88.66 | 0.06 | [6 empty] | 70.37 | 0.06 |  |  |  |  | 75.23 | 0.07 | 71.45 | 0.05 | 44.3 | 0.04 | 27.15 | 0.07 | [120 empty] | 61.12 | 0.06 | 62.1 | 0.18 | 61.75 | 0.17 | 62.11 | 0.13 | 61.51 | 0.11 | 61.9 | 0.06 | [32 empty] | 88.63 | 0.04 | [22 empty] | 88.89 | 0.05 | [34 empty] | 81.51 | 0.14 | 81.45 | 0.15 | 79.39 | 0.18 | 79.47 | 0.15 | 79.5 | 0.09 | 79.34 | 0.21 | 79.33 | 0.2 | 79.37 | 0.18 | 79.4 | 0.14 | 79.73 | 0.2 | 79.7 | 0.2 | 79.64 | 0.17 | 79.47 | 0.12 | 79.76 | 0.06 | 79.41 | 0.11 | 79.4 | 0.11 | 79.43 | 0.09 | 79.63 | 0.08 | 79.83 | 0.09 | 79.35 | 0.12 | 79.38 | 0.12 | 79.45 | 0.09 | 79.63 | 0.09 | 79.85 | 0.08 | 79.56 | 0.11 | 79.54 | 0.09 | 79.59 | 0.1 | 79.74 | 0.09 | 79.79 | 0.08 | [84 empty] | No Economizer | 79.901 | 0.026 | 67.149 | 0.03 | 61.511 | 0.02 | 58.417 | 0.029 | 81.787 | 0.012 | 64.1 | 0.031 | 1329.4 | 3.2 | 1290.4 | 3.1 | 0.155 | 0.001 | -0.104 | 0.001 | 0.074 | 0.003 | 1.0797 | 0.0052 | 29.409 | 0.001 | 2880 | 7 | 292.6 | 3.7 |  | 0 |  |  | 0.63386 | 6035.5917 | 23.4975 | 0 | 0 | 6035.5917 | 0.01121 | 31.4674 | 60.8771 | 13.7208 | 13.2156 | 0.0085918 | 29.0568 | 0.01121 | 31.4674 | 0.0096895 | 25.3079 | 79.901 | 67.149 | 25.153 | 38111.2757 | 27556.8652 | 2587.4 | 0.23171 | 37192.8288 | 26638.4183 | 12.9142 | 0.24007 | -6.3144 | -19.0239 | 54.8671 | 38111.2757 | 37176.639 | 934.6367 | 0 | 38111.2757 | 100%
5 | C-ONE-OB | 30N0031 | C-ONE-OB | None | on | N/A | 3 turns | unsealed | unsealed |  |  | horizontal | 0 | 0 | CUST 1 | 2/24/2014 | 20:29:00 | 10 Ton | 0:30:00 | 80/67 - 95/70 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.16 lbs | 208/230/1 | TU1 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 5.16 |  | 5.5 |  | 230.3 | 0.9 | 15.5 | 0 | 28583 | 55 | 27641 | 134 | 6361 | 69 | 34950 | 90 | 10.154 | 919 |  | 30.8 | [36 empty] | Out-of-box refrigerant charge unsealed cab | R22 5.16 lbs manuf. Unsealed cab: Meriam set @ 100%: Horiz airflow. ID Pulley is 3 turns open from fully closed for 1200 scfm @ 0.15 esp. | 80.004 | 0.019 | 67.15 | 0.013 | 94.852 | 0.011 | 70.143 | 0.025 | 79.64 | 0.07 | 66.03 | 0.03 | 69.65 | 0.01 | 0.359 | 0.003 | 2.128 | 0.0064 | 28583 | 55 | 6361 | 69 | 10.154 | 0.034 | [6 empty] | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13.4 | 0 | 13.4 | 0 | 13.4 | 0 | 2972.4 | 5.3 | 2972.4 | 5.3 | 2972.4 | 5.3 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 12.7 | 0 | 12.7 | 0 | 12.7 | 0 | 2777.4 | 4.8 | [9 empty] | 228.3 | 0.9 | 0.8 | 0 | 173.8 | 0.8 | 23 |  | 3442.6 | [22 empty] | 263.7 | 0.22 | 189.24 | 0.04 | 120.99 | 0.06 | 68.25 | 0.08 |  |  | 103.68 | 0.04 | [6 empty] | 75.24 | 0.05 |  |  |  |  | 80.53 | 0.01 | 76.53 | 0.04 | 47.67 | 0.01 | 28.85 | 0.04 | [120 empty] | 65.44 | 0.03 | 66.48 | 0.04 | 66.01 | 0.05 | 66.49 | 0.03 | 65.75 | 0.04 | 66.32 | 0.04 | [32 empty] | 103.52 | 0.05 | [22 empty] | 103.9 | 0.05 | [34 empty] | 94.58 | 0.09 | 94.63 | 0.1 | 79.51 | 0.06 | 79.59 | 0.06 | 79.58 | 0.06 | 79.47 | 0.05 | 79.47 | 0.05 | 79.54 | 0.06 | 79.53 | 0.05 | 80.44 | 0.05 | 80.38 | 0.05 | 80.13 | 0.04 | 79.94 | 0.04 | 80.62 | 0.05 | 80.06 | 0.08 | 79.77 | 0.08 | 79.93 | 0.07 | 80.43 | 0.06 | 80.07 | 0.07 | 79.57 | 0.1 | 79.62 | 0.08 | 79.79 | 0.07 | 79.93 | 0.07 | 80.1 | 0.07 | 79.94 | 0.06 | 80.26 | 0.05 | 79.96 | 0.06 | 80.07 | 0.07 | 80.04 | 0.06 | [84 empty] | No Economizer | 80.004 | 0.019 | 67.15 | 0.013 | 65.924 | 0.014 | 61.462 | 0.018 | 94.852 | 0.011 | 70.143 | 0.025 | 1874.4 | 2.8 | 1810.4 | 2.7 | 0.15 | 0.002 | -0.187 | 0.001 | 0.359 | 0.003 | 2.128 | 0.0064 | 29.403 | 0.001 | 3442 | 8 | 468.4 | 4.9 |  | 0 |  |  | 0.73577 | 8434.0492 | 31.903 | 0 | 0 | 8434.0492 | 0.011186 | 31.4666 | 65.1882 | 14.0631 | 13.3345 | 0.0099349 | 33.7238 | 0.011186 | 31.4666 | 0.010578 | 27.3549 | 80.004 | 67.15 | 27.1748 | 36196.7626 | 29989.667 | 2973.6 | 0.28038 | 34706.9982 | 28499.9026 | 10.0834 | 0.331 | -4.2917 | -14.8158 | 57.8578 | 36196.7626 | 34678.289 | 1518.4736 | 0 | 36196.7626 | 100%
5 | C-ONE | 30N0032 | C-ONE | None | on | N/A | 3 turns | unsealed | unsealed | 945 |  | horizontal | 0 | 0 | CUST 1 | 2/23/2014 | 13:28:22 | 10 Ton | 0:30:00 | 80/67 95/70 | ENG 1 | TECH 3 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | Out of Box 5.3 lbs (5.5 Factory Charge) | 208/230/1 | TU3 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 5.3 |  | 5.5 |  | 230.3 | 0.9 | 15.9 | 0 | 29964 | 85 | 28974 | 140 | 6776 | 92 | 36746 | 111 | 10.4689 | 945 |  | 30.6 | [36 empty] | Out-of-box refrigerant charge unsealed cab, no econo, default fan speed, measure rpm--factory 3 turns open from fully closed. | Out-of-box R22 refrigerant charge of 5.3 lbs. After test was completed 5.3 lbs of refrigerant was recovered from unit into reclaim tank and accurately weighed and ID blower fan speed was measured to be 3 turns. Unsealed cab: Meriam set @ 100%: Horiz airfl | 79.996 | 0.025 | 67.145 | 0.03 | 94.847 | 0.015 | 69.981 | 0.012 | 79.59 | 0.1 | 65.27 | 0.06 | 69.78 | 0.03 | 0.311 | 0.004 | 2.1132 | 0.0077 | 29964 | 85 | 6776 | 92 | 10.469 | 0.038 | [6 empty] | 229.8 | 0.9 | 229.8 | 0.9 | 229.8 | 0.9 | 13.7 | 0 | 13.7 | 0 | 13.7 | 0 | 3029.1 | 5.6 | 3029.1 | 5.6 | 3029.1 | 5.6 | 229.9 | 0.9 | 229.9 | 0.9 | 229.9 | 0.9 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 |  | 227.8 | 0.9 | 227.8 | 0.9 | 227.8 | 0.9 | 13 | 0 | 13 | 0 | 13 | 0 | 2832.7 | 5.2 | [9 empty] | 228.2 | 0.9 | 0.8 | 0 | 173.7 | 0.9 | 23 |  | 3509.4 | [22 empty] | 270.05 | 0.26 | 186.24 | 0.08 | 122.75 | 0.07 | 63.49 | 0.1 |  |  | 102.56 | 0.07 | [6 empty] | 73.25 | 0.06 |  |  |  |  | 82.68 | 0.06 | 74.37 | 0.07 | 48.98 | 0.04 | 25.39 | 0.06 | [120 empty] | 64.68 | 0.07 | 66.34 | 0.07 | 65.91 | 0.07 | 66.21 | 0.06 | 65.45 | 0.05 | 65.89 | 0.07 | [32 empty] | 102.83 | 0.07 | [22 empty] | 103.12 | 0.06 | [34 empty] | 95.15 | 0.11 | 93.87 | 0.23 | 79.75 | 0.1 | 79.73 | 0.09 | 79.57 | 0.09 | 79.84 | 0.11 | 79.78 | 0.11 | 79.75 | 0.11 | 79.62 | 0.1 | 81.32 | 0.07 | 81.11 | 0.08 | 80.96 | 0.07 | 80.61 | 0.07 | 80.95 | 0.07 | 80.1 | 0.1 | 80 | 0.1 | 79.97 | 0.09 | 80.02 | 0.08 | 79.97 | 0.07 | 79.62 | 0.1 | 79.66 | 0.11 | 79.71 | 0.09 | 79.78 | 0.07 | 79.96 | 0.06 | 79.72 | 0.08 | 79.69 | 0.07 | 79.72 | 0.07 | 79.83 | 0.07 | 79.86 | 0.06 | [84 empty] | No Economizer | 79.996 | 0.025 | 67.145 | 0.03 | 65.185 | 0.034 | 61.136 | 0.032 | 94.847 | 0.015 | 69.981 | 0.012 | 1871.1 | 3.5 | 1800.8 | 3.3 | 0.15 | 0.002 | -0.163 | 0.001 | 0.311 | 0.004 | 2.1132 | 0.0077 | 29.31 | 0.001 | 3510 | 8 | 480 | 5.1 |  | 0 |  |  | 0.75586 | 8431.2417 | 31.7338 | 0 | 0 | 8431.2417 | 0.011184 | 31.4627 | 64.4291 | 14.0619 | 13.3155 | 0.0098097 | 33.5845 | 0.011184 | 31.4627 | 0.010541 | 27.1332 | 79.996 | 67.145 | 26.9483 | 38062.1041 | 31499.5133 | 3030 | 0.2717 | 36532.1715 | 29969.5807 | 10.408 | 0.29761 | -4.5144 | -15.5669 | 57.8332 | 38062.1041 | 36502.7943 | 1559.3099 | 0 | 38062.1041 | 100%
5 | C-22C-D#2 | 30N0033 | C-22C-D#2 | None | on | N/A |  | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/25/2014 | 5:14:08 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 |  |  | 80 | 57 | 82 |  | 5.5 |  | 5.5 | [17 empty] | 11.715 |  |  |  | 2 | 6.45 | 82.121 | 30.017 | 59.317 | 0.32 | 452.8 | 1282 | 13.436 | 33139.09 | 0.2419 | 3120.382 | 0.00433 | 20.8011 | 142.253 | 1.86 | 134.167 | 251.5 | 10.855 | 5.26 | 12.96 | 3.4 | 30.7 | 0.186 | 287.46 | 0.09 | 253.2 | 282.41 | 12.3768 | 282.41 | 0.98 |  | C/D test factory chg, low speed fan 760 rpm, sealed cab, no econo | [514 empty] | No Economizer | 79.676 |  | 55.42 |  | 57.61 |  | 47.542 | [5 empty] | 1266.3 |  | 1235.5 |  | 0.212 |  |  |  | -0.029 |  | 0.9849 |  | 29.423 |  | 2665 |  | 288.9 |  |  | 0 |  |  | 0.63161 | 5810.0941 | 30.7711 | 0 | 0 | 5810.0941 | 0.0036502 | 23.1243 | 56.9784 | 11.5938 | 13.0769 | 0.00078408 | 0.83191 | 0.0036502 | 23.1243 | 0.004597 | 18.8214 | 79.676 | 55.42 | 18.6686 | 25888.0238 | 31650.0643 | 2376.1 | 0.31326 | 25007.03 | 30769.0705 | 9.3835 | 0.42472 | -4.4557 | -22.6976 | 40.2212 | 25888.0238 | 24999.7979 | 888.2259 | 0 | 25888.0238 | 100%
5 | C-22C-D#3 | 30N0034 | C-22C-D#3 | None | on | N/A |  | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/25/2014 | 5:44:31 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 |  |  | 80 | 57 | 82 |  | 5.5 |  | 5.5 | [17 empty] | 11.715 |  |  |  | 3 | 6.45 | 81.725 | 30.017 | 59.007 | 0.32 | 453 | 1282 | 13.436 | 33139.09 | 0.2419 | 3089.442 | 0.00433 | 20.5949 | 142.382 | 1.14 | 132.837 | 249.9 | 10.838 | 4.48 | 12.96 | 3.34 | 30.7 | 0.186 | 285.05 | 0.092 | 253.4 | 282.66 | 12.3638 | 282.66 | 0.99 |  | C/D test factory chg, low speed fan 760 rpm, sealed cab, no econo | [514 empty] | No Economizer | 79.697 |  | 55.356 |  | 57.889 |  | 47.603 | [5 empty] | 1267.1 |  | 1235.2 |  | 0.212 |  |  |  | -0.029 |  | 0.986 |  | 29.434 |  | 2644 |  | 289.1 |  |  | 0 |  |  | 0.63205 | 5810.752 | 30.7637 | 0 | 0 | 5810.752 | 0.0036089 | 23.084 | 57.257 | 11.5938 | 13.0837 | 0.00078408 | 0.83191 | 0.0036089 | 23.084 | 0.0045623 | 18.8512 | 79.697 | 55.356 | 18.6982 | 25484.8657 | 31294.4547 | 2354.9 | 0.31537 | 24603.1638 | 30412.7528 | 9.3053 | 0.43214 | -4.3858 | -22.44 | 40.1799 | 25484.8657 | 24595.9826 | 888.8831 | 0 | 25484.8657 | 100%
5 | C-22C-D#4 | 30N0035 | C-22C-D#4 | None | on | N/A |  | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/25/2014 | 6:14:31 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 |  |  | 80 | 57 | 82 |  | 5.5 |  | 5.5 | [17 empty] | 11.715 |  |  |  | 4 | 6.45 | 81.99 | 30.017 | 59.052 | 0.32 | 452.8 | 1282 | 13.436 | 33139.09 | 0.2419 | 3077.979 | 0.00433 | 20.5184 | 142.284 | 0.8 | 132.344 | 251.3 | 10.749 | 4.08 | 12.96 | 3.28 | 31 | 0.186 | 286.35 | 0.101 | 253.3 | 282.47 | 12.3055 | 282.47 | 0.99 |  | C/D test factory chg, low speed fan 760 rpm, sealed cab, no econo | [514 empty] | No Economizer | 79.666 |  | 55.318 |  | 58.071 |  | 47.628 | [5 empty] | 1267.1 |  | 1234.8 |  | 0.212 |  |  |  | -0.03 |  | 0.9852 |  | 29.431 |  | 2655 |  | 289.1 |  |  | 0 |  |  | 0.63228 | 5808.814 | 30.7537 | 0 | 0 | 5808.814 | 0.0035945 | 23.0607 | 57.4387 | 11.5938 | 13.088 | 0.00078408 | 0.83191 | 0.0035945 | 23.0607 | 0.0045323 | 18.8626 | 79.666 | 55.318 | 18.7096 | 25274.7535 | 30987.3989 | 2365.9 | 0.31948 | 24393.0177 | 30105.663 | 9.1876 | 0.43876 | -4.3511 | -22.2273 | 40.0618 | 25274.7535 | 24385.8851 | 888.8684 | 0 | 25274.7535 | 100%
5 | C-22C-D#5 | 30N0036 | C-22C-D#5 | None | on | N/A |  | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/25/2014 | 6:44:31 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 |  |  | 80 | 57 | 82 |  | 5.5 |  | 5.5 | [17 empty] | 11.715 |  |  |  | 5 | 6.45 | 81.794 | 30.017 | 58.97 | 0.32 | 452.1 | 1282 | 13.436 | 33139.09 | 0.2419 | 3076.873 | 0.00433 | 20.5112 | 142.492 | 1.17 | 132.297 | 249.3 | 10.818 | 4.48 | 12.96 | 3.31 | 30.6 | 0.186 | 284.42 | 0.094 | 253.6 | 282.88 | 12.3509 | 282.88 | 0.99 |  | C/D test factory chg, low speed fan 760 rpm, sealed cab, no econo | [514 empty] | No Economizer | 79.714 |  | 55.333 |  | 58.162 |  | 47.63 | [5 empty] | 1265.1 |  | 1232.8 |  | 0.211 |  |  |  | -0.031 |  | 0.983 |  | 29.436 |  | 2646 |  | 288.7 |  |  | 0 |  |  | 0.63288 | 5798.6965 | 30.5591 | 0 | 0 | 5798.6965 | 0.0035919 | 23.0694 | 57.5291 | 11.5938 | 13.0902 | 0.00078408 | 0.83191 | 0.0035919 | 23.0694 | 0.0045121 | 18.8627 | 79.714 | 55.333 | 18.7095 | 25281.8229 | 30874.4187 | 2357.3 | 0.31823 | 24400.788 | 29993.3837 | 9.2218 | 0.44229 | -4.3599 | -22.1849 | 39.9355 | 25281.8229 | 24393.694 | 888.129 | 0 | 25281.8229 | 100%
5 | C-22C-D#6 | 30N0037 | C-22C-D#6 | None | on | N/A |  | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/25/2014 | 7:14:31 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 |  |  | 80 | 57 | 82 |  | 5.5 |  | 5.5 | [17 empty] | 11.715 |  |  |  | 6 | 6.45 | 81.821 | 30.017 | 58.96 | 0.32 | 452.3 | 1282 | 13.436 | 33139.09 | 0.2419 | 3073.802 | 0.00433 | 20.4907 | 142.377 | 1.53 | 132.165 | 250.1 | 10.751 | 4.83 | 12.96 | 3.3 | 31 | 0.186 | 285.91 | 0.101 | 253.4 | 282.65 | 12.3055 | 282.65 | 0.99 |  | C/D test factory chg, low speed fan 760 rpm, sealed cab, no econo | [514 empty] | No Economizer | 79.683 |  | 55.281 |  | 58.193 |  | 47.591 | [5 empty] | 1265.1 |  | 1233.3 |  | 0.212 |  |  |  | -0.031 |  | 0.9842 |  | 29.448 |  | 2650 |  | 288.9 |  |  | 0 |  |  | 0.63302 | 5798.4419 | 30.7164 | 0 | 0 | 5798.4419 | 0.0035695 | 23.0374 | 57.56 | 11.5938 | 13.0908 | 0.00078408 | 0.83191 | 0.0035695 | 23.0374 | 0.0044855 | 18.8413 | 79.683 | 55.281 | 18.6882 | 25218.9481 | 30786.9664 | 2361.1 | 0.31954 | 24337.7673 | 29905.7856 | 9.1841 | 0.44504 | -4.3493 | -22.123 | 39.8191 | 25218.9481 | 24330.7154 | 888.2327 | 0 | 25218.9481 | 100%
5 | C-22C-D#7 | 30N0038 | C-22C-D#7 | None | on | N/A |  | sealed | unsealed | 760 |  | horizontal | 0 | 0 | CUST 1 | 2/25/2014 | 7:44:31 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU5 | RTU5 | 3 | R22 | PSC Air Handler | 5.5 lbs | 208/230/1 |  |  | 80 | 57 | 82 |  | 5.5 |  | 5.5 | [17 empty] | 11.715 |  |  |  | 7 | 6.45 | 81.854 | 30.017 | 58.959 | 0.32 | 452.7 | 1282 | 13.436 | 33139.09 | 0.2419 | 3066.382 | 0.00433 | 20.4412 | 142.42 | 1.51 | 131.846 | 250.7 | 10.707 | 4.86 | 12.96 | 3.35 | 30.8 | 0.185 | 286.39 | 0.106 | 253.5 | 282.74 | 12.2731 | 282.74 | 0.99 |  | C/D test factory chg, low speed fan 760 rpm, sealed cab, no econo | [514 empty] | No Economizer | 79.69 |  | 55.35 |  | 58.262 |  | 47.662 | [5 empty] | 1266.1 |  | 1234.5 |  | 0.212 |  |  |  | -0.031 |  | 0.9847 |  | 29.448 |  | 2656 |  | 289.1 |  |  | 0 |  |  | 0.63303 | 5802.1855 | 30.7462 | 0 | 0 | 5802.1855 | 0.0036071 | 23.0804 | 57.629 | 11.5938 | 13.0927 | 0.00078408 | 0.83191 | 0.0036071 | 23.0804 | 0.0045046 | 18.8788 | 79.69 | 55.35 | 18.7256 | 25266.9327 | 30720.5185 | 2366.9 | 0.31972 | 24385.1713 | 29838.7571 | 9.1812 | 0.44614 | -4.3547 | -22.061 | 39.8586 | 25266.9327 | 24378.0836 | 888.8491 | 0 | 25266.9327 | 100%
4 | L-55-1ER-DM | 30T0010 | L-55-1ER-DM | 1 Finger | off | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 10:24:55 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.1 | 1 | 1.6 | 0 | 6677 | 30 | 6411 | 57 | 2717 | 65 | 9396 | 73 | 19.9068 | 786 |  | 12.73 | [36 empty] | Econo 1F-open, no compressor, 55/51 ambient, 60% inlet 54% outlet Meriam,--adjust code tester speed to match total static of run L-55-1E-DM-SPWCT-SSR | R22 7 LBS: OFB: Econo 1 Finger Opened: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.979 | 0.027 | 62 | 0.026 | 55.006 | 0.014 | 50.998 | 0.018 | 74.7 | 0.05 | 69.85 | 0.03 | 72.44 | 0.07 | 0.018 | 0.004 | 1.1178 | 0.0062 | 6677 | 30 | 2717 | 65 | 19.897 | 0.281 | [6 empty] | 458.1 | 2.1 | 463 | 2.2 | 461.9 | 2.2 | 1.6 | 0 | 1.3 | 0 | 1.6 | 0 | 608.5 | 7.7 | 557.6 | 8.9 | -10 | 0 | 462 |  | 462 |  | 459 |  | 1.3 |  | 1.5 |  | 1.3 |  | 0.36 | [29 empty] | 21 |  |  | 378 | 380 | 380 | 0.9 | 0.8 | 1 | 500 | 0.62 | 12.2 | 17.9 | [164 empty] | 69.98 | 0.04 | 71.75 | 0.07 | 70.66 | 0.07 | 71.26 | 0.06 | 70.29 | 0.05 | 70.89 | 0.04 | [32 empty] | 73.08 | 0.02 |  |  | 54.68 | 0.07 | 54.52 | 0.06 | 54.53 | 0.09 | 54.33 | 0.07 | 54.43 | 0.1 | 54.43 | 0.1 | [8 empty] | 73.92 | 0.04 | [34 empty] | 55.5 | 0.05 | 55.2 | 0.06 | 74.56 | 0.05 | 74.69 | 0.05 | 74.39 | 0.05 | 74.21 | 0.06 | 74.46 | 0.06 | 74.07 | 0.07 | 74.43 | 0.05 | 58.8 | 0.05 | 64.22 | 0.08 | 64.39 | 0.08 | 72.76 | 0.08 | 58.87 | 0.11 | 63.13 | 0.15 | 61.45 | 0.05 | 62.83 | 0.16 | 57.77 | 0.04 | 58.75 | 0.12 | 61.53 | 0.08 | 61.39 | 0.17 | 58.6 | 0.07 | 58.3 | 0.1 | 58.85 | 0.13 | 63.53 | 0.21 | 58.15 | 0.15 | 58.3 | 0.09 | 58.11 | 0.13 | 63.08 | 0.25 | [84 empty] | Economizer test | 74.979 | 0.027 | 62 | 0.026 | 69.931 | 0.015 | 59.481 | 0.022 | 55.006 | 0.014 | 50.998 | 0.018 | 1220 | 3.4 | 1174 | 3.3 | 0.674 | 0.001 | -0.18 | 0.001 | 0.018 | 0.004 | 1.1178 | 0.0062 | 29.372 | 0.001 | 472 | 6 | 390 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.77412 | 5455.1537 | 92.9594 | 251.4545 | 1157.9199 | 4297.2338 | 0.0084021 | 26.1587 | 69.1569 | 13.0296 | 13.4185 | 0.0069789 | 20.7765 | 0.0087856 | 27.6089 | 0.0083585 | 25.9113 | 70.7505 | 59.8579 | 25.7227
4 | L-55-2ER-DM | 30T0011 | L-55-2ER-DM | 2 Finger | off | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 11:40:47 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.1 | 0.8 | 1.6 | 0 | 8033 | 330 | 7760 | 65 | 3266 | 143 | 11302 | 466 | 23.7437 | 785 |  | 12.8 | [36 empty] | Econo 2F-open, no compressor, 55/51, 60% inlet 54% outlet Meriam, ambient--ambient adjust code tester speed to match total static of run L-55-2E-DM-SPWCT-SSR | R22 7 LBS: OFB: Econo 2 Finger Opened: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.005 | 0.015 | 61.999 | 0.025 | 54.994 | 0.01 | 51.004 | 0.017 | 74.68 | 0.05 | 68.89 | 0.03 | 71.77 | 0.05 | 0.012 | 0.004 | 1.1456 | 0.0067 | 8033 | 330 | 3266 | 143 | 23.735 | 0.951 | [6 empty] | 458.1 | 2.2 | 462.7 | 2.2 | 461.9 | 2.2 | 1.6 | 0 | 1.3 | 0 | 1.6 | 0 | 608.7 | 7.8 | 559 | 8.9 | -10 | 0 | 463 |  | 457 |  | 458 |  | 1.3 |  | 1.4 |  | 1.2 |  | 0.36 | [29 empty] | 21 |  |  | 484 | 483 | 484 | 1 | 0.8 | 1 | 490 | 0.61 | 12.8 | 18 | [164 empty] | 68.92 | 0.04 | 70.43 | 0.06 | 69.08 | 0.06 | 70.08 | 0.05 | 68.89 | 0.05 | 69.88 | 0.04 | [32 empty] | 72.89 | 0.02 |  |  | 54.77 | 0.07 | 54.57 | 0.05 | 54.51 | 0.08 | 54.16 | 0.07 | 54.31 | 0.1 | 54.33 | 0.1 | [8 empty] | 73.72 | 0.03 | [34 empty] | 55.01 | 0.06 | 54.82 | 0.09 | 73.91 | 0.06 | 74.23 | 0.05 | 74.12 | 0.04 | 73.02 | 0.1 | 73.52 | 0.08 | 72.91 | 0.11 | 73.81 | 0.06 | 58.35 | 0.06 | 65.6 | 0.1 | 64.18 | 0.09 | 73.07 | 0.07 | 61.08 | 0.15 | 64.96 | 0.06 | 62.36 | 0.08 | 63.18 | 0.24 | 57.8 | 0.05 | 58.19 | 0.11 | 59.68 | 0.09 | 60.55 | 0.12 | 58.06 | 0.07 | 58.34 | 0.1 | 57.77 | 0.11 | 60.96 | 0.27 | 57.17 | 0.14 | 57.57 | 0.09 | 57.5 | 0.1 | 62.46 | 0.14 | [84 empty] | Economizer test | 75.005 | 0.015 | 61.999 | 0.025 | 69.002 | 0.01 | 58.985 | 0.02 | 54.994 | 0.01 | 51.004 | 0.017 | 1234.3 | 3.6 | 1189.5 | 3.5 | 0.672 | 0.001 | -0.157 | 0.001 | 0.012 | 0.004 | 1.1456 | 0.0067 | 29.375 | 0.001 | 476 | 6 | 390 |  | 0.26201 | 311.656 | 13.029 | 0.157 | 0.76133 | 5529.0895 | 93.9072 | 311.6605 | 1435.19 | 4093.8996 | 0.0083131 | 25.8356 | 68.2407 | 13.0294 | 13.3942 | 0.0069849 | 20.7801 | 0.0087788 | 27.6078 | 0.0082685 | 25.5867 | 69.8233 | 59.3679 | 25.4012
4 | L-55-3ER-DM | 30T0012 | L-55-3ER-DM | 3 Finger | off | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 15:21:14 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.3 | 0.8 | 1.6 | 0 | 9768 | 32 | 9422 | 73 | 3988 | 73 | 13760 | 84 | 28.5477 | 785 |  | 13.8 | [36 empty] | Econo 3F-open, no compressor, 55/51 ambient, 60% inlet 54% outlet Meriam,--adjust code tester speed to match total static of run L-55-3E-DM-SPWCT-SSR | R22 7 LBS: OFB: Econo 3 Finger Opened: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75 | 0.022 | 61.999 | 0.024 | 55.003 | 0.011 | 51.009 | 0.02 | 74.75 | 0.05 | 67.86 | 0.05 | 70.99 | 0.05 | 0.011 | 0.004 | 1.1885 | 0.0066 | 9768 | 32 | 3988 | 73 | 28.562 | 0.358 | [6 empty] | 458.3 | 2.2 | 463.1 | 2.2 | 461.7 | 2.2 | 1.6 | 0 | 1.3 | 0 | 1.6 | 0 | 615.8 | 7.6 | 555.5 | 8.8 | -10 | 0 | 460 |  | 465 |  | 456 |  | 1.3 |  | 1.5 |  | 1.3 |  | 0.36 | [29 empty] | 21 |  |  | 485 | 487 | 487 | 0.9 | 0.8 | 1.1 | 510 | 0.61 | 13.8 | 18.3 | [164 empty] | 67.78 | 0.05 | 69.97 | 0.04 | 68.25 | 0.04 | 69.52 | 0.04 | 67.85 | 0.04 | 69.09 | 0.04 | [32 empty] | 72.3 | 0.03 |  |  | 55.04 | 0.08 | 54.83 | 0.06 | 54.86 | 0.1 | 54.66 | 0.07 | 54.83 | 0.11 | 54.84 | 0.11 | [8 empty] | 73.5 | 0.06 | [34 empty] | 55.62 | 0.05 | 55.58 | 0.09 | 74.35 | 0.05 | 74.56 | 0.03 | 74.22 | 0.04 | 73.66 | 0.08 | 74.09 | 0.06 | 73.57 | 0.1 | 74.12 | 0.06 | 58.62 | 0.04 | 66.61 | 0.11 | 63.93 | 0.1 | 72.08 | 0.09 | 58.36 | 0.07 | 64.95 | 0.06 | 61.3 | 0.06 | 61.67 | 0.18 | 57.53 | 0.03 | 58.23 | 0.08 | 59.57 | 0.07 | 60.27 | 0.12 | 58.65 | 0.05 | 57.79 | 0.08 | 57.37 | 0.09 | 62.46 | 0.2 | 57.54 | 0.1 | 57.82 | 0.07 | 57.37 | 0.08 | 60.87 | 0.11 | [84 empty] | Economizer test | 75 | 0.022 | 61.999 | 0.024 | 67.851 | 0.008 | 58.382 | 0.018 | 55.003 | 0.011 | 51.009 | 0.02 | 1257.2 | 3.5 | 1212.1 | 3.4 | 0.665 | 0.001 | -0.13 | 0.001 | 0.011 | 0.004 | 1.1885 | 0.0066 | 29.337 | 0.001 | 482 | 6 | 390 |  | 0.3205 | 388.4757 | 13.03 | 0.13 | 0.74381 | 5644.2953 | 94.6946 | 388.4699 | 1788.8636 | 3855.4317 | 0.0082112 | 25.4448 | 67.1072 | 13.0296 | 13.3643 | 0.0069854 | 20.7828 | 0.00878 | 27.6079 | 0.0081682 | 25.1968 | 68.6764 | 58.7683 | 25.0156
4 | L-55-CE-DM | 30T0013 | L-55-CE-DM | closed | off | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 5:52:18 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.5 | 1.2 | 1.6 | 0 | 4586 | 21 | 4483 | 41 | 1719 | 53 | 6306 | 59 | 13.6494 | 786 |  | 11.9 | [36 empty] | Econo closed, no compressor, 55/51 ambient, 60% inlet 54% outlet Meriam,--adjust code tester speed to match total static of run L-55-CE-DM-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.999 | 0.008 | 62.002 | 0.023 | 54.989 | 0.018 | 50.979 | 0.017 | 74.66 | 0.03 | 71.16 | 0.03 | 73.23 | 0.01 | 0.018 | 0.006 | 1.055 | 0.0096 | 4586 | 21 | 1719 | 53 | 13.668 | 0.207 | [6 empty] | 458.5 | 2.3 | 463.2 | 2.3 | 461.5 | 2.3 | 1.6 | 0 | 1.3 | 0 | 1.6 | 0 | 607.3 | 8.1 | 554.6 | 9.4 | -10 | 0 | 459 |  | 460 |  | 460 |  | 1.3 |  | 1.5 |  | 1.2 |  | 0.35 | [29 empty] | 21 |  |  | 482 | 482 | 480 | 0.8 | 0.8 | 1 | 450 | 0.62 | 11.9 | 17.6 | [164 empty] | 71.56 | 0.03 | 72.39 | 0.05 | 71.98 | 0.05 | 71.98 | 0.04 | 71.87 | 0.03 | 71.88 | 0.03 | [32 empty] | 72.12 | 0.09 |  |  | 54.02 | 0.06 | 53.83 | 0.2 | 53.78 | 0.08 | 53.56 | 0.07 | 53.59 | 0.09 | 53.63 | 0.09 | [8 empty] | 73.53 | 0.04 | [34 empty] | 54.91 | 0.08 | 54.25 | 0.07 | 74.19 | 0.07 | 74.44 | 0.05 | 74.38 | 0.04 | 73.74 | 0.09 | 73.97 | 0.09 | 73.67 | 0.08 | 74.16 | 0.06 | 58.82 | 0.04 | 57.41 | 0.07 | 60.84 | 0.1 | 70.85 | 0.04 | 60.39 | 0.07 | 60.64 | 0.13 | 61 | 0.11 | 73 | 0.08 | 59.4 | 0.08 | 61.06 | 0.11 | 60.3 | 0.14 | 72.46 | 0.1 | 61.06 | 0.08 | 60.6 | 0.1 | 63.57 | 0.12 | 70.91 | 0.11 | 60.59 | 0.16 | 60.54 | 0.08 | 61.38 | 0.15 | 71.72 | 0.06 | [84 empty] | Economizer test | 74.999 | 0.008 | 62.002 | 0.023 | 71.415 | 0.014 | 60.289 | 0.016 | 54.989 | 0.018 | 50.979 | 0.017 | 1187.7 | 5.4 | 1137.4 | 5.2 | 0.683 | 0.001 | -0.217 | 0.002 | 0.018 | 0.006 | 1.055 | 0.0096 | 29.283 | 0.002 | 462 | 6 | 380 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.77518 | 5295.3825 | 91.2639 | 159.3847 | 733.9757 | 4561.4068 | 0.0085314 | 26.6614 | 70.6398 | 13.0292 | 13.4574 | 0.0069728 | 20.7657 | 0.0087822 | 27.6101 | 0.0085186 | 26.4479 | 72.2334 | 60.6115 | 26.2589
4 | L-55-OER-DM | 30T0014 | L-55-OER-DM | open | off | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 16:44:45 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.3 | 0.9 | 1.6 | 0 | 16828 | 65 | 16247 | 98 | 7106 | 106 | 23941 | 106 | 49.4649 | 785 |  | 13.3 | [36 empty] | Econo fully open, no compressor, 55/51 ambient, 60% inlet 54% outlet Meriam,--adjust code tester speed to match total static of run L-55-OE-DM-SPWCT-SSR | R22 7 LBS: OFB: Econo Fully Opened: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.011 | 0.035 | 62.001 | 0.026 | 54.994 | 0.009 | 51.002 | 0.018 | 74.62 | 0.08 | 62.66 | 0.03 | 67.74 | 0.1 | 0.002 | 0.003 | 1.1573 | 0.0046 | 16828 | 65 | 7106 | 106 | 49.455 | 0.623 | [6 empty] | 458.3 | 2.2 | 463.2 | 2.2 | 461.8 | 2.2 | 1.6 | 0 | 1.3 | 0 | 1.6 | 0 | 617.6 | 8 | 556.1 | 9.2 | -10 | 0 | 460 |  | 458 |  | 458 |  | 1.4 |  | 1.5 |  | 1.3 |  | 0.37 | [29 empty] | 21 |  |  | 487 | 487 | 488 | 0.8 | 0.9 | 1.1 | 500 | 0.61 | 13.3 | 18.1 | [164 empty] | 62.57 | 0.05 | 64.63 | 0.05 | 62.91 | 0.06 | 64.23 | 0.06 | 62.56 | 0.05 | 63.83 | 0.05 | [32 empty] | 62.42 | 0.04 |  |  | 55.1 | 0.12 | 54.93 | 0.1 | 55 | 0.14 | 54.74 | 0.11 | 54.97 | 0.17 | 54.99 | 0.17 | [8 empty] | 68.86 | 0.03 | [34 empty] | 55.59 | 0.07 | 55.96 | 0.11 | 74.32 | 0.07 | 74.51 | 0.07 | 74.26 | 0.05 | 74.09 | 0.08 | 74.16 | 0.07 | 74.02 | 0.08 | 74.21 | 0.07 | 58.2 | 0.05 | 57.62 | 0.06 | 57.18 | 0.11 | 57.43 | 0.09 | 56.54 | 0.08 | 56.56 | 0.13 | 56.76 | 0.14 | 58.12 | 0.09 | 57.02 | 0.06 | 56.65 | 0.09 | 56.56 | 0.1 | 57.81 | 0.1 | 57.61 | 0.07 | 56.8 | 0.1 | 57.15 | 0.13 | 57.88 | 0.14 | 56.56 | 0.11 | 56.58 | 0.06 | 56.77 | 0.09 | 57.3 | 0.12 | [84 empty] | Economizer test | 75.011 | 0.035 | 62.001 | 0.026 | 62.615 | 0.011 | 55.461 | 0.015 | 54.994 | 0.009 | 51.002 | 0.018 | 1236.6 | 2.5 | 1200.5 | 2.4 | 0.542 | 0.001 | -0.014 | 0.001 | 0.002 | 0.003 | 1.1573 | 0.0046 | 29.337 | 0.001 | 484 | 6 | 400 |  | 0.57831 | 694.2593 | 13.029 | 0.014 | 0.82008 | 5609.1549 | 76.441 | 694.2691 | 3197.0962 | 2412.0586 | 0.0077556 | 23.7161 | 61.7949 | 13.0294 | 13.2277 | 0.0069838 | 20.7789 | 0.0087787 | 27.6092 | 0.0076631 | 23.3711 | 63.6178 | 56.0262 | 23.1715
4 | L-75629575-1E3 | 30T0015 | L-75629575-1E3 | 1 Finger | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 14:01:57 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.6 | 1.3 | 6.2 | 0 | 19581 | 61 | 18945 | 96 | -565 | 92 | 19016 | 98 | 6.0793 | 785 |  | 11.87 | [36 empty] | Factory charge, 3 turns, Econo 1-F open unsealed cab, 60% inlet 54% outlet Meriam,--adust code tester speed to match total static of run L-1E3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.993 | 0.018 | 61.996 | 0.03 | 95 | 0.006 | 75.001 | 0.017 | 74.62 | 0.06 | 60 | 0.04 | 65.79 | 0.03 | 0.013 | 0.005 | 1.0817 | 0.0073 | 19581 | 61 | -565 | 92 | 6.079 | 0.035 | [6 empty] | 458.6 | 2.5 | 461.6 | 2.5 | 461.5 | 2.5 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2782.1 | 25.1 | 1497.6 | 28.1 | 346.1 | 19.1 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.35 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2360 |  | 0.69 | [8 empty] | 458.3 | 2.5 | 0.8 | 0 | 366.6 | 1.4 | 21 |  | 3127.6 | 480 | 480 | 480 | 0.9 | 1 | 0.9 | 460 | 0.62 | 11.87 | 17.7 |  |  |  |  | 214.85 | 0.22 | 99.66 | 0.06 |  |  |  |  | 221.97 | 0.14 | 167.88 | 0.08 | 108.51 | 0.05 | 59.38 | 0.1 |  |  | 96.6 | 0.07 | 106.22 | 0.07 | 6.56 | 0.07 |  |  | 60.94 | 0.49 |  |  |  |  | 75.6 | 0.2 | 65.2 | 0.19 | 44.46 | 0.13 | 20.74 | 0.14 | [120 empty] | 59.35 | 0.05 | 59.78 | 0.06 | 59.86 | 0.05 | 59.84 | 0.05 | 59.78 | 0.05 | 59.18 | 0.03 | [32 empty] | 96.38 | 0.06 |  |  | 94.66 | 0.15 | 94.77 | 0.12 | 94.46 | 0.15 | 94.76 | 0.15 | 94.55 | 0.19 | 94.57 | 0.19 | [8 empty] | 92.94 | 0.06 | [34 empty] | 94.68 | 0.05 | 94.45 | 0.08 | 74.97 | 0.06 | 74.92 | 0.05 | 74.85 | 0.05 | 75.24 | 0.07 | 75.13 | 0.07 | 75.32 | 0.07 | 75.06 | 0.05 | 91.46 | 0.06 | 84.44 | 0.09 | 85.11 | 0.09 | 76.95 | 0.05 | 86.54 | 0.12 | 85.74 | 0.07 | 87.82 | 0.08 | 85.85 | 0.19 | 90.19 | 0.06 | 89.43 | 0.11 | 89.04 | 0.1 | 89.81 | 0.19 | 87.17 | 0.18 | 89.35 | 0.12 | 90.08 | 0.12 | 84.98 | 0.3 | 89.61 | 0.18 | 88.77 | 0.12 | 89.64 | 0.13 | 84.77 | 0.16 | [84 empty] | L-55-1ER-DM | 74.993 | 0.018 | 61.996 | 0.03 | 59.885 | 0.018 | 56.683 | 0.021 | 95 | 0.006 | 75.001 | 0.017 | 1196.8 | 4.1 | 1157.3 | 4 | 0.662 | 0.001 | -0.177 | 0.002 | 0.013 | 0.005 | 1.0817 | 0.0073 | 29.177 | 0.002 | 3128 | 9 | 380 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.75609 | 5452.7313 | 90.0055 | 259.3893 | 1103.7905 | 4348.9408 | 0.0098205 | 29.7419 | 59.1289 | 14.0999 | 13.1692 | 0.013922 | 38.1581 | 0.0087796 | 27.6059 | 0.0090246 | 24.1875 | 79.0732 | 64.9451 | 24.003 | 31292.8872 | 26100.1721 | 2748 | 0.29971 | 30303.1359 | 25110.4208 | 9.6877 | 0.2146 | -5.7389 | -19.9443 | 53.6793 | 31292.8872 | 18639.4478 | 1005.9808 | 11647.4585 | 31292.8872 | 100%
4 | L-75629575-2E3 | 30T0016 | L-75629575-2E3 | 2 Finger | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 15:48:46 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.5 | 1.4 | 6.2 | 0 | 18441 | 67 | 17781 | 116 | -2375 | 85 | 16064 | 88 | 5.1306 | 786 |  | 12.5 | [36 empty] | Factory charge, 3 turns, Econo 2-F open unsealed cab, 60% inlet 54% outlet Meriam,--adust code tester speed to match total static of run L-2E3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75 | 0.027 | 61.999 | 0.028 | 94.999 | 0.009 | 75.001 | 0.015 | 74.58 | 0.08 | 60.98 | 0.05 | 66.5 | 0.06 | 0.011 | 0.005 | 1.1104 | 0.0075 | 18441 | 67 | -2375 | 85 | 5.131 | 0.031 | [6 empty] | 458.5 | 2.7 | 461.5 | 2.7 | 461.5 | 2.7 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2779.2 | 25.9 | 1500.5 | 30.3 | 351.5 | 19.5 | 460 |  | 460 |  | 460 |  | 1.4 |  | 1.5 |  | 1.3 |  | 0.35 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4.1 |  | 3.4 |  | 2360 |  | 0.68 | [8 empty] | 458.1 | 2.7 | 0.8 | 0 | 366.2 | 1.5 | 21 |  | 3137.2 | 480 | 480 | 480 | 0.9 | 0.9 | 0.9 | 500 | 0.63 | 12.5 | 18 |  |  |  |  | 215 | 0.21 | 99.55 | 0.06 |  |  |  |  | 222.15 | 0.17 | 168.22 | 0.07 | 108.55 | 0.05 | 59.67 | 0.1 |  |  | 96.28 | 0.07 | 106.26 | 0.07 | 6.71 | 0.07 |  |  | 61.48 | 0.59 |  |  |  |  | 76.03 | 0.22 | 65.85 | 0.2 | 44.73 | 0.15 | 21.12 | 0.13 | [120 empty] | 60.4 | 0.05 | 60.73 | 0.05 | 61.15 | 0.05 | 60.7 | 0.05 | 61.09 | 0.05 | 60.03 | 0.05 | [32 empty] | 96.13 | 0.05 |  |  | 94.31 | 0.17 | 94.51 | 0.13 | 94.22 | 0.17 | 94.63 | 0.15 | 94.41 | 0.19 | 94.43 | 0.19 | [8 empty] | 92.87 | 0.07 | [34 empty] | 94.76 | 0.05 | 94.46 | 0.08 | 75.19 | 0.07 | 75.05 | 0.07 | 74.96 | 0.06 | 75.78 | 0.09 | 75.45 | 0.08 | 75.9 | 0.11 | 75.29 | 0.08 | 92.09 | 0.04 | 84.27 | 0.08 | 86.38 | 0.08 | 76.89 | 0.05 | 87.96 | 0.1 | 85.71 | 0.06 | 88 | 0.07 | 88.28 | 0.27 | 91.53 | 0.07 | 90.39 | 0.14 | 89.32 | 0.11 | 89.57 | 0.29 | 89.97 | 0.09 | 89.07 | 0.13 | 91.16 | 0.15 | 86.98 | 0.23 | 89.73 | 0.16 | 89.24 | 0.1 | 90.75 | 0.12 | 86.53 | 0.17 | [84 empty] | L-55-2ER-DM | 75 | 0.027 | 61.999 | 0.028 | 60.889 | 0.028 | 57.598 | 0.027 | 94.999 | 0.009 | 75.001 | 0.015 | 1214.5 | 4.2 | 1170.6 | 4 | 0.654 | 0.001 | -0.153 | 0.002 | 0.011 | 0.005 | 1.1104 | 0.0075 | 29.138 | 0.002 | 3131 | 10 | 390 |  | 0.26201 | 311.656 | 13.029 | 0.157 | 0.77257 | 5521.6804 | 89.9397 | 320.0544 | 1361.9437 | 4159.7367 | 0.010048 | 30.2102 | 60.1164 | 14.0999 | 13.1971 | 0.013922 | 38.1581 | 0.00878 | 27.6079 | 0.0093363 | 24.7716 | 79.9675 | 65.5673 | 24.583 | 31071.3837 | 26306.743 | 2741 | 0.30108 | 30047.2778 | 25282.6372 | 9.5967 | 0.2151 | -5.6272 | -19.8511 | 54.6764 | 31071.3837 | 15661.1274 | 1041.4892 | 14368.7671 | 31071.3837 | 100%
4 | L-75629575-3E3 | 30T0017 | L-75629575-3E3 | 3 Finger | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 21:01:28 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.8 | 1.6 | 6.2 | 0 | 17254 | 65 | 16623 | 122 | -4482 | 109 | 12767 | 106 | 4.0737 | 786 |  | 13.57 | [36 empty] | Factory charge, 3 turns, Econo 3-F open unsealed cab, 60% inlet 54% outlet Meriam,--adust code tester speed to match total static of run L-3E3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.008 | 0.043 | 62 | 0.022 | 94.997 | 0.009 | 75.002 | 0.012 | 74.56 | 0.1 | 62.06 | 0.05 | 67.19 | 0.07 | 0.023 | 0.004 | 1.1606 | 0.0054 | 17254 | 65 | -4482 | 109 | 4.075 | 0.035 | [6 empty] | 458.8 | 2.8 | 461.2 | 2.8 | 461.2 | 2.8 | 6.2 | 0 | 5.1 | 0 | 5.5 | 0 | 2785.2 | 27.4 | 1496.8 | 30.9 | 348.3 | 20.6 | 460 |  | 460 |  | 460 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.36 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2360 |  | 0.68 | [8 empty] | 458.4 | 2.8 | 0.8 | 0 | 366.9 | 1.5 | 21 |  | 3137.9 | 480 | 480 | 480 | 0.8 | 0.9 | 1 | 520 | 0.64 | 13.57 | 18.3 |  |  |  |  | 215.1 | 0.2 | 99.46 | 0.05 |  |  |  |  | 222.36 | 0.14 | 168.27 | 0.05 | 108.63 | 0.04 | 59.64 | 0.06 |  |  | 95.82 | 0.06 | 106.3 | 0.06 | 6.84 | 0.06 |  |  | 62.6 | 0.29 |  |  |  |  | 76.88 | 0.13 | 66.78 | 0.12 | 45.3 | 0.08 | 21.48 | 0.09 | [120 empty] | 61.47 | 0.07 | 61.68 | 0.05 | 62.39 | 0.07 | 61.65 | 0.04 | 62.33 | 0.06 | 61.01 | 0.04 | [32 empty] | 95.71 | 0.04 |  |  | 94.09 | 0.17 | 94.44 | 0.15 | 94.14 | 0.18 | 94.57 | 0.15 | 94.36 | 0.2 | 94.39 | 0.2 | [44 empty] | 94.69 | 0.05 | 94.25 | 0.1 | 75.12 | 0.09 | 75.01 | 0.08 | 74.95 | 0.06 | 75.65 | 0.11 | 75.37 | 0.09 | 75.75 | 0.12 | 75.25 | 0.08 | 92.5 | 0.07 | 84.24 | 0.14 | 87.16 | 0.14 | 77.93 | 0.09 | 89.2 | 0.1 | 85.86 | 0.1 | 89.27 | 0.11 | 89.41 | 0.34 | 91.53 | 0.07 | 91.11 | 0.14 | 90.19 | 0.14 | 89.77 | 0.26 | 87.2 | 0.13 | 90.11 | 0.16 | 92.01 | 0.17 | 85.77 | 0.2 | 90.38 | 0.19 | 89.65 | 0.15 | 91.61 | 0.17 | 87.28 | 0.21 | [84 empty] | L-55-3ER-DM | 75.008 | 0.043 | 62 | 0.022 | 62.039 | 0.014 | 58.595 | 0.023 | 94.997 | 0.009 | 75.002 | 0.012 | 1241.2 | 2.9 | 1197.1 | 2.9 | 0.643 | 0.001 | -0.131 | 0.003 | 0.023 | 0.004 | 1.1606 | 0.0054 | 29.209 | 0.001 | 3134 | 9 | 390 |  | 0.3205 | 388.4757 | 13.03 | 0.13 | 0.75653 | 5629.504 | 90.4287 | 405.6608 | 1726.2335 | 3903.2705 | 0.010356 | 30.8438 | 61.2825 | 14.0999 | 13.2289 | 0.013923 | 38.1591 | 0.0087787 | 27.6085 | 0.0096742 | 25.4202 | 81.1771 | 66.3962 | 25.2354 | 31572.5343 | 26879.2904 | 2744 | 0.29663 | 30550.0976 | 25856.8537 | 9.748 | 0.22031 | -5.6084 | -19.8947 | 55.661 | 31572.5343 | 12319.3213 | 1040.4306 | 18212.7824 | 31572.5343 | 100%
4 | L-75629575-OE3 | 30T0018 | L-75629575-OE3 | open | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 22:30:26 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.9 | 1.4 | 6.2 | 0 | 11177 | 58 | 10804 | 71 | -12699 | 230 | -1535 | 247 | -0.49104 | 786 |  | 12.12 | [36 empty] | Factory charge, 3 turns, Econo fully open unsealed cab, 60% inlet 54% outlet Meriam,--adust code tester speed to match total static of run L-OE3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.997 | 0.023 | 61.899 | 0.068 | 94.998 | 0.009 | 75.004 | 0.02 | 74.69 | 0.04 | 66 | 0.05 | 70.05 | 0.08 | 0.001 | 0.004 | 1.0808 | 0.0066 | 11177 | 58 | -12699 | 230 | 0 | 0 | [6 empty] | 458.9 | 2.6 | 461.4 | 2.6 | 461.2 | 2.6 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2785.5 | 25.9 | 1494.1 | 29.1 | 340 | 19.4 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.4 |  | 0.36 | 460 |  | 460 |  | 460 |  | 4 |  | 4 |  | 3.5 |  | 2360 |  | 0.67 | [8 empty] | 458.5 | 2.6 | 0.8 | 0 | 367 | 1.5 | 21 |  | 3128 | 480 | 480 | 480 | 0.5 | 0.6 | 0.6 | 280 | 0.62 | 12.12 | 17.7 |  |  |  |  | 216.06 | 0.22 | 99.99 | 0.05 |  |  |  |  | 224.11 | 0.15 | 167.74 | 0.06 | 109.19 | 0.05 | 58.55 | 0.07 |  |  | 96.96 | 0.06 | 106.62 | 0.07 | 6.63 | 0.07 |  |  | 66.86 | 0.32 |  |  |  |  | 81.76 | 0.16 | 70.83 | 0.14 | 48.39 | 0.1 | 22.44 | 0.11 | [120 empty] | 65.49 | 0.05 | 65.94 | 0.06 | 66.36 | 0.07 | 65.92 | 0.06 | 66.29 | 0.06 | 65.25 | 0.05 | [32 empty] | 96.82 | 0.04 |  |  | 93.8 | 0.19 | 94.15 | 0.14 | 94 | 0.2 | 94.47 | 0.15 | 94.3 | 0.2 | 94.32 | 0.2 | [44 empty] | 94.74 | 0.07 | 94.01 | 0.1 | 75.21 | 0.05 | 75.09 | 0.04 | 75.05 | 0.04 | 75.48 | 0.07 | 75.41 | 0.06 | 75.58 | 0.06 | 75.29 | 0.04 | 93.02 | 0.05 | 94.05 | 0.08 | 94.91 | 0.17 | 94.45 | 0.13 | 94.23 | 0.13 | 95.53 | 0.19 | 95.29 | 0.2 | 93.67 | 0.14 | 93.76 | 0.07 | 94.95 | 0.17 | 95.23 | 0.18 | 92.02 | 0.17 | 90.85 | 0.13 | 93.63 | 0.16 | 92.95 | 0.21 | 91.05 | 0.19 | 93.72 | 0.19 | 93.3 | 0.11 | 93.57 | 0.15 | 91.62 | 0.25 | [84 empty] | L-55-OER-DM | 74.997 | 0.023 | 61.899 | 0.068 | 66.015 | 0.021 | 62.262 | 0.031 | 94.998 | 0.009 | 75.004 | 0.02 | 1200.9 | 3.7 | 1149.9 | 3.6 | 0.511 | 0.002 | -0.016 | 0.003 | 0.001 | 0.004 | 1.0808 | 0.0066 | 29.226 | 0.001 | 3126 | 9 | 380 |  | 0.57831 | 694.2593 | 13.029 | 0.014 | 0.81854 | 5401.012 | 69.0313 | 772.0938 | 3285.53 | 2115.482 | 0.011884 | 33.9993 | 65.1965 | 14.0999 | 13.3408 | 0.013925 | 38.161 | 0.0087148 | 27.5359 | 0.011086 | 27.931 | 87.2089 | 70.3142 | 27.7305 | 33857.9917 | 28533.4701 | 2746 | 0.27681 | 32796.6556 | 27472.134 | 10.4916 | 0.20757 | -6.2688 | -22.0124 | 59.4304 | 33857.9917 | -2134.0196 | 1082.7863 | 34909.2251 | 33857.9917 | 100%
4 | L-75629575-E3 | 30T0001 | L-75629575-E3 | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 7:48:28 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.9 | 1.3 | 6.3 | 0 | 21875 | 74 | 21165 | 132 | 2400 | 74 | 24278 | 112 | 7.7714 | 786 |  | 11.3 | [36 empty] | Factory charge, 3 turns, Econo closed unsealed cab, 60% inlet 54% outlet Meriam,--adust code tester speed to match total static of run L-E3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.003 | 0.019 | 61.998 | 0.03 | 95.001 | 0.005 | 74.998 | 0.015 | 74.57 | 0.08 | 58.06 | 0.04 | 64.75 | 0.07 | 0.017 | 0.005 | 1.0395 | 0.0064 | 21875 | 74 | 2400 | 74 | 7.772 | 0.041 | [6 empty] | 458.9 | 2.5 | 461.6 | 2.5 | 461 | 2.5 | 6.3 | 0 | 5 | 0 | 5.5 | 0 | 2801.5 | 25.2 | 1478.9 | 27.6 | 322.2 | 19.3 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.5 |  | 1.3 |  | 0.35 | 462 |  | 462 |  | 462 |  | 4.1 |  | 4.1 |  | 3.5 |  | 2360 |  | 0.68 | [8 empty] | 458.6 | 2.5 | 0.8 | 0 | 367.5 | 1.4 | 21 |  | 3128.5 | 480 | 480 | 480 | 0.8 | 0.8 | 1 | 430 | 0.62 | 11.3 | 17.1 |  |  |  |  | 214.49 | 0.19 | 100.09 | 0.05 |  |  |  |  | 221.74 | 0.11 | 166.2 | 0.07 | 108.44 | 0.04 | 57.75 | 0.09 |  |  | 97.49 | 0.07 | 106.12 | 0.06 | 6.03 | 0.07 |  |  | 59.11 | 0.22 |  |  |  |  | 75.09 | 0.1 | 63.04 | 0.15 | 44.16 | 0.06 | 18.88 | 0.14 | [120 empty] | 57.29 | 0.05 | 58.65 | 0.06 | 57.95 | 0.06 | 58.69 | 0.05 | 57.65 | 0.04 | 57.86 | 0.05 | [32 empty] | 97.36 | 0.05 |  |  | 95.38 | 0.12 | 95.36 | 0.11 | 95.22 | 0.12 | 95.3 | 0.11 | 95.14 | 0.12 | 95.17 | 0.11 | [8 empty] | 93.52 | 0.06 | [34 empty] | 94.75 | 0.04 | 94.67 | 0.08 | 75.02 | 0.07 | 74.96 | 0.07 | 74.86 | 0.06 | 75.24 | 0.07 | 75.19 | 0.07 | 75.28 | 0.08 | 75.06 | 0.07 | 90.33 | 0.05 | 91.85 | 0.08 | 88.95 | 0.09 | 79.22 | 0.06 | 87.05 | 0.07 | 88.38 | 0.07 | 88.46 | 0.08 | 77.79 | 0.07 | 88.86 | 0.05 | 87.43 | 0.09 | 88.46 | 0.08 | 77.57 | 0.08 | 84.68 | 0.13 | 87.47 | 0.08 | 85.57 | 0.09 | 77.17 | 0.1 | 87.15 | 0.12 | 86.58 | 0.07 | 87.21 | 0.12 | 77.02 | 0.07 | [84 empty] | L-55-CE-DM | 75.003 | 0.019 | 61.998 | 0.03 | 57.93 | 0.014 | 54.993 | 0.019 | 95.001 | 0.005 | 74.998 | 0.015 | 1170 | 3.6 | 1138 | 3.5 | 0.682 | 0.002 | -0.226 | 0.002 | 0.017 | 0.005 | 1.0395 | 0.0064 | 29.264 | 0.001 | 3124 | 9 | 380 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.76714 | 5352.4354 | 91.1784 | 169.2082 | 720.0387 | 4632.3967 | 0.0094701 | 29.0261 | 57.1629 | 14.0999 | 13.1155 | 0.013919 | 38.1552 | 0.0087786 | 27.6072 | 0.0084983 | 23.1385 | 77.715 | 63.9775 | 22.9515 | 32513.9609 | 26400.963 | 2744 | 0.28804 | 31528.2126 | 25415.2147 | 10.0923 | 0.20235 | -6.0746 | -20.5521 | 51.949 | 32513.9609 | 23918.0246 | 1000.9528 | 7594.9836 | 32513.9609 | 100%
4 | L-95-3+10-C | 30T0006 | L-95-3+10-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 3:40:11 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7.7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 7 |  | 458.9 | 1.4 | 6.3 | 0 | 22013 | 74 | 21318 | 112 | 2097 | 91 | 24112 | 123 | 7.657 | 785 |  | 11.8 | [36 empty] | Closed damper, +10% charge 95F Test, adjust code tester speed to match--total static of run L-E3-SPWCT-SS (see row 27) | R22 7.7 LBS: OFB: Econo Closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.001 | 0.019 | 62 | 0.031 | 95.003 | 0.015 | 74.995 | 0.018 | 74.48 | 0.09 | 58.09 | 0.05 | 64.37 | 0.02 | 0.029 | 0.005 | 1.0647 | 0.0075 | 22013 | 74 | 2097 | 91 | 7.657 | 0.043 | [6 empty] | 458.9 | 2.5 | 461.6 | 2.5 | 461.2 | 2.5 | 6.3 | 0 | 5.1 | 0 | 5.5 | 0 | 2806.1 | 25.2 | 1486.9 | 28.4 | 343 | 18.9 | 462 |  | 461 |  | 460 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.36 | 462 |  | 462 |  | 461 |  | 4.1 |  | 4 |  | 3.4 |  | 2370 |  | 0.68 | [8 empty] | 458.5 | 2.5 | 0.8 | 0 | 370.2 | 1.5 | 21 |  | 3151.2 | 491 | 490 | 490 | 0.8 | 0.8 | 1 | 470 | 0.63 | 11.8 | 17.3 |  |  |  |  | 216.79 | 0.27 | 97.87 | 0.08 |  |  |  |  | 223.24 | 0.18 | 166.78 | 0.17 | 108.96 | 0.06 | 57.82 | 0.19 |  |  | 93.87 | 0.08 | 106.9 | 0.09 | 9.03 | 0.08 | [8 empty] | 74.97 | 0.28 | 62.99 | 0.38 | 44.16 | 0.18 | 18.83 | 0.33 | [120 empty] | 57.47 | 0.06 | 58.57 | 0.08 | 57.88 | 0.08 | 58.63 | 0.07 | 57.67 | 0.05 | 57.91 | 0.05 | [32 empty] | 93.74 | 0.06 |  |  | 94.29 | 0.19 | 93.94 | 0.62 | 94.09 | 0.25 | 94.27 | 0.2 | 93.44 | 0.32 | 93.48 | 0.32 | [8 empty] | 91.43 | 0.07 | [34 empty] | 94.73 | 0.08 | 94.6 | 0.1 | 74.79 | 0.1 | 74.78 | 0.07 | 74.77 | 0.06 | 74.97 | 0.11 | 74.9 | 0.12 | 75.08 | 0.1 | 74.9 | 0.07 | 89.77 | 0.07 | 91.47 | 0.08 | 88.87 | 0.1 | 78.76 | 0.05 | 87.05 | 0.07 | 88.91 | 0.07 | 88.74 | 0.07 | 77.79 | 0.07 | 88.96 | 0.04 | 87.71 | 0.08 | 89.13 | 0.09 | 77.65 | 0.1 | 85 | 0.08 | 87.43 | 0.08 | 85.26 | 0.14 | 77.58 | 0.1 | 86.69 | 0.19 | 86.63 | 0.12 | 86.25 | 0.17 | 77.34 | 0.07 | [84 empty] | L-55-CE-DM | 75.001 | 0.019 | 62 | 0.031 | 58.074 | 0.011 | 55.12 | 0.022 | 95.003 | 0.015 | 74.995 | 0.018 | 1178.9 | 4.2 | 1157 | 4.1 | 0.682 | 0.001 | -0.227 | 0.002 | 0.029 | 0.005 | 1.0647 | 0.0075 | 29.502 | 0.002 | 3149 | 9 | 390 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.78394 | 5391.5252 | 92.7007 | 169.5823 | 721.6293 | 4669.8958 | 0.0094677 | 29.0198 | 57.2901 | 14.0999 | 13.1195 | 0.013916 | 38.1522 | 0.0087804 | 27.6086 | 0.0085375 | 23.2161 | 77.6998 | 63.9689 | 23.025 | 32321.196 | 26409.5305 | 2759 | 0.29134 | 31306.5134 | 25394.8479 | 9.9417 | 0.20251 | -5.9948 | -20.4098 | 52.1073 | 32321.196 | 23682.2093 | 1030.4068 | 7608.5799 | 32321.196 | 100%
4 | L-95-3+40-C | 30T0007 | L-95-3+40-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 10:37:08 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 9.8 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.8 |  | 7 |  | 458.6 | 1.4 | 6.3 | 0 | 22337 | 110 | 21563 | 197 | 1938 | 131 | 24276 | 126 | 7.5815 | 785 |  | 12.95 | [36 empty] | Closed Damper, +40% charge, 95F Test, adjust code tester speed to match total static--of run L-E3-SPWCT-SS (see row 27) | R22 9.8 LBS: OFB: Econo Closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.987 | 0.054 | 62.004 | 0.034 | 94.997 | 0.01 | 74.988 | 0.019 | 74.49 | 0.14 | 58.37 | 0.05 | 64.46 | 0.02 | 0.072 | 0.006 | 1.1196 | 0.0082 | 22337 | 110 | 1938 | 131 | 7.582 | 0.044 | [6 empty] | 458.6 | 2.7 | 461.3 | 2.7 | 461.5 | 2.7 | 6.3 | 0 | 5.1 | 0 | 5.6 | 0 | 2815.3 | 26.4 | 1505.7 | 29.8 | 386.3 | 20.1 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.5 |  | 0.37 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4.1 |  | 4.3 |  | 2410 |  | 0.7 | [8 empty] | 458.3 | 2.7 | 0.8 | 0 | 371.8 | 1.6 | 21 |  | 3202.8 | 480 | 480 | 480 | 0.9 | 0.9 | 1.1 | 490 | 0.63 | 0.1295 | 18.1 |  |  |  |  | 222.39 | 0.18 | 95.48 | 0.04 |  |  |  |  | 227.5 | 0.18 | 169.64 | 0.12 | 110.32 | 0.06 | 59.31 | 0.14 |  |  | 91.4 | 0.05 | 108.72 | 0.06 | 13.24 | 0.05 | [8 empty] | 74.77 | 0.17 | 63.55 | 0.23 | 44.09 | 0.11 | 19.45 | 0.2 | [120 empty] | 57.69 | 0.05 | 58.9 | 0.07 | 58.27 | 0.06 | 58.94 | 0.06 | 58 | 0.06 | 58.14 | 0.05 | [32 empty] | 91.26 | 0.04 |  |  | 94.22 | 0.25 | 94.76 | 0.97 | 93.81 | 0.28 | 94.18 | 0.19 | 92.77 | 0.33 | 92.79 | 0.33 | [44 empty] | 94.85 | 0.06 | 94.71 | 0.08 | 74.94 | 0.1 | 74.87 | 0.11 | 74.77 | 0.09 | 75.21 | 0.1 | 75.12 | 0.1 | 75.28 | 0.11 | 75 | 0.1 | 89.74 | 0.05 | 91.42 | 0.07 | 88.88 | 0.09 | 78.73 | 0.08 | 86.89 | 0.07 | 88.64 | 0.07 | 88.51 | 0.06 | 77.62 | 0.11 | 88.73 | 0.06 | 87.53 | 0.08 | 88.87 | 0.08 | 77.51 | 0.12 | 84.72 | 0.08 | 87.31 | 0.08 | 85.07 | 0.13 | 77.45 | 0.13 | 86.52 | 0.17 | 86.5 | 0.08 | 86.05 | 0.15 | 77.25 | 0.09 | [84 empty] | L-55-CE-DM | 74.987 | 0.054 | 62.004 | 0.034 | 58.28 | 0.022 | 55.248 | 0.028 | 94.997 | 0.01 | 74.988 | 0.019 | 1205.3 | 4.5 | 1190.6 | 4.4 | 0.682 | 0.002 | -0.242 | 0.002 | 0.072 | 0.006 | 1.1196 | 0.0082 | 29.696 | 0.002 | 3202 | 9 | 400 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.78594 | 5509.9867 | 95.3927 | 175.0944 | 745.0954 | 4764.8913 | 0.0094793 | 29.0362 | 57.4941 | 14.0998 | 13.1249 | 0.013911 | 38.1456 | 0.0087863 | 27.6117 | 0.0085627 | 23.2938 | 77.7147 | 63.9909 | 23.1022 | 32696.3644 | 26739.6804 | 2802 | 0.29249 | 31656.7398 | 25700.0559 | 9.8866 | 0.20838 | -5.934 | -20.2206 | 52.1713 | 32696.3644 | 23791.8487 | 1055.7838 | 7848.7319 | 32696.3644 | 100%
4 | L-95-3-10-C | 30T0008 | L-95-3+10-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 3:40:11 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 6.3 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 7 |  | 458.8 | 1.5 | 6.2 | 0 | 21350 | 91 | 20654 | 150 | 1505 | 89 | 22856 | 112 | 7.3256 | 785 |  | 11.5 | [36 empty] | Closed Damper, -10% charge, 95F Test, adjust code tester speed to match total--static of run L-E3-SPWCT-SS (see row 27) | R22 6.3 LBS: OFB: Econo Closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.999 | 0.036 | 62.002 | 0.031 | 95.001 | 0.008 | 74.986 | 0.022 | 74.5 | 0.1 | 58.58 | 0.07 | 64.76 | 0.03 | 0.028 | 0.007 | 1.0627 | 0.0096 | 21350 | 91 | 1505 | 89 | 7.326 | 0.039 | [6 empty] | 458.8 | 2.7 | 461.6 | 2.7 | 461.3 | 2.7 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2787.7 | 26.4 | 1488.4 | 29.7 | 332.4 | 19.7 | 462 |  | 462 |  | 461 |  | 1.4 |  | 1.5 |  | 1.3 |  | 0.36 | 462 |  | 462 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2340 |  | 0.67 | [8 empty] | 458.5 | 2.6 | 0.8 | 0 | 370.1 | 1.5 | 21 |  | 3121.1 | 490 | 491 | 491 | 0.8 | 0.8 | 1 | 460 | 0.63 | 11.5 | 17.4 |  |  |  |  | 211.33 | 0.17 | 103.11 | 0.04 |  |  |  |  | 220.31 | 0.13 | 166.57 | 0.04 | 108.02 | 0.04 | 58.54 | 0.05 |  |  | 101.22 | 0.06 | 105.12 | 0.06 | 2.01 | 0.05 | [8 empty] | 75.47 | 0.08 | 64.37 | 0.11 | 44.48 | 0.05 | 19.89 | 0.09 | [120 empty] | 57.89 | 0.06 | 59.17 | 0.07 | 58.51 | 0.07 | 59.16 | 0.06 | 58.25 | 0.05 | 58.34 | 0.05 | [32 empty] | 101.18 | 0.04 |  |  | 94.24 | 0.19 | 93.56 | 0.89 | 94.03 | 0.28 | 94.3 | 0.19 | 93.35 | 0.33 | 93.39 | 0.33 | [8 empty] | 98.07 | 0.05 | [34 empty] | 94.95 | 0.09 | 94.79 | 0.11 | 74.98 | 0.1 | 74.91 | 0.08 | 74.81 | 0.06 | 75.25 | 0.12 | 75.15 | 0.12 | 75.29 | 0.11 | 75.01 | 0.08 | 89.92 | 0.05 | 91.56 | 0.06 | 88.93 | 0.1 | 78.76 | 0.05 | 87.03 | 0.07 | 88.64 | 0.07 | 88.51 | 0.07 | 77.62 | 0.08 | 88.8 | 0.05 | 87.55 | 0.07 | 88.82 | 0.09 | 77.4 | 0.09 | 84.89 | 0.07 | 87.25 | 0.08 | 85.08 | 0.11 | 77.54 | 0.1 | 86.65 | 0.14 | 86.62 | 0.08 | 86.14 | 0.13 | 77.25 | 0.07 | [84 empty] | L-55-CE-DM | 74.999 | 0.036 | 62.002 | 0.031 | 58.54 | 0.027 | 55.493 | 0.029 | 95.001 | 0.008 | 74.986 | 0.022 | 1178.6 | 5.4 | 1154.9 | 5.3 | 0.682 | 0.001 | -0.226 | 0.002 | 0.028 | 0.007 | 1.0627 | 0.0096 | 29.484 | 0.002 | 3120 | 9 | 390 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.78533 | 5384.9676 | 92.5324 | 169.2076 | 720.0409 | 4664.9267 | 0.0094676 | 29.0186 | 57.7547 | 14.0998 | 13.1321 | 0.013908 | 38.1436 | 0.0087822 | 27.6101 | 0.0086432 | 23.4447 | 77.6951 | 63.9671 | 23.2532 | 31046.3743 | 25770.8927 | 2730 | 0.30012 | 30031.1174 | 24755.6358 | 9.6254 | 0.20845 | -5.7654 | -19.9405 | 52.5033 | 31046.3743 | 22430.6518 | 1031.1885 | 7584.534 | 31046.3743 | 100%
4 | L-95-3-40-C | 30T0009 | L-95-3+40-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 10:37:08 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 9.8 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.8 |  | 7 |  | 458.6 | 1.4 | 6.1 | 0 | 13729 | 66 | 13249 | 86 | 420 | 69 | 14150 | 100 | 4.6792 | 786 |  | 10.8 | [36 empty] | Closed Damper, -40% charge, 95F Test, adjust code tester--speed to match total static of run L-E3-SPWCT-SS (see row 27) | R22 4.2 LBS: OFB: Econo closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.004 | 0.02 | 61.999 | 0.026 | 95.015 | 0.016 | 75.009 | 0.032 | 74.6 | 0.05 | 64.09 | 0.04 | 68.42 | 0.01 | 0.001 | 0.005 | 1.0249 | 0.0069 | 13729 | 66 | 420 | 69 | 4.679 | 0.036 | [6 empty] | 458.6 | 2.7 | 461.1 | 2.7 | 461.3 | 2.7 | 6.1 | 0 | 5 | 0 | 5.4 | 0 | 2714.5 | 27.2 | 1496.3 | 30.8 | 309.5 | 20.3 | 460 |  | 460 |  | 461 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.35 | 461 |  | 460 |  | 462 |  | 3.9 |  | 3.9 |  | 3.4 |  | 2260 |  | 0.68 | [8 empty] | 458.3 | 2.7 | 0.8 | 0 | 369.8 | 1.6 | 21 |  | 3030.8 | 490 | 491 | 492 | 0.8 | 0.8 | 0.9 | 460 | 0.62 | 10.8 | 17.1 |  |  |  |  | 198.26 | 0.2 | 101.11 | 0.05 |  |  |  |  | 208.55 | 0.17 | 188.2 | 0.04 | 104.19 | 0.06 | 84.01 | 0.05 |  |  | 97.91 | 0.05 | 100.72 | 0.07 | -0.39 | 0.05 |  |  | 68.96 | 0.03 |  |  |  |  | 61.62 | 0.06 | 73.5 | 0.03 | 34.88 | 0.04 | 38.63 | 0.05 | [120 empty] | 63.75 | 0.06 | 65.24 | 0.05 | 64.24 | 0.05 | 65.19 | 0.04 | 63.97 | 0.04 | 64.33 | 0.04 | [32 empty] | 97.82 | 0.04 |  |  | 95.53 | 0.18 | 95.46 | 0.18 | 95.4 | 0.16 | 95.36 | 0.19 | 95.34 | 0.17 | 95.37 | 0.17 | [8 empty] | 94.43 | 0.05 | [34 empty] | 95.24 | 0.07 | 94.68 | 0.1 | 75.09 | 0.05 | 75.01 | 0.05 | 74.82 | 0.04 | 75.46 | 0.06 | 75.32 | 0.06 | 75.5 | 0.06 | 75.11 | 0.05 | 89.76 | 0.08 | 91.37 | 0.1 | 88.77 | 0.11 | 78.78 | 0.05 | 86.8 | 0.1 | 88.17 | 0.09 | 88.03 | 0.09 | 77.42 | 0.06 | 88.62 | 0.08 | 87.18 | 0.11 | 88.3 | 0.1 | 77.3 | 0.06 | 85.4 | 0.11 | 86.96 | 0.11 | 84.9 | 0.13 | 77.64 | 0.09 | 86.41 | 0.17 | 86.46 | 0.1 | 86.07 | 0.15 | 77.31 | 0.06 | [84 empty] | L-55-CE-DM | 75.004 | 0.02 | 61.999 | 0.026 | 64.118 | 0.024 | 57.972 | 0.028 | 95.015 | 0.016 | 75.009 | 0.032 | 1163.4 | 3.9 | 1127.8 | 3.8 | 0.682 | 0.002 | -0.217 | 0.002 | 0.001 | 0.005 | 1.0249 | 0.0069 | 29.385 | 0.002 | 3024 | 9 | 380 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.78307 | 5258.4248 | 90.3611 | 165.8071 | 705.5458 | 4552.879 | 0.0094695 | 29.0244 | 63.3349 | 14.1003 | 13.2747 | 0.013925 | 38.1656 | 0.008779 | 27.6079 | 0.0087993 | 24.9749 | 77.7107 | 63.9752 | 24.7839 | 22298.3591 | 18142.5512 | 2644 | 0.40469 | 21309.8216 | 17154.0137 | 7.0469 | 0.44084 | -4.2405 | -14.3758 | 52.0009 | 22298.3591 | 13845.0834 | 1004.3354 | 7448.9404 | 22298.3591 | 100%
4 | L-95-3+10-1 | 30T0033 | L-95-3+10-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 4:27:17 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7.7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 7 |  | 458.9 | 1.3 | 6.3 | 0 | 20207 | 71 | 19520 | 132 | -788 | 96 | 19418 | 107 | 6.1508 | 785 |  | 13.1 | [36 empty] | 1 Finger Open, +10% charge 95F Test, adjust code tester speed to match--total static of run L-1E3-SPWCT-SS (see row 33) | R22 7.7 LBS: OFB: Econo open 1F: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.007 | 0.03 | 61.996 | 0.032 | 95.005 | 0.007 | 75.014 | 0.023 | 74.51 | 0.1 | 59.89 | 0.06 | 65.33 | 0.04 | 0.039 | 0.005 | 1.1361 | 0.0074 | 20207 | 71 | -788 | 96 | 6.152 | 0.037 | [6 empty] | 458.9 | 2.4 | 461.5 | 2.4 | 461.2 | 2.4 | 6.3 | 0 | 5.1 | 0 | 5.5 | 0 | 2807.1 | 24.3 | 1488.9 | 27.4 | 349.6 | 18.4 | 461 |  | 462 |  | 461 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.4 | 462 |  | 461 |  | 461 |  | 4.1 |  | 4 |  | 3.4 |  | 2380 |  | 0.68 | [8 empty] | 458.5 | 2.4 | 0.8 | 0 | 370.4 | 1.4 | 21 |  | 3171.4 | 490 | 490 | 490 | 0.9 | 0.8 | 1.1 | 500 | 0.61 | 13.1 | 18.1 |  |  |  |  | 216.91 | 0.32 | 97.67 | 0.07 |  |  |  |  | 223.31 | 0.23 | 168.04 | 0.12 | 108.98 | 0.07 | 59.07 | 0.15 |  |  | 93.65 | 0.08 | 106.94 | 0.1 | 9.27 | 0.08 | [8 empty] | 75.64 | 0.33 | 64.79 | 0.34 | 44.6 | 0.22 | 20.19 | 0.26 | [120 empty] | 59.39 | 0.07 | 59.81 | 0.11 | 59.81 | 0.1 | 59.86 | 0.08 | 59.74 | 0.08 | 59.26 | 0.06 | [32 empty] | 93.46 | 0.05 |  |  | 93.75 | 0.3 | 93.52 | 0.87 | 93.48 | 0.4 | 93.79 | 0.26 | 92.91 | 0.39 | 92.95 | 0.38 | [8 empty] | 91.2 | 0.07 | [34 empty] | 94.79 | 0.09 | 94.51 | 0.12 | 74.86 | 0.11 | 74.82 | 0.09 | 74.79 | 0.07 | 75.12 | 0.13 | 74.99 | 0.13 | 75.24 | 0.12 | 74.98 | 0.08 | 91.03 | 0.09 | 85.75 | 0.34 | 85.58 | 0.25 | 77.24 | 0.13 | 88.37 | 0.45 | 87.07 | 0.4 | 88.18 | 0.15 | 86.83 | 0.39 | 90.65 | 0.09 | 89.56 | 0.15 | 87.71 | 0.26 | 88.7 | 0.37 | 88.17 | 0.35 | 88.96 | 0.14 | 89.4 | 0.18 | 84.69 | 0.32 | 89.1 | 0.21 | 88.83 | 0.15 | 89.66 | 0.16 | 84.91 | 0.31 | [84 empty] | L-55-1ER-DM | 75.007 | 0.03 | 61.996 | 0.032 | 59.869 | 0.03 | 56.689 | 0.027 | 95.005 | 0.007 | 75.014 | 0.023 | 1219 | 4 | 1193.9 | 3.9 | 0.662 | 0.001 | -0.181 | 0.001 | 0.039 | 0.005 | 1.1361 | 0.0074 | 29.518 | 0.002 | 3157 | 9 | 400 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.78621 | 5554.0233 | 92.852 | 262.3059 | 1116.1847 | 4437.8386 | 0.0098124 | 29.7289 | 59.0828 | 14.1001 | 13.1688 | 0.013932 | 38.1706 | 0.0087763 | 27.6056 | 0.009032 | 24.1916 | 79.0561 | 64.9277 | 23.9997 | 31819.7112 | 26623.6718 | 2757 | 0.29572 | 30771.4149 | 25575.3755 | 9.747 | 0.21146 | -5.7291 | -19.9733 | 53.7266 | 31819.7112 | 18961.8057 | 1065.5002 | 11792.4054 | 31819.7112 | 100%
4 | L-95-3+20-1 | 30T0034 | L-95-3+20-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 5:25:14 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 8.4 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 8.4 |  | 7 |  | 458.8 | 1.2 | 6.3 | 0 | 19939 | 80 | 19253 | 168 | -1122 | 98 | 18816 | 103 | 5.9319 | 785 |  | 13.3 | [36 empty] | 1 Finger Open, +20% charge 95F Test, adjust code tester speed to match total static--of run L-1E3-SPWCT-SS (see row 33) | R22 8.4 LBS: OFB: Econo open 1F: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.004 | 0.031 | 62.001 | 0.027 | 95 | 0.018 | 74.997 | 0.021 | 74.51 | 0.12 | 60.11 | 0.05 | 65.56 | 0.01 | 0.046 | 0.005 | 1.1411 | 0.0077 | 19939 | 80 | -1122 | 98 | 5.932 | 0.036 | [6 empty] | 458.8 | 2.5 | 461.4 | 2.5 | 461.2 | 2.5 | 6.3 | 0 | 5.1 | 0 | 5.5 | 0 | 2812.3 | 24.6 | 1491.4 | 27.6 | 359.6 | 18.6 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.37 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.5 |  | 2390 |  | 0.69 | [8 empty] | 458.5 | 2.5 | 0.8 | 0 | 370.6 | 1.4 | 21 |  | 3181.6 | 480 | 480 | 480 | 0.8 | 0.8 | 1.1 | 500 | 0.63 | 0.133 | 18.1 |  |  |  |  | 219.04 | 0.3 | 96.57 | 0.05 |  |  |  |  | 224.84 | 0.23 | 168.89 | 0.1 | 109.47 | 0.07 | 59.42 | 0.13 |  |  | 92.75 | 0.06 | 107.63 | 0.1 | 11.06 | 0.07 | [8 empty] | 75.5 | 0.3 | 64.85 | 0.28 | 44.52 | 0.19 | 20.33 | 0.21 | [120 empty] | 59.58 | 0.05 | 59.92 | 0.07 | 60.01 | 0.07 | 59.97 | 0.06 | 59.95 | 0.05 | 59.36 | 0.05 | [32 empty] | 92.54 | 0.05 |  |  | 94.47 | 0.24 | 93.56 | 0.8 | 94.42 | 0.22 | 94.56 | 0.16 | 93.71 | 0.29 | 93.74 | 0.29 | [44 empty] | 94.76 | 0.08 | 94.58 | 0.11 | 74.84 | 0.1 | 74.79 | 0.1 | 74.77 | 0.08 | 75.11 | 0.1 | 74.97 | 0.1 | 75.24 | 0.1 | 74.96 | 0.08 | 91.45 | 0.13 | 85.97 | 0.53 | 85.84 | 0.35 | 77.23 | 0.18 | 88.58 | 0.66 | 87.36 | 0.6 | 88.49 | 0.21 | 86.99 | 0.58 | 91.06 | 0.12 | 89.91 | 0.13 | 88.13 | 0.38 | 89.18 | 0.48 | 88.39 | 0.62 | 89.35 | 0.14 | 89.78 | 0.24 | 84.99 | 0.33 | 89.49 | 0.27 | 89.15 | 0.17 | 90.03 | 0.15 | 85.25 | 0.38 | [84 empty] | L-55-1ER-DM | 75.004 | 0.031 | 62.001 | 0.027 | 60.096 | 0.019 | 56.876 | 0.023 | 95 | 0.018 | 74.997 | 0.021 | 1221.4 | 4.1 | 1196.8 | 4.1 | 0.662 | 0.001 | -0.184 | 0.002 | 0.046 | 0.005 | 1.1411 | 0.0077 | 29.549 | 0.002 | 3172 | 9 | 400 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.78446 | 5562.3372 | 93.0775 | 264.4685 | 1125.4064 | 4436.9307 | 0.0098199 | 29.7428 | 59.3115 | 14.0999 | 13.175 | 0.013918 | 38.1542 | 0.0087803 | 27.6093 | 0.0090897 | 24.3098 | 79.0798 | 64.9463 | 24.1183 | 31285.1827 | 26389.9054 | 2772 | 0.30241 | 30237.6562 | 25342.3789 | 9.5327 | 0.21388 | -5.6245 | -19.7683 | 53.9332 | 31285.1827 | 18353.0298 | 1064.8296 | 11867.3233 | 31285.1827 | 100%
4 | L-95-3+20-C | 30T0035 | L-95-3+20-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 6:35:00 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 8.4 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 8.4 |  | 7 |  | 458.7 | 1.5 | 6.3 | 0 | 22130 | 90 | 21429 | 125 | 2064 | 68 | 24196 | 119 | 7.6449 | 785 |  | 12.15 | [36 empty] | Closed damper, +20% charge 95F Test, adjust code tester speed to match total static--of run L-E3-SPWCT-SS (see row 27) | R22 8.4 LBS: OFB: Econo Fully Closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75 | 0.029 | 62.005 | 0.021 | 95.003 | 0.008 | 74.997 | 0.025 | 74.56 | 0.1 | 58.23 | 0.06 | 64.37 | 0.01 | 0.043 | 0.006 | 1.0819 | 0.0082 | 22130 | 90 | 2064 | 68 | 7.645 | 0.042 | [6 empty] | 458.7 | 2.6 | 461.5 | 2.7 | 461.3 | 2.7 | 6.3 | 0 | 5.1 | 0 | 5.5 | 0 | 2807.2 | 26.3 | 1495.1 | 29.7 | 357.7 | 19.6 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.36 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2390 |  | 0.69 | [8 empty] | 458.4 | 2.6 | 0.8 | 0 | 370.8 | 1.6 | 21 |  | 3171.8 | 480 | 480 | 480 | 0.8 | 0.8 | 1.1 | 490 | 0.6 | 0.1215 | 17.7 |  |  |  |  | 218.77 | 0.24 | 96.67 | 0.04 |  |  |  |  | 224.54 | 0.17 | 167.92 | 0.12 | 109.38 | 0.05 | 58.54 | 0.13 |  |  | 92.85 | 0.06 | 107.55 | 0.08 | 10.87 | 0.06 | [8 empty] | 74.85 | 0.18 | 63.19 | 0.26 | 44.11 | 0.11 | 19.08 | 0.21 | [120 empty] | 57.55 | 0.06 | 58.68 | 0.06 | 58.02 | 0.06 | 58.73 | 0.05 | 57.79 | 0.04 | 57.97 | 0.04 | [32 empty] | 92.68 | 0.03 |  |  | 94.26 | 0.26 | 94.53 | 0.49 | 93.97 | 0.26 | 94.23 | 0.17 | 92.89 | 0.31 | 92.91 | 0.31 | [44 empty] | 94.87 | 0.07 | 94.77 | 0.1 | 74.92 | 0.09 | 74.87 | 0.09 | 74.8 | 0.07 | 75.16 | 0.09 | 75.07 | 0.1 | 75.25 | 0.09 | 75 | 0.07 | 89.66 | 0.06 | 91.37 | 0.07 | 89.01 | 0.1 | 78.84 | 0.06 | 86.8 | 0.07 | 88.64 | 0.08 | 88.56 | 0.07 | 77.65 | 0.07 | 88.75 | 0.05 | 87.49 | 0.08 | 88.9 | 0.09 | 77.59 | 0.09 | 84.69 | 0.08 | 87.2 | 0.09 | 85.07 | 0.12 | 77.54 | 0.1 | 86.48 | 0.14 | 86.43 | 0.08 | 86.14 | 0.14 | 77.28 | 0.08 | [84 empty] | L-55-CE-DM | 75 | 0.029 | 62.005 | 0.021 | 58.138 | 0.015 | 55.154 | 0.023 | 95.003 | 0.008 | 74.997 | 0.025 | 1186.7 | 4.5 | 1168.1 | 4.5 | 0.682 | 0.002 | -0.232 | 0.002 | 0.043 | 0.006 | 1.0819 | 0.0082 | 29.587 | 0.002 | 3165 | 10 | 390 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.77655 | 5426.512 | 93.59 | 171.4398 | 729.5331 | 4696.9789 | 0.0094741 | 29.0295 | 57.3614 | 14.1 | 13.1211 | 0.013917 | 38.1542 | 0.0087839 | 27.6122 | 0.0085419 | 23.2366 | 77.7109 | 63.9819 | 23.0473 | 32462.4292 | 26502.3718 | 2775 | 0.29175 | 31450.7819 | 25490.7245 | 9.9371 | 0.20521 | -5.9822 | -20.3495 | 52.1073 | 32462.4292 | 23744.4142 | 1027.3328 | 7690.6821 | 32462.4292 | 100%
4 | L-95-3+30-1 | 30T0036 | L-95-3+30-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 8:37:26 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 9.1 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.1 |  | 7 |  | 458.4 | 1.5 | 6.3 | 0 | 20278 | 84 | 19537 | 182 | -1070 | 128 | 19208 | 130 | 6.0213 | 785 |  | 14.15 | [36 empty] | 1 Finger Open, +30% charge 95F Test, adjust code tester speed to match total static--of run L-1E3-SPWCT-SS (see row 33) | R22 9.1 LBS: OFB: Econo 1 Finger Open: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.002 | 0.042 | 61.995 | 0.037 | 95.002 | 0.011 | 75.009 | 0.02 | 74.48 | 0.13 | 60.1 | 0.06 | 65.53 | 0.02 | 0.076 | 0.005 | 1.1732 | 0.0074 | 20278 | 84 | -1070 | 128 | 6.021 | 0.044 | [6 empty] | 458.4 | 2.6 | 461.4 | 2.7 | 461.5 | 2.6 | 6.3 | 0 | 5.1 | 0 | 5.6 | 0 | 2810.7 | 26.1 | 1502.4 | 29.8 | 379.3 | 19.8 | 460 |  | 460 |  | 460 |  | 1.2 |  | 1.5 |  | 1.3 |  | 0.4 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4.1 |  | 3.5 |  | 2400 |  | 0.68 | [8 empty] | 458.1 | 2.6 | 0.8 | 0 | 371.4 | 1.5 | 21 |  | 3202.4 | 480 | 480 | 480 | 0.9 | 0.9 | 1.1 | 520 | 0.64 | 0.1415 | 18.4 |  |  |  |  | 220.75 | 0.24 | 95.78 | 0.04 |  |  |  |  | 226.1 | 0.19 | 169.97 | 0.1 | 109.88 | 0.06 | 60.09 | 0.13 |  |  | 91.89 | 0.06 | 108.19 | 0.08 | 12.41 | 0.07 | [8 empty] | 75.43 | 0.27 | 65.2 | 0.29 | 44.51 | 0.18 | 20.69 | 0.22 | [120 empty] | 59.61 | 0.07 | 60.14 | 0.08 | 60.18 | 0.09 | 60.15 | 0.07 | 60.05 | 0.07 | 59.48 | 0.05 | [32 empty] | 91.77 | 0.04 |  |  | 94.56 | 0.22 | 95.24 | 0.68 | 94.32 | 0.22 | 94.44 | 0.18 | 93.08 | 0.36 | 93.11 | 0.36 | [44 empty] | 94.81 | 0.07 | 94.54 | 0.1 | 74.91 | 0.11 | 74.86 | 0.1 | 74.8 | 0.09 | 75.21 | 0.11 | 75.07 | 0.11 | 75.31 | 0.11 | 75 | 0.09 | 91.4 | 0.1 | 86.46 | 0.2 | 86.1 | 0.16 | 77.45 | 0.12 | 88.96 | 0.26 | 87.97 | 0.3 | 88.58 | 0.11 | 86.92 | 0.28 | 90.91 | 0.09 | 89.77 | 0.15 | 87.75 | 0.18 | 89.04 | 0.24 | 88.5 | 0.3 | 89.08 | 0.16 | 89.34 | 0.19 | 83.63 | 0.26 | 89.31 | 0.24 | 89.05 | 0.15 | 89.82 | 0.17 | 83.65 | 0.27 | [84 empty] | L-55-1ER-DM | 75.002 | 0.042 | 61.995 | 0.037 | 60.078 | 0.025 | 56.829 | 0.032 | 95.002 | 0.011 | 75.009 | 0.02 | 1236.2 | 3.9 | 1216.1 | 3.9 | 0.662 | 0.002 | -0.199 | 0.002 | 0.076 | 0.005 | 1.1732 | 0.0074 | 29.657 | 0.003 | 3190 | 9 | 410 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.79649 | 5630.0118 | 94.5785 | 275.0386 | 1170.3748 | 4459.6371 | 0.0098477 | 29.8004 | 59.2815 | 14.1 | 13.1744 | 0.013928 | 38.1658 | 0.0087769 | 27.605 | 0.0090659 | 24.2795 | 79.1905 | 65.0233 | 24.0851 | 32176.923 | 26901.0176 | 2780 | 0.29487 | 31100.3894 | 25824.484 | 9.7493 | 0.2155 | -5.7152 | -19.9089 | 53.8125 | 32176.923 | 18722.5728 | 1094.2685 | 12360.0817 | 32176.923 | 100%
4 | L-95-3+30-C | 30T0037 | L-95-3+30-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 7:27:06 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 9.1 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.1 |  | 7 |  | 458.5 | 0.8 | 6.3 | 0 | 22299 | 103 | 21554 | 148 | 2084 | 104 | 24384 | 137 | 7.6679 | 785 |  | 12.26 | [36 empty] | Closed damper, +30% charge 95F Test, adjust code tester speed to match total static of--run L-E3-SPWCT-SS (see row 27) | R22 9.1 LBS: OFB: Econo Fully Closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.999 | 0.033 | 62.002 | 0.03 | 95.002 | 0.013 | 74.994 | 0.014 | 74.5 | 0.11 | 58.19 | 0.04 | 64.4 | 0.01 | 0.056 | 0.007 | 1.096 | 0.0099 | 22299 | 103 | 2084 | 104 | 7.667 | 0.046 | [6 empty] | 458.5 | 2.3 | 461.3 | 2.3 | 461.4 | 2.3 | 6.3 | 0 | 5.1 | 0 | 5.5 | 0 | 2804.8 | 23 | 1503 | 26 | 375.5 | 17.6 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.4 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.5 |  | 2390 |  | 0.69 | [8 empty] | 458.2 | 2.3 | 0.8 | 0 | 371.2 | 1.4 | 21 |  | 3172.2 | 480 | 480 | 480 | 0.8 | 0.8 | 1 | 480 | 0.62 | 0.1226 | 17.5 |  |  |  |  | 220.62 | 0.2 | 95.88 | 0.05 |  |  |  |  | 226 | 0.15 | 168.61 | 0.11 | 109.84 | 0.05 | 58.77 | 0.12 |  |  | 91.88 | 0.05 | 108.14 | 0.06 | 12.26 | 0.06 | [8 empty] | 74.8 | 0.17 | 63.35 | 0.27 | 44.09 | 0.11 | 19.26 | 0.23 | [120 empty] | 57.57 | 0.06 | 58.72 | 0.07 | 58.06 | 0.07 | 58.77 | 0.06 | 57.82 | 0.06 | 58 | 0.05 | [32 empty] | 91.76 | 0.04 |  |  | 94.23 | 0.23 | 94.89 | 0.49 | 93.85 | 0.29 | 94.12 | 0.18 | 92.82 | 0.35 | 92.84 | 0.35 | [44 empty] | 94.82 | 0.06 | 94.67 | 0.09 | 74.89 | 0.08 | 74.84 | 0.08 | 74.79 | 0.08 | 75.12 | 0.09 | 75.03 | 0.09 | 75.21 | 0.08 | 74.97 | 0.06 | 89.62 | 0.06 | 91.33 | 0.07 | 88.98 | 0.09 | 78.79 | 0.07 | 86.77 | 0.07 | 88.63 | 0.07 | 88.53 | 0.07 | 77.66 | 0.09 | 88.74 | 0.06 | 87.45 | 0.09 | 88.89 | 0.08 | 77.6 | 0.09 | 84.66 | 0.08 | 87.2 | 0.09 | 85.07 | 0.11 | 77.53 | 0.11 | 86.44 | 0.15 | 86.39 | 0.09 | 86.09 | 0.13 | 77.23 | 0.08 | [84 empty] | L-55-CE-DM | 74.999 | 0.033 | 62.002 | 0.03 | 58.128 | 0.023 | 55.14 | 0.03 | 95.002 | 0.013 | 74.994 | 0.014 | 1193.7 | 5.4 | 1176.4 | 5.4 | 0.682 | 0.002 | -0.238 | 0.002 | 0.056 | 0.007 | 1.096 | 0.0099 | 29.624 | 0.001 | 3180 | 8 | 390 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.77025 | 5458.6454 | 94.255 | 173.6423 | 738.9077 | 4719.7377 | 0.009477 | 29.037 | 57.3578 | 14.0999 | 13.1208 | 0.013915 | 38.1513 | 0.0087822 | 27.6101 | 0.0085362 | 23.228 | 77.7285 | 63.9923 | 23.0402 | 32734.4694 | 26687.2673 | 2790 | 0.29089 | 31725.0918 | 25677.8897 | 9.9764 | 0.2058 | -5.9968 | -20.3708 | 52.079 | 32734.4694 | 23920.4848 | 1025.0173 | 7788.9673 | 32734.4694 | 100%
4 | L-95-3+40-1 | 30T0038 | L-95-3+40-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 9:40:48 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 9.8 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.8 |  | 7 |  | 458.4 | 1.5 | 6.3 | 0 | 20275 | 72 | 19535 | 156 | -1073 | 97 | 19201 | 122 | 5.9872 | 785 |  | 14 | [36 empty] | 1 Finger Open, +40% charge, 95F Test, adjust code tester speed to match total static--of run L-1E3-SPWCT-SS (see row 33) | R22 9.8 LBS: OFB: Econo 1 Finger Open: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.997 | 0.024 | 62 | 0.028 | 95.001 | 0.017 | 74.993 | 0.031 | 74.47 | 0.11 | 60.13 | 0.04 | 65.59 | 0.01 | 0.081 | 0.005 | 1.1796 | 0.0073 | 20275 | 72 | -1073 | 97 | 5.988 | 0.042 | [6 empty] | 458.4 | 2.6 | 461.2 | 2.6 | 461.4 | 2.6 | 6.3 | 0 | 5.1 | 0 | 5.6 | 0 | 2814.9 | 25.6 | 1506.7 | 28.8 | 391.9 | 19.4 | 460 |  | 460 |  | 460 |  | 1.2 |  | 1.4 |  | 1.3 |  | 0.38 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.5 |  | 2410 |  | 0.69 | [8 empty] | 458.1 | 2.6 | 0.8 | 0 | 371.5 | 1.5 | 21 |  | 3212.5 | 480 | 480 | 480 | 0.9 | 0.9 | 1.2 | 520 | 0.63 | 0.14 | 18.5 |  |  |  |  | 222.69 | 0.24 | 95.39 | 0.05 |  |  |  |  | 227.78 | 0.21 | 170.64 | 0.11 | 110.41 | 0.07 | 60.23 | 0.13 |  |  | 91.22 | 0.06 | 108.81 | 0.08 | 13.42 | 0.05 | [8 empty] | 75.39 | 0.29 | 65.13 | 0.29 | 44.49 | 0.18 | 20.64 | 0.22 | [120 empty] | 59.62 | 0.05 | 60.2 | 0.07 | 60.26 | 0.07 | 60.2 | 0.06 | 60.11 | 0.06 | 59.5 | 0.05 | [32 empty] | 91.1 | 0.05 |  |  | 94.49 | 0.18 | 94.25 | 0.74 | 94.24 | 0.21 | 94.42 | 0.18 | 93.14 | 0.36 | 93.17 | 0.35 | [44 empty] | 94.82 | 0.08 | 94.54 | 0.11 | 74.92 | 0.1 | 74.86 | 0.09 | 74.78 | 0.07 | 75.23 | 0.11 | 75.09 | 0.12 | 75.32 | 0.1 | 75 | 0.08 | 91.44 | 0.06 | 86.56 | 0.09 | 86.14 | 0.09 | 77.45 | 0.08 | 89.01 | 0.11 | 88.04 | 0.15 | 88.6 | 0.06 | 86.91 | 0.18 | 90.97 | 0.07 | 89.78 | 0.13 | 87.72 | 0.09 | 89.03 | 0.2 | 88.64 | 0.09 | 89.11 | 0.12 | 89.33 | 0.13 | 83.58 | 0.2 | 89.27 | 0.18 | 89.04 | 0.12 | 89.83 | 0.14 | 83.65 | 0.21 | [84 empty] | L-55-1ER-DM | 74.997 | 0.024 | 62 | 0.028 | 60.121 | 0.014 | 56.851 | 0.023 | 95.001 | 0.017 | 74.993 | 0.031 | 1239.1 | 3.8 | 1219.8 | 3.8 | 0.662 | 0.002 | -0.201 | 0.002 | 0.081 | 0.005 | 1.1796 | 0.0073 | 29.682 | 0.002 | 3207 | 9 | 410 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.79397 | 5642.7426 | 94.8662 | 276.4158 | 1176.2472 | 4466.4954 | 0.0098513 | 29.8061 | 59.327 | 14.0999 | 13.1755 | 0.013914 | 38.1503 | 0.0087813 | 27.6087 | 0.0090689 | 24.2932 | 79.1977 | 65.0309 | 24.0995 | 32201.2261 | 26909.985 | 2797 | 0.29645 | 31125.6746 | 25834.4335 | 9.7055 | 0.21718 | -5.7067 | -19.8706 | 53.8143 | 32201.2261 | 18708.3565 | 1093.2761 | 12399.5935 | 32201.2261 | 100%
4 | L-95-3-20-1 | 30T0039 | L-95-3+20-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 5:25:14 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 5.6 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 8.4 |  | 7 |  | 458.8 | 1.4 | 6.2 | 0 | 18727 | 73 | 18062 | 125 | -2145 | 98 | 16580 | 122 | 5.3329 | 785 |  | 13.1 | [36 empty] | 1-Finger Open, -20% charge, 95F Test, adjust code tester speed to match total--static of run L-1E3-SPWCT-SS (see row 33) | R22 5.6 LBS: OFB: Econo open 1F: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.996 | 0.026 | 61.996 | 0.028 | 95.003 | 0.018 | 75.011 | 0.022 | 74.54 | 0.09 | 60.9 | 0.06 | 66.06 | 0.03 | 0.035 | 0.005 | 1.128 | 0.0067 | 18727 | 73 | -2145 | 98 | 5.332 | 0.042 | [6 empty] | 458.8 | 2.7 | 461.5 | 2.7 | 461.1 | 2.7 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2780.3 | 26.9 | 1486.2 | 30.1 | 329.1 | 20.2 | 461 |  | 462 |  | 461 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.36 | 462 |  | 461 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2310 |  | 0.68 | [8 empty] | 458.5 | 2.7 | 0.8 | 0 | 370 | 1.5 | 21 |  | 3101 | 493 | 494 | 495 | 0.8 | 0.9 | 1.1 | 490 | 0.63 | 13.1 | 18.1 |  |  |  |  | 208.45 | 0.21 | 103.5 | 0.05 |  |  |  |  | 218.73 | 0.15 | 170.5 | 0.06 | 107.52 | 0.05 | 62.98 | 0.06 |  |  | 100.72 | 0.06 | 104.17 | 0.07 | 0.67 | 0.06 | [8 empty] | 76.09 | 0.05 | 69.59 | 0.08 | 44.87 | 0.03 | 24.71 | 0.08 | [120 empty] | 60.35 | 0.04 | 61.05 | 0.06 | 61.05 | 0.07 | 61.02 | 0.06 | 60.88 | 0.05 | 60.28 | 0.04 | [32 empty] | 100.61 | 0.05 |  |  | 94.32 | 0.28 | 93.96 | 0.61 | 94.25 | 0.27 | 94.52 | 0.19 | 93.64 | 0.3 | 93.67 | 0.29 | [8 empty] | 97.46 | 0.05 | [34 empty] | 95.08 | 0.1 | 94.77 | 0.12 | 75.1 | 0.11 | 75 | 0.09 | 74.85 | 0.07 | 75.48 | 0.12 | 75.31 | 0.12 | 75.54 | 0.11 | 75.14 | 0.08 | 91.69 | 0.12 | 86.09 | 0.38 | 85.95 | 0.26 | 77.36 | 0.15 | 88.56 | 0.49 | 87.06 | 0.47 | 88.25 | 0.18 | 86.7 | 0.45 | 90.84 | 0.11 | 89.79 | 0.13 | 87.88 | 0.33 | 88.93 | 0.4 | 88.11 | 0.54 | 89.16 | 0.14 | 89.68 | 0.2 | 85.12 | 0.31 | 89.61 | 0.23 | 89.22 | 0.16 | 90 | 0.15 | 85.1 | 0.31 | [84 empty] | L-55-1ER-DM | 74.996 | 0.026 | 61.996 | 0.028 | 60.856 | 0.025 | 57.474 | 0.023 | 95.003 | 0.018 | 75.011 | 0.022 | 1216.7 | 3.6 | 1187.3 | 3.6 | 0.662 | 0.001 | -0.18 | 0.001 | 0.035 | 0.005 | 1.128 | 0.0067 | 29.463 | 0.002 | 3109 | 9 | 400 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.79062 | 5532.254 | 92.3387 | 261.5796 | 1113.0998 | 4419.1542 | 0.0098153 | 29.7309 | 60.0654 | 14.1001 | 13.1957 | 0.01393 | 38.1677 | 0.0087789 | 27.6058 | 0.0092691 | 24.6904 | 79.0515 | 64.9303 | 24.4974 | 28952.9715 | 25208.7035 | 2709 | 0.31934 | 27902.9233 | 24158.6554 | 8.9749 | 0.22382 | -5.2335 | -18.9862 | 54.5905 | 28952.9715 | 16128.786 | 1067.7413 | 11756.4442 | 28952.9715 | 100%
4 | L-95-3-20-C | 30T0040 | L-95-3+20-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/23/2014 | 6:35:00 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 5.6 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 8.4 |  | 7 |  | 458.8 | 1.4 | 6.2 | 0 | 20517 | 85 | 19846 | 139 | 976 | 76 | 21494 | 121 | 6.9335 | 785 |  | 11.8 | [36 empty] | Closed Damper, -20% charge, 95F Test, adjust code tester speed to match total--static of run L-E3-SPWCT-SS (see row 27) | R22 5.6 LBS: OFB: Econo closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.004 | 0.026 | 62 | 0.032 | 95.001 | 0.013 | 74.998 | 0.015 | 74.54 | 0.09 | 59.19 | 0.07 | 65.18 | 0.03 | 0.025 | 0.006 | 1.0595 | 0.0082 | 20517 | 85 | 976 | 76 | 6.933 | 0.042 | [6 empty] | 458.8 | 2.6 | 461.4 | 2.6 | 461.2 | 2.5 | 6.2 | 0 | 5 | 0 | 5.4 | 0 | 2770.2 | 25.7 | 1489.7 | 28.7 | 329.9 | 19.3 | 460 |  | 459 |  | 458 |  | 1.4 |  | 1.5 |  | 1.3 |  | 0.36 | 460 |  | 461 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2320 |  | 0.68 | [8 empty] | 458.5 | 2.5 | 0.8 | 0 | 369.9 | 1.5 | 21 |  | 3100.9 | 491 | 492 | 494 | 0.8 | 0.8 | 1 | 480 | 0.63 | 11.8 | 17.4 |  |  |  |  | 208.21 | 0.2 | 103.47 | 0.05 |  |  |  |  | 218.34 | 0.13 | 170.7 | 0.06 | 107.39 | 0.04 | 63.31 | 0.06 |  |  | 100.52 | 0.09 | 104.08 | 0.07 | 0.61 | 0.06 |  |  | 64.63 | 0.08 |  |  |  |  | 74.95 | 0.06 | 68.59 | 0.07 | 44.13 | 0.04 | 24.46 | 0.08 | [120 empty] | 58.47 | 0.07 | 59.81 | 0.09 | 59.02 | 0.09 | 59.82 | 0.07 | 58.75 | 0.05 | 59.01 | 0.05 | [32 empty] | 100.42 | 0.05 |  |  | 94.28 | 0.22 | 93.58 | 0.57 | 94.13 | 0.23 | 94.34 | 0.19 | 93.39 | 0.28 | 93.42 | 0.28 | [8 empty] | 97.42 | 0.06 | [34 empty] | 94.95 | 0.11 | 94.72 | 0.14 | 74.95 | 0.14 | 74.9 | 0.1 | 74.8 | 0.06 | 75.21 | 0.16 | 75.11 | 0.16 | 75.28 | 0.15 | 75.02 | 0.1 | 89.91 | 0.07 | 91.56 | 0.08 | 88.92 | 0.1 | 78.81 | 0.05 | 87.07 | 0.06 | 88.76 | 0.08 | 88.68 | 0.07 | 77.71 | 0.08 | 88.92 | 0.05 | 87.62 | 0.08 | 88.99 | 0.09 | 77.53 | 0.1 | 85.06 | 0.08 | 87.33 | 0.07 | 85.11 | 0.11 | 77.59 | 0.13 | 86.75 | 0.15 | 86.7 | 0.1 | 86.15 | 0.13 | 77.31 | 0.07 | [84 empty] | L-55-CE-DM | 75.004 | 0.026 | 62 | 0.032 | 59.131 | 0.024 | 55.889 | 0.03 | 95.001 | 0.013 | 74.998 | 0.015 | 1178.1 | 4.6 | 1151.8 | 4.5 | 0.682 | 0.002 | -0.224 | 0.002 | 0.025 | 0.006 | 1.0595 | 0.0082 | 29.447 | 0.002 | 3100 | 9 | 390 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.78726 | 5376.26 | 92.284 | 168.4578 | 716.8456 | 4659.4144 | 0.0094649 | 29.0148 | 58.3437 | 14.0999 | 13.1478 | 0.013919 | 38.1552 | 0.0087797 | 27.6086 | 0.0087344 | 23.688 | 77.6919 | 63.9621 | 23.496 | 29670.821 | 24964.9792 | 2710 | 0.31173 | 28654.7164 | 23948.8746 | 9.2435 | 0.22223 | -5.5189 | -19.3482 | 52.8154 | 29670.821 | 21078.3213 | 1032.2209 | 7560.2788 | 29670.821 | 100%
4 | L-95-3-30-1 | 30T0041 | L-95-3+30-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 2014-03-22 | 8:37:26 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 4.9 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.1 |  | 7 |  | 458.9 | 1.2 | 6.2 | 0 | 15909 | 54 | 15355 | 105 | -2393 | 81 | 13514 | 103 | 4.3891 | 785 |  | 13.3 | [36 empty] | 1 Finger Open, -30% charge, 95F Test, adjust code tester speed to match total--static of run L-1E3-SPWCT-SS (see row 33) | R22 4.9 LBS: OFB: Econo open 1F: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.998 | 0.015 | 62.001 | 0.031 | 95.003 | 0.013 | 74.996 | 0.025 | 74.59 | 0.07 | 62.89 | 0.05 | 67.67 | 0.04 | 0.028 | 0.005 | 1.1172 | 0.007 | 15909 | 54 | -2393 | 81 | 4.389 | 0.036 | [6 empty] | 458.9 | 2.5 | 461.4 | 2.6 | 461.1 | 2.6 | 6.2 | 0 | 5 | 0 | 5.4 | 0 | 2760.3 | 25.5 | 1486.3 | 28.9 | 318.6 | 19.3 | 461 |  | 460 |  | 460 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.36 | 459 |  | 460 |  | 460 |  | 4 |  | 3.9 |  | 3.4 |  | 2300 |  | 0.67 | [8 empty] | 458.5 | 2.5 | 0.8 | 0 | 369.9 | 1.5 | 21 |  | 3080.9 | 491 | 491 | 492 | 0.8 | 0.8 | 1.1 | 500 | 0.62 | 13.3 | 18 |  |  |  |  | 204.06 | 0.22 | 102.7 | 0.03 |  |  |  |  | 215.01 | 0.13 | 177.09 | 0.06 | 106.31 | 0.04 | 70.77 | 0.07 |  |  | 99.49 | 0.05 | 102.7 | 0.07 | -0.01 | 0.07 |  |  | 68.41 | 0.04 |  |  |  |  | 71.87 | 0.06 | 72.56 | 0.03 | 42.09 | 0.04 | 30.47 | 0.05 | [120 empty] | 62.27 | 0.04 | 63.09 | 0.06 | 63.01 | 0.05 | 63.08 | 0.05 | 62.84 | 0.05 | 62.27 | 0.04 | [32 empty] | 99.41 | 0.05 |  |  | 94.41 | 0.24 | 94.69 | 0.77 | 94.43 | 0.23 | 94.73 | 0.18 | 93.89 | 0.3 | 93.92 | 0.3 | [8 empty] | 96.11 | 0.04 | [34 empty] | 95.22 | 0.06 | 94.78 | 0.09 | 75.19 | 0.08 | 75.08 | 0.07 | 74.88 | 0.05 | 75.62 | 0.08 | 75.44 | 0.08 | 75.67 | 0.08 | 75.22 | 0.06 | 91.82 | 0.09 | 86.35 | 0.33 | 86.11 | 0.24 | 77.41 | 0.11 | 89.01 | 0.48 | 87.23 | 0.44 | 88.37 | 0.16 | 86.77 | 0.38 | 91.03 | 0.09 | 89.97 | 0.14 | 87.84 | 0.28 | 88.79 | 0.38 | 88.66 | 0.43 | 89.37 | 0.14 | 89.74 | 0.2 | 85.28 | 0.29 | 89.77 | 0.24 | 89.55 | 0.12 | 90.23 | 0.15 | 85.33 | 0.31 | [84 empty] | L-55-1ER-DM | 74.998 | 0.015 | 62.001 | 0.031 | 62.879 | 0.019 | 58.32 | 0.024 | 95.003 | 0.013 | 74.996 | 0.025 | 1213.3 | 3.9 | 1178.9 | 3.7 | 0.662 | 0.001 | -0.177 | 0.001 | 0.028 | 0.005 | 1.1172 | 0.007 | 29.432 | 0.001 | 3079 | 9 | 390 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.77176 | 5495.3178 | 91.6854 | 259.3896 | 1103.7892 | 4391.5286 | 0.0098131 | 29.7272 | 62.1072 | 14.1 | 13.2473 | 0.013917 | 38.1532 | 0.0087818 | 27.6094 | 0.0093055 | 25.2239 | 79.0462 | 64.9254 | 25.0355 | 25782.3706 | 22340.337 | 2689 | 0.35596 | 24764.2227 | 21322.1891 | 8.0429 | 0.31028 | -4.6917 | -16.9389 | 54.4869 | 25782.3706 | 13108.8508 | 1035.372 | 11638.1477 | 25782.3706 | 100%
4 | L-95-3-30-C | 30T0042 | L-95-3+30-C | closed | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 2014-03-22 | 7:27:06 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 4.2 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.1 |  | 7 |  | 458.7 | 1.4 | 6.2 | 0 | 18221 | 80 | 17605 | 110 | 551 | 85 | 18772 | 97 | 6.1127 | 786 |  | 12.1 | [36 empty] | Closed Damper, -30% charge, 95F Test, adjust code tester speed to match total--static of run L-E3-SPWCT-SS (see row 27) | R22 4.2 LBS: OFB: Econo closed: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.004 | 0.031 | 62.002 | 0.03 | 95.006 | 0.016 | 74.983 | 0.021 | 74.54 | 0.09 | 60.92 | 0.05 | 66.33 | 0.03 | 0.028 | 0.005 | 1.0652 | 0.007 | 18221 | 80 | 551 | 85 | 6.112 | 0.035 | [6 empty] | 458.7 | 2.6 | 461.5 | 2.6 | 461.3 | 2.6 | 6.2 | 0 | 5 | 0 | 5.4 | 0 | 2756.2 | 26.2 | 1488.2 | 29.5 | 315.1 | 19.4 | 459 |  | 458 |  | 460 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.36 | 461 |  | 460 |  | 460 |  | 4 |  | 3.9 |  | 3.3 |  | 2290 |  | 0.68 | [8 empty] | 458.4 | 2.6 | 0.8 | 0 | 370 | 1.5 | 21 |  | 3071 | 490 | 491 | 492 | 0.8 | 0.8 | 1 | 470 | 0.62 | 12.1 | 17.4 |  |  |  |  | 203.92 | 0.23 | 102.64 | 0.04 |  |  |  |  | 214.63 | 0.12 | 176.59 | 0.03 | 106.19 | 0.04 | 70.4 | 0.05 |  |  | 99.13 | 0.04 | 102.65 | 0.08 | 0.01 | 0.08 |  |  | 67.01 | 0.05 |  |  |  |  | 70.8 | 0.06 | 71.26 | 0.04 | 41.37 | 0.04 | 29.89 | 0.05 | [120 empty] | 60.33 | 0.04 | 61.69 | 0.06 | 60.87 | 0.05 | 61.69 | 0.05 | 60.63 | 0.04 | 60.87 | 0.04 | [32 empty] | 99.06 | 0.02 |  |  | 94.03 | 0.26 | 93.69 | 0.54 | 93.82 | 0.31 | 94.1 | 0.23 | 93.17 | 0.32 | 93.21 | 0.32 | [8 empty] | 96 | 0.04 | [34 empty] | 95.02 | 0.1 | 94.67 | 0.12 | 75 | 0.11 | 74.93 | 0.09 | 74.81 | 0.06 | 75.29 | 0.13 | 75.17 | 0.13 | 75.35 | 0.11 | 75.04 | 0.08 | 89.94 | 0.05 | 91.54 | 0.07 | 88.88 | 0.09 | 78.73 | 0.05 | 87.1 | 0.08 | 88.7 | 0.1 | 88.56 | 0.08 | 77.67 | 0.08 | 88.95 | 0.07 | 87.61 | 0.11 | 88.86 | 0.1 | 77.47 | 0.1 | 85.35 | 0.1 | 87.37 | 0.11 | 85.13 | 0.15 | 77.61 | 0.1 | 86.79 | 0.18 | 86.75 | 0.1 | 86.17 | 0.16 | 77.33 | 0.07 | [84 empty] | L-55-CE-DM | 75.004 | 0.031 | 62.002 | 0.03 | 60.904 | 0.022 | 56.71 | 0.024 | 95.006 | 0.016 | 74.983 | 0.021 | 1182.7 | 3.9 | 1153.4 | 3.9 | 0.682 | 0.002 | -0.224 | 0.002 | 0.028 | 0.005 | 1.0652 | 0.007 | 29.441 | 0.001 | 3071 | 9 | 390 |  | 0.14013 | 159.3838 | 13.029 | 0.217 | 0.78657 | 5378.6615 | 92.4122 | 168.4578 | 716.8454 | 4661.8161 | 0.0094638 | 29.0135 | 60.1174 | 14.0999 | 13.1932 | 0.013904 | 38.1406 | 0.008781 | 27.61 | 0.0087996 | 24.1913 | 77.6913 | 63.9603 | 23.9994 | 26968.8951 | 22685.7454 | 2681 | 0.33929 | 25953.2281 | 21670.0783 | 8.4511 | 0.29382 | -5.0141 | -17.5739 | 52.8056 | 26968.8951 | 18388.2126 | 1031.899 | 7548.7836 | 26968.8951 | 100%
4 | L-95-3-40-1 | 30T0043 | L-95-3+40-1 | 1 Finger | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 2014-03-22 | 9:40:48 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 4.2 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 9.8 |  | 7 |  | 458.6 | 1.6 | 6.1 | 0 | 11215 | 40 | 10812 | 72 | -2746 | 71 | 8467 | 73 | 2.7925 | 786 |  | 12.5 | [36 empty] | 1 Finger Open, -40% charge, 95F Test, adjust code tester speed to match total--static of run L-1E3-SPWCT-SS (see row 33) | R22 4.2 LBS: OFB: Econo open 1F: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.003 | 0.013 | 61.996 | 0.032 | 95.007 | 0.01 | 75.014 | 0.019 | 74.63 | 0.05 | 66.27 | 0.05 | 69.76 | 0.02 | 0.019 | 0.005 | 1.102 | 0.0076 | 11215 | 40 | -2746 | 71 | 2.792 | 0.025 | [6 empty] | 458.6 | 2.9 | 461.2 | 2.9 | 461.1 | 2.9 | 6.1 | 0 | 4.9 | 0 | 5.4 | 0 | 2726.8 | 29.2 | 1488.3 | 32.8 | 305.4 | 21.7 | 460 |  | 461 |  | 460 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.36 | 460 |  | 459 |  | 459 |  | 3.9 |  | 3.9 |  | 3.3 |  | 2260 |  | 0.67 | [8 empty] | 458.2 | 2.9 | 0.8 | 0 | 370.1 | 1.7 | 21 |  | 3041.1 | 492 | 491 | 491 | 0.9 | 0.8 | 1.1 | 480 | 0.62 | 12.5 | 17.9 |  |  |  |  | 198.31 | 0.22 | 101.19 | 0.04 |  |  |  |  | 208.64 | 0.17 | 188.98 | 0.03 | 104.22 | 0.06 | 84.75 | 0.06 |  |  | 97.99 | 0.04 | 100.74 | 0.07 | -0.44 | 0.06 |  |  | 70.57 | 0.03 |  |  |  |  | 62.2 | 0.05 | 75.06 | 0.03 | 35.31 | 0.04 | 39.75 | 0.04 | [120 empty] | 66 | 0.05 | 66.89 | 0.05 | 66.66 | 0.05 | 66.85 | 0.05 | 66.5 | 0.05 | 66.05 | 0.04 | [32 empty] | 97.88 | 0.04 |  |  | 94.42 | 0.3 | 93.67 | 0.77 | 94.5 | 0.26 | 94.81 | 0.18 | 93.92 | 0.28 | 93.95 | 0.28 | [8 empty] | 94.47 | 0.05 | [34 empty] | 95.26 | 0.07 | 94.73 | 0.1 | 75.25 | 0.06 | 75.12 | 0.05 | 74.95 | 0.04 | 75.72 | 0.07 | 75.51 | 0.06 | 75.76 | 0.06 | 75.27 | 0.05 | 91.98 | 0.08 | 86.43 | 0.33 | 86.21 | 0.23 | 77.52 | 0.12 | 89.19 | 0.48 | 87.25 | 0.4 | 88.41 | 0.13 | 86.85 | 0.34 | 91.21 | 0.06 | 90.16 | 0.13 | 87.91 | 0.28 | 88.87 | 0.36 | 89.1 | 0.31 | 89.63 | 0.14 | 89.9 | 0.2 | 85.3 | 0.26 | 90.02 | 0.19 | 89.79 | 0.1 | 90.38 | 0.13 | 85.18 | 0.32 | [84 empty] | L-55-1ER-DM | 75.003 | 0.013 | 61.996 | 0.032 | 66.333 | 0.019 | 59.696 | 0.03 | 95.007 | 0.01 | 75.014 | 0.019 | 1207.8 | 4.2 | 1168 | 4.1 | 0.662 | 0.001 | -0.174 | 0.002 | 0.019 | 0.005 | 1.102 | 0.0076 | 29.412 | 0.002 | 3032 | 10 | 390 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.78263 | 5434.3602 | 90.8377 | 257.1841 | 1094.3864 | 4339.9739 | 0.0098152 | 29.7333 | 65.5504 | 14.1002 | 13.3351 | 0.013931 | 38.1705 | 0.0087773 | 27.6057 | 0.0093444 | 26.1096 | 79.0616 | 64.9336 | 25.9185 | 20730.93 | 17621.9598 | 2642 | 0.43496 | 19709.889 | 16600.9187 | 6.5006 | 0.45896 | -3.8148 | -13.5112 | 54.0889 | 20730.93 | 8130.538 | 1038.3877 | 11562.0044 | 20730.93 | 100%
4 | L-95-3-10-1 | 30T0044 | L-95-3+10-1 | 1 Finger | on | N/A |  | unsealed | unsealed | [5 empty] | CUST 4 | 2014-03-22 | 4:27:17 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 4.2 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7.7 |  | 7 |  | 458.7 | 1.3 | 6.2 | 0 | 19438 | 65 | 18759 | 141 | -1437 | 127 | 17999 | 155 | 5.7542 | 785 |  | 12.9 | [36 empty] | 1 Finger Open, -10% charge, 95F Test, adjust code tester speed to match total--static of run L-1E3-SPWCT-SS (see row 33) | R22 6.3 LBS: OFB: Econo open 1F: Unsealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.004 | 0.022 | 62.001 | 0.027 | 94.995 | 0.018 | 75.004 | 0.025 | 74.57 | 0.09 | 60.42 | 0.05 | 65.8 | 0.02 | 0.034 | 0.005 | 1.1263 | 0.0068 | 19438 | 65 | -1437 | 127 | 5.754 | 0.052 | [6 empty] | 458.7 | 2.5 | 461.4 | 2.5 | 461.1 | 2.5 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2789.7 | 25.2 | 1485.3 | 27.9 | 338.5 | 18.9 | 457 |  | 459 |  | 459 |  | 1.4 |  | 1.5 |  | 1.3 |  | 0.37 | 458 |  | 458 |  | 459 |  | 4.1 |  | 4 |  | 3.4 |  | 2330 |  | 0.68 | [8 empty] | 458.3 | 2.5 | 0.8 | 0 | 370.1 | 1.5 | 21 |  | 3121.1 | 491 | 490 | 491 | 0.8 | 0.8 | 1.1 | 500 | 0.64 | 12.9 | 17.9 |  |  |  |  | 211.61 | 0.21 | 102.99 | 0.05 |  |  |  |  | 220.59 | 0.17 | 166.85 | 0.06 | 108.11 | 0.05 | 58.74 | 0.06 |  |  | 101.17 | 0.07 | 105.21 | 0.07 | 2.22 | 0.05 | [8 empty] | 76.27 | 0.08 | 65.34 | 0.1 | 44.99 | 0.05 | 20.35 | 0.09 | [120 empty] | 59.82 | 0.06 | 60.51 | 0.05 | 60.57 | 0.06 | 60.45 | 0.05 | 60.4 | 0.05 | 59.71 | 0.04 | [32 empty] | 101.07 | 0.06 |  |  | 94.18 | 0.24 | 94.26 | 0.75 | 94.01 | 0.29 | 94.31 | 0.22 | 93.49 | 0.32 | 93.52 | 0.32 | [8 empty] | 98.06 | 0.05 | [34 empty] | 95.14 | 0.08 | 94.8 | 0.1 | 75.14 | 0.08 | 75.02 | 0.07 | 74.85 | 0.07 | 75.52 | 0.09 | 75.37 | 0.09 | 75.55 | 0.08 | 75.15 | 0.06 | 91.45 | 0.15 | 86.14 | 0.33 | 85.95 | 0.25 | 77.36 | 0.13 | 88.55 | 0.47 | 86.99 | 0.43 | 88.08 | 0.17 | 86.7 | 0.4 | 90.57 | 0.13 | 89.56 | 0.14 | 87.49 | 0.27 | 88.54 | 0.37 | 88.08 | 0.45 | 88.89 | 0.14 | 89.39 | 0.19 | 84.93 | 0.31 | 89.34 | 0.23 | 89.08 | 0.14 | 89.84 | 0.15 | 85.18 | 0.31 | [84 empty] | L-55-1ER-DM | 75.004 | 0.022 | 62.001 | 0.027 | 60.347 | 0.034 | 57.075 | 0.035 | 94.995 | 0.018 | 75.004 | 0.025 | 1215.2 | 3.7 | 1187.1 | 3.6 | 0.662 | 0.001 | -0.179 | 0.002 | 0.034 | 0.005 | 1.1263 | 0.0068 | 29.477 | 0.001 | 3128 | 9 | 400 |  | 0.21419 | 251.4581 | 13.03 | 0.18 | 0.79081 | 5531.2348 | 92.3231 | 260.8498 | 1110.0129 | 4421.222 | 0.0098129 | 29.7268 | 59.5562 | 14.0998 | 13.1819 | 0.013925 | 38.1611 | 0.0087803 | 27.6093 | 0.0091494 | 24.4359 | 79.0458 | 64.9249 | 24.2429 | 30332.7492 | 25872.3689 | 2728 | 0.30695 | 29282.6479 | 24822.2677 | 9.3615 | 0.21694 | -5.4839 | -19.4896 | 54.1569 | 30332.7492 | 17552.5745 | 1067.5628 | 11712.6119 | 30332.7492 | 100%
4 | L-55-T1ER-DM | 30T0028 | L-55-T1ER-DM | 1 Finger | off | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 9:08:55 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.3 | 0.3 | 1.6 | 0 | 5422 | 21 | 5195 | 51 | 2157 | 54 | 7581 | 64 | 16.2682 | 785 |  | 11.9 | [36 empty] | Econo 1F-open, tape around damper perimeter frame gaps, no compressor, 55/51 ambient, 60% inlet 54% outlet Meriam, adjust code tester speed to match total static of run L-55-T1E-DM-SPWCT-SSR--ambient, 60% inlet 54% outlet Meriam, adjust code tester speed- | R22 7 LBS: OFB: Econo 1 Finger Opened: Sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.006 | 0.015 | 62.001 | 0.027 | 54.999 | 0.014 | 50.998 | 0.021 | 74.7 | 0.03 | 70.69 | 0.03 | 72.96 | 0.03 | 0.013 | 0.005 | 1.0743 | 0.0075 | 5422 | 21 | 2157 | 54 | 16.255 | 0.228 | [6 empty] | 458.3 | 1.8 | 463.4 | 1.8 | 461.7 | 1.8 | 1.6 | 0 | 1.3 | 0 | 1.6 | 0 | 609 | 6.7 | 555.4 | 7.2 | -10 | 0 | 463 |  | 462 |  | 458 |  | 1.3 |  | 1.5 |  | 1.3 |  | 0.35 | [29 empty] | 21 |  |  | 478 | 478 | 478 | 0.9 | 0.8 | 1 | 0.45 | 0.61 | 11.9 | 17.3 | [164 empty] | 70.8 | 0.04 | 71.93 | 0.07 | 71.02 | 0.07 | 71.55 | 0.06 | 70.85 | 0.03 | 71.38 | 0.04 | [32 empty] | 73.14 | 0.03 |  |  | 54.52 | 0.07 | 54.36 | 0.06 | 54.23 | 0.08 | 53.98 | 0.07 | 54.07 | 0.11 | 54.09 | 0.11 | [8 empty] | 74.15 | 0.03 | [34 empty] | 54.98 | 0.08 | 54.59 | 0.09 | 74.29 | 0.07 | 74.47 | 0.06 | 74.36 | 0.04 | 73.96 | 0.09 | 74.09 | 0.09 | 73.94 | 0.08 | 74.29 | 0.06 | 61.31 | 0.08 | 63.16 | 0.26 | 66.01 | 0.08 | 73.03 | 0.05 | 64.72 | 0.08 | 63.87 | 0.13 | 65.59 | 0.09 | 64.19 | 0.13 | 63.5 | 0.07 | 64.74 | 0.1 | 63.88 | 0.15 | 64.06 | 0.17 | 65.43 | 0.09 | 65.17 | 0.09 | 63.39 | 0.08 | 63.32 | 0.25 | 63.96 | 0.14 | 65.38 | 0.13 | 63.22 | 0.09 | 63.81 | 0.13 | [84 empty] | Economizer test | 75.006 | 0.015 | 62.001 | 0.027 | 70.817 | 0.007 | 59.939 | 0.023 | 54.999 | 0.014 | 50.998 | 0.021 | 1196.8 | 4.2 | 1149.7 | 4.1 | 0.678 | 0.001 | -0.198 | 0.002 | 0.013 | 0.005 | 1.0743 | 0.0075 | 29.358 | 0.001 | 466 | 6 | 380 |  | 0.17089 | 196.4724 | 13.029 | 0.198 | 0.76755 | 5342.2271 | 91.5755 | 196.476 | 904.7613 | 4437.4659 | 0.0084751 | 26.4521 | 70.0494 | 13.0295 | 13.4416 | 0.0069805 | 20.7765 | 0.0087799 | 27.6093 | 0.0084376 | 26.2137 | 71.6268 | 60.2993 | 26.0266
4 | L-55-T2ER-DM | 30T0029 | L-55-T2ER-DM | 2 Finger | off | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 12:52:36 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.1 | 0.6 | 1.5 | 0 | 7197 | 40 | 6931 | 92 | 2920 | 68 | 10120 | 94 | 21.3953 | 786 |  | 12.82 | [36 empty] | Econo 2F-open, tape around damper perimeter frame gaps, no compressor,--55/51, 60% inlet 54% outlet Meriam, ambient adjust code tester speed to match--total static of run L-55-T2E-DM-SPWCT-SSR | R22 7 LBS: OFB: Econo 2 Finger Opened: Sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.978 | 0.03 | 61.999 | 0.024 | 54.997 | 0.014 | 51.002 | 0.023 | 74.65 | 0.05 | 69.43 | 0.03 | 72.28 | 0.11 | 0.012 | 0.006 | 1.1235 | 0.0089 | 7197 | 40 | 2920 | 68 | 21.391 | 0.303 | [6 empty] | 458.1 | 2 | 462.7 | 2 | 461.9 | 2 | 1.5 | 0 | 1.3 | 0 | 1.6 | 0 | 607.2 | 7.3 | 558.8 | 8.4 | -10 | 0 | 463 |  | 462 |  | 458 |  | 1.7 |  | 1.5 |  | 1.3 |  | 0.36 | [29 empty] | 21 |  |  | 484 | 484 | 485 | 0.9 | 0.9 | 1 | 480 | 0.62 | 12.82 | 18 | [164 empty] | 69.42 | 0.04 | 70.93 | 0.05 | 69.58 | 0.05 | 70.59 | 0.05 | 69.37 | 0.05 | 70.39 | 0.03 | [32 empty] | 73.3 | 0.04 |  |  | 54.77 | 0.07 | 54.59 | 0.05 | 54.54 | 0.08 | 54.2 | 0.07 | 54.36 | 0.11 | 54.38 | 0.11 | [8 empty] | 74.06 | 0.04 | [34 empty] | 54.99 | 0.06 | 54.8 | 0.08 | 73.98 | 0.06 | 74.27 | 0.04 | 74.19 | 0.03 | 73.24 | 0.09 | 73.64 | 0.07 | 73.15 | 0.09 | 73.91 | 0.06 | 61.76 | 0.06 | 69.94 | 0.06 | 66.12 | 0.08 | 73.57 | 0.07 | 60.71 | 0.06 | 68.23 | 0.06 | 64.05 | 0.07 | 65.77 | 0.22 | 59.82 | 0.05 | 61.44 | 0.1 | 63.96 | 0.1 | 60.41 | 0.15 | 61 | 0.06 | 60.8 | 0.1 | 61.63 | 0.09 | 59.67 | 0.14 | 60.65 | 0.11 | 60.03 | 0.12 | 61.54 | 0.09 | 60.21 | 0.1 | [84 empty] | Economizer test | 74.978 | 0.03 | 61.999 | 0.024 | 69.552 | 0.024 | 59.287 | 0.021 | 54.997 | 0.014 | 51.002 | 0.023 | 1223 | 4.8 | 1177.1 | 4.8 | 0.673 | 0.001 | -0.169 | 0.001 | 0.012 | 0.006 | 1.1235 | 0.0089 | 29.369 | 0.001 | 473 | 6 | 390 |  | 0.23302 | 274.2895 | 13.029 | 0.169 | 0.77137 | 5472.588 | 93.0665 | 274.2941 | 1263.1123 | 4209.4758 | 0.0083692 | 26.032 | 68.7806 | 13.0294 | 13.4086 | 0.0069831 | 20.7789 | 0.0087852 | 27.6082 | 0.0083266 | 25.7842 | 70.3779 | 59.6662 | 25.5962
4 | L-55-T3ER-DM | 30T0030 | L-55-T3ER-DM | 3 Finger | off | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 14:09:30 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.3 | 1 | 1.6 | 0 | 8960 | 68 | 8665 | 101 | 3712 | 75 | 12676 | 93 | 26.4083 | 785 |  | 13.3 | [36 empty] | Econo 3F-open, tape around damper perimeter frame gaps, no compressor, 55/51--ambient, 60% inlet 54% outlet Meriam, adjust code tester speed to match total--static of run L-55-T3E-DM-SPWCT-SSR | R22 7 LBS: OFB: Econo 3 Finger Opened: Sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.966 | 0.039 | 61.999 | 0.029 | 55.011 | 0.013 | 51.004 | 0.021 | 74.69 | 0.06 | 68.31 | 0.04 | 71.46 | 0.1 | 0.009 | 0.006 | 1.1732 | 0.0065 | 8960 | 68 | 3712 | 75 | 26.404 | 0.367 | [6 empty] | 458.3 | 2.2 | 462.8 | 2.2 | 461.8 | 2.2 | 1.6 | 0 | 1.3 | 0 | 1.6 | 0 | 611.6 | 7.8 | 558.4 | 8.9 | -10 | 0 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.5 |  | 1.3 |  | 0.36 | [29 empty] | 21 |  |  | 484 | 484 | 482 | 0.9 | 0.9 | 1 | 500 | 0.62 | 13.3 | 18.3 | [164 empty] | 68.22 | 0.06 | 70.31 | 0.06 | 68.6 | 0.07 | 69.92 | 0.06 | 68.25 | 0.06 | 69.54 | 0.06 | [32 empty] | 72.79 | 0.05 |  |  | 54.97 | 0.1 | 54.77 | 0.08 | 54.77 | 0.11 | 54.53 | 0.09 | 54.7 | 0.12 | 54.72 | 0.12 | [8 empty] | 73.83 | 0.04 | [34 empty] | 55.44 | 0.08 | 55.35 | 0.11 | 74.24 | 0.06 | 74.46 | 0.05 | 74.2 | 0.06 | 73.54 | 0.1 | 73.92 | 0.06 | 73.5 | 0.11 | 74.05 | 0.06 | 61.2 | 0.1 | 69.59 | 0.09 | 65.15 | 0.12 | 72.71 | 0.13 | 60.51 | 0.14 | 67.26 | 0.06 | 62.81 | 0.11 | 63.26 | 0.22 | 59.1 | 0.07 | 61.46 | 0.17 | 61.73 | 0.13 | 60.34 | 0.16 | 60.25 | 0.08 | 59.6 | 0.13 | 59.67 | 0.13 | 60.43 | 0.15 | 60.24 | 0.13 | 59.35 | 0.14 | 61.02 | 0.11 | 59.63 | 0.13 | [84 empty] | Economizer test | 74.966 | 0.039 | 61.999 | 0.029 | 68.365 | 0.028 | 58.655 | 0.029 | 55.011 | 0.013 | 51.004 | 0.021 | 1249.3 | 3.5 | 1203.9 | 3.4 | 0.667 | 0.001 | -0.137 | 0.004 | 0.009 | 0.006 | 1.1732 | 0.0065 | 29.354 | 0.002 | 480 | 6 | 400 |  | 0.29171 | 351.1853 | 13.03 | 0.137 | 0.77554 | 5603.2128 | 94.3368 | 351.1823 | 1617.1371 | 3986.0757 | 0.0082664 | 25.6376 | 67.5895 | 13.0298 | 13.3777 | 0.0069809 | 20.7799 | 0.008788 | 27.6084 | 0.0082148 | 25.3728 | 69.2203 | 59.0647 | 25.1839
4 | L-55-TCE-DM | 30T0031 | L-55-TCE-DM | closed | off | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 7:48:38 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.2 | 0.4 | 1.5 | 0 | 2469 | 24 | 2340 | 47 | 965 | 43 | 3435 | 56 | 7.5828 | 786 |  | 10.5 | [36 empty] | Econo closed, tape around damper perimeter frame gaps, no compressor, 55/51--ambient, 60% inlet 54% outlet Meriam, adjust code tester speed to match total--static of run L-55-TCE-DM-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: Sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.984 | 0.018 | 61.998 | 0.024 | 54.992 | 0.013 | 51.001 | 0.017 | 74.65 | 0.04 | 72.76 | 0.02 | 74.4 | 0.04 | 0.008 | 0.006 | 0.9925 | 0.0077 | 2469 | 24 | 965 | 43 | 7.591 | 0.146 | [6 empty] | 458.2 | 1.9 | 463.4 | 1.9 | 461.8 | 1.9 | 1.5 | 0 | 1.3 | 0 | 1.6 | 0 | 601.2 | 6.9 | 555.5 | 7.8 | -10 | 0 | 461 |  | 461 |  | 458 |  | 1.4 |  | 1.5 |  | 1.3 |  | 0.34 | [29 empty] | 21 |  |  | 480 | 482 | 482 | 0.8 | 0.7 | 0.9 | 420 | 0.6 | 10.5 | 17 | [164 empty] | 72.9 | 0.03 | 73.56 | 0.03 | 73.45 | 0.02 | 73.17 | 0.03 | 73.26 | 0.03 | 73.12 | 0.03 | [32 empty] | 73.62 | 0.02 |  |  | 54.19 | 0.05 | 54.11 | 0.04 | 53.85 | 0.06 | 53.69 | 0.04 | 53.71 | 0.06 | 53.74 | 0.06 | [8 empty] | 74.14 | 0.02 | [34 empty] | 54.86 | 0.06 | 54.29 | 0.06 | 74.27 | 0.05 | 74.45 | 0.03 | 74.38 | 0.03 | 74.01 | 0.04 | 74.1 | 0.05 | 73.99 | 0.04 | 74.28 | 0.04 | 62.5 | 0.08 | 60.91 | 0.07 | 66.65 | 0.08 | 72.94 | 0.04 | 66.71 | 0.04 | 65.66 | 0.08 | 66.48 | 0.08 | 74 | 0.05 | 65.57 | 0.03 | 68.65 | 0.04 | 69.14 | 0.05 | 74.28 | 0.05 | 68.98 | 0.04 | 67.53 | 0.05 | 66.46 | 0.05 | 73.46 | 0.05 | 66.12 | 0.06 | 68.11 | 0.05 | 66.91 | 0.04 | 72.3 | 0.07 | [84 empty] | Economizer test | 74.984 | 0.018 | 61.998 | 0.024 | 72.993 | 0.009 | 61.056 | 0.026 | 54.992 | 0.013 | 51.001 | 0.017 | 1152 | 4.5 | 1102.4 | 4.4 | 0.69 | 0.001 | -0.245 | 0.002 | 0.008 | 0.006 | 0.9925 | 0.0077 | 29.331 | 0.001 | 453 | 6 | 360 |  | 0.062075 | 68.4313 | 13.029 | 0.245 | 0.75139 | 5120.6333 | 89.3621 | 68.4321 | 315.1299 | 4805.5034 | 0.0086724 | 27.1872 | 72.2416 | 13.0293 | 13.4983 | 0.0069838 | 20.7784 | 0.0087831 | 27.6074 | 0.0086382 | 26.9634 | 73.7575 | 61.3868 | 26.7802
4 | L-55-TOER-DM | 30T0032 | L-55-TOER-DM | open | off | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/22/2014 | 18:23:36 | 10 Ton | 0:20:00 | 75/62 - 55/51 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 55 | 51 | 7 |  | 7 |  | 458.1 | 1 | 1.6 | 0 | 17063 | 115 | 16508 | 157 | 7241 | 145 | 24311 | 209 | 50.2293 | 785 |  | 13.1 | [36 empty] | Econo fully open, tape around damper perimeter frame gaps, no compressor, 55/51 ambient,--60% inlet 54% outlet Meriam, adjust code tester speed to match total static of run L-55-TOE-DM-SPWCT-SSR | R22 7 LBS: OFB: Econo Fully Opened: Sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.987 | 0.031 | 61.997 | 0.027 | 54.994 | 0.013 | 51.006 | 0.022 | 74.59 | 0.07 | 62.49 | 0.04 | 67.4 | 0.05 | 0.008 | 0.007 | 1.1656 | 0.0146 | 17063 | 115 | 7241 | 145 | 50.211 | 0.689 | [243 empty] | 62.47 | 0.05 | 64.74 | 0.08 | 62.95 | 0.09 | 64.29 | 0.07 | 62.53 | 0.07 | 63.85 | 0.06 | [32 empty] | 61.84 | 0.04 |  |  | 55.16 | 0.1 | 55.01 | 0.08 | 55.15 | 0.12 | 54.82 | 0.09 | 55.06 | 0.15 | 55.08 | 0.15 | [8 empty] | 68.86 | 0.05 | [34 empty] | 55.69 | 0.09 | 56.06 | 0.14 | 74.35 | 0.07 | 74.52 | 0.05 | 74.27 | 0.05 | 74.17 | 0.08 | 74.22 | 0.08 | 74.09 | 0.07 | 74.22 | 0.05 | 60.31 | 0.09 | 58.63 | 0.07 | 57.2 | 0.09 | 57.32 | 0.07 | 56.71 | 0.07 | 56.73 | 0.1 | 56.86 | 0.13 | 57.23 | 0.1 | 57.2 | 0.06 | 56.74 | 0.09 | 56.73 | 0.15 | 58.09 | 0.1 | 57.76 | 0.09 | 57.02 | 0.13 | 57.27 | 0.16 | 58.8 | 0.26 | 56.8 | 0.17 | 56.84 | 0.12 | 56.92 | 0.14 | 57.77 | 0.14 | [84 empty] | Economizer test | 74.987 | 0.031 | 61.997 | 0.027 | 62.466 | 0.021 | 55.373 | 0.026 | 54.994 | 0.013 | 51.006 | 0.022 | 1240.3 | 7.8 | 1205.6 | 7.5 | 0.537 | 0.002 | -0.012 | 0.006 | 0.008 | 0.007 | 1.1656 | 0.0146 | 29.352 | 0.002 | 484 | 6 | 400 |  | 0.58525 | 705.5832 | 13.029 | 0.012 | 0.81836 | 5627.5962 | 76.0576 | 705.5937 | 3249.2415 | 2378.3547 | 0.0077449 | 23.6658 | 61.6476 | 13.0294 | 13.2238 | 0.0069859 | 20.7812 | 0.0087817 | 27.6067 | 0.0076473 | 23.3177 | 63.4595 | 55.944 | 23.1185
4 | L-75629575-T1E3 | 30T0019 | L-75629575-T1E3 | 1 Finger | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 11:42:28 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.6 | 1.5 | 6.2 | 0 | 20641 | 75 | 19962 | 109 | 899 | 74 | 21540 | 92 | 6.8906 | 786 |  | 11.7 | [36 empty] | Factory charge, 3 turns, Econo 1 Finger open damper, tape around damper--perimeter frame gaps, unsealed cab, 60% inlet 54% outlet Meriam, adust code--tester speed to match total static of run L-T1E3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.007 | 0.018 | 62.006 | 0.024 | 95.002 | 0.006 | 74.998 | 0.018 | 74.64 | 0.07 | 59.16 | 0.04 | 65.32 | 0.07 | 0.017 | 0.005 | 1.0621 | 0.0072 | 20641 | 75 | 899 | 74 | 6.891 | 0.034 | [6 empty] | 458.6 | 2.6 | 461.5 | 2.6 | 461.4 | 2.6 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2782.4 | 25.6 | 1498.4 | 29.8 | 343.5 | 19.5 | 460 |  | 460 |  | 460 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.36 | 460 |  | 460 |  | 460 |  | 4 |  | 4 |  | 3.4 |  | 2350 |  | 0.68 | [8 empty] | 458.2 | 2.6 | 0.8 | 0 | 367.1 | 1.5 | 21 |  | 3128.1 | 480 | 480 | 480 | 0.9 | 0.8 | 0.9 | 460 | 0.62 | 11.7 | 17.5 |  |  |  |  | 214.69 | 0.2 | 99.88 | 0.05 |  |  |  |  | 221.84 | 0.13 | 167.05 | 0.07 | 108.47 | 0.04 | 58.58 | 0.08 |  |  | 97.16 | 0.06 | 106.18 | 0.06 | 6.3 | 0.06 |  |  | 59.98 | 0.31 |  |  |  |  | 75.21 | 0.14 | 64.07 | 0.17 | 44.23 | 0.09 | 19.84 | 0.14 | [120 empty] | 58.43 | 0.05 | 59.26 | 0.06 | 59.08 | 0.05 | 59.29 | 0.05 | 58.91 | 0.05 | 58.55 | 0.04 | [32 empty] | 96.92 | 0.06 |  |  | 95.07 | 0.12 | 95.1 | 0.1 | 94.83 | 0.13 | 95.05 | 0.14 | 94.84 | 0.17 | 94.85 | 0.17 | [8 empty] | 93.18 | 0.06 | [34 empty] | 94.76 | 0.05 | 94.62 | 0.09 | 75.03 | 0.07 | 74.96 | 0.07 | 74.85 | 0.05 | 75.3 | 0.08 | 75.2 | 0.08 | 75.36 | 0.08 | 75.08 | 0.06 | 88.95 | 0.05 | 81.78 | 0.09 | 84.19 | 0.08 | 76.67 | 0.04 | 81.69 | 0.06 | 82.86 | 0.07 | 85.36 | 0.06 | 86.16 | 0.15 | 84.38 | 0.04 | 84.11 | 0.07 | 85.17 | 0.08 | 86.4 | 0.13 | 81.47 | 0.06 | 82.35 | 0.06 | 85.16 | 0.06 | 84.63 | 0.22 | 83.89 | 0.09 | 81.63 | 0.08 | 84.61 | 0.07 | 85.02 | 0.12 | [84 empty] | L-55-T1ER-DM | 75.007 | 0.018 | 62.006 | 0.024 | 59.004 | 0.013 | 55.898 | 0.021 | 95.002 | 0.006 | 74.998 | 0.018 | 1184.1 | 4 | 1148.7 | 4 | 0.669 | 0.001 | -0.201 | 0.002 | 0.017 | 0.005 | 1.0621 | 0.0072 | 29.231 | 0.001 | 3126 | 9 | 390 |  | 0.17089 | 196.4724 | 13.029 | 0.198 | 0.78837 | 5404.8507 | 90.2813 | 205.9303 | 876.3026 | 4528.5482 | 0.0096156 | 29.3221 | 58.2156 | 14.0999 | 13.1449 | 0.013919 | 38.1552 | 0.0087829 | 27.6129 | 0.0087697 | 23.6954 | 78.2742 | 64.38 | 23.5031 | 31451.0051 | 26019.2496 | 2736 | 0.29691 | 30428.0653 | 24996.3097 | 9.7339 | 0.21033 | -5.819 | -20.0586 | 52.8729 | 31451.0051 | 21173.5389 | 1039.2314 | 9238.2348 | 31451.0051 | 100%
4 | L-75629575-T2E3-1 | 30T0020 | L-75629575-T2E3-1 | 2 Finger | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 17:38:27 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.5 | 1.3 | 6.2 | 0 | 19208 | 56 | 18576 | 104 | -1115 | 81 | 18092 | 95 | 5.7894 | 786 |  | 12.28 | [36 empty] | Factory charge, 3 turns, Econo 2 Fingers open damper, tape around damper--perimeter frame gaps, unsealed cab, cab, 60% inlet 54% outlet Meriam, adust--code tester speed to match total static of run L-T2E3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.992 | 0.014 | 61.998 | 0.026 | 95 | 0.007 | 74.996 | 0.017 | 74.6 | 0.07 | 60.28 | 0.04 | 66.01 | 0.05 | 0.012 | 0.004 | 1.0885 | 0.0061 | 19208 | 56 | -1115 | 81 | 5.789 | 0.035 | [6 empty] | 458.5 | 2.6 | 461.1 | 2.6 | 461.5 | 2.6 | 6.2 | 0 | 5.1 | 0 | 5.5 | 0 | 2765.2 | 25.3 | 1508.5 | 28.9 | 360.1 | 19.2 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.36 | 460 |  | 460 |  | 460 |  | 4 |  | 4 |  | 3.5 |  | 2360 |  | 0.68 | [8 empty] | 458.1 | 2.5 | 0.8 | 0 | 366.2 | 1.5 | 21 |  | 3127.2 | 480 | 480 | 480 | 0.9 | 1 | 0.8 | 480 | 0.63 | 12.28 | 17.6 |  |  |  |  | 214.86 | 0.21 | 99.68 | 0.05 |  |  |  |  | 222.02 | 0.13 | 167.8 | 0.06 | 108.51 | 0.04 | 59.28 | 0.08 |  |  | 96.38 | 0.06 | 106.22 | 0.07 | 6.54 | 0.07 |  |  | 60.97 | 0.31 |  |  |  |  | 75.63 | 0.15 | 65.11 | 0.15 | 44.48 | 0.09 | 20.64 | 0.11 | [120 empty] | 59.71 | 0.06 | 59.96 | 0.07 | 60.2 | 0.07 | 60 | 0.06 | 60.19 | 0.04 | 59.41 | 0.03 | [32 empty] | 96.2 | 0.04 |  |  | 94.52 | 0.14 | 94.64 | 0.12 | 94.33 | 0.15 | 94.6 | 0.15 | 94.39 | 0.2 | 94.42 | 0.2 | [8 empty] | 92.91 | 0.06 | [34 empty] | 94.6 | 0.06 | 94.34 | 0.08 | 74.91 | 0.06 | 74.87 | 0.06 | 74.86 | 0.06 | 75.17 | 0.07 | 75.05 | 0.07 | 75.27 | 0.07 | 75.02 | 0.05 | 85.02 | 0.07 | 79.6 | 0.07 | 83.54 | 0.09 | 76.13 | 0.06 | 83.11 | 0.06 | 81.3 | 0.09 | 86.37 | 0.11 | 86.1 | 0.24 | 88.06 | 0.09 | 86.32 | 0.1 | 85.6 | 0.12 | 90.34 | 0.19 | 84.95 | 0.13 | 87.44 | 0.18 | 87.75 | 0.14 | 86.75 | 0.27 | 87.38 | 0.19 | 86.78 | 0.19 | 86.69 | 0.14 | 88.13 | 0.22 | [84 empty] | L-55-T2ER-DM | 74.992 | 0.014 | 61.998 | 0.026 | 60.19 | 0.016 | 56.97 | 0.022 | 95 | 0.007 | 74.996 | 0.017 | 1201.8 | 3.4 | 1159.7 | 3.3 | 0.658 | 0.001 | -0.169 | 0.002 | 0.012 | 0.004 | 1.0885 | 0.0061 | 29.135 | 0.001 | 3125 | 9 | 380 |  | 0.23302 | 274.2895 | 13.029 | 0.169 | 0.75436 | 5471.9776 | 89.6472 | 285.3391 | 1214.2191 | 4257.7585 | 0.0099209 | 29.9474 | 59.4356 | 14.0999 | 13.1777 | 0.013917 | 38.1533 | 0.0087812 | 27.6073 | 0.0091237 | 24.3696 | 79.464 | 65.2191 | 24.1855 | 31528.9391 | 26302.688 | 2745 | 0.29715 | 30537.965 | 25311.7138 | 9.7721 | 0.21412 | -5.7619 | -20.0283 | 53.9787 | 31528.9391 | 17716.4471 | 1007.4054 | 12805.0866 | 31528.9391 | 100%
4 | L-75629575-T3E3 | 30T0021 | L-75629575-T3E3 | 3 Finger | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 19:44:05 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.7 | 1.3 | 6.2 | 0 | 17862 | 50 | 17229 | 111 | -3355 | 66 | 14505 | 82 | 4.6357 | 786 |  | 13.22 | [36 empty] | Factory charge, 3 turns, Econo 3 Fingers open damper, tape around damper perimeter frame gaps,--unsealed cab, cab, 60% inlet 54% outlet Meriam, adust code tester speed to match total static of run--L-T3E3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.997 | 0.018 | 62 | 0.022 | 95.003 | 0.007 | 75.001 | 0.011 | 74.54 | 0.08 | 61.45 | 0.04 | 66.55 | 0.02 | 0.014 | 0.004 | 1.1323 | 0.0059 | 17862 | 50 | -3355 | 66 | 4.635 | 0.028 | [6 empty] | 458.7 | 2.5 | 461 | 2.5 | 461.3 | 2.5 | 6.2 | 0 | 5.1 | 0 | 5.5 | 0 | 2774.4 | 25.4 | 1504.4 | 28.3 | 354.8 | 19.2 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.35 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.5 |  | 2360 |  | 0.69 | [8 empty] | 458.4 | 2.5 | 0.8 | 0 | 366.6 | 1.5 | 21 |  | 3137.6 | 480 | 480 | 480 | 0.8 | 0.9 | 0.9 | 500 | 0.63 | 13.22 | 18.1 |  |  |  |  | 214.99 | 0.21 | 99.53 | 0.05 |  |  |  |  | 222.17 | 0.14 | 168.09 | 0.06 | 108.57 | 0.04 | 59.52 | 0.07 |  |  | 95.91 | 0.06 | 106.26 | 0.07 | 6.73 | 0.07 |  |  | 61.87 | 0.32 |  |  |  |  | 76.3 | 0.14 | 66.03 | 0.14 | 44.92 | 0.09 | 21.11 | 0.1 | [120 empty] | 60.94 | 0.07 | 61.01 | 0.06 | 61.6 | 0.06 | 61.02 | 0.05 | 61.61 | 0.05 | 60.44 | 0.03 | [32 empty] | 95.82 | 0.04 |  |  | 94.14 | 0.17 | 94.38 | 0.13 | 94.17 | 0.18 | 94.52 | 0.14 | 94.35 | 0.18 | 94.38 | 0.18 | [44 empty] | 94.62 | 0.05 | 94.25 | 0.1 | 74.96 | 0.06 | 74.89 | 0.06 | 74.88 | 0.06 | 75.29 | 0.07 | 75.13 | 0.07 | 75.38 | 0.07 | 75.07 | 0.06 | 85.79 | 0.05 | 81.09 | 0.07 | 85.07 | 0.08 | 77.74 | 0.09 | 83.69 | 0.06 | 82.49 | 0.07 | 87.47 | 0.12 | 88.81 | 0.26 | 88.94 | 0.07 | 86.9 | 0.1 | 86.98 | 0.12 | 89.88 | 0.25 | 85.3 | 0.1 | 88.87 | 0.16 | 89.62 | 0.13 | 84.84 | 0.25 | 88.59 | 0.17 | 88 | 0.16 | 88.25 | 0.12 | 88.71 | 0.21 | [84 empty] | L-55-T3ER-DM | 74.997 | 0.018 | 62 | 0.022 | 61.432 | 0.013 | 58.073 | 0.017 | 95.003 | 0.007 | 75.001 | 0.011 | 1225.9 | 3.2 | 1182.6 | 3.1 | 0.648 | 0.001 | -0.141 | 0.002 | 0.014 | 0.004 | 1.1323 | 0.0059 | 29.173 | 0.002 | 3129 | 9 | 390 |  | 0.29171 | 351.1853 | 13.03 | 0.137 | 0.76603 | 5567.172 | 90.0281 | 370.6148 | 1577.0853 | 3990.0867 | 0.010237 | 30.5971 | 60.666 | 14.1 | 13.2121 | 0.013921 | 38.158 | 0.0087813 | 27.6087 | 0.009497 | 25.079 | 80.7023 | 66.0753 | 24.8919 | 31761.9777 | 26770.9137 | 2739 | 0.29432 | 30738.1735 | 25747.1095 | 9.8236 | 0.21693 | -5.7052 | -20.0363 | 55.1155 | 31761.9777 | 14083.2589 | 1041.4865 | 16637.2323 | 31761.9777 | 100%
4 | L-75629575-TE3 | 30T0022 | L-75629575-TE3 | closed | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 9:36:25 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.8 | 1.4 | 6.2 | 0 | 22551 | 109 | 21872 | 157 | 4282 | 79 | 26838 | 111 | 8.6157 | 787 |  | 10.2 | [36 empty] | Factory charge, 3 turns, Econo Closed damper, tape around damper perimeter--frame gaps, 60% inlet 54% outlet Meriam, adust code tester speed to match--total static of run L-TE3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.946 | 0.034 | 61.998 | 0.02 | 95 | 0.008 | 74.997 | 0.029 | 74.54 | 0.11 | 57.2 | 0.05 | 64.48 | 0.17 | 0.018 | 0.007 | 1.0002 | 0.0091 | 22551 | 109 | 4282 | 79 | 8.617 | 0.041 | [6 empty] | 458.8 | 2.5 | 461.7 | 2.5 | 461.3 | 2.5 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2788.9 | 25.2 | 1489.9 | 28.6 | 325.8 | 19.4 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.35 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2350 |  | 0.68 | [8 empty] | 458.4 | 2.5 | 0.8 | 0 | 367.6 | 1.4 | 21 |  | 3108.6 | 480 | 480 | 480 | 0.8 | 0.8 | 1 | 430 | 0.61 | 10.2 | 16.9 |  |  |  |  | 213.9 | 0.2 | 99.73 | 0.07 |  |  |  |  | 220.72 | 0.17 | 167.17 | 0.1 | 108.12 | 0.05 | 59.05 | 0.11 |  |  | 96.97 | 0.08 | 105.92 | 0.06 | 6.19 | 0.07 |  |  | 57.21 | 0.4 |  |  |  |  | 72.47 | 0.16 | 61.41 | 0.22 | 42.44 | 0.11 | 18.97 | 0.18 | [120 empty] | 56.46 | 0.06 | 58.04 | 0.07 | 56.98 | 0.06 | 58.08 | 0.06 | 56.73 | 0.05 | 57.25 | 0.04 | [32 empty] | 96.85 | 0.06 |  |  | 95.88 | 0.09 | 95.8 | 0.09 | 95.81 | 0.1 | 95.67 | 0.1 | 95.61 | 0.11 | 95.64 | 0.1 | [8 empty] | 93.1 | 0.07 | [34 empty] | 94.64 | 0.07 | 94.64 | 0.1 | 74.86 | 0.1 | 74.86 | 0.08 | 74.79 | 0.07 | 74.97 | 0.11 | 74.98 | 0.11 | 74.98 | 0.1 | 74.9 | 0.07 | 86.48 | 0.06 | 88.62 | 0.08 | 82.61 | 0.09 | 77.03 | 0.06 | 80.88 | 0.09 | 83.83 | 0.13 | 84.08 | 0.09 | 76.81 | 0.08 | 82.23 | 0.05 | 81.03 | 0.07 | 81.05 | 0.1 | 76.16 | 0.07 | 77.01 | 0.08 | 79.79 | 0.08 | 81.41 | 0.07 | 75.2 | 0.07 | 80.69 | 0.09 | 78.67 | 0.07 | 80.24 | 0.06 | 76.8 | 0.09 | [84 empty] | L-55-TCE-DM | 74.946 | 0.034 | 61.998 | 0.02 | 57.069 | 0.024 | 54.05 | 0.027 | 95 | 0.008 | 74.997 | 0.029 | 1147 | 5.3 | 1116.9 | 5.1 | 0.689 | 0.002 | -0.256 | 0.002 | 0.018 | 0.007 | 1.0002 | 0.0091 | 29.265 | 0.001 | 3115 | 9 | 370 |  | 0.062075 | 68.4313 | 13.029 | 0.245 | 0.75611 | 5257.0037 | 90.4063 | 72.7686 | 309.656 | 4947.3477 | 0.009094 | 28.2292 | 56.3129 | 14.0999 | 13.0911 | 0.013918 | 38.1542 | 0.0087921 | 27.608 | 0.0081644 | 22.5658 | 76.1376 | 62.875 | 22.3816 | 30740.7186 | 25012.4861 | 2745 | 0.30476 | 29786.4653 | 24058.2327 | 9.5623 | 0.21687 | -5.8476 | -19.8247 | 50.8227 | 30740.7186 | 26506.6302 | 968.3827 | 3265.7057 | 30740.7186 | 100%
4 | L-75629575-TOE3 | 30T0023 | L-75629575-TOE3 | open | on | N/A | 3 turns | sealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 23:44:03 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 458.7 | 1.3 | 6.2 | 0 | 11011 | 43 | 10622 | 81 | -12646 | 167 | -1647 | 191 | -0.52687 | 786 |  | 12.14 | [36 empty] | Factory charge, 3 turns, Econo Fully open damper, tape around damper perimeter frame gaps,--unsealed cab, cab, 60% inlet 54% outlet Meriam, adust code tester speed to match total static of run--L-TOE3-SPWCT-SS | R22 7 LBS: OFB: Econo Closed: sealed around damper perimeter: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 75.005 | 0.019 | 62.015 | 0.054 | 95.001 | 0.006 | 75.002 | 0.016 | 74.68 | 0.06 | 66.14 | 0.05 | 70.04 | 0.06 | 0.001 | 0.003 | 1.0822 | 0.0047 | 11011 | 43 | -12646 | 167 | 0 | 0 | [6 empty] | 458.7 | 2.5 | 461.4 | 2.5 | 461.2 | 2.5 | 6.2 | 0 | 5 | 0 | 5.5 | 0 | 2783.6 | 25.3 | 1494.6 | 28.5 | 342.2 | 19.1 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.35 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.4 |  | 2370 |  | 0.68 | [8 empty] | 458.3 | 2.5 | 0.8 | 0 | 367.2 | 1.4 | 21 |  | 3138.2 | 480 | 480 | 480 | 0.8 | 0.8 | 0.9 | 470 | 0.63 | 12.14 | 17.6 |  |  |  |  | 215.98 | 0.22 | 100 | 0.06 |  |  |  |  | 224.09 | 0.13 | 167.51 | 0.06 | 109.18 | 0.04 | 58.32 | 0.07 |  |  | 96.98 | 0.05 | 106.6 | 0.07 | 6.6 | 0.07 |  |  | 66.95 | 0.25 |  |  |  |  | 82 | 0.13 | 70.86 | 0.12 | 48.54 | 0.08 | 22.33 | 0.1 | [120 empty] | 65.62 | 0.05 | 66.21 | 0.05 | 66.62 | 0.06 | 66.17 | 0.05 | 66.5 | 0.06 | 65.45 | 0.05 | [32 empty] | 96.89 | 0.03 |  |  | 93.71 | 0.19 | 94.4 | 0.27 | 93.94 | 0.2 | 94.48 | 0.16 | 94.32 | 0.19 | 94.33 | 0.19 | [44 empty] | 94.9 | 0.06 | 94.12 | 0.09 | 75.39 | 0.05 | 75.21 | 0.03 | 75.1 | 0.04 | 75.74 | 0.05 | 75.66 | 0.05 | 75.79 | 0.05 | 75.44 | 0.04 | 91.35 | 0.08 | 93.63 | 0.09 | 94.98 | 0.15 | 94.52 | 0.11 | 94.1 | 0.14 | 95.24 | 0.17 | 95.28 | 0.18 | 94.53 | 0.14 | 93.4 | 0.07 | 94.69 | 0.18 | 94.78 | 0.15 | 92.21 | 0.12 | 90.65 | 0.15 | 93.29 | 0.18 | 92.98 | 0.14 | 90.81 | 0.17 | 93.55 | 0.19 | 93.1 | 0.14 | 93.49 | 0.14 | 91.7 | 0.18 | [84 empty] | L-55-TOER-DM | 75.005 | 0.019 | 62.015 | 0.054 | 66.159 | 0.018 | 62.407 | 0.029 | 95.001 | 0.006 | 75.002 | 0.016 | 1201.3 | 2.6 | 1150.9 | 2.5 | 0.507 | 0.001 | -0.011 | 0.002 | 0.001 | 0.003 | 1.0822 | 0.0047 | 29.244 | 0.001 | 3126 | 8 | 380 |  | 0.58525 | 705.5832 | 13.029 | 0.012 | 0.81979 | 5401.1315 | 68.5505 | 702.7603 | 2990.4798 | 2410.6516 | 0.011631 | 33.4549 | 65.3392 | 14.1 | 13.345 | 0.013922 | 38.159 | 0.0087893 | 27.6194 | 0.011149 | 28.0346 | 86.1223 | 69.6611 | 27.8338 | 30360.5208 | 26940.4602 | 2746 | 0.30869 | 29297.5437 | 25877.4831 | 9.3722 | 0.21049 | -5.6211 | -20.783 | 59.7984 | 30360.5208 | -2242.6718 | 1084.5836 | 31518.609 | 30360.5208 | 100%
4 | L-22A | 30T0002 | L-22A | none | on | N/A | 5 turns | sealed | unsealed | 664 |  |  | 0 | 0 | CUST 4 | 3/20/2014 | 11:53:55 | 10 Ton | 0:30:00 | 80/67 95/70 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 7 |  | 7 |  | 459.4 | 1.3 | 6.3 | 0 | 25303 | 45 | 24119 | 140 | 10025 | 94 | 35337 | 103 | 11.4582 | 664 |  | 4.7 | [36 empty] | A test factory chg, low speed fan 664 rpm, sealed cab, no econo | R22 7 LBS: OFB: sealed cab:Inlet Meriam set @ 100%: Outlet @ 100% Horiz airflow. ID Pulley is 5 turns open from fully closed | 79.996 | 0.027 | 67.149 | 0.028 | 94.853 | 0.008 | 69.892 | 0.051 | 79.18 | 0.12 | 61.56 | 0.05 | 68.96 | 0.02 | -0.199 | 0.002 | 0.7472 | 0.0021 | 25303 | 45 | 10025 | 94 | 11.46 | 0.043 | [6 empty] | 459.4 | 2.4 | 461.6 | 2.5 | 460.5 | 2.4 | 6.3 | 0 | 5 | 0 | 5.4 | 0 | 2797.9 | 24.5 | 1463.5 | 27.4 | 285.6 | 18.4 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.3 | 460 |  | 460 |  | 460 |  | 4.1 |  | 4 |  | 3.5 |  | 2360 |  | 0.68 | [8 empty] | 459 | 2.4 | 0.8 | 0 | 371.1 | 1.4 | 21 |  | 3082.1 | 480 | 480 | 480 | 0.7 | 0.6 | 0.8 | 340 | 0.6 | 4.7 | 14 |  |  |  |  | 214.56 | 0.21 | 99.77 | 0.08 |  |  |  |  | 221.84 | 0.16 | 166.38 | 0.12 | 108.52 | 0.05 | 57.86 | 0.14 |  |  | 96.82 | 0.09 | 106.18 | 0.07 | 6.41 | 0.08 |  |  | 60.67 | 0.66 |  |  |  |  | 76.62 | 0.22 | 64.89 | 0.3 | 45.24 | 0.14 | 19.65 | 0.26 | [120 empty] | 61.13 | 0.06 | 62.87 | 0.08 | 61.49 | 0.07 | 62.89 | 0.07 | 61.18 | 0.05 | 62.08 | 0.06 | [32 empty] | 96.75 | 0.06 |  |  | 95.98 | 0.11 | 95.87 | 0.1 | 95.99 | 0.09 | 95.77 | 0.11 | 95.81 | 0.12 | 95.84 | 0.12 | [8 empty] | 93.58 | 0.09 | [34 empty] | 94.68 | 0.09 | 94.67 | 0.09 | 79.57 | 0.11 | 79.57 | 0.1 | 79.44 | 0.08 | 79.69 | 0.12 | 79.66 | 0.12 | 79.74 | 0.11 | 79.56 | 0.09 | 80.7 | 0.08 | 80.46 | 0.07 | 80.13 | 0.07 | 79.82 | 0.07 | 80.34 | 0.06 | 80.69 | 0.08 | 80.12 | 0.08 | 80.05 | 0.08 | 79.78 | 0.06 | 80 | 0.05 | 80.15 | 0.08 | 79.96 | 0.08 | 79.57 | 0.06 | 79.62 | 0.06 | 79.95 | 0.07 | 79.6 | 0.08 | 79.45 | 0.07 | 79.51 | 0.08 | 79.68 | 0.07 | 79.73 | 0.06 | [84 empty] | No Economizer | 79.996 | 0.027 | 67.149 | 0.028 | 61.496 | 0.015 | 58.274 | 0.022 | 94.853 | 0.008 | 69.892 | 0.051 | 1234.8 | 1.8 | 1200 | 1.7 | 0.361 | 0.001 | -0.067 | 0.001 | -0.199 | 0.002 | 0.7472 | 0.0021 | 29.538 | 0.001 | 3084 | 7 | 330 |  |  | 0 |  |  | 0.70774 | 5606.5415 | 50.8925 | 0 | 0 | 5606.5415 | 0.011187 | 31.4659 | 60.7883 | 14.0615 | 13.2146 | 0.0097391 | 33.508 | 0.011187 | 31.4659 | 0.0096051 | 25.2123 | 79.996 | 67.149 | 25.0394 | 36030.5364 | 25845.3591 | 2754 | 0.26087 | 35077.9424 | 24892.7652 | 11.3742 | 0.24636 | -6.4265 | -19.2077 | 54.5094 | 36030.5364 | 35061.2995 | 969.2369 | 0 | 36030.5364 | 100%
4 | L-75629575-NE3-SS | 30T0003 | L-75629575-NE3-SS | none | on | N/A | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/21/2014 | 4:50:55 | 10 Ton | 0:30:03 | 75/62 95/75 | ENG 1 | TECH 4 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 | 380/460/3 | TU5 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 7 |  | 7 |  | 459.2 | 1.4 | 6.3 | 0 | 22651 | 102 | 21958 | 123 | 5569 | 58 | 28225 | 123 | 9.0873 | 789 |  | 8.96 | [36 empty] | Factory charge, 3 turns, no econo, unsealed cab, 60% inlet 54% outlet Meriam,--adust code tester speed to match total static of run L-E3-SPWCT-SS | R22 7 LBS: OFB: Unsealed cab:Inlet Meriam set @ 60%: Outlet @ 54% Horiz airflow. ID Pulley is 3 turns open from fully closed | 74.999 | 0.015 | 61.994 | 0.021 | 95 | 0.008 | 75.011 | 0.03 | 74.57 | 0.08 | 56.76 | 0.05 | 63.72 | 0.03 | 0.017 | 0.007 | 0.9517 | 0.0081 | 22651 | 102 | 5569 | 58 | 9.088 | 0.045 | [6 empty] | 459.2 | 2.6 | 462.1 | 2.6 | 460.9 | 2.6 | 6.3 | 0 | 5 | 0 | 5.5 | 0 | 2808.6 | 25.8 | 1466.8 | 28.6 | 297.1 | 19.5 | 461 |  | 458 |  | 460 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.34 | 462 |  | 457 |  | 460 |  | 4.1 |  | 3.9 |  | 3.4 |  | 2350 |  | 0.67 | [8 empty] | 458.9 | 2.5 | 0.8 | 0 | 367.9 | 1.4 | 21 |  | 3108.9 | 483 | 485 | 485 | 0.8 | 0.7 | 1 | 410 | 0.6 | 8.96 | 16.5 |  |  |  |  | 213.2 | 0.24 | 99.13 | 0.1 |  |  |  |  | 219.26 | 0.2 | 169.96 | 0.14 | 107.66 | 0.06 | 62.3 | 0.16 |  |  | 96.4 | 0.08 | 105.7 | 0.08 | 6.57 | 0.07 |  |  | 54.62 | 1.48 |  |  |  |  | 69.01 | 0.34 | 60.42 | 0.4 | 40.09 | 0.23 | 20.33 | 0.29 | [120 empty] | 56.21 | 0.07 | 58.03 | 0.07 | 56.55 | 0.05 | 58.07 | 0.07 | 56.34 | 0.05 | 57.17 | 0.06 | [32 empty] | 96.31 | 0.08 |  |  | 96.14 | 0.11 | 96.04 | 0.09 | 96.14 | 0.09 | 95.97 | 0.1 | 95.99 | 0.11 | 96.01 | 0.11 | [8 empty] | 92.25 | 0.08 | [34 empty] | 94.76 | 0.04 | 94.81 | 0.06 | 74.96 | 0.06 | 74.93 | 0.06 | 74.83 | 0.05 | 75.07 | 0.06 | 75.08 | 0.06 | 75.1 | 0.06 | 74.95 | 0.05 | 76.87 | 0.06 | 76.46 | 0.03 | 76.26 | 0.04 | 76.1 | 0.04 | 75.65 | 0.17 | 76.62 | 0.06 | 76.13 | 0.06 | 75.68 | 0.07 | 75.98 | 0.06 | 76.12 | 0.06 | 76.08 | 0.09 | 75.61 | 0.07 | 75.43 | 0.06 | 75.43 | 0.06 | 75.49 | 0.04 | 74.98 | 0.06 | 74.99 | 0.06 | 75 | 0.06 | 75.08 | 0.06 | 75.26 | 0.04 | [84 empty] | No Economizer | 74.999 | 0.015 | 61.994 | 0.021 | 56.624 | 0.019 | 53.373 | 0.025 | 95 | 0.008 | 75.011 | 0.03 | 1117.8 | 4.8 | 1090.5 | 4.7 | 0.685 | 0.002 | -0.275 | 0.003 | 0.017 | 0.007 | 0.9517 | 0.0081 | 29.263 | 0.001 | 3106 | 9 | 370 |  |  | 0 |  |  | 0.78241 | 5128.4262 | 87.7569 | 0 | 0 | 5128.4262 | 0.0087769 | 27.6043 | 55.8416 | 14.1 | 13.0777 | 0.01393 | 38.1678 | 0.0087769 | 27.6043 | 0.0078898 | 22.1592 | 74.999 | 61.994 | 21.9687 | 28901.9449 | 23579.3731 | 2736 | 0.32309 | 27938.6493 | 22616.0775 | 8.9951 | 0.23917 | -5.6356 | -19.1574 | 49.8194 | 28901.9449 | 27924.8752 | 977.0697 | 0 | 28901.9449 | 100%
4 | L-ONE-5T | 30T0004 | L-ONE-5T | none | on | N/A | 5 turns | unsealed | unsealed | 663 |  |  | 0 | 0 | CUST 4 | 3/20/2014 | 3:43:53 | 10 Ton | 0:30:00 | 80/67 - 95/70 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 6.375 | 380/460/3 | TU5 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 6.375 |  | 7 |  | 459.9 | 1.5 | 6.4 | 0 | 26805 | 74 | 25665 | 145 | 8947 | 158 | 35761 | 159 | 11.4289 | 663 |  | 9.9 | [36 empty] | Out-of-box refrigerant charge, unsealed cab, no econo, low fan speed, 663 rpm | R22 7 LBS: OFB: Unsealed cab:Inlet Meriam set @ 100%: Outlet @ 100% Horiz airflow. ID Pulley is 5 turns open from fully closed | 80.004 | 0.029 | 66.998 | 0.054 | 94.997 | 0.022 | 70 | 0.035 | 79.21 | 0.1 | 62.3 | 0.05 | 69.13 | 0.02 | -0.095 | 0.002 | 0.9258 | 0.0041 | 26805 | 74 | 8947 | 158 | 11.43 | 0.057 | [6 empty] | 459.9 | 2.6 | 461.7 | 2.6 | 460.2 | 2.6 | 6.4 | 0 | 5.1 | 0 | 5.4 | 0 | 2837.5 | 26 | 1439.9 | 29.5 | 291.4 | 19.5 | 462 |  | 461 |  | 461 |  | 1.4 |  | 1.4 |  | 1.3 |  | 0.34 | 462 |  | 461 |  | 460 |  | 4.2 |  | 3.9 |  | 3.5 |  | 2400 |  | 0.67 | [8 empty] | 459.6 | 2.6 | 0.8 | 0 | 371.1 | 1.5 | 21 |  | 3152.1 | 483 | 484 | 484 | 0.8 | 0.7 | 1 | 440 | 0.61 | 9.9 | 16.5 | [6 empty] | 100.89 | 0.09 |  |  |  |  | 223.78 | 0.2 | 166.29 | 0.13 | 109.13 | 0.06 | 57.16 | 0.15 |  |  | 98.03 | 0.09 | [6 empty] | 61.47 | 0.53 |  |  |  |  | 78.54 | 0.2 | 65.43 | 0.29 | 46.46 | 0.13 | 18.96 | 0.28 | [120 empty] | 62.22 | 0.08 | 63.1 | 0.1 | 62.01 | 0.07 | 63.18 | 0.09 | 62.01 | 0.06 | 62.56 | 0.08 | [32 empty] | 97.92 | 0.09 | [58 empty] | 94.57 | 0.07 | 94.8 | 0.08 | 79.29 | 0.07 | 79.37 | 0.07 | 79.39 | 0.07 | 79.28 | 0.07 | 79.27 | 0.07 | 79.41 | 0.06 | 79.35 | 0.07 | 80.54 | 0.05 | 80.34 | 0.05 | 80.02 | 0.06 | 79.74 | 0.06 | 80.4 | 0.05 | 81.49 | 0.06 | 80.78 | 0.07 | 80.65 | 0.07 | 80.5 | 0.05 | 80.58 | 0.05 | 81 | 0.07 | 80.66 | 0.07 | 80.34 | 0.05 | 80.24 | 0.05 | 80.32 | 0.06 | 79.8 | 0.08 | 79.71 | 0.06 | 79.71 | 0.06 | 79.73 | 0.07 | 79.86 | 0.05 | [84 empty] | No Economizer | 80.004 | 0.029 | 66.998 | 0.054 | 62.329 | 0.023 | 58.949 | 0.038 | 94.997 | 0.022 | 70 | 0.035 | 1375.9 | 3.1 | 1336.1 | 3 | 0.3 | 0.002 | -0.08 | 0.001 | -0.095 | 0.002 | 0.9258 | 0.0041 | 29.528 | 0.001 | 3129 | 8 | 360 |  |  | 0 |  |  | 0.71332 | 6236.4154 | 47.0896 | 0 | 0 | 6236.4154 | 0.011074 | 31.3439 | 61.6157 | 14.0655 | 13.2374 | 0.009789 | 33.5983 | 0.011074 | 31.3439 | 0.0098252 | 25.6554 | 80.004 | 66.998 | 25.4811 | 36562.8906 | 27522.5242 | 2769 | 0.25848 | 35494.9275 | 26454.5611 | 11.3439 | 0.25149 | -5.8628 | -18.3883 | 55.4376 | 36562.8906 | 35475.8342 | 1087.0564 | 0 | 36562.8906 | 100%
4 | L-ONE-SS | 30T0005 | L-ONE-SS | none | on | N/A | 2.5 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/19/2014 | 23:52:01 | 10 Ton | 0:10:00 | 80/67 - 95/70 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 7 |  | 7 |  | 459.1 | 1.5 | 6.6 | 0 | 31370 | 84 | 30298 | 165 | 5236 | 206 | 36612 | 221 | 10.6709 | 808 |  | 22.9 | [36 empty] | Out-of-box refrigerant charge unsealed cab, no econo, default fan speed 2.5 turns, measure rpm | R22 7 LBS: OFB: Unsealed cab:Inlet Meriam set @ 100%: Outlet @ 100% Horiz airflow. ID Pulley is 2.5 turns open from fully closed | 80.01 | 0.012 | 66.985 | 0.067 | 95.003 | 0.015 | 69.994 | 0.019 | 79.41 | 0.06 | 65.83 | 0.07 | 70.81 | 0.02 | 0.225 | 0.006 | 1.2069 | 0.0057 | 31370 | 84 | 5236 | 206 | 10.671 | 0.069 | [6 empty] | 459.1 | 2.5 | 461.2 | 2.5 | 460.8 | 2.5 | 6.6 | 0 | 5.4 | 0 | 5.7 | 0 | 2953.4 | 25.3 | 1483.8 | 27.9 | 477.5 | 19.1 | 461 |  | 461 |  | 462 |  | 1.5 |  | 1.6 |  | 1.4 |  | 0.52 | 459 |  | 459 |  | 460 |  | 4.2 |  | 4 |  | 3.5 |  | 2410 |  | 0.69 | [8 empty] | 458.7 | 2.5 | 0.8 | 0 | 369.9 | 1.6 | 21 |  | 3430.9 | 485 | 486 | 487 | 1.4 | 1.3 | 1.7 | 870 | 0.65 | 22.9 | 23 | [6 empty] | 102.18 | 0.09 |  |  |  |  | 227.36 | 0.18 | 165.47 | 0.14 | 110.26 | 0.06 | 55.21 | 0.14 |  |  | 99.12 | 0.06 | [6 empty] | 65.19 | 0.3 |  |  |  |  | 84.12 | 0.11 | 68.5 | 0.31 | 49.92 | 0.07 | 18.58 | 0.28 | [120 empty] | 65.94 | 0.08 | 66.91 | 0.1 | 66.17 | 0.09 | 66.85 | 0.09 | 66.12 | 0.07 | 66.28 | 0.08 | [36 empty] | 97.5 | 0.12 | 97.2 | 0.34 | 97.61 | 0.11 | 97.39 | 0.12 | 97.42 | 0.13 | 97.46 | 0.13 | [44 empty] | 94.73 | 0.12 | 96.12 | 0.13 | 79.76 | 0.08 | 79.78 | 0.07 | 79.68 | 0.05 | 79.84 | 0.09 | 79.82 | 0.09 | 79.88 | 0.08 |  |  | 81.24 | 0.07 | 81 | 0.06 | 80.57 | 0.06 | 80.21 | 0.05 | 81.02 | 0.04 | 81.6 | 0.05 | 80.75 | 0.05 | 80.64 | 0.05 | 80.92 | 0.04 | 81.12 | 0.04 | 81.06 | 0.06 | 80.59 | 0.06 | 80.59 | 0.04 | 80.53 | 0.04 | 80.49 | 0.05 | 79.78 | 0.1 | 79.95 | 0.1 | 79.94 | 0.09 | 79.88 | 0.06 | 80.07 | 0.06 | [84 empty] | No Economizer | 80.01 | 0.012 | 66.985 | 0.067 | 65.951 | 0.03 | 61.549 | 0.057 | 95.003 | 0.015 | 69.994 | 0.019 | 2052.6 | 4.8 | 1987.2 | 4.7 | 0.25 | 0.003 | -0.159 | 0.001 | 0.225 | 0.006 | 1.2069 | 0.0057 | 29.548 | 0.001 | 3431 | 10 | 630 |  |  | 0 |  |  | 0.87998 | 9235.1264 | 58.3642 | 0 | 0 | 9235.1264 | 0.011063 | 31.3333 | 65.071 | 14.0656 | 13.3356 | 0.0097829 | 33.5931 | 0.011063 | 31.3333 | 0.010629 | 27.4168 | 80.01 | 66.985 | 27.2014 | 38158.384 | 33111.2153 | 2801 | 0.25053 | 36207.3911 | 31160.2224 | 10.553 | 0.31284 | -4.1319 | -14.939 | 58.2698 | 38158.384 | 36169.6105 | 1988.7735 | 0 | 38158.384 | 100%
4 | L-22B | 30T0024 | L-22B | none | on | N/A | 5 turns | sealed | unsealed | 664 |  |  | 0 | 0 | CUST 4 | 3/20/2014 | 13:57:47 | 10 Ton | 0:30:00 | 80/67 82 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 | TU5 | AHRI 210/240 2008 | 80 | 67 | 82 |  | 7 |  | 7 |  | 459.3 | 1.4 | 6 | 0 | 27455 | 45 | 26147 | 134 | 11049 | 72 | 38515 | 89 | 14.0259 | 664 |  | 4.7 | [36 empty] | B test factory chg, low speed fan 664 rpm, sealed cab, no econo | R22 7 LBS: OFB: sealed cab:Inlet Meriam set @ 100%: Outlet @ 100% Horiz airflow. ID Pulley is 5 turns open from fully closed | 79.993 | 0.021 | 67.149 | 0.019 | 81.841 | 0.01 | 66.734 | 0.028 | 79.18 | 0.1 | 60.09 | 0.04 | 67.91 | 0.02 | -0.191 | 0.002 | 0.7472 | 0.002 | 27455 | 45 | 11049 | 72 | 14.028 | 0.055 | [6 empty] | 459.3 | 2.6 | 461.4 | 2.6 | 460.7 | 2.6 | 6 | 0 | 4.7 | 0 | 5.1 | 0 | 2615.2 | 26 | 1459.4 | 30.5 | 130.6 | 19.5 | 460 |  | 460 |  | 460 |  | 1.3 |  | 1.4 |  | 1.3 |  | 0.31 | 460 |  | 460 |  | 460 |  | 3.8 |  | 3.6 |  | 3.1 |  | 2020 |  | 0.64 | [8 empty] | 458.9 | 2.6 | 0.8 | 0 | 376 | 1.5 | 21 |  | 2747 | 480 | 480 | 480 | 0.7 | 0.6 | 0.7 | 350 | 0.63 | 4.7 | 14 |  |  |  |  | 177.91 | 0.17 | 86.71 | 0.05 |  |  |  |  | 185.97 | 0.09 | 149.23 | 0.08 | 96.43 | 0.03 | 52.8 | 0.09 |  |  | 84.31 | 0.06 | 93.5 | 0.06 | 6.79 | 0.08 |  |  | 60.72 | 0.25 |  |  |  |  | 75.68 | 0.11 | 63.49 | 0.19 | 44.61 | 0.07 | 18.88 | 0.19 | [120 empty] | 59.58 | 0.04 | 61 | 0.06 | 59.97 | 0.06 | 60.98 | 0.06 | 59.75 | 0.05 | 60.27 | 0.05 | [32 empty] | 84.11 | 0.05 |  |  | 82.91 | 0.08 | 82.77 | 0.07 | 82.78 | 0.08 | 82.61 | 0.08 | 82.63 | 0.09 | 82.65 | 0.09 | [8 empty] | 82.22 | 0.05 | [34 empty] | 81.62 | 0.08 | 82.02 | 0.08 | 79.45 | 0.1 | 79.45 | 0.09 | 79.33 | 0.07 | 79.53 | 0.1 | 79.51 | 0.11 | 79.57 | 0.1 | 79.48 | 0.08 | 79.92 | 0.06 | 79.78 | 0.05 | 79.78 | 0.07 | 79.63 | 0.06 | 79.2 | 0.05 | 79.83 | 0.07 | 79.98 | 0.08 | 79.98 | 0.08 | 79.14 | 0.06 | 79.21 | 0.05 | 79.65 | 0.07 | 79.9 | 0.08 | 79.06 | 0.06 | 79.21 | 0.06 | 79.8 | 0.06 | 79.31 | 0.08 | 78.82 | 0.07 | 79 | 0.07 | 79.47 | 0.06 | 79.55 | 0.05 | [84 empty] | No Economizer | 79.993 | 0.021 | 67.149 | 0.019 | 59.938 | 0.011 | 57.417 | 0.02 | 81.841 | 0.01 | 66.734 | 0.028 | 1235 | 1.7 | 1200 | 1.7 | 0.356 | 0.001 | -0.069 | 0.001 | -0.191 | 0.002 | 0.7472 | 0.002 | 29.466 | 0.002 | 2746 | 9 | 330 |  |  | 0 |  |  | 0.70723 | 5624.7729 | 50.1876 | 0 | 0 | 5624.7729 | 0.011188 | 31.466 | 59.2308 | 13.7373 | 13.1739 | 0.010444 | 31.1027 | 0.011188 | 31.466 | 0.0094522 | 24.6654 | 79.993 | 67.149 | 24.4927 | 39222.8631 | 28027.877 | 2416 | 0.21023 | 38267.8633 | 27072.8772 | 13.9359 | 0.18893 | -6.9732 | -20.7622 | 54.3945 | 39222.8631 | 38251.4484 | 971.4147 | 0 | 39222.8631 | 100%
4 | L-22C-L22D Cyclic #2 | 30T0025 | L-22C/L22D Cyclic #2 | none | on | N/A |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/20/2014 | 16:56:18 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 |  |  | 80 | 57 | 82 |  | 7 |  | 7 | [17 empty] | 11.985 |  |  |  | 2 | 6.033 | 82.022 | 30.017 | 63.558 | 0.36 | 434.6 | 1200.1 | 13.461 | 32699.943 | 0.242 | 2928.55 | 0.00447 | 22.2974 | 150.191 | 11.83 | 134.52 | 265.5 | 10.56 | 11.83 | 14.03 | 0 | 0 | 0.179 | 277.32 | 0.145 | 272.8 | 272.83 | 13.0128 | 272.83 | 0.98 | [516 empty] | No Economizer | 79.67 |  | 54.376 |  | 56.056 |  | 46.601 | [5 empty] | 1218.1 |  | 1185 |  | 0.393 |  |  |  | -0.236 |  | 0.7183 |  | 29.385 |  | 2710 |  | -0.1 |  |  | 0 |  |  | 0.96337 | 5606.1183 | 54.7112 | 0 | 0 | 5606.1183 | 0.003063 | 22.479 | 55.0926 | 11.5938 | 13.0368 | 0.00078408 | 0.83191 | 0.003063 | 22.479 | 0.004497 | 18.3367 | 79.67 | 54.376 | 18.1035 | 24529.2024 | 33068.0714 | 2275.4 | 0.3166 | 23232.6418 | 31771.5108 | 8.5729 | 0.37245 | -4.3754 | -24.5774 | 40.5062 | 24529.2024 | 23222.2382 | 1306.9641 | 0 | 24529.2024 | 100%
4 | L-22C-L22D Cyclic #3 | 30T0026 | L-22C/L22D Cyclic #3 | none | on | N/A |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/20/2014 | 17:26:18 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 |  |  | 80 | 57 | 82 |  | 7 |  | 7 | [17 empty] | 11.985 |  |  |  | 3 | 6.033 | 81.765 | 30.017 | 62.953 | 0.36 | 434.4 | 1200.1 | 13.461 | 32699.943 | 0.242 | 2981.181 | 0.00447 | 22.698 | 150.198 | 11.13 | 136.937 | 266.1 | 10.753 | 11.13 | 14.03 | 0 | 0 | 0.182 | 277.23 | 0.126 | 272.8 | 272.84 | 13.1461 | 272.84 | 0.98 | [516 empty] | No Economizer | 79.707 |  | 54.253 |  | 56.37 |  | 46.433 | [5 empty] | 1219.2 |  | 1184.7 |  | 0.394 |  |  |  | -0.235 |  | 0.7244 |  | 29.368 |  | 2708 |  | -0.1 |  |  | 0 |  |  | 0.96217 | 5608.288 | 54.8365 | 0 | 0 | 5608.288 | 0.0029859 | 22.4034 | 55.4078 | 11.5938 | 13.0436 | 0.00078408 | 0.83191 | 0.0029859 | 22.4034 | 0.0043422 | 18.2446 | 79.707 | 54.253 | 18.0118 | 24629.1511 | 32706.4187 | 2273.6 | 0.31507 | 23333.7009 | 31410.9685 | 8.6166 | 0.39116 | -4.3916 | -24.2992 | 39.7965 | 24629.1511 | 23323.6769 | 1305.4742 | 0 | 24629.1511 | 100%
4 | L-22C-L22D Cyclic #4 | 30T0027 | L-22C/L22D Cyclic #4 | none | on | N/A |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 4 | 3/20/2014 | 17:56:18 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 1 | RTU4 | RTU4 | 3 | R22 | PSC Air Handler | 7 LBS | 380/460/3 |  |  | 80 | 57 | 82 |  | 7 |  | 7 | [17 empty] | 11.985 |  |  |  | 4 | 6.033 | 81.889 | 30.017 | 62.539 | 0.36 | 434.3 | 1200.1 | 13.461 | 32699.943 | 0.242 | 2960.524 | 0.00447 | 22.5407 | 149.989 | 11.99 | 135.988 | 266.7 | 10.623 | 12 | 14.03 | 0 | 0 | 0.181 | 278.69 | 0.139 | 272.5 | 272.46 | 13.0549 | 272.46 | 0.98 | [516 empty] | No Economizer | 79.66 |  | 53.996 |  | 56.519 |  | 46.204 | [5 empty] | 1219.5 |  | 1184.6 |  | 0.395 |  |  |  | -0.238 |  | 0.7232 |  | 29.358 |  | 2709 |  | -0.1 |  |  | 0 |  |  | 0.96153 | 5608.5392 | 54.971 | 0 | 0 | 5608.5392 | 0.0028542 | 22.2477 | 55.5575 | 11.5938 | 13.0462 | 0.00078408 | 0.83191 | 0.0028542 | 22.2477 | 0.0041967 | 18.1226 | 79.66 | 53.996 | 17.8901 | 24439.7815 | 32443.1998 | 2274.7 | 0.31766 | 23145.1318 | 31148.5501 | 8.5438 | 0.40407 | -4.3576 | -24.1025 | 39.2144 | 24439.7815 | 23135.4625 | 1304.3191 | 0 | 24439.7815 | 100%
3 | 1-OEH | 75N0018 | 1-OEH | open | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/27/2013 | 10:41:35 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 6.6 | 0 | 28942 | 298 | 28817 | 334 | 14866 | 367 | 43825 | 560 | 27.6848 | [39 empty] | Econ Open No Compressors 55/51 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.003 | 0.019 | 62.004 | 0.046 | 54.987 | 0.027 | 50.996 | 0.027 | 74.68 | 0.06 | 64.36 | 0.13 | 67.28 | 0.08 | 0.102 | 0.009 | 0.9025 | 0.0021 | 28942 | 298 | 14866 | 367 | 27.692 | 0.598 | [6 empty] | 230.2 | 0.8 | 230.6 | 0.8 | 229.8 | 0.8 | 6.6 | 0.1 | 6.2 | 0.1 | 6.5 | 0.1 | 1425.2 | 16.3 | 1109.2 | 13.3 | 157.6 | 15.6 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.2 |  | 0.52 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1575 | [174 empty] | 64.7 | 0.13 | 63.38 | 0.16 | 63.16 | 0.18 | 66.38 | 0.12 | 66.16 | 0.12 | 65.95 | 0.12 | [18 empty] | 55.44 | 0.11 | [12 empty] | 55.4 | 0.06 | 55.36 | 0.02 | [20 empty] | 55.63 | 0.13 | 55.3 | 0.02 |  |  |  |  | 57.18 | 0.02 | 54.62 | 0.03 | [24 empty] | 55.63 | 0.26 | 54.54 | 0.2 | 74.79 | 0.05 | 74.69 | 0.06 | 74.4 | 0.05 | 74.4 | 0.05 | 74.39 | 0.05 | 74.41 | 0.06 |  |  | 72.95 | 0.06 | 70.5 | 0.11 | 68.63 | 0.14 | 67.56 | 0.24 | 67.76 | 0.3 | 60.43 | 0.49 | 59.9 | 0.55 | 62.33 | 0.65 | 62.69 | 0.22 | 61.28 | 0.21 | 58.18 | 0.3 | 56.85 | 0.4 | 59.25 | 0.27 | 59.52 | 0.3 | 60.16 | 0.28 | 58.69 | 0.33 | [30 empty] | 58.98 | 0.56 | 59.06 | 0.44 | 56.7 | 0.46 | 56.87 | 0.55 | 55.61 | 0.33 | 55.49 | 0.35 | [50 empty] | Economizer test | 75.003 | 0.019 | 62.004 | 0.046 | 64.632 | 0.114 | 56.238 | 0.061 | 54.987 | 0.027 | 50.996 | 0.027 | 2556.1 | 3 | 2480.5 | 3 | 0.782 | 0.002 | -0.08 | 0.019 | 0.102 | 0.009 | 0.9025 | 0.0021 | 29.292 | 0.001 | 1583 | 27 | 1550 |  | 0.4367 | 1083.2359 | 13.029 | 0.08 | 1.6274 | 11549.8891 | 227.8826 | 1083.2434 | 4988.388 | 6561.5011 | 0.008005 | 24.659 | 63.0046 | 13.0292 | 13.2786 | 0.0069823 | 20.7755 | 0.0087826 | 27.6115 | 0.0076408 | 23.8379 | 66.3742 | 57.5404 | 23.4418
3 | 1-CEH | 75N0060 | 1-CEH | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/27/2013 | 8:43:58 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 6.6 | 0 | 6318 | 95 | 5589 | 90 | 5469 | 90 | 11793 | 101 | 7.5742 |  | 1530 | [37 empty] | Econ Closed No Compressors 55/51 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.012 | 0.009 | 62.028 | 0.039 | 55.002 | 0.028 | 51.061 | 0.018 | 74.47 | 0.02 | 72.48 | 0.04 | 73.51 | 0.04 | 0.078 | 0.002 | 0.9015 | 0.0017 | 6318 | 95 | 5469 | 90 | 7.575 | 0.144 | [6 empty] | 230.2 | 0.8 | 230.6 | 0.8 | 229.7 | 0.8 | 6.6 | 0.1 | 6.2 | 0.1 | 6.4 | 0.1 | 1411.6 | 16.5 | 1105.7 | 13.6 | 145.5 | 15.4 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.2 |  | 0.52 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1550 | [174 empty] | 73.03 | 0.03 | 72.45 | 0.04 | 71.76 | 0.04 | 73.06 | 0.03 | 73 | 0.03 | 73 | 0.03 | [18 empty] | 54.39 | 0.03 | [12 empty] | 54.76 | 0.02 | 54.57 | 0.02 | [20 empty] | 54.48 | 0.03 | 54.6 | 0.01 |  |  |  |  | 58.66 | 0.11 | 54.04 | 0.03 | [24 empty] | 54.68 | 0.08 | 54.53 | 0.05 | 74.46 | 0.02 | 74.29 | 0.03 | 74 | 0.03 | 74.15 | 0.02 | 74.14 | 0.02 | 74.14 | 0.03 |  |  | 72.87 | 0.08 | 74.05 | 0.04 | 74.16 | 0.03 | 73.68 | 0.03 | 59.51 | 0.13 | 72.32 | 0.1 | 74.27 | 0.03 | 74.32 | 0.03 | 65.65 | 0.11 | 69.19 | 0.14 | 72.02 | 0.06 | 72.35 | 0.06 | 64.44 | 0.11 | 67.81 | 0.12 | 70.13 | 0.09 | 69.99 | 0.07 | [30 empty] | 54.33 | 0.11 | 54.19 | 0.1 | 54.28 | 0.1 | 54.3 | 0.1 | 54.33 | 0.09 | 54.31 | 0.1 | [50 empty] | Economizer test | 75.012 | 0.009 | 62.028 | 0.039 | 72.753 | 0.034 | 60.581 | 0.032 | 55.002 | 0.028 | 51.061 | 0.018 | 2570.7 | 2.4 | 2461.3 | 2.3 | 1.176 | 0.002 | -0.504 | 0.003 | 0.078 | 0.002 | 0.9015 | 0.0017 | 29.282 | 0 | 1557 | 27 | 1530 |  | 0.038931 | 95.8197 | 13.03 | 0.504 | 1.4796 | 11433.5901 | 340.0455 | 95.819 | 441.23 | 10992.36 | 0.0087275 | 27.3656 | 71.2734 | 13.0298 | 13.4903 | 0.0070133 | 20.8129 | 0.0087963 | 27.6287 | 0.0083892 | 26.6326 | 74.2422 | 61.6466 | 26.272
3 | 2-OEH | 75N0073 | 2-OEH | open | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/26/2013 | 0:25:20 | 10 Ton | 0:30:00 | 75/62 70/60 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 70 | 60 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 0.1 | 6.5 | 0 | 5015 | 53 | 4236 | 62 | 1197 | 374 | 6213 | 368 | 4.037 |  |  |  |  | 110.78 | 0.01 | 0 | [32 empty] | Economizer Open No Compressor 70/60 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.002 | 0.004 | 62 | 0.043 | 70.001 | 0.016 | 60.132 | 0.092 | 74.33 | 0.03 | 72.78 | 0.03 | 73.9 | 0.01 | 0.09 | 0.002 | 0.8892 | 0.0021 | 5015 | 53 | 1197 | 374 | 4.038 | 0.267 | -2964 | 308 | 0 | 0 | 0 | 0 | 230.1 | 0.7 | 230 | 0.7 | 229.9 | 0.7 | 6.5 | 0.1 | 6.3 | 0.1 | 6.4 | 0.1 | 1378 | 15.7 | 1128.4 | 12.4 | 160.8 | 15.2 | 231 |  | 228 |  | 229 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.53 | [31 empty] | 1550 | [22 empty] | 123.15 | 0.06 | 76.01 | 0.25 | 70.64 | 0.02 | -5.36 | 0.24 | 122.73 | 0.06 | 70.4 | 0.02 | 70.44 | 0.03 | 0.04 | 0.02 | [8 empty] | 122.64 | 0.06 | 71.5 | 0.03 | 70.39 | 0.03 | 1.1 | 0.02 | 29.15 | 13.01 | 30.45 | 0.01 | -2964 | 308 | 2327 | 308 | [38 empty] | 122.29 | 0.05 | 72.21 | 0.05 | 70.24 | 0.02 | 1.98 | 0.04 | [6 empty] | 121.89 | 0.04 | 70.33 | 0.02 | 70.04 | 0.02 | -0.29 | 0.03 | [6 empty] | 121.6 | 0.04 | 71.52 | 0.04 | 69.9 | 0.02 | 1.61 | 0.04 | 70.3 | 0.04 | -3 | 0.01 | 30.43 | 0.01 | 110.85 | 0.01 | -2964 | 308 | 0 | 0 | [26 empty] | 72.96 | 0.03 | 72.69 | 0.03 | 72.9 | 0.02 | 73 | 0.04 | 72.93 | 0.04 | 72.93 | 0.04 | [18 empty] | 70.4 | 0.02 | [12 empty] | 70.89 | 0.03 | 70.41 | 0.03 | [20 empty] | 70.64 | 0.03 | 70.3 | 0.04 |  |  |  |  | 71.72 | 0.05 | 71.23 | 0.04 | [24 empty] | 69.49 | 0.06 | 69.39 | 0.06 | 74.36 | 0.02 | 74.51 | 0.03 | 74.21 | 0.03 | 74.24 | 0.03 | 74.33 | 0.03 | 74.39 | 0.03 |  |  | 73.79 | 0.07 | 73.26 | 0.05 | 72.89 | 0.05 | 72.81 | 0.06 | 73.38 | 0.04 | 71.26 | 0.09 | 70.64 | 0.08 | 71.29 | 0.1 | 71.74 | 0.06 | 71.7 | 0.05 | 70.8 | 0.05 | 70.47 | 0.06 | 71.22 | 0.04 | 71.35 | 0.04 | 71.58 | 0.05 | 70.89 | 0.05 | [30 empty] | 70.46 | 0.05 | 70.16 | 0.05 | 69.61 | 0.05 | 69.76 | 0.05 | 69.77 | 0.05 | 69.77 | 0.06 | [50 empty] | 1-OEH | 75.002 | 0.004 | 62 | 0.043 | 73.154 | 0.016 | 61.238 | 0.07 | 70.001 | 0.016 | 60.132 | 0.092 | 2560.2 | 3.1 | 2436.5 | 3 | 0.769 | 0.002 | -0.078 | 0.003 | 0.09 | 0.002 | 0.8892 | 0.0021 | 29.144 | 0.001 | 1539 | 27 | 1550 |  | 0.4367 | 1083.2359 | 13.029 | 0.08 | 1.6619 | 11376.0953 | 220.1192 | 1085.6791 | 4852.767 | 6523.3282 | 0.0087685 | 27.0755 | 71.4921 | 13.4234 | 13.5031 | 0.0087527 | 26.3589 | 0.0087802 | 27.6086 | 0.0087181 | 27.0901 | 72.8688 | 61.2117 | 26.6848 | 4445.1671 | 3758.7608 | -11 | -0.0084458 | -93.7162 | -780.1225 | -0.060894 | 0.93699 | -0.39075 | -1.3767 | 51.0184 | 4445.1671 | 5898.8709 | 4610.7376 | -6064.4414 | 4445.1671 | 100%
3 | 3-OEH | 75N0077 | 3-OEH | open | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/26/2013 | 12:18:59 | 10 Ton | 0:30:00 | 75/62 65/57 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 65 | 57 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 0.2 | 6.4 | 0 | 12989 | 104 | 12374 | 143 | 5626 | 151 | 18620 | 190 | 12.0129 | [39 empty] | Econ Open No Compressors 65/57 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.006 | 0.005 | 62.012 | 0.035 | 65.006 | 0.017 | 57.196 | 0.023 | 74.42 | 0.03 | 69.94 | 0.05 | 71.68 | 0.03 | 0.096 | 0.009 | 0.8971 | 0.0022 | 12989 | 104 | 5626 | 151 | 12.02 | 0.236 | [6 empty] | 229.9 | 0.8 | 229.8 | 0.8 | 230.1 | 0.8 | 6.4 | 0.1 | 6.3 | 0.1 | 6.4 | 0.1 | 1367.6 | 16 | 1125.7 | 14.3 | 181.9 | 15.9 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.3 |  | 6.3 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1560 | [174 empty] | 70.03 | 0.05 | 69.52 | 0.06 | 69.55 | 0.06 | 70.69 | 0.04 | 70.59 | 0.04 | 70.58 | 0.04 | [18 empty] | 65.93 | 0.12 | [12 empty] | 66.28 | 0.04 | 65.81 | 0.05 | [20 empty] | 66.23 | 0.12 | 65.78 | 0.03 |  |  |  |  | 67.22 | 0.04 | 66.76 | 0.06 | [24 empty] | 64.63 | 0.15 |  |  | 74.36 | 0.02 | 74.52 | 0.03 | 74.23 | 0.03 | 74.26 | 0.03 | 74.34 | 0.03 | 74.4 | 0.03 |  |  | 73.21 | 0.06 | 72.44 | 0.05 | 71.52 | 0.05 | 71.35 | 0.06 | 71.29 | 0.06 | 68.09 | 0.14 | 67.16 | 0.16 | 68.27 | 0.15 | 68.3 | 0.07 | 68.37 | 0.08 | 67.06 | 0.12 | 65.91 | 0.12 | 67.4 | 0.07 | 67.52 | 0.09 | 67.85 | 0.09 | 67.02 | 0.1 | [30 empty] | 66.64 | 0.2 | 66.52 | 0.2 | 65.24 | 0.19 | 65.43 | 0.2 | 65.1 | 0.11 | 65.07 | 0.12 | [50 empty] | 1-OEH | 75.006 | 0.005 | 62.012 | 0.035 | 70.291 | 0.034 | 59.635 | 0.033 | 65.006 | 0.017 | 57.196 | 0.023 | 2562.4 | 3.1 | 2457.3 | 3 | 0.786 | 0.002 | -0.076 | 0.017 | 0.096 | 0.009 | 0.8971 | 0.0022 | 29.226 | 0.001 | 1550 | 27 | 1540 |  | 0.4367 | 1083.2359 | 13.029 | 0.08 | 1.6304 | 11449.7488 | 226.9059 | 1066.4042 | 4813.7999 | 6635.9489 | 0.008507 | 26.2865 | 68.6606 | 13.2918 | 13.4277 | 0.0081208 | 24.452 | 0.0087871 | 27.6172 | 0.0083702 | 26.0118 | 70.8047 | 60.0439 | 25.6144 | 7694.4323 | 5891.8192 | 10 | 0.0044357 | 3212.8422 | 1410.2291 | 2.0728 | 0.90714 | -0.67202 | -2.1441 | 47.7145 | 7694.4323 | 18381.5072 | 4549.6532 | -15236.7281 | 7694.4323 | 100%
3 | 4-OEH 2nd | 75N0081 | 4-OEH | open | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/27/2013 | 0:49:05 | 10 Ton | 0:30:00 | 75/62 60/54 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 60 | 54 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 0.2 | 6.5 | 0 | 20697 | 80 | 20273 | 120 | 10949 | 172 | 31657 | 184 | 19.9729 | [39 empty] | Economizer Open No Compressors 60/54 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75 | 0.01 | 61.999 | 0.04 | 60.001 | 0.016 | 53.987 | 0.016 | 74.55 | 0.04 | 67.23 | 0.04 | 69.55 | 0.02 | 0.094 | 0.002 | 0.8956 | 0.0019 | 20697 | 80 | 10949 | 172 | 19.978 | 0.356 | [6 empty] | 230.1 | 0.8 | 230.3 | 0.8 | 230 | 0.8 | 6.5 | 0.1 | 6.2 | 0.1 | 6.4 | 0.1 | 1402.2 | 15.7 | 1112.9 | 14.1 | 182.9 | 15.6 | 230 |  | 231 |  | 229 |  | 3.1 |  | 3.6 |  | 3.5 |  | 0.52 | [31 empty] | 1560 | [174 empty] | 67.8 | 0.04 | 66.62 | 0.05 | 66.85 | 0.04 | 68.39 | 0.04 | 68.19 | 0.04 | 67.83 | 0.04 | [18 empty] | 60.05 | 0.07 | [12 empty] | 60.59 | 0.02 | 60.49 | 0.02 | [20 empty] | 60.25 | 0.11 | 61 | 0.02 |  |  |  |  | 61.2 | 0.02 | 60.91 | 0.02 | [24 empty] | 60.16 | 0.08 | 59.65 | 0.07 | 74.68 | 0.04 | 74.6 | 0.04 | 74.32 | 0.04 | 74.31 | 0.04 | 74.32 | 0.04 | 74.33 | 0.05 |  |  | 72.9 | 0.06 | 71.43 | 0.05 | 69.81 | 0.07 | 69.27 | 0.11 | 70.22 | 0.1 | 64.41 | 0.2 | 63.48 | 0.23 | 65.53 | 0.35 | 65.33 | 0.14 | 64.74 | 0.09 | 61.97 | 0.08 | 60.91 | 0.13 | 62.95 | 0.08 | 63.15 | 0.1 | 63.75 | 0.1 | 62.29 | 0.1 | [30 empty] | 62.76 | 0.17 | 62.84 | 0.17 | 61.1 | 0.22 | 61.06 | 0.18 | 59.93 | 0.08 | 59.88 | 0.1 | [50 empty] | 1-OEH | 75 | 0.01 | 61.999 | 0.04 | 67.527 | 0.026 | 57.879 | 0.03 | 60.001 | 0.016 | 53.987 | 0.016 | 2554.7 | 2.7 | 2461.8 | 2.6 | 0.766 | 0.002 | -0.083 | 0.002 | 0.094 | 0.002 | 0.8956 | 0.0019 | 29.229 | 0 | 1585 | 27 | 1560 |  | 0.4367 | 1083.2359 | 13.029 | 0.08 | 1.6578 | 11478.1424 | 221.5372 | 1108.8797 | 5055.801 | 6422.3414 | 0.0081888 | 25.3536 | 65.8692 | 13.1597 | 13.3543 | 0.0074378 | 22.4899 | 0.00878 | 27.6079 | 0.007938 | 24.8667 | 68.4024 | 58.6272 | 24.4629 | 10222.8149 | 6978.35 | 25 | 0.0083465 | 5654.6414 | 2410.1764 | 3.5676 | 0.90791 | -0.89063 | -2.5332 | 40.8943 | 10222.8149 | 31464.4791 | 4633.9002 | -25875.5644 | 10222.8149 | 100%
3 | C8-55-NE-CAB | 75N0143 | C8-55-NE-CAB | none | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 11:51:22 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.7 | 1.7 | 6.3 | 0 | 2713 | 17 | 3284 | 41 | 0 | 2 | 2713 | 17 | 1.783 | 899 | [38 empty] | No econo, unsealed cabinet, Inlet static location inside Cabinet, no compressor--55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--duct removed from supply sampling box (without code tester), record total static, 5 m | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.002 | 0.008 | 62.013 | 0.021 | 55 | 0.006 | 50.998 | 0.014 | 74.51 | 0.03 | 75.73 | 0.03 | 75.79 | 0 | 0.187 | 0.004 | 0.8385 | 0.0024 | 2713 | 17 | 0 | 2 | 1.783 | 0.017 | [6 empty] | 229.7 | 1.2 | 230.1 | 1.2 | 230.4 | 1.2 | 6.3 | 0.1 | 6.2 | 0.1 | 6.4 | 0.1 | 1351.4 | 14.7 | 1142.4 | 21.4 | 169.7 | 10.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.2 |  | 0.61 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1525 | [22 empty] | 93.16 | 0.02 | 55.46 | 0.01 | 55.18 | 0.01 | -0.28 | 0.02 | [16 empty] | 93.61 | 0.01 | 55.59 | 0.02 | 55.43 | 0.01 | 0.17 | 0.02 | [8 empty] | 93.55 | 0.01 | 55.32 | 0.02 | 55.4 | 0.01 | 0.07 | 0.02 | 93.06 | 0.01 | 55.12 | 0.01 | -0.07 | 0.02 | [24 empty] | 93.76 | 0 | 55.54 | 0.01 | 55.52 | 0 | 0.03 | 0.01 | [20 empty] | 93.46 | 0.01 | 55.19 | 0.02 | 55.34 | 0.01 | -0.15 | 0.02 | [12 empty] | 95.29 | 0.02 | 55.19 | 0.02 | 56.37 | 0.01 | 1.18 | 0.03 | 94.39 | 0.01 | 55.87 | 0.01 | -0.8 | 0.02 | [12 empty] | 76.65 | 0.02 | 75.71 | 0.02 | 75.4 | 0.01 | 75.36 | 0.02 | 75.67 | 0.02 |  |  | 55.27 | 0.02 |  |  | 56.01 | 0.02 | 56.25 | 0.01 | 56.13 | 0.02 |  |  | 55.45 | 0.02 | 55.87 | 0.02 | 55.81 | 0.01 |  |  | 55.61 | 0.01 | [28 empty] | 76.23 | 0.01 | [8 empty] | 55.06 | 0.01 | 55.05 | 0.02 | [8 empty] | 55.9 | 0.02 | 55.66 | 0.01 | 56.16 | 0.03 | 55.19 | 0.02 | [10 empty] | 56.22 | 0.01 | 55.11 | 0.03 | 54.85 | 0.03 | 75.06 | 0.02 | 74.98 | 0.03 | 75.21 | 0.02 | 75.2 | 0.02 | 75.14 | 0.03 | 75.15 | 0.03 |  |  | 74.51 | 0.02 | 74.54 | 0.03 | 74.74 | 0.02 | 74.6 | 0.03 | 75.18 | 0.03 | 75 | 0.03 | 74.85 | 0.04 | 74.53 | 0.03 | 74.53 | 0.04 | 75 | 0.03 | 74.8 | 0.03 | 74.28 | 0.04 | 74.62 | 0.03 | 74.73 | 0.02 | 74.76 | 0.02 | 74.28 | 0.02 | [78 empty] | 55.37 | 0.05 | [8 empty] | 75.82 | 0.02 | 75.87 | 0.02 | No Economizer | 75.002 | 0.008 | 62.013 | 0.021 | 76.014 | 0.009 | 62.354 | 0.016 | 55 | 0.006 | 50.998 | 0.014 | 2480.7 | 3.6 | 2369.7 | 3.4 | 1.166 | 0.001 | -0.488 | 0.003 | 0.187 | 0.004 | 0.8385 | 0.0024 | 29.352 | 0.001 | 1521 | 11 | 1510 |  |  | 0 |  |  | 1.5371 | 10963.6188 | 324.6064 | 0 | 0 | 10963.6188 | 0.0087887 | 27.618 | 74.4769 | 13.0295 | 13.576 | 0.0069803 | 20.7765 | 0.0087887 | 27.618 | 0.0087753 | 27.8501 | 75.002 | 62.013 | 27.4752 | 1565.119 | 1381.7194 | 11 | 0.023987 | -2480.6295 | -2664.0291 | -1.6309 | 0.97741 | -0.14276 | -0.52512 | 51.7563 | 1565.119 | -2545.1049 | 4110.2238 | 0 | 1565.119 | 100%
3 | Run 2-21A no optimized charge | 75N0005 | Run 2-21A A Test | none | on | on |  | sealed | unsealed |  | 10 |  | 0 | 0 | CUST 9 | 2/26/2013 | 13:26:17 | 10 Ton | 0:30:00 | 80/67 95 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 80 | 67 | 95 |  | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 0 | 27.5 | 0 | 56211 | 61 | 55660 | 153 | 23527 | 78 | 79761 | 107 | 9.613 |  |  |  |  | 113.96 | 0.01 | 2.76 | [32 empty] | . | Manuf. charge R-22: 3000 scfm at .25 ESP (per client): sealed air leaks on unit`s base and doors: 36 hours @ 210 microns vacuum: The blower wheel was changed out from a 7` to 10` pulley with A55 Belt. manuf motor pulley adj. | 79.844 | 0.011 | 67.17 | 0.01 | 94.871 | 0.014 | 70.461 | 0.016 | 79.38 | 0.06 | 62.79 | 0.04 | 66.33 | 0.02 | -1.022 | 0.003 | 1.2997 | 0.0021 | 56211 | 61 | 23527 | 78 | 9.613 | 0.03 | 82026 | 94 | 9.886 | 0.029 | 2.76 | 0.17 | 229.8 | 0.7 | 229.9 | 0.7 | 230.2 | 0.7 | 27.5 | 0.1 | 25 | 0.1 | 25.3 | 0.1 | 6280.8 | 28.7 | 3165.1 | 34 | 2016.5 | 24.7 | 229 |  | 230 |  | 229 |  | 5.5 |  | 5.8 |  | 5.6 |  | 0.43 | 228 |  | 230 |  | 229 |  | 9.9 |  | 9.3 |  | 10 |  | 3240 |  | 0.84 | 230 | 228 | 228 | 10 | 9.4 | 10.1 | 3270 | 0.84 | [31 empty] | 257.44 | 0.32 | 196.39 | 0.05 | 119.18 | 0.09 | 77.21 | 0.09 | 246.87 | 0.26 | 101.08 | 0.05 | 116.11 | 0.08 | 15.03 | 0.08 | [8 empty] | 71.95 | 0.07 | 72.93 | 0.04 | 42.05 | 0.04 | 30.87 | 0.06 | 582.69 | 1.08 | 39.82 | 0.02 | 82026 | 94 | 43200 | 81 | [38 empty] | 257.67 | 0.33 | 201.84 | 0.09 | 119.25 | 0.09 | 82.6 | 0.09 | [6 empty] | 249.44 | 0.25 | 100.32 | 0.05 | 116.87 | 0.07 | 16.55 | 0.09 | [6 empty] | 69.86 | 0.08 | 77.25 | 0.05 | 40.64 | 0.05 | 36.61 | 0.09 | 100.94 | 0.05 | 567.07 | 1.15 | 39.58 | 0.02 | 114.67 | 0.01 | 82026 | 94 | 42581 | 89 | [26 empty] | 62.07 | 0.04 | 62.38 | 0.05 | 62.18 | 0.05 | 61.93 | 0.05 | 62.48 | 0.04 | [34 empty] | 101.89 | 0.05 | 103.78 | 9.69 | [20 empty] | 100.07 | 0.06 | 100.94 | 0.05 | [12 empty] | 75.71 | 0.03 | [18 empty] | 96.36 | 0.17 | 94.38 | 0.13 | 80.6 | 0.06 | 80.42 | 0.06 | 80.31 | 0.05 | 80.34 | 0.06 | 80.14 | 0.05 | 80.77 | 0.05 |  |  | 81.24 | 0.06 | 80.76 | 0.05 | 80.82 | 0.05 | 80.77 | 0.05 | 80.19 | 0.05 | 80.65 | 0.05 | 80.04 | 0.05 | 80.2 | 0.06 | 79.88 | 0.06 | 79.96 | 0.05 | 79.91 | 0.06 | 79.98 | 0.05 | 79.85 | 0.06 | 79.93 | 0.06 | 79.57 | 0.05 | [94 empty] | No Economizer | 79.844 | 0.011 | 67.17 | 0.01 | 63.091 | 0.01 | 59.143 | 0.013 | 94.871 | 0.014 | 70.461 | 0.016 | 3082 | 2.5 | 2964.5 | 2.4 | 0.251 | 0.002 | -0.377 | 0.002 | -1.022 | 0.003 | 1.2997 | 0.0021 | 29.165 | 0.001 | 8297 | 24 | 1100 |  |  | 0 |  |  | 1.032 | 13949.6288 | 87.4159 | 0 | 0 | 13949.6288 | 0.011239 | 31.4853 | 62.059 | 14.0656 | 13.2563 | 0.01018 | 33.9987 | 0.011239 | 31.4853 | 0.0097655 | 25.7766 | 79.844 | 67.17 | 25.5244 | 83151.9956 | 59542.4884 | 7197 | 0.2954 | 79696.046 | 56086.5388 | 9.6054 | 0.29242 | -5.9609 | -17.785 | 54.7092 | 83151.9956 | 79634.6411 | 3517.3546 | 0 | 83151.9956 | 100%
3 | Run 3-21A AHRI Out of the Box | 75N0006 | Run 3-21A AHRI out of box | none | on | on | 3 turns | sealed | sealed |  | 10 |  | 0 | 0 | CUST 10 | 9/12/2013 | 17:15:54 | 10 Ton | 0:30:00 | 80/67 95 | ENG 1 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 80 | 67 | 95 |  | 7.6 | 8.1 | 7.6 | 8.1 | 231.1 | 0.2 | 27.8 | 0 | 58347 | 125 | 60486 | 189 | 22337 | 110 | 80704 | 171 | 9.4712 |  |  |  |  | 112.7 | 0.05 | 5.61 | [32 empty] | . | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: Sealed the unit and ductwork: 10` blower pulley with A55 belt at 3000 scfm 0.25 static: motor pulley 3 turns opened form complete closed: no economizer. | 80.001 | 0.016 | 67.197 | 0.017 | 94.836 | 0.063 | 75.84 | 0.015 | 80.41 | 0.05 | 62.4 | 0.04 | 65.27 | 0.01 | -1.108 | 0.007 | 1.2896 | 0.0049 | 58347 | 125 | 22337 | 110 | 9.471 | 0.034 | 85500 | 85 | 10.034 | 0.03 | 5.61 | 0.21 | 231.1 | 0.5 | 230.4 | 0.5 | 230.6 | 0.5 | 27.8 | 0.1 | 25.4 | 0.1 | 28.6 | 0.1 | 6388.5 | 25.8 | 3702.8 | 30.2 | 2132.8 | 23.4 | 231 |  | 230 |  | 230 |  | 6 |  | 5.9 |  | 5.7 |  | 0.44 | 229 |  | 230 |  | 229 |  | 11 |  | 10.5 |  | 10.1 |  | 3410 |  | 0.82 | 230 | 229 | 229 | 10.6 | 9.7 | 10.3 | 3310 | 0.82 | [8 empty] | 8520 | [22 empty] | 276.45 | 0.45 | 189.99 | 0.1 | 124.5 | 0.12 | 65.49 | 0.15 | 257.03 | 0.44 | 102.46 | 0.13 | 119.08 | 0.13 | 16.62 | 0.11 | [8 empty] | 78.31 | 0.09 | 67.85 | 0.26 | 46.24 | 0.05 | 21.61 | 0.3 | 566.05 | 0.81 | 40.25 | 0.04 | 85500 | 85 | 41011 | 67 | [38 empty] | 266.81 | 0.41 | 206.37 | 0.08 | 121.84 | 0.11 | 84.52 | 0.08 | [6 empty] | 254.99 | 0.41 | 103.66 | 0.09 | 118.49 | 0.12 | 14.84 | 0.08 | [6 empty] | 69.46 | 0.08 | 79.47 | 0.04 | 40.4 | 0.05 | 39.06 | 0.08 | 102.03 | 0.11 | 651.24 | 0.97 | 40.63 | 0.03 | 115.24 | 0.01 | 85500 | 85 | 48585 | 72 | [26 empty] | 61.77 | 0.04 | 61.93 | 0.03 | 61.99 | 0.03 | 61.86 | 0.05 | 61.66 | 0.04 | 61.56 | 0.04 | [32 empty] | 102.82 | 0.1 | 102.77 | 0.09 | [20 empty] | 101.84 | 0.1 | 102.03 | 0.11 |  |  |  |  | 70.95 | 0.23 | 79.6 | 0.04 | [24 empty] | 94.58 | 0.12 | 93.47 | 0.22 | 80.57 | 0.04 | 80.64 | 0.04 | 80.24 | 0.06 | 80.72 | 0.05 | 80.52 | 0.05 | 80.54 | 0.04 |  |  | 81.05 | 0.11 | 81.06 | 0.08 | 81.07 | 0.06 | 81.08 | 0.05 | 81.29 | 0.04 | 80.99 | 0.14 | 80.93 | 0.11 | 80.9 | 0.08 | 81.23 | 0.05 | 81.27 | 0.05 | 80.82 | 0.06 | 80.88 | 0.05 | 81.05 | 0.05 | 81.16 | 0.05 | 81.32 | 0.05 | 80.89 | 0.07 | [92 empty] | No Economizer | 80.001 | 0.016 | 67.197 | 0.017 | 62.63 | 0.011 | 59.052 | 0.017 | 94.836 | 0.063 | 75.84 | 0.015 | 3061.3 | 5.9 | 2961.1 | 5.7 | 0.25 | 0.003 | -0.432 | 0.003 | -1.108 | 0.007 | 1.2896 | 0.0049 | 29.276 | 0.001 | 8521 | 25 | 1190 |  |  | 0 |  |  | 1.1308 | 13867.7354 | 86.9677 | 0 | 0 | 13867.7354 | 0.011221 | 31.5047 | 61.4992 | 14.1022 | 13.245 | 0.014704 | 38.9805 | 0.011221 | 31.5047 | 0.009818 | 25.7211 | 80.001 | 67.197 | 25.4448 | 84036.2987 | 61578.6897 | 7331 | 0.29774 | 80271.6496 | 57814.0406 | 9.4204 | 0.25215 | -6.0598 | -18.5018 | 55.2612 | 84036.2987 | 80204.3941 | 3831.9046 | 0 | 84036.2987 | 100%
3 | 3-21A AHRI Verification H | 75N0007 | 3-21A AHRI Verification H | none | on | on | 6 turns | sealed | sealed |  | 10 | horizontal | 0 | 0 | CUST 10 | 9/19/2013 | 19:19:57 | 10 Ton | 0:30:00 | 80/67 95 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 8.0 lbs / ck2: 8.5 lbs | 230/208/3 | TU2 | AHRI 340-360 | 80 | 67 | 95 |  | 8 | 8.5 | 7.6 | 8.1 | 232.1 | 0.2 | 27.3 | 0 | 59613 | 75 | 60499 | 363 | 26631 | 80 | 86269 | 122 | 10.4708 |  |  |  |  | 110.73 | 0.12 | 0.45 | [32 empty] | . | New R22 CK 1 : 8.0 lbs / Ck 2 : 8 lbs 8 oz: Sealed the unit and ductwork: 10` blower pulley with A55 belt @ 0.25 SP: motor pulley 6 turns opened from closed: No econo Meriam set to 100%: Horizontal airflow disch config. set on floor | 79.699 | 0.014 | 67.249 | 0.017 | 94.543 | 0.019 | 70.768 | 0.006 | 79.7 | 0.14 | 59.16 | 0.03 | 64.07 | 0.03 | -0.663 | 0.002 | 0.9479 | 0.0021 | 59613 | 75 | 26631 | 80 | 10.471 | 0.028 | 86658 | 96 | 10.517 | 0.026 | 0.45 | 0.18 | 232.1 | 0.4 | 231.4 | 0.4 | 231.6 | 0.4 | 27.3 | 0.1 | 24.9 | 0.1 | 28.2 | 0.1 | 6306 | 22.8 | 3777.2 | 26.6 | 1933.2 | 19.9 | 230 |  | 229 |  | 228 |  | 5.5 |  | 5.4 |  | 5.4 |  | 0.35 | 228 |  | 229 |  | 229 |  | 11.1 |  | 10.6 |  | 10.1 |  | 3450 |  | 0.81 | 229 | 229 | 229 | 10.7 | 9.8 | 10.4 | 3370 | 0.87 | [8 empty] | 8280 | [22 empty] | 275.94 | 0.16 | 184.78 | 0.09 | 124.35 | 0.04 | -60.42 | 0.1 | 256.12 | 0.16 | 101.18 | 0.05 | 118.81 | 0.05 | 17.63 | 0.04 | [8 empty] | 78.29 | 0.05 | 56.96 | 0.67 | 46.21 | 0.03 | 10.75 | 0.67 | 666.18 | 0.37 | 39.85 | 0.02 | 86658 | 96 | 47221 | 88 | [38 empty] | 264.98 | 0.25 | 203.51 | 0.06 | 121.32 | 0.07 | 82.19 | 0.07 | [6 empty] | 252.93 | 0.24 | 102.33 | 0.04 | 117.89 | 0.07 | 15.56 | 0.06 | [6 empty] | 69.59 | 0.06 | 76.27 | 0.05 | 40.47 | 0.04 | 35.8 | 0.07 | 101.63 | 0.06 | 570 | 0.51 | 40.21 | 0.01 | 114.67 | 0.01 | 86658 | 96 | 42440 | 36 | [26 empty] | 58.73 | 0.05 | 58.95 | 0.04 | 59.36 | 0.05 | 59.46 | 0.04 | 59.5 | 0.04 | 59.6 | 0.04 | [18 empty] | 101.18 | 0.05 | [12 empty] | 102.13 | 0.04 | 101.5 | 0.06 | [20 empty] | 101.4 | 0.05 | 101.63 | 0.06 |  |  |  |  | 62.6 | 0.46 | 76.19 | 0.04 | [24 empty] | 93.95 | 0.06 | 94.83 | 0.12 | 80.03 | 0.08 | 80.18 | 0.08 | 79.84 | 0.08 | 79.92 | 0.1 | 79.99 | 0.1 | 80.03 | 0.09 |  |  | 80.33 | 0.1 | 80.35 | 0.09 | 80.48 | 0.08 | 80.57 | 0.09 |  |  | 80.29 | 0.12 | 80.29 | 0.11 | 80.38 | 0.11 | 80.72 | 0.08 | 80.76 | 0.07 | 80.6 | 0.1 | 80.66 | 0.09 | 80.9 | 0.07 | 80.91 | 0.09 | 80.89 | 0.08 | 80.53 | 0.1 | [30 empty] | 88.71 | 0.13 | 88.5 | 0.13 | 84.35 | 0.13 | 83.83 | 0.16 | 84.34 | 0.08 | 83.65 | 0.04 | [50 empty] | No Economizer | 79.699 | 0.014 | 67.249 | 0.017 | 59.469 | 0.022 | 57.077 | 0.019 | 94.543 | 0.019 | 70.768 | 0.006 | 2619.2 | 3 | 2539.5 | 2.8 | 0.25 | 0.002 | -0.291 | 0.002 | -0.663 | 0.002 | 0.9479 | 0.0021 | 29.224 | 0.001 | 8239 | 19 | 850 |  |  | 0 |  |  | 0.92323 | 11940.5128 | 74.5853 | 0 | 0 | 11940.5128 | 0.011332 | 31.5516 | 58.5458 | 14.0599 | 13.1612 | 0.0105 | 34.2718 | 0.011332 | 31.5516 | 0.0093586 | 24.4491 | 79.699 | 67.249 | 24.2237 | 87498.8791 | 60619.2929 | 7389 | 0.28822 | 84852.3888 | 57972.8025 | 10.2989 | 0.17436 | -7.3279 | -21.1532 | 54.0786 | 87498.8791 | 84807.358 | 2691.5212 | 0 | 87498.8791 | 100%
3 | Run 3-20N95 | 75N0011 | Run 3-20N95 | none | on | on | 4.5 turns | sealed | unsealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/21/2013 | 17:39:26 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 |  | 7.6 | 8.1 | 230.4 | 0.2 | 28.4 | 0 | 56383 | 112 | 55977 | 274 | 14656 | 165 | 71052 | 164 | 8.087 |  |  |  |  | 109.03 | 0.02 | 10.65 | [32 empty] | . | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo Meriam set to 100%: Horizontal airflow disch config. set on floor | 74.996 | 0.023 | 61.999 | 0.039 | 94.806 | 0.022 | 75.053 | 0.023 | 74.5 | 0.11 | 55.39 | 0.05 | 60.29 | 0.03 | 0.274 | 0.002 | 0.99 | 0.0019 | 56383 | 112 | 14656 | 165 | 8.087 | 0.033 | 79520 | 63 | 9.051 | 0.03 | 10.65 | 0.21 | 230.4 | 0.8 | 229.6 | 0.8 | 229.6 | 0.8 | 28.4 | 0.1 | 25.9 | 0.1 | 28.9 | 0.1 | 6530.7 | 35.2 | 3630.7 | 42.6 | 2255.7 | 28.9 | 230.5 |  | 229.5 |  | 229.7 |  | 6.4 |  | 6.3 |  | 6.2 |  | 0.53 | 230 |  | 230 |  | 230.9 |  | 11 |  | 10.3 |  | 10 |  | 3360 |  | 0.81 | 231.1 | 230.1 | 230.2 | 10.7 | 9.6 | 10.1 | 3290 | 0.81 | [8 empty] | 8810 | [22 empty] | 267.47 | 0.2 | 177.57 | 0.13 | 122.02 | 0.06 | 55.55 | 0.12 | 248.86 | 0.21 | 101.74 | 0.06 | 116.7 | 0.06 | 14.96 | 0.04 | [8 empty] | 72.6 | 0.07 | 45.64 | 0.1 | 42.5 | 0.05 | 3.14 | 0.08 | 636.65 | 0.45 | 40.03 | 0.02 | 79520 | 63 | 43929 | 34 | [38 empty] | 258.38 | 0.31 | 200.7 | 0.07 | 119.46 | 0.09 | 81.24 | 0.07 | [6 empty] | 246.76 | 0.29 | 102.74 | 0.07 | 116.09 | 0.09 | 13.34 | 0.07 | [6 empty] | 66.4 | 0.05 | 72.37 | 0.07 | 38.26 | 0.04 | 34.11 | 0.07 | 101.89 | 0.07 | 547 | 0.6 | 40.34 | 0.02 | 114.14 | 0.01 | 79520 | 63 | 40370 | 44 | [26 empty] | 55.77 | 0.07 | 55.4 | 0.07 | 55.42 | 0.07 | 56.27 | 0.06 | 56.21 | 0.06 | 56.14 | 0.07 | [32 empty] | 102.36 | 0.05 | 101.98 | 0.07 | [20 empty] | 101.87 | 0.05 | 101.89 | 0.07 |  |  |  |  | 48.43 | 0.05 | 72.04 | 0.07 | [24 empty] | 94.35 | 0.06 | 95.56 | 0.11 | 75.04 | 0.1 | 74.97 | 0.09 | 74.61 | 0.09 | 74.63 | 0.09 | 74.66 | 0.1 | 74.67 | 0.1 |  |  | 77.46 | 0.08 | 75.51 | 0.1 | 75 | 0.1 | 74.93 | 0.1 | 76.82 | 0.08 | 76.94 | 0.09 | 76.08 | 0.1 | 75.67 | 0.1 | 75.99 | 0.1 | 75.85 | 0.08 | 76.07 | 0.09 | 76.31 | 0.09 | 75.38 | 0.1 | 75.03 | 0.1 | 74.8 | 0.11 | 74.55 | 0.12 | [30 empty] | 92.23 | 0.14 | 90.83 | 0.12 | 91.34 | 0.15 | 92.44 | 0.19 | 92.13 | 0.14 | 90.32 | 0.11 | [50 empty] | No Economizer | 74.996 | 0.023 | 61.999 | 0.039 | 55.748 | 0.041 | 52.858 | 0.045 | 94.806 | 0.022 | 75.053 | 0.023 | 2663.9 | 2.6 | 2613.2 | 2.5 | 1.221 | 0.002 | -0.303 | 0.002 | 0.274 | 0.002 | 0.99 | 0.0019 | 29.211 | 0.001 | 8786 | 29 | 1550 |  |  | 0 |  |  | 1.3646 | 12243.2245 | 374.8465 | 0 | 0 | 12243.2245 | 0.0087809 | 27.608 | 54.3834 | 14.0957 | 13.0549 | 0.014014 | 38.2119 | 0.0087809 | 27.608 | 0.007811 | 21.8603 | 74.996 | 61.999 | 21.5281 | 74437.6984 | 60567.4444 | 7236 | 0.33177 | 70426.8993 | 56556.6453 | 8.0158 | 0.18317 | -6.0799 | -20.6126 | 49.7612 | 74437.6984 | 70370.1342 | 4067.5641 | 0 | 74437.6984 | 100%
3 | Run 1-1A Out of the Box Baseline | 75N0034 | Run 1-1A Out of the Box Baseline | none | on | off |  | unsealed | unsealed |  | 7 |  | 0 | 0 | CUST 9 | 3/1/2013 | 16:45:04 | 10 Ton | 0:30:00 | 80/67 95 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 80 | 67 | 95 |  | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 0 | 19.7 | 0 | 20485 | 39 | 20759 | 198 | 13757 | 66 | 34255 | 83 | 6.027 |  |  |  |  | 114.04 | 0.01 | 7.3 | [32 empty] | . | Manuf. charge R-22: 3000 scfm at .8 ESP (per client): unsealed tape on unit`s base and doors: After two Brun In`s; The blower wheel is a 7` with A49 Belt. manuf mtr pully. New 2 compr/filters. The unit operated with Compressor 1 on and Compressor 2 off. | 79.849 | 0.008 | 67.151 | 0.011 | 94.865 | 0.007 | 69.108 | 0.042 | 79.54 | 0.09 | 73.46 | 0.07 | 74.69 | 0.01 | -0.468 | 0.005 | 1.3361 | 0.0028 | 20485 | 39 | 13757 | 66 | 6.027 | 0.031 | 36951 | 31 | 6.501 | 0.03 | 7.3 | 0.23 | 229.9 | 0.7 | 230.1 | 0.7 | 230.2 | 0.7 | 19.7 | 0.1 | 17.1 | 0.1 | 17 | 0.1 | 4474.2 | 24 | 2049.8 | 25.7 | 1209.7 | 20 | 229.7 |  | 230 |  | 229.4 |  | 6.5 |  | 6.7 |  | 6.6 |  | 0.57 | 228.3 |  | 229.1 |  | 228.1 |  | 10.6 |  | 10.4 |  | 10.7 |  | 3280 |  | 2283 | [39 empty] | 257.3 | 0.16 | 204.22 | 0.05 | 119.19 | 0.05 | 85.03 | 0.06 | 247.24 | 0.12 | 100.11 | 0.03 | 116.27 | 0.04 | 16.16 | 0.04 | [8 empty] | 71.39 | 0.04 | 73.32 | 0.03 | 41.79 | 0.03 | 31.52 | 0.05 | 575.45 | 0.4 | 39.51 | 0.01 | 36951 | 31 | 42890 | 31 | [112 empty] | 74.07 | 0.05 | 72.86 | 0.07 | 72.65 | 0.07 | 73.53 | 0.07 | 81.38 | 0.06 | 73.53 | 0.06 | [32 empty] | 99.77 | 0.05 | 99.82 | 2.54 | [20 empty] | 98.74 | 0.07 | 106.13 | 0.09 | [12 empty] | 74.46 | 0.07 | [18 empty] | 94.01 | 0.08 | 95.29 | 0.1 | 81.63 | 0.09 | 81.23 | 0.06 | 81.21 | 0.06 | 81.1 | 0.05 | 81.05 | 0.06 | 81.87 | 0.07 |  |  | 82.46 | 0.06 | 81.82 | 0.05 | 81.95 | 0.05 | 81.92 | 0.06 | 81.24 | 0.06 | 81.82 | 0.05 | 81.03 | 0.06 | 81.25 | 0.06 | 80.8 | 0.06 | 81.11 | 0.06 | 80.91 | 0.06 | 80.94 | 0.05 | 80.63 | 0.06 | 80.8 | 0.05 | 80.47 | 0.05 | [94 empty] | No Economizer | 79.849 | 0.008 | 67.151 | 0.011 | 73.846 | 0.01 | 63.915 | 0.014 | 94.865 | 0.007 | 69.108 | 0.042 | 3128.3 | 3.3 | 3000.1 | 3.1 | 0.877 | 0.003 | -0.387 | 0.002 | -0.468 | 0.005 | 1.3361 | 0.0028 | 29.522 | 0.001 | 5684 | 26 | 1720 |  |  | 0 |  |  | 1.4463 | 13869.0033 | 309.101 | 0 | 0 | 13869.0033 | 0.011224 | 31.4699 | 72.3997 | 14.0567 | 13.5336 | 0.0091326 | 32.8419 | 0.011224 | 31.4699 | 0.010344 | 29.0377 | 79.849 | 67.151 | 28.6839 | 38638.0023 | 24795.3378 | 3964 | 0.35015 | 33822.604 | 19979.9395 | 5.9505 | 0.75004 | -2.7859 | -7.4493 | 50.0472 | 38638.0023 | 33731.8883 | 4906.1139 | 0 | 38638.0023 | 100%
3 | Run 1-1B Out of the Box Baseline | 75N0035 | Run 1-1B Out of the Box Baseline | none | on | off |  | unsealed | unsealed |  | 7 |  | 0 | 0 | CUST 9 | 3/1/2013 | 19:16:14 | 10 Ton | 0:30:00 | 80/67 82 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 80 | 67 | 82 |  | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 0 | 18.5 | 0 | 21532 | 47 | 21781 | 256 | 13217 | 73 | 34761 | 86 | 6.812 |  |  |  |  | 114.52 | 0.01 | 2.23 | [32 empty] | . | Manuf. charge R-22: 3000 scfm at .8 ESP (per client): unsealed tape on unit`s base and doors: After two Brun In`s; The blower wheel is a 7` with A49 Belt. manuf mtr pully. New 2 compr/filters. The unit operated with Compressor 1 on and Compressor 2 off. | 79.852 | 0.01 | 67.15 | 0.012 | 81.884 | 0.009 | 64.831 | 0.013 | 79.66 | 0.08 | 73.27 | 0.04 | 74.45 | 0.01 | -0.459 | 0.006 | 1.3338 | 0.0036 | 21532 | 47 | 13217 | 73 | 6.812 | 0.038 | 35555 | 30 | 6.967 | 0.037 | 2.23 | 0.25 | 229.9 | 0.6 | 230.1 | 0.6 | 230.1 | 0.6 | 18.5 | 0.1 | 15.8 | 0.1 | 15.8 | 0.1 | 4179.6 | 21.2 | 2006.9 | 22.1 | 923.7 | 19.2 | 229.5 |  | 229.8 |  | 228.1 |  | 6.5 |  | 6.7 |  | 6.5 |  | 0.57 | 229.8 |  | 229.8 |  | 228.1 |  | 9.3 |  | 9.1 |  | 8.6 |  | 2710 |  | 0.75 | [39 empty] | 210.18 | 0.14 | 189.15 | 0.04 | 104.76 | 0.04 | 84.39 | 0.05 | 201.09 | 0.11 | 86.11 | 0.04 | 101.72 | 0.04 | 15.61 | 0.04 | [8 empty] | 63.27 | 0.04 | 73.68 | 0.03 | 36.15 | 0.03 | 37.53 | 0.04 | 522.91 | 0.36 | 35.17 | 0.01 | 35555 | 30 | 41494 | 30 | [112 empty] | 73.93 | 0.03 | 72.78 | 0.04 | 72.6 | 0.04 | 73.51 | 0.05 | 76.73 | 0.03 | 73.37 | 0.03 | [32 empty] | 85.64 | 0.04 | 84.95 | 7.13 | [20 empty] | 84.64 | 0.05 | 93.09 | 0.08 | [12 empty] | 74.4 | 0.04 | [18 empty] | 81.59 | 0.08 | 81.59 | 0.08 | 81.25 | 0.1 | 80.95 | 0.08 | 80.97 | 0.07 | 80.84 | 0.07 | 80.79 | 0.07 | 81.25 | 0.08 |  |  | 81.02 | 0.07 | 81 | 0.07 | 80.9 | 0.06 | 80.82 | 0.07 | 80.61 | 0.06 | 80.53 | 0.05 | 80.59 | 0.06 | 80.59 | 0.06 | 80.58 | 0.07 | 80.64 | 0.07 | 80.55 | 0.07 | 80.52 | 0.06 | 80.44 | 0.07 | 80.46 | 0.06 | 80.21 | 0.06 | [94 empty] | No Economizer | 79.852 | 0.01 | 67.15 | 0.012 | 73.531 | 0.018 | 63.86 | 0.012 | 81.884 | 0.009 | 64.831 | 0.013 | 3123.1 | 4.2 | 3000 | 4 | 0.883 | 0.003 | -0.385 | 0.002 | -0.459 | 0.006 | 1.3338 | 0.0036 | 29.557 | 0.001 | 5103 | 26 | 1720 |  |  | 0 |  |  | 1.4457 | 13853.8264 | 311.2054 | 0 | 0 | 13853.8264 | 0.011222 | 31.469 | 72.0853 | 13.7272 | 13.5259 | 0.0090755 | 29.6112 | 0.011222 | 31.469 | 0.010381 | 29.0011 | 79.852 | 67.15 | 28.6474 | 39089.6265 | 25823.6162 | 3383 | 0.29538 | 34281.4104 | 21015.4001 | 6.7179 | 0.72522 | -2.8216 | -7.7667 | 51.5873 | 39089.6265 | 34190.5013 | 4899.1252 | 0 | 39089.6265 | 100%
3 | Run 1-1C-D Out of the Box Baseline Cycle #1 | 75N0040 | Run 1-1D Out of the Box Baseline | none | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 9 | 3/1/2013 | 22:29:07 | 10 Ton |  | 80/57 82 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 |  |  | 80 | 57 | 82 |  | 7.6 | 8.1 | 7.6 | 8.1 | [16 empty] | 6.177 |  |  |  | 1 | 6.533 | 81.484 | 30.017 | 58.626 | 0.68 | 1059.1 | 3000.1 | 13.592 | 31441.369 | 0.2416 | 3631.649 | 0.00368 | 10.2253 | 64.02 | 24.95 | 66.802 | 523 | 6.627 | 24.95 | 6.81 | 0 | 0 | 0.127 | 548 | -0.084 | 563.5 | 563.49 | 7.096 | 563.49 | 1.03 | [516 empty] | No Economizer | 80.443 |  | 54.488 |  | 72.251 |  | 52.82 | [5 empty] | 2970.7 |  | 2890 |  | 0.941 |  |  |  | -0.301 |  | 1.2207 |  | 29.608 |  | 4754 |  | 0 |  |  | 0 |  |  | 0.79295 | 13260.461 | 319.4865 | 0 | 0 | 13260.461 | 0.0029465 | 22.5378 | 71.4581 | 11.5938 | 13.4416 | 0.00078408 | 0.83191 | 0.0029465 | 22.5378 | 0.0039277 | 21.6335 | 80.443 | 54.488 | 21.4419 | 14532.2679 | 28594.6883 | 3694.9 | 0.86777 | 12007.9672 | 26070.3876 | 2.5259 | 0.73554 | -1.0959 | -8.9849 | 46.4679 | 14532.2679 | 11990.3699 | 2541.898 | 0 | 14532.2679 | 100%
3 | Run 1-1C-D Out of the Box Baseline Cycle #2 | 75N0041 | Run 1-1D Out of the Box Baseline #2 | none | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 9 | 3/1/2013 | 23:23:46 | 10 Ton |  | 80/57 82 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 |  |  | 80 | 57 | 82 |  | 7.6 | 8.1 | 7.6 | 8.1 | [16 empty] | 6.177 |  |  |  | 2 | 6.533 | 81.613 | 30.017 | 58.411 | 0.68 | 1055.1 | 3000.1 | 13.592 | 31441.369 | 0.2416 | 2964.268 | 0.00368 | 8.3462 | 57.752 | 20.73 | 54.526 | 496.6 | 5.73 | 20.73 | 6.81 | 0 | 0 | 0.189 | 517.31 | 0.089 | 508.3 | 508.32 | 6.507 | 508.32 | 0.98 | [516 empty] | No Economizer | 79.565 |  | 53.954 |  | 72.253 |  | 52.788 | [5 empty] | 2957.7 |  | 2879.1 |  | 0.969 |  |  |  | -0.276 |  | 1.2252 |  | 29.609 |  | 4783 |  | 0 |  |  | 0 |  |  | 0.78322 | 13202.5244 | 327.7522 | 0 | 0 | 13202.5244 | 0.002853 | 22.2234 | 71.4698 | 11.5938 | 13.4415 | 0.00078408 | 0.83191 | 0.002853 | 22.2234 | 0.0039099 | 21.6145 | 79.565 | 53.954 | 21.4252 | 10538.0279 | 25650.5566 | 3727.9 | 1.2074 | 8055.5899 | 23168.1186 | 1.6842 | 0.74522 | -0.79818 | -8.0952 | 47.7917 | 10538.0279 | 8038.3664 | 2499.6615 | 0 | 10538.0279 | 100%
3 | Run 1-1C-D Out of the Box Baseline Cycle #3 | 75N0042 | Run 1-1D Out of the Box Baseline #3 | none | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 9 | 3/1/2013 | 23:53:46 | 10 Ton |  | 80/57 82 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 |  |  | 80 | 57 | 82 |  | 7.6 | 8.1 | 7.6 | 8.1 | [16 empty] | 6.177 |  |  |  | 3 | 6.533 | 81.84 | 30.017 | 58.284 | 0.68 | 1055 | 3000.1 | 13.592 | 31441.369 | 0.2416 | 2986.443 | 0.00368 | 8.4087 | 57.833 | 21.86 | 54.934 | 503.4 | 5.686 | 21.86 | 6.81 | 0 | 0 | 0.19 | 525.25 | 0.098 | 509 | 509.03 | 6.4763 | 509.03 | 0.97 | [516 empty] | No Economizer | 79.625 |  | 53.819 |  | 72.2 |  | 52.601 | [5 empty] | 2957.1 |  | 2879.3 |  | 0.974 |  |  |  | -0.272 |  | 1.2237 |  | 29.613 |  | 4838 |  | 0 |  |  | 0 |  |  | 0.7813 | 13201.8687 | 329.4663 | 0 | 0 | 13201.8687 | 0.0027645 | 22.1409 | 71.4187 | 11.5938 | 13.4395 | 0.00078408 | 0.83191 | 0.0027645 | 22.1409 | 0.0038208 | 21.5044 | 79.625 | 53.819 | 21.3156 | 10896.3243 | 26001.251 | 3783 | 1.1849 | 8420.0777 | 23525.0044 | 1.7404 | 0.74502 | -0.82536 | -8.2063 | 47.4409 | 10896.3243 | 8403.3049 | 2493.0194 | 0 | 10896.3243 | 100%
3 | Run 1-1C-D Out of the Box Baseline Cycle #4 (to be used with 3) | 75N0043 | Run 1-1D Out of the Box Baseline #4 | none | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 9 | 3/2/2013 | 0:23:46 | 10 Ton |  | 80/57 82 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 |  |  | 80 | 57 | 82 |  | 7.6 | 8.1 | 7.6 | 8.1 | [16 empty] | 6.177 |  |  |  | 4 | 6.533 | 82.143 | 30.017 | 58.148 | 0.68 | 1056.1 | 3000.1 | 13.592 | 31441.369 | 0.2416 | 3020.712 | 0.00368 | 8.5051 | 57.778 | 21.66 | 55.564 | 503.8 | 5.749 | 21.66 | 6.81 | 0 | 0 | 0.192 | 525.48 | 0.086 | 508.5 | 508.54 | 6.5172 | 508.54 | 0.97 | [516 empty] | No Economizer | 80.142 |  | 53.903 |  | 72.763 |  | 52.672 | [5 empty] | 2963 |  | 2882.6 |  | 0.927 |  |  |  | -0.33 |  | 1.2236 |  | 29.619 |  | 4845 |  | 0 |  |  | 0 |  |  | 0.79843 | 13214.9557 | 313.9274 | 0 | 0 | 13214.9557 | 0.0026913 | 22.1853 | 71.9646 | 11.5938 | 13.4529 | 0.00078408 | 0.83191 | 0.0026913 | 22.1853 | 0.0037285 | 21.5395 | 80.142 | 53.903 | 21.3466 | 11083.5406 | 25935.4509 | 3788.9 | 1.1667 | 8550.5055 | 23402.4158 | 1.7648 | 0.75123 | -0.83871 | -8.1774 | 47.2706 | 11083.5406 | 8533.7806 | 2549.76 | 0 | 11083.5406 | 100%
3 | Run 1-2A Out of the Box Baseline | 75N0044 | Run 1-2A Out the Box Baseline | none | on | on |  | unsealed | unsealed |  | 7 |  | 0 | 0 | CUST 9 | 3/1/2013 | 6:06:31 | 10 Ton | 0:30:00 | 80/67 95 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 80 | 67 | 95 |  | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 0 | 30.2 | 0 | 53195 | 61 | 52639 | 143 | 22331 | 87 | 75548 | 116 | 8.406 |  |  |  |  | 113.92 | 0.01 | 6.64 | [32 empty] | . | Manuf. charge R-22: 3000 scfm at 0.8 ESP (per client): unsealed tape on unit`s base and doors: After 2 Brun In's 115F & 123F: The blower wheel was changed to 7`& pulley with A49 Belt. Bob checked the change out and called it good on the belt. manuf mtr pu | 79.852 | 0.008 | 67.15 | 0.01 | 94.847 | 0.021 | 69.291 | 0.016 | 79.29 | 0.05 | 63.8 | 0.03 | 67.11 | 0.02 | -0.443 | 0.003 | 1.316 | 0.0026 | 53195 | 61 | 22331 | 87 | 8.406 | 0.029 | 80923 | 83 | 9.004 | 0.03 | 6.64 | 0.18 | 230 | 0.8 | 230.1 | 0.8 | 230 | 0.8 | 30.2 | 0.1 | 27 | 0.1 | 27 | 0.1 | 6900.9 | 34.3 | 3312.5 | 41.7 | 2086 | 31 | 228.1 |  | 229.1 |  | 227.4 |  | 6.5 |  | 6.7 |  | 6.5 |  | 0.56 | 228 |  | 230 |  | 229.9 |  | 10.6 |  | 9.7 |  | 9.8 |  | 3280 |  | 0.8 | 229 | 229.1 | 227.1 | 10.6 | 9.7 | 10.3 | 3300 | 0.81 | [31 empty] | 258.93 | 0.25 | 202.08 | 0.08 | 119.66 | 0.07 | 82.42 | 0.06 | 248.46 | 0.22 | 100.85 | 0.06 | 116.64 | 0.07 | 15.78 | 0.05 | [8 empty] | 73.19 | 0.05 | 73.17 | 0.03 | 43.01 | 0.03 | 30.16 | 0.04 | 589.74 | 1 | 39.75 | 0.02 | 80923 | 83 | 43746 | 75 | [38 empty] | 257.05 | 0.35 | 207.47 | 0.07 | 119.13 | 0.1 | 88.35 | 0.07 | [6 empty] | 249.71 | 0.28 | 99.69 | 0.06 | 117 | 0.08 | 17.31 | 0.09 | [6 empty] | 68.54 | 0.07 | 77.86 | 0.04 | 39.87 | 0.05 | 37.99 | 0.07 | 100.28 | 0.06 | 542.86 | 0.98 | 39.38 | 0.02 | 114.9 | 0.01 | 80923 | 83 | 40999 | 74 | [26 empty] | 63.2 | 0.04 | 63.64 | 0.04 | 63.34 | 0.05 | 62.98 | 0.05 | 73.84 | 0.06 | 63.57 | 0.04 | [32 empty] | 100.7 | 0.07 | 99.37 | 0.07 | [20 empty] | 99.52 | 0.06 | 100.28 | 0.06 | [12 empty] | 74.29 | 0.04 | [18 empty] | 95.04 | 0.12 | 95.06 | 0.12 | 81.03 | 0.1 | 80.78 | 0.05 | 80.6 | 0.04 | 80.57 | 0.04 | 80.34 | 0.04 | 81.24 | 0.07 |  |  | 82 | 0.06 | 81.23 | 0.05 | 81.31 | 0.05 | 81.27 | 0.04 | 80.52 | 0.04 | 81.09 | 0.05 | 80.19 | 0.05 | 80.37 | 0.05 | 79.93 | 0.05 | 80.26 | 0.05 | 80.14 | 0.05 | 80.17 | 0.05 | 79.93 | 0.05 | 80.07 | 0.05 | 79.65 | 0.04 | [94 empty] | No Economizer | 79.852 | 0.008 | 67.15 | 0.01 | 64.191 | 0.008 | 59.632 | 0.011 | 94.847 | 0.021 | 69.291 | 0.016 | 3080.5 | 3 | 3003.2 | 3 | 0.893 | 0.003 | -0.393 | 0.002 | -0.443 | 0.003 | 1.316 | 0.0026 | 29.555 | 0.001 | 8987 | 29 | 1720 |  |  | 0 |  |  | 1.4356 | 13913.1806 | 315.0655 | 0 | 0 | 13913.1806 | 0.011222 | 31.469 | 62.7554 | 14.0575 | 13.2845 | 0.0092767 | 32.9966 | 0.011222 | 31.469 | 0.0098118 | 26.0958 | 79.852 | 67.15 | 25.745 | 79638.8062 | 57088.2736 | 7267 | 0.31143 | 74843.7646 | 52293.2321 | 8.328 | 0.32098 | -5.724 | -17.0966 | 54.6737 | 79638.8062 | 74758.1561 | 4880.6501 | 0 | 79638.8062 | 100%
3 | Run 1-2B Out of the Box Baseline | 75N0045 | Run 1-2B Out the Box Baseline | none | on | on |  | unsealed | unsealed |  | 7 |  | 0 | 0 | CUST 9 | 3/1/2013 | 9:41:25 | 10 Ton | 0:30:00 | 80/67 82 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 7.6 lbs/ck2: 8.1 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 80 | 67 | 82 |  | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 0 | 27.5 | 0 | 52707 | 58 | 52227 | 144 | 24104 | 75 | 76834 | 108 | 9.793 |  |  |  |  | 114.35 | 0.01 | 1.71 | [32 empty] | no doors external tape | Manuf. charge R-22: 3000 scfm at .8 ESP (per client): unsealed tape on unit`s base and doors: After two Brun In`s; The blower wheel is a 7` with A49 Belt. manuf mtr pully. New 2 compr/filters | 79.85 | 0.006 | 67.151 | 0.01 | 81.995 | 0.016 | 64.54 | 0.01 | 79.38 | 0.05 | 64.05 | 0.04 | 67.22 | 0.02 | -0.438 | 0.003 | 1.3187 | 0.0026 | 52707 | 58 | 24104 | 75 | 9.793 | 0.041 | 78172 | 95 | 9.963 | 0.039 | 1.71 | 0.19 | 229.8 | 0.7 | 229.9 | 0.7 | 230.2 | 0.7 | 27.5 | 0.1 | 24.6 | 0.1 | 24.8 | 0.1 | 6227.9 | 34.1 | 3308.2 | 43.1 | 1617.4 | 28.1 | 229 |  | 228 |  | 228 |  | 6.5 |  | 6.7 |  | 6.5 |  | 0.58 | 229 |  | 230 |  | 230 |  | 9.3 |  | 9.3 |  | 8.7 |  | 2750 |  | 0.76 | 228 | 229 | 229 | 9.4 | 9.5 | 8.4 | 2710 | 0.77 | [31 empty] | 212.82 | 0.19 | 187.67 | 0.05 | 105.63 | 0.06 | 82.04 | 0.06 | 203.29 | 0.16 | 86.96 | 0.04 | 102.47 | 0.05 | 15.51 | 0.05 | 65.34 | 0.05 | 73.31 | 0.03 | [12 empty] | 538.68 | 0.89 | 35.44 | 0.01 | 78172 | 95 | 42511 | 71 | [14 empty] | 37.65 | 0.03 | 35.66 | 0.04 | [20 empty] | 210.28 | 0.26 | 191.08 | 0.06 | 104.8 | 0.09 | 86.28 | 0.07 | [6 empty] | 203.7 | 0.2 | 85.93 | 0.06 | 102.61 | 0.07 | 16.68 | 0.07 | [6 empty] | 60.36 | 0.06 | 77.1 | 0.04 | 34.02 | 0.05 | 43.07 | 0.06 | 86.39 | 0.06 | 493.35 | 0.94 | 35.12 | 0.02 | 115.15 | 0.01 | 78172 | 95 | 39483 | 76 | [26 empty] | 63.62 | 0.04 | 64.23 | 0.04 | 63.94 | 0.05 | 63.6 | 0.04 | 64 | 0.04 | [34 empty] | 86.63 | 0.06 | 85.5 | 0.07 | [20 empty] | 85.52 | 0.06 | 86.39 | 0.06 | [12 empty] | 74.03 | 0.04 | [18 empty] | 80.64 | 0.08 | 81.82 | 0.12 | 80.58 | 0.54 | 80.36 | 0.05 | 80.25 | 0.05 | 80.23 | 0.04 | 80 | 0.04 | 80.38 | 0.05 | [126 empty] | No Economizer | 79.85 | 0.006 | 67.151 | 0.01 | 64.376 | 0.008 | 59.502 | 0.01 | 81.995 | 0.016 | 64.54 | 0.01 | 3081 | 3 | 3009.3 | 2.9 | 0.897 | 0.003 | -0.391 | 0.002 | -0.438 | 0.003 | 1.3187 | 0.0026 | 29.609 | 0.001 | 7845 | 29 | 1740 |  |  | 0 |  |  | 1.4541 | 13911.5639 | 317.1196 | 0 | 0 | 13911.5639 | 0.011223 | 31.4699 | 62.9219 | 13.7282 | 13.2882 | 0.0088466 | 29.3871 | 0.011223 | 31.4699 | 0.009686 | 26.0039 | 79.85 | 67.151 | 25.6487 | 80981.8553 | 56519.0777 | 6105 | 0.2573 | 76125.5644 | 51662.7867 | 9.7037 | 0.34976 | -5.8212 | -16.9281 | 53.8163 | 80981.8553 | 76039.9927 | 4941.8626 | 0 | 80981.8553 | 100%
3 | 3-2000-115 | 75N0046 | 3-2000-115 | none | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/11/2013 | 13:52:48 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 1.2 | 31.5 | 0 | 28978 | 51 | 28078 | 100 | 2731 | 84 | 31711 | 83 | 3.1613 |  |  |  |  | 116.97 | 0.01 | 26.79 | [32 empty] | Lg rstrct CK1, 2000 cfm, clsd dmpr 75/62 ID, 115/80 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 75.004 | 0.011 | 62.001 | 0.026 | 114.998 | 0.017 | 80.008 | 0.022 | 74.56 | 0.04 | 61.98 | 0.02 | 66.06 | 0.02 | 0.792 | 0.003 | 0.59 | 0.0016 | 28978 | 51 | 2731 | 84 | 3.161 | 0.013 | 43317 | 87 | 4.318 | 0.016 | 26.79 | 0.22 | 230.4 | 1.1 | 230.1 | 1.1 | 229.5 | 1.1 | 31.5 | 0.1 | 28.3 | 0.1 | 31.6 | 0.1 | 7255.1 | 43.4 | 3658.4 | 55.3 | 2776.1 | 36.9 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6 |  | 5.9 |  | 0.5 | 230 |  | 230 |  | 230 |  | 12.3 |  | 11.6 |  | 11.2 |  | 3920 |  | 0.85 | 230 | 230 | 230 | 12.7 | 11.5 | 12.1 | 4110 | 0.86 | [8 empty] | 10040 | [14 empty] | 298.09 | 0.21 | 119.64 | 0.05 |  |  | 10.58 | 0.03 | 302.9 | 0.22 | 297.36 | 0.09 | 131.45 | 0.05 | 165.91 | 0.08 | 182.44 | 0.22 | 119.54 | 0.04 | 95.1 | 0.08 | -24.44 | 0.08 | [8 empty] | 41.58 | 0.04 | 81.83 | 0.03 | 18.28 | 0.04 | 63.55 | 0.05 | 145.53 | 1.15 | 45.77 | 0.01 | 43317 | 87 | 10361 | 82 | [18 empty] | 130.22 | 0.05 | 98.61 | 0.04 | [16 empty] | 326.99 | 0.19 | 231.6 | 0.04 | 137.43 | 0.05 | 94.17 | 0.05 | 316.46 | 0.19 |  |  | 11.79 | 0.03 | 315.52 | 0.19 | 122.48 | 0.04 | 134.63 | 0.05 | 12.15 | 0.04 | [6 empty] | 72.55 | 0.04 | 78.11 | 0.05 | 42.46 | 0.03 | 35.65 | 0.07 | 123.21 | 0.05 | 570.18 | 0.33 | 46.75 | 0.01 | 114.84 | 0.01 | 43317 | 87 | 38827 | 24 | [14 empty] | 123.07 | 0.05 | 134.86 | 0.05 | [8 empty] | 62.61 | 0.05 | 61.8 | 0.04 | 61.33 | 0.04 | 63.87 | 0.05 | 63.76 | 0.05 | 63.69 | 0.04 | [18 empty] | 119.54 | 0.04 | [12 empty] | 99.77 | 0.04 | 123.01 | 0.05 | [20 empty] | 120.7 | 0.04 | 123.21 | 0.05 | 99.77 | 0.04 | 123.01 | 0.05 | 83.51 | 0.03 | 77.57 | 0.05 | [12 empty] | 120.22 | 0.04 | 123.66 | 0.05 | 123.36 | 0.05 | [6 empty] | 115.95 | 0.08 | 115.3 | 0.06 | 75.04 | 0.05 | 74.73 | 0.04 | 74.86 | 0.05 | 74.78 | 0.05 | 74.86 | 0.05 | 74.85 | 0.05 |  |  | 77.03 | 0.12 | 75.1 | 0.07 | 75.01 | 0.07 | 75.04 | 0.07 | 99.12 | 0.37 | 81.19 | 0.19 | 75.42 | 0.07 | 75.08 | 0.06 | 91.45 | 0.43 | 80.99 | 0.14 | 82.39 | 0.13 | 77.23 | 0.08 | 85.53 | 0.11 | 84.33 | 0.12 | 83.28 | 0.14 | 78.3 | 0.13 | [30 empty] | 115.33 | 0.07 | 115.24 | 0.06 | 115.27 | 0.07 | 115.35 | 0.07 | 115.11 | 0.07 | 114.87 | 0.09 | [50 empty] | No Economizer | 75.004 | 0.011 | 62.001 | 0.026 | 62.02 | 0.013 | 56.894 | 0.02 | 114.998 | 0.017 | 80.008 | 0.022 | 2063.7 | 2.8 | 2000 | 2.7 | 1.463 | 0.002 | -0.278 | 0.002 | 0.792 | 0.003 | 0.59 | 0.0016 | 29.183 | 0.001 | 10031 | 31 | 1400 |  |  | 0 |  |  | 1.6033 | 9366.0386 | 343.7474 | 0 | 0 | 9366.0386 | 0.0087803 | 27.6093 | 60.4167 | 14.607 | 13.2203 | 0.013775 | 42.9185 | 0.0087803 | 27.6093 | 0.0086454 | 24.2956 | 75.004 | 62.001 | 23.9046 | 34697.9659 | 32790.0086 | 8631 | 0.84897 | 31092.9758 | 29185.0185 | 3.0997 | 0.33773 | -3.7047 | -14.5873 | 52.9779 | 34697.9659 | 31036.3911 | 3661.5748 | 0 | 34697.9659 | 100%
3 | Run 3-20N115 | 75N0061 | Run 3-20N115 | none | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/22/2013 | 13:39:00 | 10 Ton | 0:30:00 | 75/62 - 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 |  | 7.6 | 8.1 | 230.3 | 0.2 | 32.9 | 0 | 52999 | 138 | 53089 | 342 | 8856 | 207 | 61863 | 214 | 5.806 |  |  |  |  | 109.21 | 0.01 | 19.69 | [32 empty] | . | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo Meriam set to 100%: Horizontal airflow disch config. set on floor | 74.996 | 0.03 | 62.004 | 0.041 | 115 | 0.014 | 80.005 | 0.028 | 74.73 | 0.15 | 56.48 | 0.05 | 61.12 | 0.04 | 0.261 | 0.002 | 0.9827 | 0.0019 | 52999 | 138 | 8856 | 207 | 5.806 | 0.027 | 77035 | 82 | 7.23 | 0.021 | 19.69 | 0.29 | 230.3 | 0.8 | 229.9 | 0.8 | 229.7 | 0.8 | 32.9 | 0.1 | 29.9 | 0.1 | 33.2 | 0.1 | 7566.3 | 33.2 | 3777.7 | 39.9 | 3088 | 29 | 229.3 |  | 229.7 |  | 228.7 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.54 | 230.5 |  | 228.6 |  | 229 |  | 13.1 |  | 12.4 |  | 11.9 |  | 4245 |  | 0.86 | 229.1 | 228.3 | 227.6 | 12.9 | 11.8 | 12.5 | 4270 | 0.87 | [8 empty] | 10695 | [22 empty] | 341.51 | 0.31 | 189.94 | 0.14 | 140.89 | 0.07 | -49.05 | 0.11 | 323.12 | 0.3 | 124.28 | 0.07 | 136.5 | 0.07 | 12.22 | 0.04 | [8 empty] | 77.97 | 0.09 | 48.55 | 0.06 | 46.01 | 0.05 | 2.54 | 0.04 | 683.59 | 0.69 | 47.35 | 0.02 | 77035 | 82 | 42288 | 40 | [38 empty] | 337.93 | 0.29 | 224.15 | 0.1 | 140.05 | 0.07 | 84.1 | 0.07 | [6 empty] | 325.6 | 0.28 | 124.75 | 0.07 | 137.1 | 0.07 | 12.36 | 0.06 | [6 empty] | 76 | 0.05 | 70.3 | 0.18 | 44.75 | 0.03 | 25.55 | 0.16 | 124.38 | 0.07 | 601 | 0.55 | 47.51 | 0.02 | 113.27 | 0.03 | 77035 | 82 | 39525 | 49 | [26 empty] | 56.85 | 0.07 | 56.24 | 0.07 | 55.82 | 0.07 | 57.73 | 0.06 | 57.68 | 0.06 | 57.66 | 0.07 | [18 empty] | 124.28 | 0.07 | [12 empty] | 124.68 | 0.06 | 124.7 | 0.07 | [20 empty] | 124.36 | 0.07 | 124.38 | 0.07 |  |  |  |  | 50.8 | 0.06 | 69.92 | 0.17 | [24 empty] | 115.48 | 0.11 | 116.62 | 0.16 | 75.23 | 0.13 | 75.17 | 0.12 | 74.8 | 0.13 | 74.82 | 0.13 | 74.88 | 0.14 | 74.88 | 0.12 |  |  | 80.7 | 0.11 | 76.28 | 0.14 | 75.27 | 0.11 | 75.2 | 0.13 | 79.97 | 0.1 | 79.33 | 0.13 | 77.51 | 0.14 | 76.55 | 0.13 | 78.66 | 0.13 | 78.2 | 0.1 | 78.4 | 0.13 | 78.45 | 0.13 | 77.78 | 0.14 | 76.98 | 0.13 | 76.57 | 0.14 | 76.33 | 0.15 | [30 empty] | 111.54 | 0.18 | 110.4 | 0.16 | 110.52 | 0.19 | 110.27 | 0.18 | 111.08 | 0.19 | 109.04 | 0.27 | [50 empty] | No Economizer | 74.996 | 0.03 | 62.004 | 0.041 | 56.771 | 0.048 | 54.093 | 0.048 | 115 | 0.014 | 80.005 | 0.028 | 2655.5 | 2.6 | 2600.8 | 2.5 | 1.208 | 0.002 | -0.301 | 0.002 | 0.261 | 0.002 | 0.9827 | 0.0019 | 29.232 | 0.002 | 10655 | 30 | 1570 |  |  | 0 |  |  | 1.402 | 12177.1947 | 369.0957 | 0 | 0 | 12177.1947 | 0.0087842 | 27.6116 | 55.369 | 14.607 | 13.0843 | 0.013772 | 42.9152 | 0.0087842 | 27.6116 | 0.008259 | 22.596 | 74.996 | 62.004 | 22.2544 | 65235.6654 | 57360.5352 | 9085 | 0.47531 | 61136.979 | 53261.8489 | 5.7379 | 0.15902 | -5.3572 | -19.627 | 51.6577 | 65235.6654 | 61075.5739 | 4160.0915 | 0 | 65235.6654 | 100%
3 | C8-95-NE | 75N0155 | C8-95-NE | none | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/23/2015 | 22:19:00 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 230.1 | 1.7 | 28.3 | 0 | 54300 | 117 | 53735 | 204 | 13438 | 133 | 67752 | 187 | 7.669 | 898 | [38 empty] | Baseline no economizer, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD,--75F DB, 62F WB ID conditions, Inlet Meriam @ 75%: Outlet @ 75% Horiz airflow.--7` blower pulley A49 belt, 4.5 turns open from closed, 870 RPM, 2700 scfm,--adjust code tester speed | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.024 | 0.031 | 61.998 | 0.035 | 94.796 | 0.015 | 75.011 | 0.024 | 74.56 | 0.08 | 55.83 | 0.04 | 60.11 | 0.02 | 0.095 | 0.006 | 0.9183 | 0.0037 | 54300 | 117 | 13438 | 133 | 7.669 | 0.025 | [6 empty] | 230.1 | 1.4 | 229.6 | 1.4 | 229.8 | 1.4 | 28.3 | 0.1 | 25.9 | 0.1 | 29.2 | 0.1 | 6505.6 | 53.2 | 3670.9 | 71.4 | 2329 | 40.4 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.4 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.7 |  | 10.4 |  | 9.8 |  | 3350 |  | 0.82 | 230 | 230 | 230 | 10.6 | 10.2 | 9.2 | 3200 | 0.71 | 228.4 |  | 2.4 |  | 527.1 |  | 115 |  | 8782.1 | [22 empty] | 261.51 | 0.27 | 191.85 | 0.05 | 120.37 | 0.08 | 71.47 | 0.07 | [16 empty] | 66.18 | 0.06 | 76.08 | 0.05 | 38.17 | 0.04 | 37.91 | 0.06 | [8 empty] | 249.22 | 0.27 | 100.48 | 0.06 | 116.84 | 0.08 | 16.35 | 0.04 | 246.59 | 0.27 | 116.06 | 0.08 | 14.64 | 0.06 | [24 empty] | 262.93 | 0.24 | 195.39 | 0.06 | 120.77 | 0.07 | 74.61 | 0.06 | [20 empty] | 69.55 | 0.05 | 70.68 | 0.04 | 40.51 | 0.04 | 30.18 | 0.05 | [12 empty] | 252.44 | 0.23 | 102.06 | 0.06 | 117.78 | 0.07 | 15.72 | 0.04 | 249.75 | 0.22 | 116.99 | 0.07 | 14.51 | 0.05 | [12 empty] | 56.65 | 0.04 | 56.01 | 0.04 | 55.18 | 0.03 | 55.2 | 0.04 | 56.07 | 0.04 |  |  | 100.7 | 0.06 |  |  | 71.75 | 0.05 | 76.07 | 0.04 | 189.33 | 0.05 |  |  | 102.7 | 0.06 | 72.29 | 0.05 | 78.26 | 0.04 |  |  | 104.55 | 0.05 | [28 empty] | 56.68 | 0.04 | [8 empty] | 102.48 | 0.07 | 101.43 | 0.06 | [8 empty] | 73.21 | 0.04 | 101.38 | 0.06 | 70.05 | 0.04 | 102.69 | 0.06 | [10 empty] | 192.37 | 0.06 | 94.85 | 0.11 | 95.03 | 0.1 | 74.93 | 0.07 | 75.01 | 0.07 | 74.82 | 0.07 | 74.92 | 0.07 | 74.94 | 0.07 | 75 | 0.07 |  |  | 75.08 | 0.07 | 75.16 | 0.07 | 75 | 0.07 | 76.39 | 0.07 | 75.77 | 0.07 | 75.56 | 0.07 | 75.43 | 0.07 | 75.27 | 0.07 | 76.04 | 0.06 | 75.71 | 0.07 | 75.68 | 0.06 | 75.7 | 0.06 | 75.16 | 0.07 | 75.6 | 0.07 | 75.37 | 0.07 | 75.63 | 0.06 | [88 empty] | 56.38 | 0.03 | 56.65 | 0.04 | No Economizer | 75.024 | 0.031 | 61.998 | 0.035 | 56.097 | 0.023 | 53.029 | 0.024 | 94.796 | 0.015 | 75.011 | 0.024 | 2556.6 | 5.1 | 2524.3 | 5 | 1.155 | 0.002 | -0.545 | 0.003 | 0.095 | 0.006 | 0.9183 | 0.0037 | 29.402 | 0.001 | 8835 | 19 | 1590 |  |  | 0 |  |  | 1.5104 | 11742.0402 | 342.5217 | 0 | 0 | 11742.0402 | 0.0087736 | 27.6068 | 54.5866 | 14.0952 | 13.0638 | 0.013979 | 38.1714 | 0.0087736 | 27.6068 | 0.0078231 | 21.9585 | 75.024 | 61.998 | 21.5907 | 70641.2844 | 57594.3787 | 7245 | 0.35004 | 66383.6409 | 53336.7352 | 7.5137 | 0.19032 | -6.0161 | -20.4374 | 49.7826 | 70641.2844 | 66323.2863 | 4317.9981 | 0 | 70641.2844 | 100%
3 | C8-95-NE-CAB | 75N0160 | C8-95-NE-CAB | none | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 17:06:22 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.7 | 1.6 | 27.9 | 0 | 53130 | 124 | 52461 | 195 | 14012 | 120 | 67156 | 129 | 7.623 | 900 | [38 empty] | No econo, unsealed cabinet, Inlet static location inside Cabinet, 95F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions, duct removed--from supply sampling box (without code tester), record total static, 5 minute snapshot | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.047 | 0.021 | 61.991 | 0.019 | 95.013 | 0.01 | 75.009 | 0.03 | 74.56 | 0.07 | 55.59 | 0.03 | 60.2 | 0.03 | 0.165 | 0.004 | 0.8559 | 0.0024 | 53130 | 124 | 14012 | 120 | 7.623 | 0.02 | [6 empty] | 229.7 | 1.3 | 229.2 | 1.3 | 230.1 | 1.3 | 27.9 | 0.1 | 25.9 | 0.1 | 29.5 | 0.1 | 6396.1 | 49 | 3759.9 | 67.2 | 2413.9 | 37.3 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.5 |  | 9.8 |  | 3360 |  | 0.82 | 230 | 230 | 230 | 10.5 | 10.4 | 9.3 | 3240 | 0.71 | 228 |  | 2.4 |  | 525 |  | 115 |  | 8810 | [22 empty] | 262.45 | 0.14 | 194 | 0.03 | 120.61 | 0.04 | 73.39 | 0.04 | [16 empty] | 65.35 | 0.04 | 77.27 | 0.03 | 37.52 | 0.03 | 39.74 | 0.03 | [8 empty] | 250.47 | 0.14 | 101.22 | 0.03 | 117.18 | 0.04 | 15.96 | 0.03 | 247.84 | 0.13 | 116.41 | 0.04 | 14.27 | 0.04 | [24 empty] | 265.27 | 0.16 | 196.47 | 0.04 | 121.41 | 0.04 | 75.06 | 0.03 | [20 empty] | 69.54 | 0.04 | 71.24 | 0.04 | 40.45 | 0.03 | 30.79 | 0.06 | [12 empty] | 254.9 | 0.17 | 102.89 | 0.04 | 118.46 | 0.05 | 15.57 | 0.04 | 252.23 | 0.16 | 117.69 | 0.05 | 14.34 | 0.04 | [12 empty] | 56.68 | 0.06 | 56.05 | 0.06 | 55.03 | 0.05 | 54.7 | 0.06 | 55.11 | 0.06 |  |  | 101.28 | 0.03 |  |  | 72.21 | 0.03 | 76.56 | 0.03 | 190.4 | 0.03 |  |  | 103.49 | 0.04 | 72.07 | 0.04 | 77.88 | 0.03 |  |  | 105.31 | 0.03 | [28 empty] | 56.57 | 0.06 | [8 empty] | 103.35 | 0.04 | 102.14 | 0.05 | [8 empty] | 73.81 | 0.03 | 102.25 | 0.04 | 69.53 | 0.04 | 103.51 | 0.04 | [10 empty] | 194.53 | 0.02 | 95.72 | 0.09 | 95.69 | 0.1 | 74.95 | 0.1 | 75 | 0.09 | 74.92 | 0.09 | 75 | 0.1 | 74.99 | 0.1 | 75.01 | 0.09 |  |  | 74.96 | 0.09 | 75.04 | 0.09 | 74.98 | 0.08 | 76.32 | 0.09 | 75.65 | 0.09 | 75.43 | 0.09 | 75.25 | 0.09 | 75.11 | 0.09 | 76.1 | 0.08 | 75.52 | 0.09 | 75.5 | 0.08 | 75.48 | 0.08 | 75.01 | 0.09 | 75.47 | 0.1 | 75.28 | 0.1 | 75.46 | 0.09 | [78 empty] | 94.28 | 0.23 | [8 empty] | 56.45 | 0.05 | 56.31 | 0.05 | No Economizer | 75.047 | 0.021 | 61.991 | 0.019 | 55.841 | 0.014 | 52.772 | 0.017 | 95.013 | 0.01 | 75.009 | 0.03 | 2473.9 | 3.5 | 2430.2 | 3.5 | 1.191 | 0.002 | -0.502 | 0.003 | 0.165 | 0.004 | 0.8559 | 0.0024 | 29.251 | 0.001 | 8810 | 17 | 1570 |  |  | 0 |  |  | 1.5381 | 11368.4068 | 340.0313 | 0 | 0 | 11368.4068 | 0.0087636 | 27.6015 | 54.3029 | 14.1003 | 13.0567 | 0.013926 | 38.1656 | 0.0087636 | 27.6015 | 0.0077417 | 21.8077 | 75.047 | 61.991 | 21.4333 | 70122.545 | 56598.6423 | 7240 | 0.35238 | 65924.6618 | 52400.7591 | 7.4829 | 0.1898 | -6.1682 | -20.7441 | 49.4433 | 70122.545 | 65865.7869 | 4256.7581 | 0 | 70122.545 | 100%
3 | C8-95-NE-DUCT | 75N0161 | C8-95-NE-DUCT | none | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 15:41:51 | 10 Ton | 0:15:02 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.7 | 1.8 | 27.8 | 0 | 53071 | 135 | 52401 | 196 | 14094 | 116 | 67178 | 151 | 7.626 | 900 | [38 empty] | No econo, unsealed cabinet, Inlet static location inside duct (AHRI location), 95F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions, duct removed--from supply sampling box (without code tester), record total static, 5 mi | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.033 | 0.015 | 61.997 | 0.028 | 94.996 | 0.018 | 75.004 | 0.02 | 74.63 | 0.08 | 55.64 | 0.06 | 60.11 | 0.03 | 0.18 | 0.005 | 0.8505 | 0.0031 | 53071 | 135 | 14094 | 116 | 7.626 | 0.025 | [6 empty] | 229.7 | 1.5 | 229.4 | 1.5 | 230.3 | 1.5 | 27.8 | 0.1 | 25.9 | 0.1 | 29.6 | 0.1 | 6382.8 | 53.6 | 3783.7 | 76.6 | 2426.2 | 40.4 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.1 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.5 |  | 9.8 |  | 3370 |  | 0.72 | 230 | 230 | 230 | 10.56 | 10.5 | 9.3 | 3230 | 0.72 | 228.1 |  | 2.4 |  | 524.6 |  | 115 |  | 8809.6 | [22 empty] | 263 | 0.21 | 194.25 | 0.04 | 120.77 | 0.06 | 73.47 | 0.06 | [16 empty] | 65.46 | 0.06 | 77.37 | 0.04 | 37.62 | 0.04 | 39.75 | 0.06 | [8 empty] | 251 | 0.2 | 101.31 | 0.06 | 117.34 | 0.06 | 16.03 | 0.05 | 248.34 | 0.22 | 116.56 | 0.06 | 14.2 | 0.06 | [24 empty] | 264.47 | 0.25 | 196.39 | 0.06 | 121.19 | 0.07 | 75.2 | 0.05 | [20 empty] | 68.64 | 0.04 | 71.36 | 0.04 | 39.84 | 0.03 | 31.52 | 0.05 | [12 empty] | 254.2 | 0.26 | 102.96 | 0.06 | 118.27 | 0.08 | 15.31 | 0.05 | 251.54 | 0.25 | 117.5 | 0.07 | 14.09 | 0.06 | [12 empty] | 56.73 | 0.04 | 55.99 | 0.05 | 54.98 | 0.05 | 54.67 | 0.06 | 55.1 | 0.05 |  |  | 101.35 | 0.06 |  |  | 72.28 | 0.04 | 76.7 | 0.05 | 190.37 | 0.06 |  |  | 103.52 | 0.06 | 72.37 | 0.07 | 78.1 | 0.04 |  |  | 105.36 | 0.05 | [28 empty] | 56.53 | 0.04 | [8 empty] | 103.4 | 0.06 | 102.36 | 0.06 | [8 empty] | 73.88 | 0.05 | 102.46 | 0.07 | 69.72 | 0.09 | 103.49 | 0.06 | [10 empty] | 194.74 | 0.06 | 95.78 | 0.09 | 96.14 | 0.19 | 75.08 | 0.09 | 75.07 | 0.08 | 75.15 | 0.08 | 75.19 | 0.08 | 75.19 | 0.09 | 75.18 | 0.08 |  |  | 74.97 | 0.07 | 75.04 | 0.07 | 74.96 | 0.06 | 76.23 | 0.07 | 75.63 | 0.08 | 75.44 | 0.08 | 75.27 | 0.08 | 75.1 | 0.08 | 76.06 | 0.07 | 75.52 | 0.08 | 75.51 | 0.08 | 75.48 | 0.08 | 74.99 | 0.08 | 75.45 | 0.07 | 75.27 | 0.07 | 75.45 | 0.07 | [78 empty] | 97.59 | 0.35 | [8 empty] | 56.41 | 0.05 | 56.27 | 0.05 | No Economizer | 75.033 | 0.015 | 61.997 | 0.028 | 55.802 | 0.014 | 52.744 | 0.023 | 94.996 | 0.018 | 75.004 | 0.02 | 2464.5 | 4.5 | 2424.2 | 4.5 | 1.189 | 0.002 | -0.497 | 0.003 | 0.18 | 0.005 | 0.8505 | 0.0031 | 29.283 | 0.001 | 8809 | 19 | 1570 |  |  | 0 |  |  | 1.5456 | 11326.1094 | 338.6222 | 0 | 0 | 11326.1094 | 0.0087709 | 27.606 | 54.2564 | 14.0998 | 13.0557 | 0.013925 | 38.1611 | 0.0087709 | 27.606 | 0.0077355 | 21.7915 | 75.033 | 61.997 | 21.4152 | 70117.6317 | 56476.4395 | 7239 | 0.35236 | 65914.9392 | 52273.747 | 7.4827 | 0.18898 | -6.1908 | -20.7766 | 49.415 | 70117.6317 | 65856.0451 | 4261.5865 | 0 | 70117.6317 | 100%
3 | C8-55-CE3 | 75N0033 | C8-55-CE3 | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 4:55:27 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.6 | 6.5 | 0 | 4828 | 22 | 4322 | 36 | 3571 | 124 | 8403 | 118 | 5.406 | 899 | [38 empty] | Econo closed (2.0V), unsealed cabinet, Inlet static location inside Cabinet, no compressor 55F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions, duct removed from supply sampling box--(without code tester), record total- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.008 | 0.012 | 61.999 | 0.035 | 54.995 | 0.029 | 51.009 | 0.022 | 74.46 | 0.02 | 72.93 | 0.02 | 73.55 | 0.01 | 0.151 | 0.005 | 0.878 | 0.003 | 4828 | 22 | 3571 | 124 | 5.406 | 0.086 | [6 empty] | 229.9 | 1 | 230.3 | 1 | 230.1 | 1 | 6.5 | 0 | 6.2 | 0 | 6.5 | 0 | 1385.3 | 13.2 | 1125.7 | 18.4 | 168.9 | 10 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.2 |  | 6.3 |  | 0.62 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1540 | [22 empty] | 93.05 | 0.04 | 55.36 | 0.01 | 55.1 | 0.02 | -0.26 | 0.02 | [16 empty] | 93.48 | 0.04 | 55.52 | 0.01 | 55.35 | 0.02 | 0.18 | 0.02 | [8 empty] | 93.38 | 0.05 | 54.98 | 0.02 | 55.3 | 0.03 | 0.32 | 0.04 | 92.94 | 0.03 | 55.05 | 0.02 | -0.12 | 0.02 | [24 empty] | 93.67 | 0.05 | 55.42 | 0.03 | 55.46 | 0.03 | -0.04 | 0.02 | [20 empty] | 93.42 | 0.05 | 55.02 | 0.01 | 55.32 | 0.03 | -0.3 | 0.03 | [12 empty] | 95.37 | 0.05 | 54.93 | 0.02 | 56.42 | 0.03 | 1.5 | 0.04 | 94.07 | 0.04 | 55.69 | 0.02 | -0.76 | 0.02 | [12 empty] | 74.14 | 0.02 | 72.99 | 0.03 | 71.96 | 0.03 | 72.85 | 0.03 | 73.13 | 0.03 |  |  | 55.01 | 0.02 |  |  | 55.96 | 0.01 | 56.2 | 0.02 | 55.98 | 0.02 |  |  | 55.61 | 0.02 | 55.66 | 0.03 | 55.71 | 0.01 |  |  | 55.74 | 0.02 | [28 empty] | 74.05 | 0.03 | [8 empty] | 54.93 | 0.02 | 54.93 | 0.02 | [8 empty] | 55.82 | 0.02 | 55.65 | 0.02 | 55.86 | 0.04 | 55.15 | 0.02 | [10 empty] | 56.15 | 0.01 | 55.42 | 0.11 | 54.66 | 0.18 | 75.14 | 0.02 | 75.06 | 0.02 | 75.34 | 0.02 | 75.27 | 0.03 | 75.19 | 0.02 | 75.19 | 0.02 |  |  | 74.43 | 0.04 | 73.28 | 0.08 | 74.93 | 0.03 | 65.68 | 0.19 | 75.03 | 0.03 | 74.74 | 0.04 | 74.71 | 0.04 | 73.95 | 0.09 | 74.68 | 0.06 | 73.24 | 0.05 | 74.22 | 0.04 | 67.02 | 0.07 | 74.62 | 0.03 | 74.18 | 0.05 | 74.78 | 0.03 | 64.79 | 0.12 | [78 empty] | 54.91 | 0.1 | [8 empty] | 73.35 | 0.03 | 73.81 | 0.03 | Economizer test | 75.008 | 0.012 | 61.999 | 0.035 | 73.292 | 0.01 | 60.981 | 0.023 | 54.995 | 0.029 | 51.009 | 0.022 | 2534 | 4.4 | 2431 | 4.2 | 1.13 | 0.002 | -0.398 | 0.002 | 0.151 | 0.005 | 0.878 | 0.003 | 29.343 | 0.001 | 1554 | 10 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5372 | 11258.0931 | 322.7219 | 21.3792 | 98.4506 | 11159.6425 | 0.0087624 | 27.5481 | 71.7548 | 13.0294 | 13.505 | 0.0069873 | 20.7829 | 0.0087781 | 27.6078 | 0.0085191 | 26.9061 | 74.8336 | 61.9127 | 26.5314
3 | C8-55-1FE3 | 75N0140 | C8-55-1FE3 | 1 finger | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 5:34:00 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 230 | 1.2 | 6.5 | 0 | 9496 | 66 | 9032 | 95 | 5617 | 120 | 15118 | 127 | 9.643 | 899 | [38 empty] | Econo 1-Finger open, unsealed cabinet, Inlet static location inside Cabinet, no compressor 55F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--duct removed from supply sampling box (without code tester), record total- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.975 | 0.015 | 62 | 0.033 | 54.993 | 0.037 | 51.018 | 0.041 | 74.58 | 0.04 | 71.39 | 0.04 | 72.32 | 0.01 | 0.128 | 0.004 | 0.8956 | 0.003 | 9496 | 66 | 5617 | 120 | 9.643 | 0.104 | [6 empty] | 230 | 0.7 | 230.1 | 0.7 | 230.1 | 0.7 | 6.5 | 0 | 6.3 | 0 | 6.5 | 0 | 1386 | 10.2 | 1131.7 | 13 | 181.7 | 8.1 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.3 |  | 0.62 | [23 empty] | 0 |  | 0 |  | 0 |  | 115 |  | 1550 | [22 empty] | 93.11 | 0.06 | 55.43 | 0.02 | 55.14 | 0.03 | -0.29 | 0.03 | [16 empty] | 93.48 | 0.07 | 55.54 | 0.01 | 55.35 | 0.04 | 0.19 | 0.03 | [8 empty] | 93.48 | 0.07 | 55.13 | 0.04 | 55.35 | 0.04 | 0.22 | 0.06 | 92.99 | 0.07 | 55.07 | 0.04 | -0.07 | 0.03 | [24 empty] | 93.71 | 0.06 | 55.48 | 0.02 | 55.48 | 0.03 | 0 | 0.03 | [20 empty] | 93.49 | 0.06 | 55.09 | 0.02 | 55.36 | 0.03 | -0.27 | 0.03 | [12 empty] | 95.48 | 0.06 | 54.98 | 0.03 | 56.47 | 0.03 | 1.49 | 0.05 | 94.19 | 0.05 | 55.75 | 0.03 | -0.75 | 0.04 | [12 empty] | 72.71 | 0.03 | 70.9 | 0.05 | 70.25 | 0.04 | 71.02 | 0.04 | 70.96 | 0.04 |  |  | 55.09 | 0.03 |  |  | 55.84 | 0.03 | 56.25 | 0.01 | 56.14 | 0.01 |  |  | 55.54 | 0.04 | 55.83 | 0.03 | 55.8 | 0.01 |  |  | 55.73 | 0.02 | [28 empty] | 72.41 | 0.03 | [8 empty] | 55.01 | 0.03 | 55 | 0.02 | [8 empty] | 55.74 | 0.03 | 55.65 | 0.02 | 56.03 | 0.04 | 55.13 | 0.03 | [10 empty] | 56.25 | 0.02 | 55.53 | 0.14 | 54.9 | 0.2 | 75.12 | 0.02 | 75.05 | 0.02 | 75.3 | 0.02 | 75.28 | 0.03 | 75.21 | 0.03 | 75.2 | 0.02 |  |  | 65.04 | 0.1 | 65.3 | 0.09 | 74.83 | 0.02 | 69.1 | 0.2 | 75.16 | 0.04 | 63.94 | 0.09 | 70.34 | 0.12 | 67 | 0.15 | 74.47 | 0.08 | 65.11 | 0.08 | 65.54 | 0.08 | 66.89 | 0.07 | 74.63 | 0.03 | 64.26 | 0.08 | 67.07 | 0.15 | 65.37 | 0.1 | [78 empty] | 54.9 | 0.18 | [8 empty] | 71.77 | 0.03 | 72.17 | 0.03 | Economizer test | 74.975 | 0.015 | 62 | 0.033 | 71.621 | 0.022 | 60.132 | 0.025 | 54.993 | 0.037 | 51.018 | 0.041 | 2556.4 | 4.3 | 2459 | 4.2 | 1.133 | 0.002 | -0.353 | 0.003 | 0.128 | 0.004 | 0.8956 | 0.003 | 29.346 | 0.001 | 1568 | 10 | 1550 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.5255 | 11394.3433 | 327.3057 | 224.4664 | 1033.66 | 10360.6833 | 0.0086238 | 26.9902 | 70.0955 | 13.0294 | 13.4614 | 0.0069926 | 20.7882 | 0.0087865 | 27.609 | 0.0083701 | 26.3359 | 73.1677 | 61.0975 | 25.9641
3 | C8-55-2FE3 | 75N0141 | C8-55-2FE3 | 2 finger | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 6:49:12 | 10 Ton | 0:15:00 | 75/62 - 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.5 | 6.5 | 0 | 11021 | 45 | 10628 | 86 | 6208 | 94 | 17235 | 117 | 10.928 | 898 | [38 empty] | Econo 2-Finger open, unsealed cabinet, Inlet static location inside Cabinet,--no compressor 55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--75F DB, 62F WB ID conditions, duct removed from supply sampling box (without code tester),--record total | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.953 | 0.014 | 61.996 | 0.03 | 55.004 | 0.025 | 51.001 | 0.02 | 74.39 | 0.04 | 70.66 | 0.03 | 71.98 | 0.02 | 0.112 | 0.005 | 0.9085 | 0.003 | 11021 | 45 | 6208 | 94 | 10.928 | 0.103 | [6 empty] | 229.9 | 0.9 | 230.2 | 0.9 | 230.3 | 0.9 | 6.5 | 0 | 6.3 | 0 | 6.5 | 0 | 1386.6 | 11.8 | 1137.6 | 16.5 | 190.3 | 9.1 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.3 |  | 0.63 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1560 | [22 empty] | 93.16 | 0.03 | 55.4 | 0.02 | 55.18 | 0.02 | -0.22 | 0.02 | [16 empty] | 93.57 | 0.03 | 55.55 | 0.02 | 55.41 | 0.02 | 0.15 | 0.02 | [8 empty] | 93.57 | 0.04 | 55.06 | 0.04 | 55.41 | 0.02 | 0.34 | 0.04 | 93.03 | 0.02 | 55.1 | 0.01 | -0.15 | 0.02 | [24 empty] | 93.77 | 0.04 | 55.59 | 0.02 | 55.52 | 0.02 | 0.07 | 0.02 | [20 empty] | 93.54 | 0.03 | 54.97 | 0.02 | 55.39 | 0.02 | -0.42 | 0.02 | [12 empty] | 95.51 | 0.03 | 54.94 | 0.02 | 56.5 | 0.01 | 1.55 | 0.02 | 94.23 | 0.03 | 55.78 | 0.01 | -0.83 | 0.02 | [12 empty] | 72.06 | 0.02 | 70.49 | 0.07 | 69.81 | 0.07 | 70.77 | 0.05 | 70.39 | 0.04 |  |  | 55.09 | 0.03 |  |  | 55.7 | 0.04 | 56.11 | 0.03 | 56.02 | 0.03 |  |  | 55.51 | 0.02 | 55.58 | 0.04 | 55.73 | 0.02 |  |  | 55.6 | 0.02 | [28 empty] | 72 | 0.03 | [8 empty] | 54.95 | 0.02 | 54.95 | 0.02 | [8 empty] | 55.62 | 0.03 | 55.57 | 0.03 | 55.72 | 0.04 | 55.24 | 0.03 | [10 empty] | 56.07 | 0.03 | 55.21 | 0.1 | 54.58 | 0.18 | 74.99 | 0.03 | 74.96 | 0.03 | 75.03 | 0.05 | 75.07 | 0.05 | 75.06 | 0.03 | 75.06 | 0.03 |  |  | 64.58 | 0.09 | 64.77 | 0.07 | 74.98 | 0.03 | 68.86 | 0.21 | 75.2 | 0.04 | 63.6 | 0.1 | 69.05 | 0.12 | 64.78 | 0.13 | 74.65 | 0.07 | 64.66 | 0.08 | 64.96 | 0.07 | 66.15 | 0.06 | 74.68 | 0.04 | 63.91 | 0.09 | 66.73 | 0.14 | 64.62 | 0.08 | [78 empty] | 54.91 | 0.12 | [8 empty] | 71.45 | 0.05 | 71.87 | 0.04 | Economizer test | 74.953 | 0.014 | 61.996 | 0.03 | 71.085 | 0.016 | 59.858 | 0.025 | 55.004 | 0.025 | 51.001 | 0.02 | 2573.7 | 4.3 | 2477.9 | 4.1 | 1.128 | 0.002 | -0.325 | 0.002 | 0.112 | 0.005 | 0.9085 | 0.003 | 29.353 | 0.001 | 1577 | 10 | 1560 |  | 0.1172 | 290.407 | 13.03 | 0.325 | 1.5248 | 11483.3578 | 328.3658 | 290.4026 | 1337.2748 | 10146.083 | 0.0085785 | 26.8113 | 69.5602 | 13.0296 | 13.4475 | 0.0069809 | 20.7782 | 0.0087891 | 27.6064 | 0.0083232 | 26.154 | 72.6366 | 60.8331 | 25.7824
3 | C8-55-3FE3 | 75N0142 | C8-55-3FE3 | 3 finger | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 8:03:29 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.7 | 1.6 | 6.5 | 0 | 14709 | 57 | 14141 | 47 | 7746 | 83 | 22462 | 93 | 14.069 | 898 | [38 empty] | Econo 3-Finger open, unsealed cabinet, Inlet static location inside Cabinet,--no compressor 55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB,--62F WB ID conditions, duct removed from supply sampling box (without code tester),--record total | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.03 | 0.02 | 62.014 | 0.014 | 54.977 | 0.018 | 50.997 | 0.017 | 74.42 | 0.06 | 69.54 | 0.06 | 71.02 | 0.02 | 0.119 | 0.006 | 0.939 | 0.003 | 14709 | 57 | 7746 | 83 | 14.069 | 0.107 | [6 empty] | 229.7 | 1.2 | 230.1 | 1.2 | 230.3 | 1.2 | 6.5 | 0.1 | 6.3 | 0 | 6.6 | 0.1 | 1391.2 | 14.5 | 1140.8 | 20.8 | 205.6 | 10.7 | 230 |  | 230 |  | 230 |  | 6.5 |  | 6.2 |  | 6.3 |  | 0.63 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1595 | [22 empty] | 93.17 | 0.04 | 55.44 | 0.02 | 55.18 | 0.02 | -0.26 | 0.03 | [16 empty] | 93.57 | 0.04 | 55.58 | 0.01 | 55.41 | 0.02 | 0.17 | 0.03 | [8 empty] | 93.57 | 0.04 | 55.06 | 0.05 | 55.41 | 0.02 | 0.35 | 0.05 | 93.03 | 0.04 | 55.1 | 0.02 | -0.09 | 0.03 | [24 empty] | 93.89 | 0.04 | 55.64 | 0.02 | 55.59 | 0.02 | 0.05 | 0.02 | [20 empty] | 93.64 | 0.03 | 55.03 | 0.02 | 55.45 | 0.02 | -0.41 | 0.03 | [12 empty] | 95.52 | 0.04 | 55.07 | 0.02 | 56.51 | 0.02 | 1.43 | 0.03 | 94.33 | 0.03 | 55.84 | 0.02 | -0.78 | 0.02 | [12 empty] | 70.82 | 0.04 | 68.91 | 0.04 | 68.67 | 0.04 | 69.77 | 0.04 | 68.79 | 0.05 |  |  | 55.09 | 0.03 |  |  | 55.59 | 0.02 | 56.11 | 0.02 | 56.08 | 0.04 |  |  | 55.48 | 0.03 | 55.57 | 0.04 | 55.75 | 0.03 |  |  | 55.58 | 0.04 | [28 empty] | 70.78 | 0.04 | [8 empty] | 55.06 | 0.02 | 55.01 | 0.02 | [8 empty] | 55.58 | 0.03 | 55.56 | 0.03 | 55.68 | 0.05 | 55.28 | 0.02 | [10 empty] | 56.09 | 0.04 | 55.2 | 0.13 | 54.61 | 0.18 | 75 | 0.05 | 74.97 | 0.04 | 75.01 | 0.07 | 75.08 | 0.07 | 75.08 | 0.06 | 75.08 | 0.05 |  |  | 61.78 | 0.09 | 62.23 | 0.09 | 74.92 | 0.04 | 72.42 | 0.17 | 74.99 | 0.05 | 60.19 | 0.12 | 64.75 | 0.16 | 60.91 | 0.13 | 74.3 | 0.09 | 61.7 | 0.1 | 62.39 | 0.1 | 63.65 | 0.08 | 74.62 | 0.05 | 60.91 | 0.1 | 63.06 | 0.19 | 62.55 | 0.08 | [78 empty] | 54.8 | 0.12 | [8 empty] | 70.15 | 0.03 | 70.66 | 0.03 | Economizer test | 75.03 | 0.02 | 62.014 | 0.014 | 69.95 | 0.019 | 59.247 | 0.013 | 54.977 | 0.018 | 50.997 | 0.017 | 2614.2 | 4.2 | 2522.5 | 4.1 | 1.115 | 0.002 | -0.274 | 0.002 | 0.119 | 0.006 | 0.939 | 0.003 | 29.359 | 0 | 1597 | 11 | 1580 |  | 0.17753 | 447.8183 | 13.029 | 0.274 | 1.5197 | 11689.8605 | 330.4237 | 447.8174 | 2062.2572 | 9627.6033 | 0.0084656 | 26.4113 | 68.4303 | 13.0289 | 13.4178 | 0.0069852 | 20.7762 | 0.0087828 | 27.6183 | 0.0082078 | 25.7514 | 71.5019 | 60.2381 | 25.3811
3 | C8-55-OE3 | 75N0145 | C8-55-OE3 | open | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 10:03:14 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.6 | 1.7 | 6.4 | 0 | 27361 | 71 | 26851 | 118 | 12509 | 130 | 39881 | 164 | 25.211 | 899 | [38 empty] | Econo 100% open, unsealed cabinet, Inlet static location inside Cabinet, no compressor--55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--duct removed from supply sampling box (without code tester), record total stat | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.02 | 0.008 | 61.995 | 0.033 | 55.024 | 0.007 | 51.019 | 0.016 | 74.7 | 0.08 | 65.23 | 0.08 | 67.42 | 0.01 | 0.221 | 0.012 | 0.8966 | 0.0032 | 27361 | 71 | 12509 | 130 | 25.211 | 0.206 | [6 empty] | 229.6 | 1.4 | 230.1 | 1.4 | 230.4 | 1.4 | 6.4 | 0.1 | 6.3 | 0.1 | 6.6 | 0.1 | 1380.4 | 16.8 | 1145 | 24.7 | 201.5 | 11.6 | 230 |  | 230 |  | 230 |  | 6.56 |  | 6.1 |  | 6.3 |  | 0.63 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1585 | [22 empty] | 93.15 | 0.03 | 55.52 | 0.02 | 55.17 | 0.02 | -0.35 | 0.03 | [16 empty] | 93.6 | 0.03 | 55.57 | 0.03 | 55.42 | 0.02 | 0.14 | 0.04 | [8 empty] | 93.61 | 0.05 | 55.59 | 0.08 | 55.44 | 0.02 | -0.16 | 0.06 | 93.08 | 0.02 | 55.14 | 0.01 | 0 | 0.03 | [24 empty] | 93.77 | 0.04 | 55.64 | 0.02 | 55.53 | 0.02 | 0.11 | 0.03 | [20 empty] | 93.46 | 0.03 | 55.24 | 0.02 | 55.35 | 0.01 | -0.11 | 0.03 | [12 empty] | 95.2 | 0.04 | 55.6 | 0.04 | 56.33 | 0.02 | 0.73 | 0.04 | 94.4 | 0.03 | 55.88 | 0.02 | -0.74 | 0.03 | [12 empty] | 67.57 | 0.06 | 65.6 | 0.06 | 63.02 | 0.06 | 63.44 | 0.07 | 63.81 | 0.06 |  |  | 55.51 | 0.06 |  |  | 55.35 | 0.04 | 56.15 | 0.04 | 56.27 | 0.05 |  |  | 55.29 | 0.03 | 55.58 | 0.07 | 55.89 | 0.04 |  |  | 55.47 | 0.04 | [28 empty] | 67.1 | 0.06 | [8 empty] | 55.14 | 0.03 | 55.13 | 0.03 | [8 empty] | 55.43 | 0.04 | 55.62 | 0.03 | 55.73 | 0.08 | 55.16 | 0.02 | [10 empty] | 56.22 | 0.06 | 55.02 | 0.08 | 54.84 | 0.09 | 75.13 | 0.05 | 75.07 | 0.04 | 75.22 | 0.05 | 75.24 | 0.05 | 75.22 | 0.05 | 75.23 | 0.05 |  |  | 61.04 | 0.11 | 61.06 | 0.11 | 72.81 | 0.05 | 66.34 | 0.2 | 71.62 | 0.09 | 56.52 | 0.14 | 56.82 | 0.17 | 55.75 | 0.11 | 74.92 | 0.06 | 59.54 | 0.1 | 61.26 | 0.11 | 60.6 | 0.1 | 70.33 | 0.18 | 58.53 | 0.1 | 57.82 | 0.17 | 59.5 | 0.09 | [78 empty] | 56.48 | 0.11 | [8 empty] | 66.77 | 0.05 | 66.24 | 0.06 | Economizer test | 75.02 | 0.008 | 61.995 | 0.033 | 65.366 | 0.018 | 56.83 | 0.024 | 55.024 | 0.007 | 51.019 | 0.016 | 2544.3 | 4.6 | 2475.2 | 4.5 | 1.176 | 0.002 | -0.11 | 0.012 | 0.221 | 0.012 | 0.8966 | 0.0032 | 29.372 | 0.001 | 1582 | 11 | 1570 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.5209 | 11479.2893 | 341.9658 | 1006.8708 | 4636.3453 | 6842.9441 | 0.0080509 | 24.8517 | 63.8451 | 13.0301 | 13.2986 | 0.0069858 | 20.7884 | 0.0087726 | 27.6047 | 0.0078176 | 24.2092 | 66.9595 | 57.8447 | 23.8389
3 | 3-52115CF | 75N0001 | 3-52115CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 18:11:50 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.2 | 32.9 | 0 | 42568 | 76 | 41692 | 193 | 1612 | 158 | 44182 | 151 | 4.1839 |  |  |  |  | 109.35 | 0.01 | 42.95 | [32 empty] | 83% Airflow, Both Stages, Closed Damper | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor: | 75.002 | 0.015 | 62.006 | 0.034 | 115.003 | 0.026 | 79.999 | 0.027 | 74.39 | 0.07 | 59.41 | 0.04 | 63.51 | 0.02 | 0.238 | 0.005 | 1.1972 | 0.0032 | 42568 | 76 | 1612 | 158 | 4.184 | 0.018 | 77442 | 56 | 7.333 | 0.022 | 42.95 | 0.19 | 230.5 | 0.9 | 230.1 | 0.9 | 229.5 | 0.9 | 32.9 | 0.1 | 29.5 | 0.1 | 32.8 | 0.1 | 7575.7 | 35.2 | 3688.6 | 43.6 | 2984.1 | 29.8 | 230 |  | 229 |  | 230 |  | 6.4 |  | 6.2 |  | 6.2 |  | 0.54 | 230 |  | 229 |  | 228 |  | 13.2 |  | 12.3 |  | 11.9 |  | 4290 |  | 0.86 | 230 | 231 | 229 | 12.8 | 11.6 | 12.2 | 4180 | 0.86 | [8 empty] | 10600 | [22 empty] | 340.82 | 0.25 | 186.87 | 0.09 | 140.74 | 0.06 | 46.12 | 0.07 | 322.2 | 0.24 | 123.52 | 0.07 | 136.29 | 0.06 | 12.77 | 0.05 | [8 empty] | 78.07 | 0.06 | 49.36 | 0.03 | 46.11 | 0.04 | 3.26 | 0.03 | 686.31 | 0.45 | 47.1 | 0.02 | 77442 | 56 | 42728 | 31 | [38 empty] | 331.49 | 0.31 | 234.81 | 0.06 | 138.54 | 0.07 | 96.27 | 0.05 | [6 empty] | 319.96 | 0.3 | 123.57 | 0.05 | 135.74 | 0.07 | 12.17 | 0.06 | [6 empty] | 74.43 | 0.04 | 81.9 | 0.05 | 43.76 | 0.02 | 38.15 | 0.05 | 123.43 | 0.08 | 575.66 | 0.5 | 47.11 | 0.02 | 115.42 | 0.01 | 77442 | 56 | 39322 | 34 | [26 empty] | 59.24 | 0.05 | 59.3 | 0.04 | 59.77 | 0.05 | 59.64 | 0.04 | 59.56 | 0.04 | 59.6 | 0.04 | [18 empty] | 123.52 | 0.07 | [12 empty] | 125.33 | 0.06 | 124.05 | 0.07 | [20 empty] | 123.66 | 0.07 | 123.43 | 0.08 | 125.33 | 0.06 | 124.05 | 0.07 | 50.91 | 0.04 | 81.89 | 0.04 | [24 empty] | 115.18 | 0.1 | 114.69 | 0.08 | 74.49 | 0.06 | 74.61 | 0.06 | 74.33 | 0.05 | 74.35 | 0.05 | 74.52 | 0.05 | 74.55 | 0.05 |  |  | 76.64 | 0.13 | 75.22 | 0.1 | 75.19 | 0.1 | 75.33 | 0.1 | 96.73 | 0.39 | 81.8 | 0.22 | 75.52 | 0.1 | 75.31 | 0.1 | 87.94 | 0.31 | 81.08 | 0.13 | 82.54 | 0.13 | 79 | 0.15 | 87.53 | 0.39 | 84.64 | 0.15 | 84.36 | 0.12 | 78.37 | 0.17 | [30 empty] | 115.15 | 0.1 | 114.74 | 0.09 | 114.85 | 0.11 | 115 | 0.1 | 114.81 | 0.1 | 114.81 | 0.12 | [50 empty] | C8-55-CE3 | 75.002 | 0.015 | 62.006 | 0.034 | 59.713 | 0.014 | 56.232 | 0.024 | 115.003 | 0.026 | 79.999 | 0.027 | 2557.1 | 3.4 | 2500 | 3.3 | 1.228 | 0.003 | -0.387 | 0.002 | 0.238 | 0.005 | 1.1972 | 0.0032 | 29.341 | 0.001 | 10560 | 31 | 1520 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.414 | 11655.8088 | 360.6646 | 22.3216 | 91.6882 | 11564.1206 | 0.0088233 | 27.7333 | 58.299 | 14.6071 | 13.1631 | 0.013765 | 42.9087 | 0.0087841 | 27.6129 | 0.0087983 | 23.8993 | 75.3195 | 62.1789 | 23.5544 | 48707.5976 | 47613.1588 | 9040 | 0.63344 | 44750.7857 | 43656.347 | 4.2378 | 0.21497 | -4.1788 | -17.0205 | 53.6382 | 48707.5976 | 43285.1221 | 4020.0377 | 1402.4378 | 48707.5976 | 100%
3 | 3-5282CF | 75N0002 | 3-5282CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 9:14:12 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.1 | 26.4 | 0 | 53180 | 88 | 52323 | 231 | 13994 | 97 | 67187 | 133 | 8.7233 |  |  |  |  | 111.91 | 0.02 | 14.55 | [32 empty] | 83% airflow, both stages, closed damper | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor: | 75.001 | 0.016 | 61.994 | 0.024 | 81.996 | 0.025 | 67.997 | 0.019 | 74.44 | 0.08 | 55.78 | 0.05 | 60.7 | 0.02 | 0.216 | 0.004 | 1.1827 | 0.0034 | 53180 | 88 | 13994 | 97 | 8.724 | 0.038 | 78623 | 58 | 10.208 | 0.04 | 14.55 | 0.17 | 230.5 | 0.8 | 230.2 | 0.8 | 229.5 | 0.8 | 26.4 | 0.1 | 23.3 | 0.1 | 26.6 | 0.1 | 6032.1 | 36.6 | 3482.6 | 41.3 | 1669.6 | 31 | 230 |  | 230 |  | 230 |  | 6.5 |  | 6.3 |  | 6.1 |  | 0.54 | 230 |  | 230 |  | 230 |  | 10 |  | 9.2 |  | 8.8 |  | 2860 |  | 0.77 | 230 | 230 | 230 | 9.5 | 8.3 | 8.9 | 2710 | 0.77 | [8 empty] | 7720 | [22 empty] | 225.02 | 0.15 | 169.31 | 0.07 | 109.51 | 0.05 | 59.8 | 0.06 | 206.38 | 0.15 | 88.16 | 0.05 | 103.48 | 0.05 | 15.32 | 0.05 | [8 empty] | 68.62 | 0.04 | 60.42 | 0.13 | 39.89 | 0.03 | 20.53 | 0.13 | 595.79 | 0.38 | 35.8 | 0.01 | 78623 | 58 | 45345 | 34 | [38 empty] | 209.11 | 0.18 | 190.2 | 0.04 | 104.39 | 0.06 | 85.81 | 0.05 | [6 empty] | 198.71 | 0.19 | 88.69 | 0.04 | 100.89 | 0.07 | 12.2 | 0.06 | [6 empty] | 56.18 | 0.04 | 73.49 | 0.03 | 30.78 | 0.03 | 42.71 | 0.04 | 87.76 | 0.05 | 480.27 | 0.42 | 35.97 | 0.01 | 114.85 | 0.01 | 78623 | 58 | 37885 | 34 | [26 empty] | 55.75 | 0.05 | 55.71 | 0.03 | 56 | 0.03 | 56.09 | 0.08 | 56.01 | 0.07 | 56.07 | 0.06 | [18 empty] | 88.16 | 0.05 | [12 empty] | 89.83 | 0.05 | 88.33 | 0.05 | [20 empty] | 88.43 | 0.05 | 87.76 | 0.05 | 89.83 | 0.05 | 88.33 | 0.05 | 61.46 | 0.13 | 73.44 | 0.03 | [24 empty] | 81.79 | 0.1 | 81.65 | 0.09 | 74.44 | 0.06 | 74.54 | 0.07 | 74.44 | 0.07 | 74.45 | 0.06 | 74.53 | 0.06 | 74.54 | 0.06 |  |  | 75.54 | 0.11 | 75 | 0.1 | 74.98 | 0.09 | 74.95 | 0.08 | 77.69 | 0.08 | 75.43 | 0.1 | 75.11 | 0.1 | 75.1 | 0.1 | 77.75 | 0.12 | 76.1 | 0.07 | 76.16 | 0.06 | 75.68 | 0.07 | 77.14 | 0.11 | 76.18 | 0.08 | 76.47 | 0.06 | 72.49 | 0.1 | [30 empty] | 81.71 | 0.09 | 81.46 | 0.09 | 81.42 | 0.1 | 81.5 | 0.1 | 81.33 | 0.09 | 81.35 | 0.12 | [50 empty] | C8-55-CE3 | 75.001 | 0.016 | 61.994 | 0.024 | 56.034 | 0.017 | 52.921 | 0.023 | 81.996 | 0.025 | 67.997 | 0.019 | 2529.1 | 3.6 | 2500 | 3.6 | 1.275 | 0.003 | -0.466 | 0.003 | 0.216 | 0.004 | 1.1827 | 0.0034 | 29.458 | 0 | 7702 | 30 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4263 | 11617.4664 | 374.4685 | 23.7634 | 103.7063 | 11513.7601 | 0.0087993 | 27.6447 | 54.6077 | 13.7485 | 13.0619 | 0.011342 | 32.1259 | 0.0087764 | 27.6043 | 0.0077783 | 21.8945 | 75.0637 | 62.0512 | 21.5472 | 70836.6559 | 57035.338 | 6162 | 0.29689 | 66858.6969 | 53057.379 | 8.6807 | 0.19918 | -6.0974 | -20.456 | 49.5199 | 70836.6559 | 66333.7209 | 4034.019 | 468.9159 | 70836.6559 | 100%
3 | 3-5295CF | 75N0003 | 3-5295CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 0:06:28 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.2 | 28.8 | 0 | 48128 | 86 | 47222 | 186 | 6832 | 137 | 54967 | 136 | 6.2985 |  |  |  |  | 109.12 | 0.01 | 29.09 | [32 empty] | 83% Airflow, Both Stages, Closed Dampers. | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor: | 75.01 | 0.017 | 61.996 | 0.03 | 95.002 | 0.023 | 75.039 | 0.016 | 74.44 | 0.07 | 57.54 | 0.06 | 62.02 | 0.03 | 0.196 | 0.005 | 1.1888 | 0.0029 | 48128 | 86 | 6832 | 137 | 6.298 | 0.028 | 77521 | 66 | 8.883 | 0.032 | 29.09 | 0.19 | 230.5 | 0.8 | 230.3 | 0.8 | 229.5 | 0.8 | 28.8 | 0.1 | 25.4 | 0.1 | 28.7 | 0.1 | 6602.4 | 37.4 | 3522.2 | 45.2 | 2124.7 | 32.2 | 288 |  | 229 |  | 229 |  | 6.4 |  | 6.3 |  | 6.1 |  | 0.52 | 229 |  | 228 |  | 230 |  | 11.2 |  | 10.3 |  | 9.9 |  | 3390 |  | 0.81 | 230 | 231 | 229 | 10.6 | 9.4 | 10.1 | 3240 | 0.81 | [8 empty] | 8730 | [22 empty] | 267.92 | 0.21 | 176 | 0.07 | 122.17 | 0.06 | 53.83 | 0.09 | 249.1 | 0.21 | 101.97 | 0.06 | 116.81 | 0.06 | 14.84 | 0.05 | [8 empty] | 72.79 | 0.05 | 46.28 | 0.06 | 42.7 | 0.03 | 3.58 | 0.06 | 637.79 | 0.55 | 40.1 | 0.02 | 77521 | 66 | 44024 | 39 | [38 empty] | 254.28 | 0.25 | 207.04 | 0.05 | 118.31 | 0.07 | 88.73 | 0.08 | [6 empty] | 243.4 | 0.24 | 102.38 | 0.06 | 115.12 | 0.07 | 12.75 | 0.06 | [6 empty] | 63.57 | 0.06 | 77.37 | 0.06 | 36.32 | 0.04 | 41.06 | 0.08 | 101.74 | 0.08 | 522.66 | 0.51 | 40.23 | 0.02 | 115.16 | 0.01 | 77521 | 66 | 39163 | 38 | [26 empty] | 57.26 | 0.06 | 57.48 | 0.05 | 57.72 | 0.05 | 57.77 | 0.08 | 57.68 | 0.08 | 57.72 | 0.07 | [18 empty] | 101.97 | 0.06 | [12 empty] | 103.77 | 0.06 | 102.31 | 0.07 | [20 empty] | 102.23 | 0.07 | 101.74 | 0.08 | 103.77 | 0.06 | 102.31 | 0.07 | 47.55 | 0.05 | 77.46 | 0.06 | [24 empty] | 94.99 | 0.11 | 94.64 | 0.08 | 74.49 | 0.06 | 74.6 | 0.05 | 74.49 | 0.06 | 74.49 | 0.05 | 74.57 | 0.05 | 74.6 | 0.05 |  |  | 76.61 | 0.11 | 75.36 | 0.09 | 75.23 | 0.09 | 75.37 | 0.09 | 85.05 | 0.16 | 76.25 | 0.11 | 75.44 | 0.08 | 75.42 | 0.09 | 84.48 | 0.25 | 79.67 | 0.1 | 78.58 | 0.1 | 77.17 | 0.1 | 83.5 | 0.25 | 80.61 | 0.12 | 79.94 | 0.08 | 74.88 | 0.11 | [30 empty] | 94.95 | 0.1 | 94.66 | 0.08 | 94.65 | 0.09 | 94.76 | 0.1 | 94.58 | 0.1 | 94.54 | 0.13 | [50 empty] | C8-55-CE3 | 75.01 | 0.017 | 61.996 | 0.03 | 57.783 | 0.023 | 54.698 | 0.026 | 95.002 | 0.023 | 75.039 | 0.016 | 2540.5 | 3.1 | 2500 | 3.1 | 1.263 | 0.003 | -0.464 | 0.003 | 0.196 | 0.005 | 1.1888 | 0.0029 | 29.429 | 0.001 | 8727 | 31 | 1490 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.3684 | 11626.3354 | 370.9441 | 24.0138 | 102.1846 | 11524.1509 | 0.0088211 | 27.6987 | 56.4146 | 14.1002 | 13.1108 | 0.013954 | 38.1948 | 0.0087756 | 27.6056 | 0.0083639 | 22.9566 | 75.1874 | 62.1284 | 22.6231 | 59010.2019 | 52381.9411 | 7237 | 0.41857 | 55190.8641 | 48562.6033 | 6.3242 | 0.19157 | -5.0756 | -18.7727 | 51.966 | 59010.2019 | 54050.8494 | 3877.2989 | 1082.0536 | 59010.2019 | 100%
3 | 3-295 | 75N0004 | 3-295 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 4:02:04 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.1 | 28.4 | 0 | 47546 | 66 | 47921 | 224 | 6818 | 54 | 54370 | 80 | 6.1932 |  |  |  |  | 109.08 | 0.01 | 31.27 | [32 empty] | 83% Airflow Both Stages, Economizer, Closed Damper | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.999 | 0.013 | 61.949 | 0.011 | 95.001 | 0.015 | 75.044 | 0.021 | 74.76 | 0.09 | 57.69 | 0.03 | 62.38 | 0.02 | 0.064 | 0.002 | 0.9199 | 0.0019 | 47546 | 66 | 6818 | 54 | 6.193 | 0.023 | 79111 | 58 | 9.012 | 0.031 | 31.27 | 0.11 | 230.3 | 0.6 | 229.7 | 0.6 | 229.7 | 0.6 | 28.4 | 0.1 | 25.9 | 0.1 | 29 | 0.1 | 6515.7 | 30.9 | 3645 | 35.5 | 2263.3 | 26.4 | 229 |  | 229 |  | 228 |  | 6.3 |  | 6.4 |  | 6.1 |  | 0.54 | 228 |  | 229 |  | 230 |  | 11 |  | 10.4 |  | 10 |  | 3410 |  | 0.82 | 231 | 229 | 228 | 10.5 | 9.6 | 10.1 | 3260 | 0.81 | [8 empty] | 8800 | [22 empty] | 270.39 | 0.21 | 177.25 | 0.05 | 122.83 | 0.06 | 54.42 | 0.08 | 251.39 | 0.21 | 102 | 0.06 | 117.44 | 0.06 | 15.44 | 0.04 | [8 empty] | 73.23 | 0.04 | 46.13 | 0.05 | 42.93 | 0.03 | 3.21 | 0.05 | 643.37 | 0.5 | 40.11 | 0.02 | 79111 | 58 | 44371 | 32 | [38 empty] | 255.64 | 0.21 | 205.78 | 0.04 | 118.67 | 0.06 | 87.11 | 0.05 | [6 empty] | 244.05 | 0.22 | 103.03 | 0.05 | 115.29 | 0.07 | 12.26 | 0.07 | [6 empty] | 65.49 | 0.04 | 77.59 | 0.04 | 37.61 | 0.03 | 39.97 | 0.05 | 102.36 | 0.06 | 535.65 | 0.45 | 40.43 | 0.02 | 115.1 | 0.01 | 79111 | 58 | 39997 | 35 | [26 empty] | 57.43 | 0.03 | 57.45 | 0.03 | 58.03 | 0.03 | 57.9 | 0.03 | 57.86 | 0.02 | 57.94 | 0.03 | [18 empty] | 102 | 0.06 | [12 empty] | 102.88 | 0.06 | 102.32 | 0.07 | [20 empty] | 102.2 | 0.07 | 102.36 | 0.06 |  |  |  |  | 48.16 | 0.04 | 77.47 | 0.03 | [24 empty] | 94.6 | 0.11 | 95.23 | 0.08 | 75.11 | 0.06 | 75.27 | 0.05 | 75.01 | 0.06 | 74.9 | 0.06 | 75.02 | 0.06 | 75.06 | 0.06 |  |  | 76.58 | 0.1 | 75.4 | 0.07 | 75.42 | 0.07 | 75.52 | 0.06 | 89.21 | 0.1 | 76.97 | 0.11 | 75.34 | 0.09 | 75.35 | 0.08 | 82.63 | 0.11 | 80.09 | 0.11 | 76.76 | 0.09 | 76.62 | 0.08 | 82.82 | 0.09 | 80.12 | 0.1 | 77.89 | 0.08 | 77.53 | 0.08 | [30 empty] | 94.99 | 0.09 | 94.65 | 0.08 | 94.84 | 0.1 | 94.9 | 0.09 | 95.37 | 0.07 | 95.11 | 0.13 | [50 empty] | C8-55-CE3 | 74.999 | 0.013 | 61.949 | 0.011 | 58.062 | 0.012 | 54.801 | 0.016 | 95.001 | 0.015 | 75.044 | 0.021 | 2573.4 | 2.6 | 2510.7 | 2.5 | 1.201 | 0.002 | -0.519 | 0.003 | 0.064 | 0.002 | 0.9199 | 0.0019 | 29.211 | 0 | 8779 | 29 | 1520 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.408 | 11770.6011 | 354.2443 | 25.3972 | 108.0712 | 11662.5299 | 0.0087951 | 27.6695 | 56.654 | 14.1003 | 13.1178 | 0.013959 | 38.1997 | 0.0087473 | 27.5719 | 0.008357 | 23.0171 | 75.1844 | 62.088 | 22.6739 | 58800.615 | 52347.3095 | 7259 | 0.42134 | 54821.891 | 48368.5854 | 6.2447 | 0.20304 | -4.9955 | -18.5304 | 51.9332 | 58800.615 | 53613.0039 | 4039.0528 | 1148.5583 | 58800.615 | 100%
3 | 5-295 recalc | 75N0008 | 5-295 | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/19/2013 | 9:43:18 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 8.59 lbs ck2: 10.35 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 8.59 | 10.35 | 7.6 | 8.1 | 230.2 | 1.3 | 28.3 | 0 | 48393 | 92 | 49600 | 155 | 4915 | 277 | 53313 | 224 | 5.9835 | 895.7 |  |  |  | 109.5 | 0.01 | 34.88 | [32 empty] | 83.3% air flow both stages closed | 2531 SCFM, VFD Setpoint 25.02%, (Manual Mode) Damper close 28% (set to 72% on Meriam M334 damper controller) with Both Stages Cooling, with Econo fully closed, The unit has NO Tape around the Unit. -0.515 Inlet static. | 75.003 | 0.043 | 61.97 | 0.021 | 95.003 | 0.008 | 75.003 | 0.023 | 74.74 | 0.07 | 57.25 | 0.03 | 60.93 | 0.02 | -0.039 | 0.002 | 0.9293 | 0.0017 | 48807 | 92 | 4904 | 277 | 6.029 | 0.032 | 81872 | 66 | 9.189 | 0.029 | 34.39 | 0.26 | 230.2 | 1 | 230.1 | 1 | 229.7 | 1 | 28.3 | 0.1 | 26.4 | 0.1 | 29.1 | 0.1 | 6487.7 | 40.7 | 3689.6 | 54.3 | 2422.4 | 32.4 | 230 |  | 229 |  | 229 |  | 6.2 |  | 6.3 |  | 6.1 |  | 0.55 | 228 |  | 228 |  | 229 |  | 10.8 |  | 10.4 |  | 10.2 |  | 3410 |  | 0.82 | 229 | 229 | 229 | 10.7 | 10.2 | 9.9 | 3340 | 0.83 | [8 empty] | 8900 | [22 empty] | 272.88 | 0.2 | 172.37 | 0.05 | 123.53 | 0.06 | 48.84 | 0.06 | 253.79 | 0.2 | 105.13 | 0.1 | 118.16 | 0.06 | 13.02 | 0.09 | [8 empty] | 72.83 | 0.05 | 48.36 | 0.04 | 42.7 | 0.03 | 5.66 | 0.03 | 646.36 | 0.63 | 41.1 | 0.03 | 81872 | 66 | 44211 | 43 | [38 empty] | 268.24 | 0.24 | 199.58 | 0.05 | 122.25 | 0.07 | 77.33 | 0.06 | [6 empty] | 255.46 | 0.23 | 103.27 | 0.05 | 118.63 | 0.07 | 15.36 | 0.05 | [6 empty] | 73.86 | 0.05 | 76.5 | 0.04 | 43.37 | 0.03 | 33.13 | 0.06 | 101.85 | 0.06 | 589.88 | 0.67 | 40.51 | 0.02 | 114.31 | 0.01 | 81872 | 66 | 43531 | 45 | [26 empty] | 56.95 | 0.03 | 57.57 | 0.03 | 57.57 | 0.03 | 56.82 | 0.03 | 57.21 | 0.03 | 57.43 | 0.04 | [32 empty] | 102.65 | 0.06 | 102.78 | 0.06 | [16 empty] | 102.99 | 0.05 | 102.58 | 0.06 | 102.18 | 0.06 | 101.85 | 0.06 |  |  |  |  | 49.39 | 0.05 | 75.49 | 0.04 | 103.53 | 0.06 | 103.53 | 0.06 | [20 empty] | 94.08 | 0.15 | 95.43 | 0.1 | 75.97 | 0.05 | 75.13 | 0.06 | 74.85 | 0.06 | 75.36 | 0.05 | 74.82 | 0.06 | 74.85 | 0.06 |  |  | 81.03 | 0.08 | 81.73 | 0.09 | 81.5 | 0.1 | 82.03 | 0.08 | 76.96 | 0.07 | 77.53 | 0.06 | 76.81 | 0.05 | 79.46 | 0.05 | 75.66 | 0.05 | 75.44 | 0.06 | 75.64 | 0.05 | 78.03 | 0.06 | 75.47 | 0.06 | 75.16 | 0.06 | 75.61 | 0.06 | 75.82 | 0.06 | [30 empty] | 93.04 | 0.07 | 92.68 | 0.06 | 92.73 | 0.06 | 92.86 | 0.08 | 92.75 | 0.06 | 92.71 | 0.09 | [38 empty] | 103.38 | 0.06 | 103.32 | 0.06 | 103.1 | 0.05 | 103.02 | 0.06 |  |  |  |  | C8-55-CE3 | 75.003 | 0.043 | 61.97 | 0.021 | 57.793 | 0.012 | 54.973 | 0.014 | 95.003 | 0.008 | 75.003 | 0.023 | 2578.6 | 2.4 | 2531 | 2.4 | 1.144 | 0.002 | -0.515 | 0.003 | -0.039 | 0.002 | 0.9293 | 0.0017 | 29.32 | 0.001 | 8910 | 28 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4456 | 11799.3784 | 340.16 | 25.2989 | 107.6548 | 11691.7235 | 0.0088072 | 27.6834 | 56.3474 | 14.1 | 13.1122 | 0.013923 | 38.16 | 0.0087601 | 27.587 | 0.0085192 | 23.1278 | 75.1872 | 62.1073 | 22.7754 | 57911.7679 | 53351.5616 | 7370 | 0.43435 | 53816.714 | 49256.5078 | 6.04 | 0.16508 | -4.908 | -18.8398 | 52.6223 | 57911.7679 | 52615.1561 | 4158.3754 | 1138.2364 | 57911.7679 | 100%
3 | 7-3A | 75N0009 | 7-3A | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/26/2013 | 7:25:05 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 5.55 lbs ck2: 7.11 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 5.55 | 7.11 | 7.6 | 8.1 | 230.4 | 1.3 | 26.3 | 0 | 29304 | 41 | 29844 | 84 | -2912 | 95 | 26390 | 112 | 3.2901 |  |  |  |  | 115.56 | 0.01 | 31.17 | [32 empty] | Closed Damper -40% charge, Both stages A-Test | 2526.1 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.413 Inlet static. | 75.001 | 0.009 | 62.001 | 0.011 | 94.993 | 0.012 | 74.998 | 0.029 | 74.76 | 0.03 | 64.15 | 0.01 | 66.96 | 0.01 | 0.036 | 0.002 | 0.9398 | 0.0018 | 29304 | 41 | -2912 | 95 | 3.29 | 0.018 | 38344 | 241 | 4.78 | 0.033 | 31.17 | 0.53 | 230.4 | 1.1 | 230.1 | 1 | 229.6 | 1 | 26.3 | 0.1 | 24.6 | 0.1 | 26.8 | 0.1 | 6023.4 | 42.9 | 3602.4 | 56.3 | 1998 | 33.8 | 228.9 |  | 229.4 |  | 228.4 |  | 6.2 |  | 6.4 |  | 6.1 |  | 0.56 | 230.9 |  | 229.4 |  | 230.1 |  | 9.9 |  | 9.4 |  | 9.4 |  | 3000 |  | 0.8 | 227.7 | 229 | 229 | 9.7 | 9.1 | 8.9 | 2840 | 0.77 | [8 empty] | 8020 | [22 empty] | 238.03 | 0.23 | 212.74 | 0.05 | 113.49 | 0.07 | 99.26 | 0.07 | 223.43 | 0.3 | 106.16 | 0.11 | 108.98 | 0.1 | 2.82 | 0.09 | [8 empty] | 53.38 | 0.07 | 76.81 | 0.02 | 28.5 | 0.06 | 48.31 | 0.06 | 352.38 | 2.01 | 41.43 | 0.04 | 38344 | 241 | 26122 | 151 | [38 empty] | 224.77 | 0.23 | 230.6 | 0.07 | 109.4 | 0.07 | 121.2 | 0.1 | [6 empty] | 215.52 | 0.35 | 105.71 | 0.06 | 106.45 | 0.11 | 0.74 | 0.09 | [6 empty] | 42.79 | 0.11 | 82.17 | 0.02 | 19.42 | 0.11 | 62.75 | 0.11 | 105.37 | 0.07 | 231.4 | 2.56 | 41.29 | 0.02 | 116.97 | 0.01 | 38344 | 241 | 17515 | 194 | [26 empty] | 63.8 | 0.03 | 64.57 | 0.03 | 64.64 | 0.03 | 63.86 | 0.03 | 64.27 | 0.03 | 64.36 | 0.03 | [32 empty] | 108.3 | 0.06 | 105.27 | 0.05 | [16 empty] | 105.03 | 0.05 | 105.43 | 0.07 | 107.24 | 0.06 | 105.37 | 0.07 |  |  |  |  | 77.41 | 0.02 | 84.83 | 0.04 | 108.01 | 0.06 | 105.31 | 0.06 | [20 empty] | 94.16 | 0.13 | 95.22 | 0.09 | 75.63 | 0.03 | 75.19 | 0.04 | 74.83 | 0.03 | 75.06 | 0.03 | 74.73 | 0.04 | 74.82 | 0.03 |  |  | 80.41 | 0.09 | 82.34 | 0.08 | 81.67 | 0.08 | 83.77 | 0.1 | 76.97 | 0.03 | 77.44 | 0.04 | 77.91 | 0.04 | 79.01 | 0.04 | 75.94 | 0.03 | 75.53 | 0.02 | 75.8 | 0.03 | 77.96 | 0.05 | 75.22 | 0.04 | 75.08 | 0.03 | 75.63 | 0.03 | 77.72 | 0.05 | [30 empty] | 93.52 | 0.08 | 93.21 | 0.1 | 93.47 | 0.09 | 93.41 | 0.08 | 93.45 | 0.1 | 93.37 | 0.09 | [50 empty] | C8-55-CE3 | 75.001 | 0.009 | 62.001 | 0.011 | 64.577 | 0.01 | 58.692 | 0.01 | 94.993 | 0.012 | 74.998 | 0.029 | 2610.9 | 2.5 | 2526.1 | 2.5 | 1.128 | 0.002 | -0.413 | 0.002 | 0.036 | 0.002 | 0.9398 | 0.0018 | 29.262 | 0.002 | 8021 | 28 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4897 | 11788.2799 | 334.7532 | 22.6552 | 96.4071 | 11691.8728 | 0.0088231 | 27.6956 | 63.0873 | 14.0997 | 13.289 | 0.013921 | 38.1553 | 0.008781 | 27.6093 | 0.0091328 | 25.4503 | 75.166 | 62.1237 | 25.0867 | 30754.5263 | 34172.9705 | 6451 | 0.7159 | 26538.629 | 29957.0732 | 3.3086 | 0.39358 | -2.6089 | -12.0787 | 55.2479 | 30754.5263 | 25451.9478 | 4285.8718 | 1016.7068 | 30754.5263 | 100%
3 | 7-5A | 75N0010 | 8-5A | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 14:08:19 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 11.63 lbs ck2: 13.59 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 11.63 | 13.59 | 7.6 | 8.1 | 230.3 | 1.4 | 29.8 | 0 | 50215 | 80 | 51218 | 164 | 5239 | 104 | 55459 | 102 | 5.8249 | 895.9 |  |  |  | 109.42 | 0.01 | 39.92 | [32 empty] | Closed damper, +40% Charge, both stages A-Test | 2535.2 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.413 Inlet static. | 74.995 | 0.017 | 62.008 | 0.013 | 94.994 | 0.012 | 74.992 | 0.03 | 74.98 | 0.07 | 56.97 | 0.03 | 61.37 | 0.02 | -0.004 | 0.003 | 0.9359 | 0.002 | 50215 | 80 | 5239 | 104 | 5.825 | 0.029 | 92314 | 61 | 9.696 | 0.046 | 39.92 | 0.1 | 230.3 | 1 | 230.1 | 1 | 229.6 | 1 | 29.8 | 0.1 | 27.9 | 0.1 | 30.2 | 0.1 | 6854.2 | 44.8 | 3739 | 53.9 | 2666.9 | 36.4 | 227.4 |  | 229.7 |  | 226.2 |  | 6.4 |  | 6.5 |  | 5.9 |  | 0.55 | 227.2 |  | 228.8 |  | 230 |  | 11.1 |  | 10.6 |  | 10.5 |  | 3500 |  | 0.83 | 227.5 | 228.4 | 229.4 | 11.9 | 11.3 | 11.1 | 3800 | 0.84 | [8 empty] | 9500 | [22 empty] | 285.24 | 0.15 | 152.37 | 0.06 | 126.86 | 0.04 | 25.51 | 0.05 | 264.76 | 0.15 | 102.36 | 0.07 | 121.26 | 0.04 | 18.91 | 0.07 | [8 empty] | 75.11 | 0.03 | 48.7 | 0.05 | 44.16 | 0.02 | 4.53 | 0.05 | 697.89 | 0.55 | 40.22 | 0.02 | 92314 | 61 | 48296 | 41 | [38 empty] | 308.72 | 0.3 | 170.21 | 0.11 | 132.94 | 0.07 | 37.27 | 0.13 | [6 empty] | 293.35 | 0.28 | 101.55 | 0.05 | 129 | 0.07 | 27.45 | 0.06 | [6 empty] | 79.82 | 0.06 | 51.06 | 0.04 | 47.17 | 0.03 | 3.89 | 0.02 | 100.54 | 0.06 | 708.55 | 0.69 | 39.97 | 0.02 | 109.56 | 0.01 | 92314 | 61 | 49309 | 47 | [26 empty] | 56.56 | 0.02 | 57.21 | 0.02 | 57.19 | 0.02 | 56.42 | 0.03 | 56.84 | 0.03 | 57.06 | 0.02 | [32 empty] | 101.42 | 0.04 | 101.31 | 0.05 | [16 empty] | 101.76 | 0.04 | 101.08 | 0.06 | 101 | 0.04 | 100.54 | 0.06 |  |  |  |  | 49.6 | 0.05 | 49.69 | 0.04 | 102.67 | 0.04 | 102.35 | 0.04 | [20 empty] | 94 | 0.16 | 95.57 | 0.12 | 75.7 | 0.04 | 75.26 | 0.04 | 74.94 | 0.04 | 75.14 | 0.04 | 74.88 | 0.04 | 74.96 | 0.04 |  |  | 80.59 | 0.07 | 82.63 | 0.08 | 81.67 | 0.08 | 84.05 | 0.13 | 77.13 | 0.04 | 77.54 | 0.04 | 77.99 | 0.04 | 79.03 | 0.04 | 76.08 | 0.03 | 75.74 | 0.03 | 75.73 | 0.05 | 77.85 | 0.06 | 75.18 | 0.06 | 75.05 | 0.05 | 75.62 | 0.05 | 77.45 | 0.06 | [30 empty] | 93.57 | 0.14 | 93.19 | 0.14 | 93.6 | 0.15 | 93.5 | 0.15 | 93.56 | 0.15 | 93.43 | 0.14 | [50 empty] | C8-55-CE3 | 74.995 | 0.017 | 62.008 | 0.013 | 57.347 | 0.006 | 54.81 | 0.009 | 94.994 | 0.012 | 74.992 | 0.03 | 2592.6 | 2.8 | 2535.2 | 2.7 | 1.087 | 0.002 | -0.413 | 0.002 | -0.004 | 0.003 | 0.9359 | 0.002 | 29.233 | 0.001 | 9521 | 45 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5161 | 11873.5913 | 323.7478 | 22.6552 | 96.4072 | 11777.1841 | 0.0088287 | 27.7 | 55.8309 | 14.0997 | 13.101 | 0.013915 | 38.1495 | 0.0087871 | 27.6145 | 0.008531 | 23.0319 | 75.1589 | 62.1297 | 22.6623 | 59815.89 | 55078.3016 | 7931 | 0.45253 | 55494.1713 | 50756.583 | 5.8286 | 0.13993 | -5.0377 | -19.328 | 52.6862 | 59815.89 | 54411.5994 | 4388.6395 | 1015.6511 | 59815.89 | 100%
3 | 3-42115CF | 75N0012 | 3-42115CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 13:51:45 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.2 | 33.3 | 0 | 46821 | 76 | 45937 | 176 | -767 | 80 | 46053 | 103 | 4.2661 |  |  |  |  | 109.45 | 0.01 | 40.97 | [32 empty] | 100% airflow, both stages, closed damper | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 100%: Horiz airflow disch config. set on floor: | 75.003 | 0.012 | 62 | 0.011 | 115.025 | 0.016 | 80.012 | 0.03 | 74.53 | 0.06 | 60.74 | 0.04 | 63.99 | 0.01 | -0.269 | 0.006 | 1.7218 | 0.0045 | 46821 | 76 | -767 | 80 | 4.266 | 0.016 | 78024 | 58 | 7.228 | 0.021 | 40.97 | 0.13 | 230.3 | 0.8 | 230 | 0.8 | 229.6 | 0.8 | 33.3 | 0.1 | 30 | 0.1 | 33.5 | 0.1 | 7660.9 | 33.1 | 3723.1 | 39.4 | 3134 | 29.3 | 230 |  | 230 |  | 230 |  | 6.7 |  | 6.5 |  | 6.4 |  | 0.57 | 230 |  | 230 |  | 230 |  | 13.3 |  | 12.4 |  | 12.1 |  | 4290 |  | 0.86 | 230 | 230 | 230 | 12.8 | 11.6 | 12.3 | 4200 | 0.87 | [8 empty] | 10800 | [22 empty] | 343.75 | 0.21 | 190.24 | 0.06 | 141.44 | 0.05 | 48.8 | 0.06 | 324.85 | 0.22 | 123.76 | 0.07 | 136.94 | 0.05 | 13.18 | 0.04 | [8 empty] | 79.68 | 0.04 | 50.43 | 0.04 | 47.13 | 0.02 | 3.3 | 0.03 | 693.21 | 0.42 | 47.17 | 0.02 | 78024 | 58 | 43166 | 28 | [38 empty] | 333 | 0.31 | 235.2 | 0.05 | 138.9 | 0.07 | 96.3 | 0.05 | [6 empty] | 321.4 | 0.3 | 123.84 | 0.06 | 136.1 | 0.07 | 12.26 | 0.06 | [6 empty] | 74.94 | 0.03 | 82.37 | 0.03 | 44.1 | 0.02 | 38.27 | 0.04 | 123.66 | 0.08 | 578.03 | 0.53 | 47.2 | 0.02 | 115.48 | 0.01 | 78024 | 58 | 39466 | 39 | [26 empty] | 60.12 | 0.06 | 60.4 | 0.05 | 61.2 | 0.05 | 61.03 | 0.08 | 60.95 | 0.08 | 61.04 | 0.07 | [18 empty] | 123.76 | 0.07 | [12 empty] | 125.6 | 0.06 | 124.31 | 0.07 | [20 empty] | 123.94 | 0.07 | 123.66 | 0.08 | 125.6 | 0.06 | 124.31 | 0.07 | 52.39 | 0.03 | 82.37 | 0.04 | [24 empty] | 115.53 | 0.11 | 114.9 | 0.1 | 74.6 | 0.05 | 74.64 | 0.04 | 74.51 | 0.05 | 74.5 | 0.05 | 74.62 | 0.05 | 74.64 | 0.05 |  |  | 76.42 | 0.08 | 75.41 | 0.08 | 75.34 | 0.08 | 75.78 | 0.08 | 95.26 | 0.54 | 87.23 | 0.17 | 75.52 | 0.08 | 75.48 | 0.08 | 92.1 | 0.51 | 81.56 | 0.14 | 79.57 | 0.15 | 78.43 | 0.16 | 84.18 | 0.14 | 81.01 | 0.12 | 83.1 | 0.12 | 77.9 | 0.16 | [30 empty] | 115.51 | 0.11 | 115.24 | 0.11 | 115.19 | 0.1 | 115.34 | 0.1 | 115.15 | 0.1 | 114.99 | 0.12 | [50 empty] | C8-55-CE3 | 75.003 | 0.012 | 62 | 0.011 | 60.949 | 0.007 | 56.997 | 0.008 | 115.025 | 0.016 | 80.012 | 0.03 | 3071.5 | 4 | 3000 | 3.9 | 0.924 | 0.003 | -0.312 | 0.002 | -0.269 | 0.006 | 1.7218 | 0.0045 | 29.385 | 0.001 | 10795 | 31 | 1700 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.399 | 13965.9722 | 325.6554 | 20.0427 | 82.3239 | 13883.6482 | 0.0088093 | 27.6989 | 59.55 | 14.6077 | 13.1956 | 0.013773 | 42.9224 | 0.0087799 | 27.6086 | 0.0089602 | 24.377 | 75.241 | 62.1298 | 24.0357 | 51160.259 | 52593.8182 | 9095 | 0.60675 | 46469.621 | 47903.1802 | 4.3047 | 0.25078 | -3.6632 | -15.6911 | 54.2979 | 51160.259 | 45132.5757 | 4766.9944 | 1260.6889 | 51160.259 | 100%
3 | 3-4282CF | 75N0013 | 3-4282CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 12:09:48 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.2 | 26.6 | 0 | 57345 | 117 | 56471 | 206 | 12424 | 132 | 69781 | 135 | 8.8364 |  |  |  |  | 112.64 | 0.01 | 12.25 | [32 empty] | 100% airflow, both stages, closed damper | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 100%: Horiz airflow disch config. set on floor: | 75.007 | 0.025 | 62.005 | 0.021 | 82.003 | 0.023 | 67.995 | 0.021 | 74.5 | 0.08 | 57.67 | 0.05 | 61.61 | 0.02 | -0.225 | 0.006 | 1.7065 | 0.0044 | 57345 | 117 | 12424 | 132 | 8.836 | 0.039 | 79518 | 58 | 10.069 | 0.04 | 12.25 | 0.18 | 230.3 | 0.8 | 230.1 | 0.8 | 229.7 | 0.8 | 26.6 | 0.1 | 23.7 | 0.1 | 27.1 | 0.1 | 6088.1 | 37.7 | 3517.3 | 45.5 | 1809.4 | 32 | 230 |  | 230 |  | 230 |  | 6.7 |  | 6.5 |  | 6.4 |  | 0.57 | 230 |  | 230 |  | 230 |  | 10.1 |  | 9.4 |  | 8.9 |  | 2880 |  | 0.78 | 230 | 230 | 230 | 9.5 | 8.4 | 9 | 2710 | 0.77 | [8 empty] | 7910 | [22 empty] | 226.65 | 0.17 | 172.71 | 0.04 | 110.02 | 0.05 | 62.69 | 0.04 | 207.78 | 0.16 | 88.29 | 0.04 | 103.94 | 0.05 | 15.65 | 0.05 | [8 empty] | 70.08 | 0.05 | 64.97 | 0.06 | 40.88 | 0.03 | 24.09 | 0.07 | 600.55 | 0.45 | 35.84 | 0.01 | 79518 | 58 | 46119 | 34 | [38 empty] | 209.47 | 0.18 | 191.09 | 0.03 | 104.5 | 0.06 | 86.59 | 0.05 | [6 empty] | 199.07 | 0.19 | 88.85 | 0.03 | 101.01 | 0.06 | 12.16 | 0.06 | [6 empty] | 56.37 | 0.04 | 74.62 | 0.03 | 30.92 | 0.03 | 43.7 | 0.05 | 87.84 | 0.05 | 480.97 | 0.43 | 36.01 | 0.01 | 115.03 | 0.01 | 79518 | 58 | 38007 | 34 | [26 empty] | 57.53 | 0.06 | 57.43 | 0.04 | 57.87 | 0.05 | 58.09 | 0.08 | 58 | 0.08 | 58.04 | 0.07 | [18 empty] | 88.29 | 0.04 | [12 empty] | 89.98 | 0.04 | 88.43 | 0.05 | [20 empty] | 88.6 | 0.05 | 87.84 | 0.05 | 89.98 | 0.04 | 88.43 | 0.05 | 65.82 | 0.07 | 74.5 | 0.03 | [24 empty] | 81.82 | 0.1 | 81.7 | 0.07 | 74.56 | 0.06 | 74.69 | 0.06 | 74.6 | 0.06 | 74.6 | 0.05 | 74.68 | 0.05 | 74.7 | 0.05 |  |  | 75.49 | 0.1 | 75.2 | 0.1 | 75.15 | 0.09 | 75.14 | 0.08 | 78.32 | 0.15 | 77.2 | 0.09 | 75.28 | 0.09 | 75.24 | 0.09 | 77.58 | 0.12 | 76.23 | 0.08 | 75.86 | 0.08 | 75.61 | 0.07 | 75.88 | 0.1 | 75.95 | 0.07 | 76.37 | 0.06 | 73.46 | 0.17 | [30 empty] | 81.73 | 0.08 | 81.46 | 0.08 | 81.41 | 0.09 | 81.53 | 0.08 | 81.36 | 0.08 | 81.35 | 0.11 | [50 empty] | C8-55-CE3 | 75.007 | 0.025 | 62.005 | 0.021 | 57.912 | 0.018 | 54.231 | 0.021 | 82.003 | 0.023 | 67.995 | 0.021 | 3047.2 | 4 | 3000 | 3.9 | 0.955 | 0.003 | -0.31 | 0.002 | -0.225 | 0.006 | 1.7065 | 0.0044 | 29.438 | 0.001 | 7897 | 31 | 1710 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4003 | 13944.1765 | 336.5811 | 19.382 | 84.5845 | 13859.592 | 0.0087978 | 27.6395 | 56.5117 | 13.7486 | 13.1117 | 0.011339 | 32.1241 | 0.0087823 | 27.6121 | 0.0080678 | 22.6662 | 75.0496 | 62.0438 | 22.3252 | 74104.3834 | 62038.9503 | 6187 | 0.28495 | 69416.9047 | 57351.4716 | 8.7903 | 0.24239 | -5.3144 | -18.5379 | 50.5808 | 74104.3834 | 68966.694 | 4756.0472 | 381.6422 | 74104.3834 | 100%
3 | 3-4295CF | 75N0014 | 3-4295CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 2:14:08 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.1 | 29.2 | 0 | 52934 | 93 | 51791 | 211 | 5866 | 171 | 58806 | 181 | 6.5904 |  |  |  |  | 109.51 | 0.03 | 25.53 | [32 empty] | 100% Airflow, Both Stages, Closed Damper | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 100%: Horiz airflow disch config. set on floor: | 75.001 | 0.015 | 61.999 | 0.034 | 94.998 | 0.012 | 75.055 | 0.02 | 74.31 | 0.07 | 58.83 | 0.05 | 62.67 | 0.02 | -0.244 | 0.005 | 1.3027 | 0.0034 | 52934 | 93 | 5866 | 171 | 6.59 | 0.031 | 78963 | 60 | 8.85 | 0.032 | 25.53 | 0.22 | 230.5 | 0.7 | 230.3 | 0.7 | 229.5 | 0.7 | 29.2 | 0.1 | 25.8 | 0.1 | 29.1 | 0.1 | 6699.8 | 33.8 | 3523.7 | 38.5 | 2223.1 | 29.4 | 230 |  | 230 |  | 229 |  | 6.7 |  | 6.5 |  | 6.4 |  | 0.57 | 229 |  | 228 |  | 228 |  | 11.2 |  | 10.3 |  | 9.9 |  | 3400 |  | 0.81 | 230 | 231 | 229 | 10.6 | 9.4 | 10 | 3230 | 0.81 | [8 empty] | 8980 | [22 empty] | 269.51 | 0.17 | 179.67 | 0.06 | 122.61 | 0.05 | 57.05 | 0.07 | 250.48 | 0.17 | 101.99 | 0.05 | 117.21 | 0.05 | 15.22 | 0.04 | [8 empty] | 74.41 | 0.05 | 48.98 | 0.14 | 43.77 | 0.03 | 5.21 | 0.14 | 642.13 | 0.42 | 40.1 | 0.01 | 78963 | 60 | 44568 | 36 | [38 empty] | 254.46 | 0.2 | 207.62 | 0.03 | 118.36 | 0.06 | 89.26 | 0.05 | [6 empty] | 243.58 | 0.19 | 102.37 | 0.04 | 115.18 | 0.06 | 12.81 | 0.06 | [6 empty] | 63.69 | 0.05 | 77.96 | 0.03 | 36.4 | 0.04 | 41.56 | 0.05 | 101.67 | 0.06 | 523.02 | 0.45 | 40.22 | 0.01 | 115.25 | 0.01 | 78963 | 60 | 39240 | 35 | [26 empty] | 58.34 | 0.05 | 58.83 | 0.04 | 59.3 | 0.04 | 59.02 | 0.06 | 58.97 | 0.06 | 59.09 | 0.05 | [18 empty] | 101.99 | 0.05 | [12 empty] | 103.76 | 0.04 | 102.27 | 0.05 | [20 empty] | 102.23 | 0.06 | 101.67 | 0.06 | 103.76 | 0.04 | 102.27 | 0.05 | 50.5 | 0.29 | 78.03 | 0.04 | [24 empty] | 94.85 | 0.1 | 94.56 | 0.08 | 74.5 | 0.06 | 74.66 | 0.05 | 74.4 | 0.06 | 74.41 | 0.05 | 74.53 | 0.05 | 74.56 | 0.05 |  |  | 75.69 | 0.11 | 75.16 | 0.11 | 75.12 | 0.1 | 75.37 | 0.09 | 84.8 | 0.24 | 80.91 | 0.12 | 75.26 | 0.1 | 75.21 | 0.1 | 83.14 | 0.29 | 78.26 | 0.09 | 77.52 | 0.1 | 77.32 | 0.09 | 79.1 | 0.07 | 77.98 | 0.08 | 79.16 | 0.07 | 75.71 | 0.11 | [30 empty] | 94.85 | 0.09 | 94.48 | 0.09 | 94.49 | 0.1 | 94.64 | 0.1 | 94.5 | 0.09 | 94.5 | 0.12 | [50 empty] | C8-55-CE3 | 75.001 | 0.015 | 61.999 | 0.034 | 59.175 | 0.018 | 55.524 | 0.025 | 94.998 | 0.012 | 75.055 | 0.02 | 3056.8 | 4 | 3000 | 3.9 | 0.945 | 0.003 | -0.309 | 0.002 | -0.244 | 0.005 | 1.3027 | 0.0034 | 29.427 | 0.001 | 8923 | 31 | 1740 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4338 | 13950.3765 | 333.0567 | 19.5966 | 83.3883 | 13866.9882 | 0.0088108 | 27.6713 | 57.7412 | 14.1003 | 13.1472 | 0.013969 | 38.2104 | 0.0087797 | 27.6079 | 0.0085111 | 23.4559 | 75.1217 | 62.0892 | 23.1064 | 63681.8568 | 58191.3306 | 7183 | 0.38497 | 58879.9593 | 53389.4331 | 6.5987 | 0.23201 | -4.5649 | -17.3805 | 52.4905 | 63681.8568 | 57921.6575 | 4876.0771 | 884.1222 | 63681.8568 | 100%
3 | 3-62115CF | 75N0015 | 3-62115CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 19:18:45 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.2 | 32.4 | 0 | 34079 | 49 | 33325 | 152 | 960 | 142 | 35040 | 141 | 3.3852 |  |  |  |  | 109.24 | 0.01 | 54.46 | [32 empty] | 66.7% Airflow, Both Stages, Closed Damper | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 53%: Horiz airflow disch config. set on floor: | 74.997 | 0.011 | 61.998 | 0.032 | 115 | 0.014 | 80.019 | 0.02 | 74.34 | 0.07 | 59.4 | 0.05 | 64.09 | 0.02 | 0.509 | 0.003 | 0.7691 | 0.0016 | 34079 | 49 | 960 | 142 | 3.385 | 0.017 | 76953 | 51 | 7.434 | 0.022 | 54.46 | 0.19 | 230.5 | 0.8 | 230 | 0.8 | 229.5 | 0.8 | 32.4 | 0.1 | 29.2 | 0.1 | 32.4 | 0.1 | 7450.4 | 33.9 | 3707.4 | 40.5 | 2900.7 | 29.3 | 229 |  | 230 |  | 231 |  | 6.1 |  | 6.1 |  | 5.9 |  | 0.51 | 229 |  | 231 |  | 231 |  | 13.2 |  | 12.2 |  | 11.9 |  | 4210 |  | 0.86 | 228 | 229 | 228 | 12.8 | 11.6 | 12.2 | 4190 | 0.86 | [8 empty] | 10400 | [22 empty] | 337.02 | 0.17 | 182.84 | 0.06 | 139.85 | 0.04 | 42.99 | 0.06 | 318.86 | 0.17 | 123.55 | 0.05 | 135.47 | 0.04 | 11.92 | 0.05 | [8 empty] | 75.89 | 0.04 | 48 | 0.04 | 44.7 | 0.03 | 3.29 | 0.04 | 674.78 | 0.44 | 47.11 | 0.02 | 76953 | 51 | 41928 | 28 | [38 empty] | 331.66 | 0.24 | 236.62 | 0.04 | 138.58 | 0.06 | 98.04 | 0.05 | [6 empty] | 320.11 | 0.24 | 123.48 | 0.03 | 135.78 | 0.06 | 12.3 | 0.05 | [6 empty] | 74.96 | 0.03 | 84.63 | 0.04 | 44.1 | 0.02 | 40.53 | 0.04 | 123.4 | 0.06 | 576.08 | 0.46 | 47.08 | 0.01 | 115.88 | 0.01 | 76953 | 51 | 39632 | 32 | [26 empty] | 59.08 | 0.07 | 59.35 | 0.05 | 59.69 | 0.05 | 59.54 | 0.07 | 59.46 | 0.07 | 59.54 | 0.06 | [18 empty] | 123.55 | 0.05 | [12 empty] | 125.34 | 0.05 | 124 | 0.06 | [20 empty] | 123.62 | 0.06 | 123.4 | 0.06 | 125.34 | 0.05 | 124 | 0.06 | 49.63 | 0.04 | 84.64 | 0.04 | [24 empty] | 115.09 | 0.1 | 114.71 | 0.07 | 76.57 | 0.06 | 77.39 | 0.07 | 76.59 | 0.07 | 77.27 | 0.08 | 74.98 | 0.06 | 74.88 | 0.06 |  |  | 89.19 | 0.33 | 80.85 | 0.2 | 76.1 | 0.1 | 75.86 | 0.09 | 98.78 | 0.36 | 88.73 | 0.22 | 76.91 | 0.13 | 75.71 | 0.12 | 97.2 | 0.29 | 88.45 | 0.23 | 84.13 | 0.12 | 78.77 | 0.09 | 97.56 | 0.49 | 86.84 | 0.14 | 84.46 | 0.12 | 79.68 | 0.17 | [30 empty] | 115.17 | 0.1 | 114.75 | 0.09 | 114.82 | 0.1 | 114.99 | 0.1 | 114.79 | 0.1 | 114.81 | 0.13 | [50 empty] | C8-55-CE3 | 74.997 | 0.011 | 61.998 | 0.032 | 59.722 | 0.012 | 56.297 | 0.018 | 115 | 0.014 | 80.019 | 0.02 | 2046.7 | 2.1 | 2000 | 2 | 1.49 | 0.002 | -0.597 | 0.003 | 0.509 | 0.003 | 0.7691 | 0.0016 | 29.341 | 0 | 10351 | 31 | 1390 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5848 | 9328.9341 | 350.0913 | 27.7242 | 113.8791 | 9215.0551 | 0.0088411 | 27.7943 | 58.1372 | 14.6072 | 13.1636 | 0.013786 | 42.9304 | 0.00878 | 27.6072 | 0.0088345 | 23.9409 | 75.4897 | 62.2665 | 23.5543 | 39554.1649 | 38851.2018 | 8961 | 0.77322 | 36004.9566 | 35301.9935 | 3.4784 | 0.20131 | -4.2399 | -17.3525 | 53.7636 | 39554.1649 | 34203.0159 | 3606.1587 | 1744.9903 | 39554.1649 | 100%
3 | 3-6282CF | 75N0016 | 3-6282CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 7:59:28 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.2 | 26.1 | 0 | 47548 | 77 | 46873 | 231 | 15240 | 92 | 62802 | 117 | 8.3358 |  |  |  |  | 109.08 | 0.03 | 17.71 | [32 empty] | 66.7% airflow, both stages, closed damper | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 53%: Horiz airflow disch config. set on floor: | 74.997 | 0.024 | 62.009 | 0.022 | 81.996 | 0.024 | 67.992 | 0.02 | 74.4 | 0.11 | 53.6 | 0.05 | 59.83 | 0.02 | 0.554 | 0.003 | 0.757 | 0.0015 | 47548 | 77 | 15240 | 92 | 8.336 | 0.037 | 76316 | 56 | 10.13 | 0.042 | 17.71 | 0.15 | 230.5 | 0.8 | 230.3 | 0.8 | 229.5 | 0.8 | 26.1 | 0.1 | 23 | 0.1 | 26.3 | 0.1 | 5955.8 | 36.5 | 3478.6 | 43.9 | 1578.1 | 30.2 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6 |  | 0.51 | 230 |  | 230 |  | 230 |  | 10 |  | 9.3 |  | 8.8 |  | 2840 |  | 0.77 | 230 | 230 | 230 | 9.5 | 8.3 | 8.9 | 2690 | 0.76 | [8 empty] | 7550 | [22 empty] | 222.84 | 0.14 | 163.41 | 0.06 | 108.82 | 0.04 | 54.58 | 0.08 | 204.52 | 0.13 | 88 | 0.06 | 102.85 | 0.04 | 14.85 | 0.04 | [8 empty] | 66.25 | 0.05 | 43.73 | 0.19 | 38.23 | 0.03 | 5.5 | 0.19 | 589.44 | 0.36 | 35.75 | 0.02 | 76316 | 56 | 43223 | 34 | [38 empty] | 208.55 | 0.17 | 189.3 | 0.03 | 104.2 | 0.06 | 85.1 | 0.05 | [6 empty] | 198.15 | 0.19 | 88.55 | 0.04 | 100.69 | 0.07 | 12.14 | 0.07 | [6 empty] | 55.86 | 0.04 | 72.26 | 0.04 | 30.53 | 0.03 | 41.73 | 0.04 | 87.68 | 0.06 | 478.87 | 0.43 | 35.92 | 0.01 | 114.65 | 0.01 | 76316 | 56 | 37701 | 36 | [26 empty] | 53.35 | 0.05 | 53.41 | 0.04 | 53.52 | 0.05 | 53.98 | 0.06 | 53.91 | 0.05 | 53.95 | 0.05 | [18 empty] | 88 | 0.06 | [12 empty] | 89.65 | 0.06 | 88.24 | 0.06 | [20 empty] | 88.24 | 0.06 | 87.68 | 0.06 | 89.65 | 0.06 | 88.24 | 0.06 | 45.5 | 0.28 | 72.26 | 0.05 | [24 empty] | 81.7 | 0.08 | 81.6 | 0.05 | 74.91 | 0.08 | 75.18 | 0.07 | 74.91 | 0.07 | 75.08 | 0.06 | 74.58 | 0.08 | 74.57 | 0.08 |  |  | 77.8 | 0.09 | 76.04 | 0.1 | 75.07 | 0.1 | 74.83 | 0.09 | 78.75 | 0.13 | 76.76 | 0.09 | 75.33 | 0.1 | 75.07 | 0.11 | 77.95 | 0.11 | 75.61 | 0.08 | 76.37 | 0.07 | 75.08 | 0.08 | 76.94 | 0.13 | 75.51 | 0.11 | 75.97 | 0.08 | 72.29 | 0.1 | [30 empty] | 81.66 | 0.1 | 81.42 | 0.1 | 81.4 | 0.11 | 81.48 | 0.11 | 81.31 | 0.11 | 81.33 | 0.13 | [50 empty] | C8-55-CE3 | 74.997 | 0.024 | 62.009 | 0.022 | 53.889 | 0.014 | 51.284 | 0.016 | 81.996 | 0.024 | 67.992 | 0.02 | 2017.8 | 2 | 2000 | 2 | 1.552 | 0.002 | -0.616 | 0.003 | 0.554 | 0.003 | 0.757 | 0.0015 | 29.445 | 0 | 7534 | 31 | 1410 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5963 | 9309.6456 | 364.6589 | 27.3216 | 119.2348 | 9190.4108 | 0.0088199 | 27.6729 | 52.2927 | 13.7484 | 13.0046 | 0.011338 | 32.1218 | 0.0087873 | 27.6152 | 0.007394 | 20.9554 | 75.0871 | 62.0907 | 20.567 | 66153.4415 | 50929.8278 | 6124 | 0.31595 | 62585.6924 | 47362.0786 | 8.3071 | 0.15477 | -7.1059 | -22.7944 | 48.1188 | 66153.4415 | 62000.6084 | 3615.4927 | 537.3405 | 66153.4415 | 100%
3 | 3-6295CF | 75N0017 | 3-6295CF | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 0:58:49 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.1 | 28.4 | 0 | 41447 | 58 | 40647 | 165 | 7895 | 150 | 49350 | 158 | 5.7719 |  |  |  |  | 108.89 | 0.01 | 35.86 | [32 empty] | 66.7% Airflow, Both Stages, Closed Dampers. | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 53%: Horiz airflow disch config. set on floor: | 74.988 | 0.019 | 62.002 | 0.033 | 95.003 | 0.014 | 75.026 | 0.023 | 74.37 | 0.1 | 56.25 | 0.06 | 61.76 | 0.02 | 0.546 | 0.003 | 0.7618 | 0.0015 | 41447 | 58 | 7895 | 150 | 5.772 | 0.028 | 76935 | 158 | 8.998 | 0.04 | 35.86 | 0.28 | 230.5 | 0.8 | 230.3 | 0.8 | 229.5 | 0.8 | 28.4 | 0.1 | 25 | 0.1 | 28.4 | 0.1 | 6516.5 | 35.3 | 3519.7 | 40.4 | 2033.7 | 29.4 | 230 |  | 230 |  | 229 |  | 6.1 |  | 6.1 |  | 6.3 |  | 0.5 | 228 |  | 229 |  | 231 |  | 11.2 |  | 10.3 |  | 9.8 |  | 3350 |  | 0.81 | 230 | 231 | 229 | 10.7 | 9.7 | 10 | 3220 | 0.81 | [8 empty] | 8600 | [22 empty] | 265.44 | 0.19 | 170.78 | 0.08 | 121.48 | 0.05 | 49.29 | 0.08 | 247.04 | 0.2 | 101.9 | 0.04 | 116.2 | 0.06 | 14.3 | 0.05 | [8 empty] | 70.44 | 0.04 | 44.14 | 0.04 | 41.12 | 0.03 | 3.02 | 0.04 | 630.69 | 0.53 | 40.07 | 0.01 | 76935 | 158 | 43399 | 38 | [38 empty] | 253.96 | 0.22 | 207.34 | 0.04 | 118.22 | 0.06 | 89.12 | 0.05 | [6 empty] | 243.08 | 0.21 | 102.3 | 0.04 | 115.03 | 0.06 | 12.73 | 0.05 | [6 empty] | 63.49 | 0.05 | 77.67 | 0.04 | 36.25 | 0.04 | 41.42 | 0.07 | 101.73 | 0.05 | 521.86 | 0.46 | 40.2 | 0.01 | 115.21 | 0.01 | 76935 | 158 | 39145 | 34 | [26 empty] | 55.82 | 0.07 | 56.19 | 0.04 | 56.4 | 0.04 | 56.33 | 0.09 | 56.26 | 0.08 | 56.31 | 0.07 | [18 empty] | 101.9 | 0.04 | [12 empty] | 103.69 | 0.04 | 102.27 | 0.05 | [20 empty] | 102.11 | 0.05 | 101.73 | 0.05 | 103.69 | 0.04 | 102.27 | 0.05 | 45.45 | 0.05 | 77.76 | 0.04 | [24 empty] | 94.93 | 0.09 | 94.58 | 0.07 | 75.8 | 0.07 | 76.38 | 0.06 | 75.87 | 0.07 | 76.32 | 0.06 | 74.82 | 0.07 | 74.75 | 0.07 |  |  | 83.56 | 0.17 | 78.39 | 0.15 | 75.7 | 0.13 | 75.53 | 0.1 | 87.45 | 0.24 | 81.74 | 0.14 | 76.28 | 0.14 | 75.56 | 0.13 | 85.85 | 0.21 | 80.25 | 0.11 | 80.02 | 0.07 | 76.04 | 0.08 | 83.48 | 0.27 | 80.38 | 0.12 | 79.29 | 0.07 | 74.83 | 0.1 | [30 empty] | 94.99 | 0.1 | 94.66 | 0.09 | 94.66 | 0.1 | 94.79 | 0.1 | 94.64 | 0.1 | 94.62 | 0.14 | [50 empty] | C8-55-CE3 | 74.988 | 0.019 | 62.002 | 0.033 | 56.51 | 0.025 | 53.766 | 0.023 | 95.003 | 0.014 | 75.026 | 0.023 | 2029 | 2 | 2000 | 2 | 1.528 | 0.002 | -0.595 | 0.003 | 0.546 | 0.003 | 0.7618 | 0.0015 | 29.427 | 0.001 | 8550 | 31 | 1420 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.6202 | 9309.6682 | 359.0198 | 27.1931 | 115.714 | 9193.9542 | 0.0088489 | 27.7417 | 54.8898 | 14.1002 | 13.0767 | 0.013943 | 38.1822 | 0.0087848 | 27.6103 | 0.0081364 | 22.3993 | 75.2391 | 62.1888 | 22.0046 | 53410.2061 | 45466.8337 | 7130 | 0.45562 | 49789.0808 | 41845.7085 | 5.8233 | 0.15511 | -5.7371 | -20.3493 | 51.154 | 53410.2061 | 48512.3275 | 3674.5549 | 1223.3236 | 53410.2061 | 100%
3 | 3-2115 | 75N0019 | 3-2115. | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 23:16:31 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 32.6 | 0 | 41268 | 47 | 41817 | 173 | 808 | 122 | 42077 | 119 | 3.9789 |  |  |  |  | 109.31 | 0.01 | 45.13 | [32 empty] | 83.3% Airflow Both Stages, Economizer, Closed Damper | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.004 | 0.009 | 61.999 | 0.022 | 115.004 | 0.027 | 80.015 | 0.022 | 74.85 | 0.07 | 59.83 | 0.03 | 63.87 | 0.02 | 0.063 | 0.002 | 0.9167 | 0.0017 | 41268 | 47 | 808 | 122 | 3.979 | 0.016 | 76687 | 72 | 7.251 | 0.022 | 45.13 | 0.15 | 230.2 | 0.7 | 229.7 | 0.7 | 229.7 | 0.7 | 32.6 | 0.1 | 29.8 | 0.1 | 33.1 | 0.1 | 7502.8 | 35.6 | 3785.2 | 38.1 | 3072.7 | 29.7 | 228 |  | 229 |  | 229 |  | 6.5 |  | 6.3 |  | 6.2 |  | 0.54 | 228 |  | 229 |  | 229 |  | 13.2 |  | 12.5 |  | 12 |  | 4270 |  | 0.86 | 229 | 227 | 229 | 12.7 | 11.6 | 12.2 | 4170 | 0.86 | [8 empty] | 10630 | [22 empty] | 342.69 | 0.4 | 189.96 | 0.08 | 141.17 | 0.09 | 48.79 | 0.08 | 324.19 | 0.39 | 124.3 | 0.1 | 136.76 | 0.1 | 12.46 | 0.04 | [8 empty] | 78.14 | 0.05 | 49.14 | 0.04 | 46.11 | 0.03 | 3.04 | 0.03 | 685.99 | 0.65 | 47.36 | 0.04 | 76687 | 72 | 42500 | 39 | [38 empty] | 330.78 | 0.45 | 234.55 | 0.08 | 138.35 | 0.11 | 96.2 | 0.06 | [6 empty] | 318.63 | 0.43 | 124.88 | 0.07 | 135.4 | 0.11 | 10.52 | 0.08 | [6 empty] | 75.33 | 0.08 | 82.85 | 0.03 | 44.3 | 0.05 | 38.55 | 0.06 | 124.78 | 0.1 | 580.57 | 0.66 | 47.55 | 0.02 | 115.55 | 0.01 | 76687 | 72 | 39476 | 44 | [26 empty] | 59.27 | 0.03 | 59.79 | 0.03 | 60.42 | 0.03 | 60.03 | 0.02 | 59.98 | 0.03 | 60.06 | 0.02 | [18 empty] | 124.3 | 0.1 | [12 empty] | 125.07 | 0.09 | 124.88 | 0.1 | [20 empty] | 124.42 | 0.1 | 124.78 | 0.1 |  |  |  |  | 51.7 | 0.04 | 82.85 | 0.03 | [24 empty] | 115.01 | 0.15 | 115.76 | 0.11 | 75.18 | 0.05 | 75.33 | 0.05 | 74.97 | 0.05 | 74.87 | 0.06 | 75.01 | 0.05 | 75.06 | 0.06 |  |  | 77.15 | 0.09 | 75.54 | 0.06 | 75.61 | 0.06 | 75.95 | 0.06 | 107.25 | 0.17 | 77.95 | 0.11 | 75.43 | 0.05 | 75.47 | 0.05 | 92.28 | 0.17 | 83.99 | 0.16 | 77.76 | 0.1 | 77.24 | 0.08 | 92.07 | 0.25 | 85.16 | 0.18 | 80.85 | 0.09 | 79.64 | 0.09 | [30 empty] | 114.32 | 0.14 | 113.85 | 0.12 | 114.18 | 0.14 | 114.33 | 0.14 | 114.43 | 0.14 | 114.42 | 0.16 | [50 empty] | C8-55-CE3 | 75.004 | 0.009 | 61.999 | 0.022 | 60.187 | 0.013 | 56.535 | 0.013 | 115.004 | 0.027 | 80.015 | 0.022 | 2572.5 | 2.4 | 2501.4 | 2.3 | 1.207 | 0.002 | -0.524 | 0.003 | 0.063 | 0.002 | 0.9167 | 0.0017 | 29.22 | 0.001 | 10575 | 33 | 1580 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.487 | 11714.8474 | 354.6954 | 25.9739 | 106.6894 | 11608.1579 | 0.0088246 | 27.7474 | 58.7 | 14.6072 | 13.1756 | 0.013781 | 42.926 | 0.008779 | 27.6079 | 0.0088653 | 24.0878 | 75.3716 | 62.1994 | 23.7251 | 47120.1889 | 46873.1326 | 8995 | 0.65152 | 42938.2242 | 42691.1679 | 4.0604 | 0.22365 | -4.0223 | -16.6716 | 53.8973 | 47120.1889 | 41236.5974 | 4249.3066 | 1634.2849 | 47120.1889 | 100%
3 | 3-21151 | 75N0020 | 3-21151 | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/25/2013 | 0:41:27 | 10 Ton | 0:30:00 | 76/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 76 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.2 | 32.7 | 0 | 36202 | 49 | 36612 | 137 | -4537 | 134 | 31660 | 145 | 2.9826 |  |  |  |  | 109.48 | 0.01 | 59.32 | [32 empty] | 83.3% Airflow Both Stages 1 Finger (0.74") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.003 | 0.01 | 62.001 | 0.024 | 114.995 | 0.022 | 80.022 | 0.022 | 74.79 | 0.05 | 61.6 | 0.02 | 65.23 | 0.01 | 0.092 | 0.002 | 0.9226 | 0.0019 | 36202 | 49 | -4537 | 134 | 2.983 | 0.017 | 77825 | 75 | 7.332 | 0.022 | 59.32 | 0.19 | 230.3 | 0.8 | 229.7 | 0.8 | 229.7 | 0.8 | 32.7 | 0.1 | 29.9 | 0.1 | 33.1 | 0.1 | 7528 | 37.2 | 3783.3 | 41.7 | 3087.2 | 31.9 | 230 |  | 228 |  | 229 |  | 6.4 |  | 6.2 |  | 6.2 |  | 0.53 | 229 |  | 229 |  | 229 |  | 13.3 |  | 12.5 |  | 12.1 |  | 4310 |  | 0.86 | 230 | 228 | 228 | 12.7 | 11.6 | 12.2 | 4180 | 0.87 | [8 empty] | 10620 | [22 empty] | 346.54 | 0.37 | 197.09 | 0.06 | 142.07 | 0.09 | 55.02 | 0.09 | 327.49 | 0.35 | 124.07 | 0.09 | 137.56 | 0.09 | 13.5 | 0.04 | [8 empty] | 81.33 | 0.05 | 51.15 | 0.03 | 48.12 | 0.03 | 3.03 | 0.02 | 697.84 | 0.67 | 47.28 | 0.03 | 77825 | 75 | 43405 | 41 | [38 empty] | 330.66 | 0.39 | 235.48 | 0.06 | 138.32 | 0.09 | 97.16 | 0.06 | [6 empty] | 318.51 | 0.38 | 124.79 | 0.06 | 135.37 | 0.1 | 10.58 | 0.07 | [6 empty] | 75.72 | 0.08 | 84.51 | 0.03 | 44.56 | 0.05 | 39.95 | 0.05 | 124.6 | 0.1 | 581.39 | 0.6 | 47.52 | 0.02 | 115.82 | 0.01 | 77825 | 75 | 39710 | 42 | [26 empty] | 61.12 | 0.03 | 61.73 | 0.02 | 62.19 | 0.03 | 61.72 | 0.03 | 61.71 | 0.02 | 61.82 | 0.03 | [18 empty] | 124.07 | 0.09 | [12 empty] | 124.9 | 0.08 | 124.68 | 0.1 | [20 empty] | 124.19 | 0.09 | 124.6 | 0.1 |  |  |  |  | 53.88 | 0.07 | 84.49 | 0.03 | [24 empty] | 114.93 | 0.12 | 115.63 | 0.11 | 75.24 | 0.04 | 75.55 | 0.04 | 75.28 | 0.05 | 74.83 | 0.04 | 74.99 | 0.04 | 75.08 | 0.04 |  |  | 77.98 | 0.12 | 75.98 | 0.05 | 75.65 | 0.05 | 75.72 | 0.05 | 91.46 | 0.12 | 80.86 | 0.18 | 76.08 | 0.07 | 75.91 | 0.06 | 94.49 | 0.18 | 91.2 | 0.11 | 90.05 | 0.16 | 90.58 | 0.16 | 90.88 | 0.11 | 89.67 | 0.13 | 89.5 | 0.12 | 90.01 | 0.12 | [30 empty] | 115.03 | 0.2 | 114.56 | 0.19 | 114.85 | 0.18 | 114.93 | 0.13 | 115.18 | 0.14 | 115.24 | 0.21 | [50 empty] | C8-55-1FE3 | 75.003 | 0.01 | 62.001 | 0.024 | 61.959 | 0.011 | 57.943 | 0.016 | 114.995 | 0.022 | 80.022 | 0.022 | 2584.5 | 2.7 | 2504.5 | 2.6 | 1.153 | 0.002 | -0.436 | 0.003 | 0.092 | 0.002 | 0.9226 | 0.0019 | 29.215 | 0.001 | 10615 | 32 | 1520 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4315 | 11726.5369 | 339.2466 | 264.1352 | 1084.9618 | 10641.5751 | 0.009244 | 29.0272 | 60.5275 | 14.6071 | 13.2239 | 0.01379 | 42.9338 | 0.0087806 | 27.6093 | 0.0092926 | 24.9853 | 78.7337 | 63.9994 | 24.6358 | 51495.2572 | 51239.0089 | 9095 | 0.6028 | 47465.3457 | 47209.0974 | 4.4715 | 0.2275 | -4.3913 | -18.2062 | 55.1658 | 51495.2572 | 30770.8076 | 4097.9902 | 16626.4595 | 51495.2572 | 100%
3 | 3-21152 | 75N0021 | 3-21152. | 2 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/25/2013 | 2:12:45 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 32.6 | 0 | 33028 | 52 | 33341 | 126 | -7288 | 85 | 25733 | 107 | 2.421 |  |  |  |  | 109.59 | 0.01 | 67.18 | [32 empty] | 83.3% Airflow Both Stages 2 Fingers (1.289") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.999 | 0.011 | 62.002 | 0.017 | 115.003 | 0.023 | 79.64 | 0.009 | 74.76 | 0.04 | 62.73 | 0.02 | 66.07 | 0.02 | 0.117 | 0.002 | 0.9274 | 0.0019 | 33028 | 52 | -7288 | 85 | 2.421 | 0.013 | 78393 | 66 | 7.376 | 0.021 | 67.18 | 0.14 | 230.2 | 0.9 | 229.5 | 0.9 | 229.7 | 0.9 | 32.6 | 0.1 | 30 | 0.1 | 33.2 | 0.1 | 7503 | 36.6 | 3806.2 | 45.1 | 3126.1 | 31.3 | 229 |  | 228 |  | 229 |  | 6.3 |  | 6.2 |  | 6.1 |  | 0.53 | 229 |  | 228 |  | 228 |  | 13.3 |  | 12.5 |  | 12.2 |  | 4320 |  | 0.86 | 229 | 228 | 228 | 12.7 | 11.6 | 12.2 | 4170 | 0.87 | [8 empty] | 10650 | [22 empty] | 348.23 | 0.38 | 200.53 | 0.07 | 142.46 | 0.09 | 58.08 | 0.08 | 328.93 | 0.37 | 123.94 | 0.1 | 137.9 | 0.09 | 13.97 | 0.04 | [8 empty] | 82.99 | 0.06 | 52.32 | 0.04 | 49.13 | 0.04 | 3.18 | 0.03 | 703.11 | 0.59 | 47.24 | 0.03 | 78393 | 66 | 43842 | 32 | [38 empty] | 330.54 | 0.4 | 236.25 | 0.07 | 138.29 | 0.1 | 97.96 | 0.08 | [6 empty] | 318.36 | 0.4 | 124.8 | 0.07 | 135.33 | 0.1 | 10.53 | 0.08 | [6 empty] | 75.94 | 0.08 | 85.81 | 0.03 | 44.7 | 0.05 | 41.11 | 0.06 | 124.53 | 0.1 | 581.46 | 0.62 | 47.52 | 0.02 | 116.04 | 0.01 | 78393 | 66 | 39842 | 43 | [26 empty] | 62.25 | 0.03 | 63.01 | 0.03 | 63.36 | 0.03 | 62.72 | 0.03 | 62.73 | 0.03 | 62.88 | 0.03 | [18 empty] | 123.94 | 0.1 | [12 empty] | 124.79 | 0.08 | 124.61 | 0.1 | [20 empty] | 124.07 | 0.09 | 124.53 | 0.1 |  |  |  |  | 55.31 | 0.06 | 85.72 | 0.04 | [24 empty] | 114.84 | 0.13 | 115.61 | 0.1 | 75.25 | 0.04 | 75.59 | 0.04 | 75.37 | 0.05 | 74.79 | 0.03 | 74.96 | 0.03 | 75.06 | 0.03 |  |  | 78.27 | 0.13 | 76.12 | 0.06 | 75.66 | 0.05 | 75.66 | 0.04 | 88.98 | 0.16 | 92.64 | 0.23 | 81.34 | 0.19 | 77.74 | 0.12 | 93.58 | 0.13 | 93.31 | 0.1 | 94.93 | 0.13 | 94.9 | 0.16 | 91.28 | 0.1 | 90.69 | 0.11 | 93.45 | 0.11 | 93.91 | 0.11 | [30 empty] | 114.02 | 0.14 | 113.52 | 0.12 | 113.9 | 0.13 | 114.1 | 0.13 | 114.33 | 0.13 | 114.29 | 0.16 | [50 empty] | C8-55-2FE3 | 74.999 | 0.011 | 62.002 | 0.017 | 63.078 | 0.016 | 58.73 | 0.02 | 115.003 | 0.023 | 79.64 | 0.009 | 2593.6 | 2.7 | 2508.1 | 2.6 | 1.128 | 0.002 | -0.382 | 0.003 | 0.117 | 0.002 | 0.9274 | 0.0019 | 29.209 | 0.001 | 10629 | 31 | 1550 |  | 0.1172 | 290.407 | 13.03 | 0.325 | 1.4744 | 11741.1117 | 332.3679 | 333.3205 | 1369.4278 | 10371.6839 | 0.0093227 | 29.3492 | 61.6036 | 14.6041 | 13.2539 | 0.013417 | 42.5208 | 0.0087822 | 27.6101 | 0.0095114 | 25.4967 | 79.6996 | 64.4442 | 25.1367 | 49459.9382 | 50992.0615 | 9079 | 0.6265 | 45304.1598 | 46836.2831 | 4.2623 | 0.23896 | -4.2125 | -18.096 | 55.9217 | 49459.9382 | 24813.1809 | 4227.6651 | 20419.0922 | 49459.9382 | 100%
3 | 3-21153 | 75N0022 | 3-21153 | 3 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/25/2013 | 3:36:45 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.1 | 32.7 | 0 | 28604 | 56 | 28715 | 122 | -11841 | 88 | 16752 | 117 | 1.5731 |  |  |  |  | 109.87 | 0.01 | 78.86 | [32 empty] | 83.3% Airflow Both Stages 3 Fingers (1.972") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75 | 0.007 | 61.993 | 0.013 | 114.997 | 0.055 | 79.954 | 0.018 | 74.66 | 0.04 | 64.26 | 0.03 | 67.29 | 0.02 | 0.152 | 0.002 | 0.9343 | 0.0019 | 28604 | 56 | -11841 | 88 | 1.573 | 0.013 | 79260 | 70 | 7.443 | 0.023 | 78.86 | 0.15 | 230.3 | 0.8 | 229.6 | 0.8 | 229.7 | 0.8 | 32.7 | 0.1 | 30 | 0.1 | 33.2 | 0.1 | 7518.9 | 34.2 | 3798.9 | 40.6 | 3130.1 | 30.3 | 229 |  | 228 |  | 228 |  | 6.4 |  | 6.3 |  | 6.1 |  | 0.57 | 228 |  | 228 |  | 229 |  | 13.3 |  | 12.6 |  | 12.2 |  | 4350 |  | 0.86 | 229 | 228 | 227 | 12.6 | 11.6 | 12.2 | 4160 | 0.86 | [8 empty] | 10690 | [22 empty] | 350.5 | 0.68 | 207.22 | 0.12 | 142.98 | 0.16 | 64.24 | 0.13 | 330.73 | 0.66 | 123.7 | 0.17 | 138.34 | 0.16 | 14.64 | 0.03 | [8 empty] | 85.98 | 0.09 | 54.83 | 0.06 | 50.94 | 0.05 | 3.89 | 0.07 | 710.16 | 0.75 | 47.15 | 0.06 | 79260 | 70 | 44537 | 34 | [38 empty] | 330.27 | 0.66 | 237.04 | 0.13 | 138.23 | 0.16 | 98.81 | 0.1 | [6 empty] | 318.09 | 0.65 | 124.68 | 0.12 | 135.27 | 0.16 | 10.58 | 0.1 | [6 empty] | 76.2 | 0.12 | 87.16 | 0.06 | 44.86 | 0.07 | 42.3 | 0.08 | 124.37 | 0.15 | 581.7 | 0.74 | 47.48 | 0.04 | 116.27 | 0.01 | 79260 | 70 | 40013 | 48 | [26 empty] | 63.83 | 0.05 | 64.69 | 0.04 | 64.93 | 0.05 | 64.11 | 0.04 | 64.15 | 0.04 | 64.35 | 0.03 | [18 empty] | 123.7 | 0.17 | [12 empty] | 124.61 | 0.16 | 124.43 | 0.17 | [20 empty] | 123.84 | 0.17 | 124.37 | 0.15 |  |  |  |  | 57.15 | 0.09 | 87.09 | 0.05 | [24 empty] | 114.76 | 0.19 | 115.5 | 0.16 | 75.2 | 0.04 | 75.58 | 0.04 | 75.32 | 0.05 | 74.72 | 0.03 | 74.89 | 0.04 | 74.99 | 0.04 |  |  | 79.11 | 0.11 | 76.67 | 0.07 | 75.72 | 0.06 | 75.75 | 0.05 | 85.96 | 0.16 | 87.45 | 0.26 | 84.8 | 0.27 | 80.61 | 0.21 | 98.51 | 0.15 | 97.57 | 0.13 | 99.62 | 0.18 | 100.91 | 0.19 | 96.38 | 0.12 | 96.05 | 0.14 | 98.12 | 0.15 | 98.74 | 0.16 | [30 empty] | 113.93 | 0.19 | 113.38 | 0.17 | 113.66 | 0.18 | 113.89 | 0.18 | 114.26 | 0.18 | 114.27 | 0.22 | [50 empty] | C8-55-3FE3 | 75 | 0.007 | 61.993 | 0.013 | 64.634 | 0.018 | 59.881 | 0.016 | 114.997 | 0.055 | 79.954 | 0.018 | 2606.6 | 2.7 | 2513.4 | 2.6 | 1.105 | 0.002 | -0.321 | 0.003 | 0.152 | 0.002 | 0.9343 | 0.0019 | 29.208 | 0.001 | 10649 | 33 | 1570 |  | 0.17753 | 447.8183 | 13.029 | 0.274 | 1.5032 | 11762.4823 | 326.2789 | 513.2126 | 2108.1473 | 9654.335 | 0.0096626 | 30.3379 | 63.1308 | 14.6065 | 13.2962 | 0.013723 | 42.86 | 0.008776 | 27.6036 | 0.0098643 | 26.2613 | 82.2214 | 65.7756 | 25.8939 | 52272.2919 | 53892.7855 | 9079 | 0.59279 | 48027.4718 | 49647.9654 | 4.51 | 0.24536 | -4.444 | -19.0906 | 56.9239 | 52272.2919 | 15788.5805 | 4321.0175 | 32162.6938 | 52272.2919 | 100%
3 | 3-2115OD | 75N0023 | 3-2115OD | open | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/25/2013 | 5:40:05 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.2 | 32.6 | 0 | 9888 | 130 | 9404 | 189 | -26214 | 212 | -16350 | 303 | -1.5416 |  |  |  |  | 115.3 | 0.03 | -119.22 | [32 empty] | 83.3% airflow both stages economizer fully open (5.047") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.736 | 0.009 | 62.231 | 0.02 | 114.947 | 0.038 | 79.78 | 0.047 | 74.19 | 0.03 | 70.44 | 0.05 | 72 | 0.03 | 0.09 | 0.003 | 0.8974 | 0.002 | 9888 | 130 | -26214 | 212 | -1.5393 | 0 | 85066 | 77 | 8.0206 | 0 |  |  | 230.3 | 0.8 | 229.6 | 0.8 | 229.7 | 0.8 | 32.6 | 0.1 | 29.8 | 0.1 | 33.1 | 0.1 | 7492.3 | 35.2 | 3785.5 | 40.4 | 3113 | 30.7 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.1 |  | 0.54 | 230 |  | 230 |  | 230 |  | 13.3 |  | 12.7 |  | 12.4 |  | 4390 |  | 0.87 | 230 | 230 | 230 | 12.5 | 11.5 | 12 | 4130 | 0.87 | [8 empty] | 10650 | [22 empty] | 355.55 | 0.39 | 224.22 | 0.09 | 144.13 | 0.09 | 80.09 | 0.1 | 334.6 | 0.38 | 122.54 | 0.1 | 139.26 | 0.09 | 16.72 | 0.04 | [8 empty] | 94.51 | 0.1 | 86.78 | 0.16 | 55.89 | 0.05 | 30.89 | 0.16 | 730.69 | 0.58 | 46.77 | 0.03 | 85066 | 77 | 50077 | 49 | [38 empty] | 325.92 | 0.49 | 237.92 | 0.08 | 137.18 | 0.12 | 100.74 | 0.08 | [6 empty] | 313.6 | 0.47 | 123.88 | 0.08 | 134.15 | 0.12 | 10.28 | 0.08 | [6 empty] | 76.17 | 0.11 | 90.19 | 0.08 | 44.84 | 0.07 | 45.35 | 0.1 | 123.25 | 0.11 | 578.74 | 0.75 | 47.21 | 0.03 | 116.81 | 0.02 | 85066 | 77 | 40279 | 54 | [26 empty] | 70.31 | 0.07 | 70.82 | 0.07 | 70.67 | 0.09 | 70.19 | 0.09 | 70.26 | 0.09 | 70.52 | 0.1 | [18 empty] | 122.54 | 0.1 | [12 empty] | 123.61 | 0.09 | 123.27 | 0.11 | [20 empty] | 122.63 | 0.1 | 123.25 | 0.11 |  |  |  |  | 88.55 | 0.14 | 90 | 0.08 | [24 empty] | 114.74 | 0.15 | 114.31 | 0.12 | 74.29 | 0.04 | 74.4 | 0.04 | 74.03 | 0.05 | 74.1 | 0.05 | 74.19 | 0.05 | 74.22 | 0.05 |  |  | 75.22 | 0.06 | 76.92 | 0.09 | 82.78 | 0.12 | 85.07 | 0.22 | 89.05 | 0.28 | 95.78 | 0.34 | 102.22 | 0.38 | 89.26 | 0.28 | 101.98 | 0.16 | 102.14 | 0.12 | 107.05 | 0.28 | 111.9 | 0.21 | 104.76 | 0.18 | 104.29 | 0.24 | 103.7 | 0.23 | 106.99 | 0.19 | [30 empty] | 106.32 | 0.68 | 105.68 | 0.59 | 110.58 | 0.47 | 110.98 | 0.4 | 114 | 0.2 | 114.15 | 0.27 | [50 empty] | C8-55-OE3 | 74.736 | 0.009 | 62.231 | 0.02 | 70.799 | 0.039 | 64.212 | 0.048 | 114.947 | 0.038 | 79.78 | 0.047 | 2566.7 | 2.9 | 2446.9 | 2.8 | 0.813 | 0.002 | -0.113 | 0.006 | 0.09 | 0.003 | 0.8974 | 0.002 | 29.207 | 0.001 | 10606 | 31 | 1520 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.5987 | 11438.2775 | 233.7071 | 1080.3809 | 4438.7265 | 6999.551 | 0.010769 | 33.559 | 69.2003 | 14.6039 | 13.4637 | 0.013566 | 42.6727 | 0.0089957 | 27.7796 | 0.011275 | 29.3087 | 90.4194 | 69.8659 | 28.917 | 53096.6162 | 58250.467 | 9086 | 0.58404 | 48706.4985 | 53860.3493 | 4.5924 | 0.28025 | -4.642 | -21.2191 | 60.9382 | 53096.6162 | -17489.9998 | 4480.3751 | 66106.2409 | 53096.6162 | 100%
3 | 3-2951 | 75N0024 | 3-2951. | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 2:50:03 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.1 | 28.3 | 0 | 43831 | 48 | 44113 | 230 | 2696 | 77 | 46529 | 82 | 5.2892 |  |  |  |  | 109.47 | 0.02 | 41.78 | [32 empty] | 83.3% airflow both stages 1 finger (0.74") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.995 | 0.021 | 62.015 | 0.022 | 95 | 0.015 | 75.043 | 0.016 | 74.77 | 0.1 | 59.04 | 0.04 | 63.34 | 0.02 | 0.092 | 0.002 | 0.925 | 0.0018 | 43831 | 48 | 2696 | 77 | 5.289 | 0.02 | 79915 | 66 | 9.084 | 0.03 | 41.78 | 0.11 | 230.2 | 0.7 | 229.5 | 0.7 | 229.8 | 0.7 | 28.3 | 0.1 | 26 | 0.1 | 29 | 0.1 | 6491.6 | 32 | 3668.3 | 37.7 | 2305.3 | 28.2 | 229 |  | 228 |  | 228 |  | 6.3 |  | 6.4 |  | 6.1 |  | 0.55 | 229 |  | 229 |  | 229 |  | 11 |  | 10.5 |  | 10.1 |  | 3410 |  | 0.82 | 228 | 229 | 228 | 10.5 | 9.6 | 10.1 | 3250 | 0.82 | [8 empty] | 8870 | [22 empty] | 272.48 | 0.22 | 181.92 | 0.07 | 123.4 | 0.06 | 58.52 | 0.09 | 253.13 | 0.21 | 102.01 | 0.06 | 117.95 | 0.06 | 15.94 | 0.04 | [8 empty] | 75.38 | 0.05 | 49.03 | 0.12 | 44.33 | 0.03 | 4.7 | 0.13 | 649.65 | 0.59 | 40.11 | 0.02 | 79915 | 66 | 45058 | 40 | [38 empty] | 255.86 | 0.23 | 206.31 | 0.04 | 118.73 | 0.07 | 87.58 | 0.06 | [6 empty] | 244.24 | 0.22 | 103.1 | 0.04 | 115.34 | 0.06 | 12.24 | 0.06 | [6 empty] | 65.72 | 0.06 | 78.45 | 0.04 | 37.78 | 0.04 | 40.67 | 0.05 | 102.35 | 0.06 | 536.35 | 0.51 | 40.46 | 0.01 | 115.24 | 0.01 | 79915 | 66 | 40115 | 39 | [26 empty] | 58.72 | 0.06 | 58.99 | 0.04 | 59.19 | 0.07 | 59.25 | 0.05 | 59.23 | 0.05 | 59.31 | 0.05 | [18 empty] | 102.01 | 0.06 | [12 empty] | 102.87 | 0.05 | 102.35 | 0.06 | [20 empty] | 102.19 | 0.06 | 102.35 | 0.06 |  |  |  |  | 51.08 | 0.23 | 78.3 | 0.04 | [24 empty] | 94.64 | 0.11 | 95.26 | 0.08 | 75.11 | 0.07 | 75.28 | 0.07 | 75.12 | 0.06 | 74.87 | 0.07 | 74.97 | 0.07 | 75.01 | 0.08 |  |  | 76.56 | 0.09 | 75.56 | 0.08 | 75.41 | 0.07 | 75.39 | 0.08 | 85.87 | 0.06 | 77.98 | 0.11 | 76.44 | 0.1 | 76.76 | 0.11 | 83.37 | 0.09 | 83.71 | 0.07 | 83.13 | 0.08 | 83.16 | 0.07 | 82.54 | 0.07 | 81.82 | 0.08 | 82.71 | 0.07 | 82.56 | 0.06 | [30 empty] | 94.85 | 0.12 | 94.56 | 0.11 | 94.75 | 0.11 | 94.82 | 0.1 | 94.87 | 0.09 | 94.93 | 0.14 | [50 empty] | C8-55-1FE3 | 74.995 | 0.021 | 62.015 | 0.022 | 59.359 | 0.018 | 55.971 | 0.019 | 95 | 0.015 | 75.043 | 0.016 | 2583.3 | 2.5 | 2514 | 2.4 | 1.144 | 0.003 | -0.427 | 0.003 | 0.092 | 0.002 | 0.925 | 0.0018 | 29.206 | 0 | 8797 | 29 | 1600 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.5227 | 11783.7534 | 337.8753 | 256.8198 | 1092.8327 | 10690.9207 | 0.0092709 | 28.6007 | 57.8363 | 14.1002 | 13.1535 | 0.013958 | 38.1987 | 0.0087917 | 27.6195 | 0.0087285 | 23.7372 | 76.8661 | 63.392 | 23.3658 | 61685.9945 | 53818.1966 | 7197 | 0.3982 | 57378.3628 | 49510.5649 | 6.5225 | 0.20192 | -5.2348 | -19.0298 | 53.0215 | 61685.9945 | 45748.8088 | 4375.9079 | 11561.2778 | 61685.9945 | 100%
3 | 3-2952 | 75N0025 | 3-2952. | 2 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 1:49:40 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.1 | 28.4 | 0 | 41416 | 66 | 41791 | 164 | -583 | 136 | 40832 | 142 | 4.6337 |  |  |  |  | 109.85 | 0.06 | 49.31 | [32 empty] | 83.3% airflow both stages 2 fingers (1.289") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.003 | 0.011 | 61.999 | 0.017 | 95.005 | 0.013 | 75.033 | 0.02 | 74.76 | 0.06 | 59.88 | 0.03 | 64.01 | 0.03 | 0.128 | 0.003 | 0.9339 | 0.0018 | 41416 | 66 | -583 | 136 | 4.634 | 0.023 | 80543 | 77 | 9.14 | 0.031 | 49.31 | 0.18 | 230.3 | 0.7 | 229.5 | 0.7 | 229.7 | 0.7 | 28.4 | 0.1 | 26 | 0.1 | 29 | 0.1 | 6509.9 | 32.4 | 3659.1 | 40 | 2301.8 | 27.2 | 231 |  | 230 |  | 227 |  | 6.3 |  | 6.4 |  | 6.1 |  | 0.55 | 229 |  | 229 |  | 228 |  | 11.1 |  | 10.5 |  | 10.1 |  | 3420 |  | 0.82 | 229 | 229 | 228 | 10.5 | 9.6 | 10.1 | 3250 | 0.81 | [8 empty] | 8870 | [22 empty] | 273.59 | 0.27 | 183.84 | 0.08 | 123.71 | 0.08 | 60.13 | 0.08 | 254.09 | 0.27 | 101.93 | 0.07 | 118.22 | 0.08 | 16.29 | 0.03 | [8 empty] | 76.43 | 0.06 | 51.51 | 0.33 | 45.01 | 0.04 | 6.5 | 0.35 | 653.27 | 0.63 | 40.09 | 0.02 | 80543 | 77 | 45578 | 56 | [38 empty] | 255.97 | 0.27 | 206.89 | 0.05 | 118.76 | 0.08 | 88.13 | 0.06 | [6 empty] | 244.35 | 0.27 | 103.09 | 0.05 | 115.37 | 0.08 | 12.29 | 0.07 | [6 empty] | 65.92 | 0.06 | 79.28 | 0.04 | 37.92 | 0.04 | 41.36 | 0.06 | 102.32 | 0.07 | 536.8 | 0.52 | 40.45 | 0.02 | 115.38 | 0.01 | 80543 | 77 | 40222 | 40 | [26 empty] | 59.51 | 0.03 | 60.02 | 0.03 | 60.23 | 0.03 | 59.93 | 0.03 | 59.93 | 0.03 | 60.06 | 0.02 | [18 empty] | 101.93 | 0.07 | [12 empty] | 102.86 | 0.06 | 102.26 | 0.07 | [20 empty] | 102.12 | 0.07 | 102.32 | 0.07 |  |  |  |  | 55.4 | 0.58 | 79.16 | 0.03 | [24 empty] | 94.57 | 0.1 | 95.22 | 0.1 | 75.13 | 0.04 | 75.36 | 0.04 | 75.1 | 0.04 | 74.84 | 0.04 | 74.97 | 0.04 | 75.04 | 0.04 |  |  | 76.48 | 0.07 | 75.53 | 0.05 | 75.44 | 0.06 | 75.45 | 0.05 | 81.55 | 0.08 | 84.22 | 0.14 | 78.8 | 0.13 | 76.7 | 0.08 | 83.72 | 0.1 | 84.2 | 0.08 | 85.21 | 0.11 | 85.4 | 0.11 | 82.7 | 0.08 | 82.45 | 0.08 | 84.48 | 0.09 | 84.75 | 0.1 | [30 empty] | 93.65 | 0.19 | 93.19 | 0.18 | 93.59 | 0.16 | 93.72 | 0.19 | 94.01 | 0.15 | 94.05 | 0.16 | [50 empty] | C8-55-2FE3 | 75.003 | 0.011 | 61.999 | 0.017 | 60.248 | 0.014 | 56.75 | 0.017 | 95.005 | 0.013 | 75.033 | 0.02 | 2597.7 | 2.5 | 2523.5 | 2.5 | 1.132 | 0.002 | -0.371 | 0.004 | 0.128 | 0.003 | 0.9339 | 0.0018 | 29.201 | 0 | 8812 | 29 | 1590 |  | 0.1172 | 290.407 | 13.03 | 0.325 | 1.5078 | 11827.421 | 335.5945 | 322.7706 | 1373.4655 | 10453.9555 | 0.0093795 | 28.8366 | 58.7402 | 14.1003 | 13.178 | 0.013949 | 38.189 | 0.0087793 | 27.6079 | 0.0089786 | 24.226 | 77.345 | 63.7178 | 23.8581 | 58882.7766 | 52811.3686 | 7222 | 0.41861 | 54601.4906 | 48530.0826 | 6.1963 | 0.20696 | -4.9785 | -18.6048 | 53.8849 | 58882.7766 | 39998.9027 | 4351.1246 | 14532.7492 | 58882.7766 | 100%
3 | 384662 | 75N0026 | 3-2953. | 3 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 0:13:35 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 0.2 | 28.6 | 0 | 39808 | 64 | 40176 | 178 | -2864 | 97 | 36941 | 98 | 4.1878 |  |  |  |  | 111.96 | 0.05 | 55.04 | [32 empty] | 83.3% Airflow both Stages 3 Fingers (1.972') | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.004 | 0.012 | 62.019 | 0.016 | 95.004 | 0.012 | 75.034 | 0.015 | 74.78 | 0.07 | 60.49 | 0.03 | 64.44 | 0.02 | 0.161 | 0.003 | 0.942 | 0.0022 | 39808 | 64 | -2864 | 97 | 4.188 | 0.018 | 82154 | 77 | 9.313 | 0.032 | 55.04 | 0.12 | 230.4 | 0.8 | 229.7 | 0.8 | 229.6 | 0.8 | 28.6 | 0.1 | 26 | 0.1 | 28.9 | 0.1 | 6558 | 34.9 | 3619.7 | 40.7 | 2263.4 | 30 | 228 |  | 229 |  | 227 |  | 6.4 |  | 6.4 |  | 6.1 |  | 0.54 | 227 |  | 229 |  | 228 |  | 11.1 |  | 10.5 |  | 10.1 |  | 3440 |  | 0.82 | 228 | 229 | 229 | 10.6 | 9.6 | 10.1 | 3260 | 0.81 | [8 empty] | 8900 | [22 empty] | 274.53 | 0.28 | 187.16 | 0.07 | 123.97 | 0.08 | 63.19 | 0.08 | 254.9 | 0.26 | 101.92 | 0.07 | 118.46 | 0.08 | 16.53 | 0.04 | [8 empty] | 77.65 | 0.06 | 63.54 | 0.3 | 45.79 | 0.04 | 17.74 | 0.31 | 655.53 | 0.59 | 40.08 | 0.02 | 82154 | 77 | 47120 | 55 | [38 empty] | 256.09 | 0.26 | 207.19 | 0.06 | 118.8 | 0.08 | 88.39 | 0.06 | [6 empty] | 244.46 | 0.27 | 103.08 | 0.05 | 115.41 | 0.08 | 12.32 | 0.07 | [6 empty] | 66.05 | 0.06 | 79.69 | 0.03 | 38 | 0.04 | 41.69 | 0.05 | 102.32 | 0.08 | 537.24 | 0.52 | 40.45 | 0.01 | 115.45 | 0.01 | 82154 | 77 | 40290 | 39 | [26 empty] | 60.11 | 0.04 | 60.68 | 0.03 | 60.84 | 0.03 | 60.46 | 0.04 | 60.47 | 0.03 | 60.62 | 0.03 | [18 empty] | 101.92 | 0.07 | [12 empty] | 102.87 | 0.06 | 102.26 | 0.08 | [20 empty] | 102.13 | 0.08 | 102.32 | 0.08 |  |  |  |  | 65.97 | 0.14 | 79.57 | 0.03 | [24 empty] | 94.54 | 0.12 | 95.24 | 0.1 | 75.1 | 0.04 | 75.35 | 0.05 | 75.14 | 0.06 | 74.86 | 0.06 | 74.98 | 0.05 | 75.03 | 0.06 |  |  | 76.98 | 0.11 | 75.82 | 0.09 | 75.5 | 0.07 | 75.47 | 0.06 | 80.56 | 0.11 | 80.91 | 0.15 | 79.32 | 0.17 | 77.3 | 0.11 | 85.77 | 0.1 | 85.91 | 0.09 | 87.08 | 0.09 | 87.83 | 0.11 | 84.55 | 0.06 | 84.44 | 0.07 | 86.16 | 0.09 | 86.64 | 0.09 | [30 empty] | 93.63 | 0.13 | 93.21 | 0.13 | 93.56 | 0.13 | 93.68 | 0.13 | 94.09 | 0.11 | 94.16 | 0.14 | [50 empty] | C8-55-3FE3 | 75.004 | 0.012 | 62.019 | 0.016 | 60.844 | 0.014 | 57.311 | 0.015 | 95.004 | 0.012 | 75.034 | 0.015 | 2610.4 | 3.1 | 2532.5 | 3 | 1.12 | 0.002 | -0.322 | 0.004 | 0.161 | 0.003 | 0.942 | 0.0022 | 29.192 | 0 | 8821 | 30 | 1590 |  | 0.17753 | 447.8183 | 13.029 | 0.274 | 1.5052 | 11870.2618 | 333.2212 | 505.0244 | 2149.0015 | 9721.2602 | 0.0097259 | 29.5355 | 59.3388 | 14.1003 | 13.1947 | 0.01395 | 38.1899 | 0.0087922 | 27.6223 | 0.0091736 | 24.5835 | 78.6526 | 64.6675 | 24.2162 | 63141.6204 | 55022.4114 | 7231 | 0.39086 | 58852.2342 | 50733.0252 | 6.6718 | 0.20519 | -5.3193 | -19.3138 | 54.3527 | 63141.6204 | 36070.8283 | 4360.9037 | 22709.8884 | 63141.6204 | 100%
3 | 3-295OD | 75N0027 | 3-295OD | open | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/23/2013 | 22:48:22 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 0.2 | 28.5 | 0 | 26615 | 60 | 26440 | 120 | -19807 | 208 | 6789 | 234 | 0.77253 |  |  |  |  | 114.55 | 0.02 | 92 | [32 empty] | 83.3% Airflow Both Stages Econo Fully Open (5.047) | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.002 | 0.006 | 62.052 | 0.013 | 95.006 | 0.019 | 75.062 | 0.015 | 74.57 | 0.04 | 64.72 | 0.04 | 67.71 | 0.02 | 0.09 | 0.004 | 0.903 | 0.0021 | 26615 | 60 | -19807 | 208 | 0.773 | 0.027 | 84841 | 70 | 9.654 | 0.032 | 92 | 0.28 | 230.4 | 0.8 | 229.7 | 0.8 | 229.6 | 0.8 | 28.5 | 0.1 | 25.9 | 0.1 | 28.9 | 0.1 | 6533.6 | 34.6 | 3620.7 | 41.1 | 2254.2 | 29.3 | 230 |  | 229 |  | 227 |  | 6.4 |  | 6.3 |  | 6.1 |  | 0.54 | 226 |  | 228 |  | 229 |  | 11.1 |  | 10.8 |  | 10.2 |  | 3450 |  | 0.82 | 230 | 228 | 226 | 10.5 | 9.6 | 10 | 3240 | 81 | [8 empty] | 8840 | [22 empty] | 276.78 | 0.34 | 197.4 | 0.07 | 124.58 | 0.09 | 72.82 | 0.07 | 256.54 | 0.32 | 101.37 | 0.07 | 118.93 | 0.09 | 17.56 | 0.04 | [8 empty] | 82.18 | 0.1 | 79.18 | 0.08 | 48.63 | 0.06 | 30.55 | 0.11 | 665.44 | 0.68 | 39.91 | 0.02 | 84841 | 70 | 49666 | 43 | [38 empty] | 255.32 | 0.27 | 207.91 | 0.08 | 118.58 | 0.08 | 89.33 | 0.08 | [6 empty] | 243.67 | 0.29 | 102.84 | 0.06 | 115.17 | 0.09 | 12.33 | 0.08 | [6 empty] | 66.21 | 0.06 | 81.22 | 0.05 | 38.11 | 0.04 | 43.1 | 0.07 | 102.06 | 0.07 | 536.7 | 0.52 | 40.37 | 0.02 | 115.71 | 0.01 | 84841 | 70 | 40430 | 40 | [26 empty] | 64.9 | 0.05 | 64.73 | 0.05 | 64.43 | 0.05 | 65.03 | 0.04 | 65.03 | 0.05 | 65.17 | 0.05 | [18 empty] | 101.37 | 0.07 | [12 empty] | 102.38 | 0.07 | 101.96 | 0.07 | [20 empty] | 101.57 | 0.08 | 102.06 | 0.07 |  |  |  |  | 80.46 | 0.07 | 81.06 | 0.05 | [24 empty] | 93.97 | 0.13 | 95.37 | 0.09 | 74.67 | 0.04 | 74.82 | 0.04 | 74.52 | 0.03 | 74.56 | 0.03 | 74.65 | 0.03 | 74.66 | 0.03 |  |  | 77.25 | 0.07 | 79.08 | 0.07 | 80.84 | 0.09 | 81.83 | 0.15 | 79.96 | 0.09 | 87.25 | 0.14 | 89.04 | 0.16 | 87.71 | 0.32 | 85.23 | 0.16 | 86.92 | 0.09 | 90.06 | 0.13 | 92.77 | 0.14 | 88.67 | 0.11 | 88.31 | 0.15 | 87.95 | 0.14 | 90.29 | 0.14 | [30 empty] | 89.58 | 0.17 | 88.85 | 0.16 | 91.41 | 0.2 | 91.4 | 0.18 | 93.45 | 0.12 | 93.37 | 0.19 | [50 empty] | C8-55-OE3 | 75.002 | 0.006 | 62.052 | 0.013 | 65.078 | 0.019 | 61.166 | 0.03 | 95.006 | 0.019 | 75.062 | 0.015 | 2564.9 | 3 | 2466.1 | 2.9 | 0.792 | 0.002 | -0.086 | 0.007 | 0.09 | 0.004 | 0.903 | 0.0021 | 29.186 | 0.001 | 8788 | 30 | 1540 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.6118 | 11559.5776 | 229.4568 | 926.1244 | 3940.8142 | 7618.7634 | 0.010573 | 31.2499 | 63.4662 | 14.1005 | 13.3131 | 0.013974 | 38.217 | 0.0088145 | 27.6462 | 0.010586 | 27.1561 | 81.8637 | 66.918 | 26.7617 | 51881.8834 | 51040.1394 | 7248 | 0.4768 | 47408.9995 | 46567.2555 | 5.3947 | 0.20612 | -4.4882 | -18.3975 | 58.6897 | 51881.8834 | 5664.969 | 4559.1431 | 41657.7712 | 51881.8834 | 100%
3 | 3-521151CF | 75N0028 | 3-521151CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 16:49:52 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.2 | 33 | 0 | 37417 | 64 | 36630 | 155 | -3825 | 71 | 33589 | 82 | 3.1604 |  |  |  |  | 109.59 | 0.01 | 57.32 | [32 empty] | 83% airflow, both stages, 1-finger (0.74") open | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor: | 74.999 | 0.019 | 62.018 | 0.016 | 115.004 | 0.014 | 80 | 0.033 | 74.4 | 0.06 | 61.18 | 0.03 | 64.85 | 0.02 | 0.267 | 0.004 | 1.2015 | 0.0028 | 37417 | 64 | -3825 | 71 | 3.16 | 0.012 | 78700 | 60 | 7.405 | 0.022 | 57.32 | 0.11 | 230.5 | 0.8 | 230 | 0.8 | 229.5 | 0.8 | 33 | 0.1 | 29.7 | 0.1 | 32.9 | 0.1 | 7607.2 | 35.1 | 3691.6 | 40.2 | 3021 | 30.3 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.1 |  | 0.53 | 230 |  | 230 |  | 230 |  | 13.5 |  | 12.5 |  | 12 |  | 4320 |  | 0.86 | 230 | 230 | 230 | 12.9 | 11.6 | 12.2 | 4200 | 0.87 | [8 empty] | 10630 | [22 empty] | 346.54 | 0.23 | 196.41 | 0.05 | 142.08 | 0.05 | 54.33 | 0.06 | 327.19 | 0.21 | 123.43 | 0.06 | 137.5 | 0.05 | 14.08 | 0.05 | [8 empty] | 82.49 | 0.04 | 52.18 | 0.03 | 48.87 | 0.03 | 3.31 | 0.03 | 702.16 | 0.49 | 47.06 | 0.02 | 78700 | 60 | 43905 | 33 | [38 empty] | 331.48 | 0.26 | 235.39 | 0.05 | 138.53 | 0.06 | 96.86 | 0.05 | [6 empty] | 319.95 | 0.26 | 123.58 | 0.05 | 135.74 | 0.06 | 12.16 | 0.06 | [6 empty] | 74.57 | 0.03 | 82.75 | 0.04 | 43.84 | 0.02 | 38.9 | 0.05 | 123.41 | 0.07 | 575.66 | 0.47 | 47.11 | 0.02 | 115.56 | 0.01 | 78700 | 60 | 39402 | 35 | [26 empty] | 61.11 | 0.05 | 61.29 | 0.04 | 61.64 | 0.05 | 61.43 | 0.07 | 61.39 | 0.07 | 61.53 | 0.06 | [18 empty] | 123.43 | 0.06 | [12 empty] | 125.49 | 0.05 | 124.01 | 0.06 | [20 empty] | 123.59 | 0.07 | 123.41 | 0.07 | 125.49 | 0.05 | 124.01 | 0.06 | 53.83 | 0.08 | 82.79 | 0.04 | [24 empty] | 115.17 | 0.1 | 114.7 | 0.09 | 74.47 | 0.06 | 74.62 | 0.05 | 74.33 | 0.06 | 74.35 | 0.05 | 74.54 | 0.05 | 74.6 | 0.04 |  |  | 76.84 | 0.14 | 75.26 | 0.12 | 75.25 | 0.1 | 75.27 | 0.1 | 103.25 | 0.31 | 92.13 | 0.37 | 92.37 | 0.37 | 77.57 | 0.22 | 90.7 | 0.37 | 89.7 | 0.12 | 95.44 | 0.12 | 96.41 | 0.13 | 90.07 | 0.11 | 89.52 | 0.12 | 93.22 | 0.12 | 93.86 | 0.16 | [30 empty] | 115.39 | 0.1 | 114.98 | 0.1 | 114.95 | 0.11 | 115.12 | 0.1 | 114.97 | 0.1 | 114.91 | 0.14 | [50 empty] | C8-55-1FE3 | 74.999 | 0.019 | 62.018 | 0.016 | 61.498 | 0.012 | 57.681 | 0.015 | 115.004 | 0.014 | 80 | 0.033 | 2565.1 | 3 | 2500.1 | 2.9 | 1.187 | 0.002 | -0.315 | 0.002 | 0.267 | 0.004 | 1.2015 | 0.0028 | 29.345 | 0.001 | 10628 | 31 | 1500 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4051 | 11649.1561 | 348.6368 | 224.5116 | 922.202 | 10726.9541 | 0.0091864 | 28.8319 | 60.0929 | 14.6071 | 13.2118 | 0.013766 | 42.9097 | 0.0087927 | 27.6216 | 0.0092424 | 24.8181 | 78.1924 | 63.7286 | 24.4751 | 50753.4498 | 50602.5222 | 9128 | 0.61383 | 46823.8472 | 46672.9195 | 4.4057 | 0.21878 | -4.3568 | -18.0995 | 55.0241 | 50753.4498 | 32659.1261 | 3995.6218 | 14098.7019 | 50753.4498 | 100%
3 | 3-52821CF | 75N0029 | 3-52821CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 10:08:32 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 0.1 | 26.3 | 0 | 51594 | 80 | 50744 | 211 | 12172 | 116 | 63778 | 123 | 8.2743 |  |  |  |  | 112.35 | 0.02 | 19.29 | [32 empty] | 83% airflow, both stages, 1-finger (0.74") open | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor: | 74.998 | 0.016 | 61.993 | 0.022 | 81.997 | 0.029 | 68.004 | 0.021 | 74.54 | 0.07 | 56.43 | 0.02 | 61.11 | 0.03 | 0.251 | 0.002 | 1.1841 | 0.0023 | 51594 | 80 | 12172 | 116 | 8.275 | 0.037 | 79024 | 57 | 10.252 | 0.041 | 19.29 | 0.16 | 230.4 | 0.8 | 230.1 | 0.8 | 229.6 | 0.8 | 26.3 | 0.1 | 23.4 | 0.1 | 26.6 | 0.1 | 6005.4 | 36.8 | 3506.9 | 43.3 | 1702.5 | 30.6 | 230 |  | 230 |  | 230 |  | 6.5 |  | 6.3 |  | 6.2 |  | 0.54 | 230 |  | 230 |  | 230 |  | 10 |  | 9.3 |  | 8.9 |  | 2870 |  | 0.77 | 230 | 230 | 230 | 9.5 | 8.4 | 8.9 | 2710 | 0.77 | [8 empty] | 7720 | [22 empty] | 225.82 | 0.19 | 171.29 | 0.06 | 109.76 | 0.06 | 61.53 | 0.05 | 207.07 | 0.18 | 88.24 | 0.04 | 103.71 | 0.06 | 15.48 | 0.04 | [8 empty] | 69.41 | 0.05 | 63.13 | 0.09 | 40.43 | 0.03 | 22.7 | 0.1 | 598 | 0.46 | 35.82 | 0.01 | 79024 | 57 | 45760 | 35 | [38 empty] | 209.03 | 0.2 | 190.34 | 0.05 | 104.36 | 0.07 | 85.99 | 0.05 | [6 empty] | 198.6 | 0.21 | 88.77 | 0.04 | 100.85 | 0.07 | 12.09 | 0.05 | [6 empty] | 56.13 | 0.04 | 73.69 | 0.03 | 30.75 | 0.03 | 42.94 | 0.04 | 87.88 | 0.06 | 480 | 0.42 | 35.99 | 0.01 | 114.89 | 0.01 | 79024 | 57 | 37872 | 33 | [26 empty] | 56.45 | 0.04 | 56.33 | 0.04 | 56.56 | 0.04 | 56.86 | 0.06 | 56.76 | 0.06 | 56.76 | 0.06 | [18 empty] | 88.24 | 0.04 | [12 empty] | 89.98 | 0.04 | 88.41 | 0.04 | [20 empty] | 88.56 | 0.04 | 87.88 | 0.06 | 89.98 | 0.04 | 88.41 | 0.04 | 64.04 | 0.08 | 73.61 | 0.03 | [24 empty] | 81.99 | 0.08 | 81.77 | 0.08 | 74.49 | 0.06 | 74.53 | 0.06 | 74.66 | 0.06 | 74.63 | 0.06 | 74.68 | 0.06 | 74.68 | 0.05 |  |  | 75.66 | 0.08 | 75.09 | 0.07 | 75.04 | 0.07 | 74.88 | 0.07 | 79.88 | 0.1 | 79.15 | 0.09 | 76.44 | 0.1 | 76.16 | 0.1 | 77.01 | 0.12 | 76.25 | 0.07 | 77.62 | 0.07 | 78.06 | 0.07 | 75.95 | 0.06 | 75.87 | 0.07 | 77.03 | 0.07 | 76.81 | 0.11 | [30 empty] | 81.94 | 0.1 | 81.83 | 0.09 | 81.79 | 0.11 | 81.81 | 0.1 | 81.57 | 0.1 | 81.52 | 0.13 | [50 empty] | C8-55-1FE3 | 74.998 | 0.016 | 61.993 | 0.022 | 56.578 | 0.014 | 53.416 | 0.018 | 81.997 | 0.029 | 68.004 | 0.021 | 2531.3 | 2.4 | 2500.2 | 2.4 | 1.23 | 0.002 | -0.386 | 0.003 | 0.251 | 0.002 | 1.1841 | 0.0023 | 29.462 | 0 | 7708 | 31 | 1530 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4306 | 11614.3076 | 361.2809 | 241.1146 | 1052.248 | 10562.0596 | 0.0090094 | 28.0139 | 55.1474 | 13.7485 | 13.0768 | 0.011347 | 32.1316 | 0.0087765 | 27.6036 | 0.0079246 | 22.1858 | 75.6348 | 62.571 | 21.8374 | 71734.8565 | 57107.2435 | 6178 | 0.29394 | 67746.0181 | 53118.4051 | 8.7891 | 0.20229 | -6.1764 | -20.4874 | 49.9521 | 71734.8565 | 62924.143 | 4046.131 | 4764.5825 | 71734.8565 | 100%
3 | 3-52951CF | 75N0030 | 3-52951CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 4:17:37 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.1 | 28.8 | 0 | 45941 | 72 | 45093 | 204 | 5047 | 105 | 50993 | 125 | 5.8318 |  |  |  |  | 109.7 | 0.03 | 35.16 | [32 empty] | 83.3% Airflow, Both Stages, 1 Finger opened (0.74") | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor: | 75.006 | 0.023 | 62.004 | 0.023 | 95 | 0.02 | 75.046 | 0.023 | 74.37 | 0.09 | 58.21 | 0.05 | 62.61 | 0.02 | 0.283 | 0.004 | 1.1907 | 0.0029 | 45941 | 72 | 5047 | 105 | 5.831 | 0.026 | 78647 | 65 | 8.994 | 0.033 | 35.16 | 0.15 | 230.5 | 0.8 | 230.3 | 0.8 | 229.5 | 0.8 | 28.8 | 0.1 | 25.4 | 0.1 | 28.8 | 0.1 | 6600.6 | 36.1 | 3529.5 | 43 | 2143.8 | 30 | 230 |  | 231 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.52 | 231 |  | 230 |  | 230 |  | 11.2 |  | 10.4 |  | 10 |  | 3400 |  | 0.81 | 229 | 228 | 229 | 10.6 | 9.6 | 10 | 3220 | 0.81 | [8 empty] | 8750 | [22 empty] | 269.78 | 0.19 | 180.63 | 0.07 | 122.69 | 0.05 | 57.94 | 0.06 | 250.7 | 0.19 | 101.98 | 0.06 | 117.27 | 0.06 | 15.29 | 0.05 | [8 empty] | 74.76 | 0.04 | 50.13 | 0.19 | 44 | 0.03 | 6.13 | 0.19 | 642.9 | 0.44 | 40.1 | 0.02 | 78647 | 65 | 44744 | 43 | [38 empty] | 253.92 | 0.21 | 207.31 | 0.05 | 118.21 | 0.06 | 89.11 | 0.04 | [6 empty] | 243.07 | 0.21 | 102.43 | 0.05 | 115.03 | 0.06 | 12.59 | 0.05 | [6 empty] | 63.39 | 0.04 | 77.5 | 0.04 | 36.19 | 0.03 | 41.31 | 0.05 | 101.67 | 0.08 | 521.6 | 0.46 | 40.24 | 0.02 | 115.19 | 0.01 | 78647 | 65 | 39089 | 34 | [26 empty] | 58.13 | 0.05 | 58.23 | 0.04 | 58.58 | 0.04 | 58.46 | 0.06 | 58.42 | 0.06 | 58.56 | 0.05 | [18 empty] | 101.98 | 0.06 | [12 empty] | 103.79 | 0.06 | 102.29 | 0.07 | [20 empty] | 102.19 | 0.08 | 101.67 | 0.08 | 103.79 | 0.06 | 102.29 | 0.07 | 52.45 | 0.34 | 77.52 | 0.04 | [24 empty] | 94.86 | 0.1 | 94.55 | 0.08 | 74.48 | 0.06 | 74.61 | 0.06 | 74.34 | 0.08 | 74.37 | 0.06 | 74.52 | 0.06 | 74.54 | 0.06 |  |  | 75.86 | 0.15 | 74.93 | 0.15 | 74.96 | 0.13 | 74.96 | 0.1 | 87.51 | 0.26 | 77.58 | 0.21 | 78.94 | 0.23 | 75.78 | 0.16 | 81.68 | 0.47 | 81.33 | 0.11 | 83.8 | 0.14 | 84.48 | 0.14 | 81.26 | 0.09 | 81.09 | 0.09 | 82.81 | 0.09 | 82.44 | 0.31 | [30 empty] | 94.93 | 0.11 | 94.6 | 0.11 | 94.61 | 0.11 | 94.73 | 0.11 | 94.57 | 0.1 | 94.56 | 0.13 | [50 empty] | C8-55-1FE3 | 75.006 | 0.023 | 62.004 | 0.023 | 58.538 | 0.019 | 55.266 | 0.017 | 95 | 0.02 | 75.046 | 0.023 | 2544.3 | 3.1 | 2499.9 | 3.1 | 1.213 | 0.002 | -0.333 | 0.002 | 0.283 | 0.004 | 1.1907 | 0.0029 | 29.419 | 0.001 | 8744 | 32 | 1520 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4231 | 11625.7369 | 356.2448 | 226.7968 | 965.076 | 10660.6609 | 0.0092118 | 28.4905 | 57.1149 | 14.1002 | 13.131 | 0.013961 | 38.2016 | 0.0087818 | 27.6114 | 0.0085121 | 23.3017 | 76.6801 | 63.2399 | 22.9548 | 64357.3879 | 54590.3476 | 7224 | 0.3831 | 60385.4914 | 50618.4511 | 6.9059 | 0.19999 | -5.5358 | -19.5652 | 52.224 | 64357.3879 | 50103.7905 | 4033.2615 | 10220.336 | 64357.3879 | 100%
3 | C8-CB30-95-CE | 75N0031 | C8-CB30-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 0 | CUST 3 | 6/27/2015 | 13:05:32 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1 | 29.6 | 0 | 44861 | 88 | 44384 | 142 | 2629 | 136 | 47492 | 163 | 4.97 | 900 | [38 empty] | 30% condenser coil block(~30 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 29` | 75.001 | 0.008 | 62.002 | 0.029 | 94.994 | 0.023 | 74.995 | 0.022 | 74.7 | 0.05 | 58.84 | 0.05 | 62.42 | 0.01 | 0.133 | 0.006 | 0.8886 | 0.0036 | 44861 | 88 | 2629 | 136 | 4.97 | 0.019 | [6 empty] | 229.7 | 0.8 | 229.4 | 0.8 | 230.2 | 0.8 | 29.6 | 0.1 | 27.4 | 0 | 31.3 | 0.1 | 6796.9 | 29.7 | 3818.6 | 42.6 | 2759.1 | 24.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 11.1 |  | 11.1 |  | 10.5 |  | 3640 |  | 0.85 | 230 | 230 | 230 | 11.5 | 11.4 | 10.2 | 3670 | 0.74 | 228.1 |  | 2.4 |  | 533 |  | 115 |  | 9548 | [22 empty] | 286.95 | 0.21 | 203.49 | 0.08 | 127.32 | 0.06 | 76.16 | 0.06 | [16 empty] | 69.31 | 0.05 | 77.85 | 0.03 | 40.31 | 0.03 | 37.54 | 0.04 | [8 empty] | 274.39 | 0.19 | 110.39 | 0.09 | 123.94 | 0.05 | 13.56 | 0.06 | 271.46 | 0.21 | 123.14 | 0.06 | 11.98 | 0.05 | [24 empty] | 302.31 | 0.27 | 209.99 | 0.09 | 131.32 | 0.07 | 78.67 | 0.08 | [20 empty] | 76.95 | 0.05 | 74.79 | 0.05 | 45.38 | 0.03 | 29.41 | 0.06 | [12 empty] | 291.5 | 0.28 | 111.04 | 0.09 | 128.52 | 0.07 | 17.48 | 0.06 | 288.27 | 0.25 | 127.67 | 0.07 | 16.15 | 0.07 | [12 empty] | 59.42 | 0.03 | 58.5 | 0.02 | 58.36 | 0.03 | 57.99 | 0.03 | 58.81 | 0.03 |  |  | 110.61 | 0.09 |  |  | 74.31 | 0.03 | 77.7 | 0.03 | 203.99 | 0.1 |  |  | 111.46 | 0.06 | 76.68 | 0.06 | 82.31 | 0.07 |  |  | 112.26 | 0.07 | [28 empty] | 59.18 | 0.03 | [8 empty] | 111.52 | 0.09 | 111.16 | 0.07 | [8 empty] | 76.14 | 0.04 | 110.94 | 0.07 | 75.81 | 0.06 | 111.68 | 0.06 | [10 empty] | 203.37 | 0.09 | 95.77 | 0.09 | 95.49 | 0.07 | 75.07 | 0.06 | 75.06 | 0.05 | 75.25 | 0.06 | 75.23 | 0.05 | 75.18 | 0.05 | 75.19 | 0.05 |  |  | 80.96 | 0.08 | 80.54 | 0.1 | 75.48 | 0.08 | 86.96 | 0.13 | 75.64 | 0.05 | 82.3 | 0.07 | 77.22 | 0.11 | 79.35 | 0.14 | 85.9 | 0.18 | 82.3 | 0.08 | 81.3 | 0.08 | 83.82 | 0.08 | 75.02 | 0.05 | 82.55 | 0.07 | 77.8 | 0.11 | 82.23 | 0.08 | [78 empty] | 94 | 0.11 | [8 empty] | 58.86 | 0.02 | 58.97 | 0.03 | C8-55-CE3 | 75.001 | 0.008 | 62.002 | 0.029 | 58.963 | 0.016 | 55.784 | 0.021 | 94.994 | 0.023 | 74.995 | 0.022 | 2524.8 | 5.1 | 2470.2 | 5 | 1.149 | 0.002 | -0.391 | 0.002 | 0.133 | 0.006 | 0.8886 | 0.0036 | 29.306 | 0.001 | 9556 | 16 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5499 | 11525.8069 | 333.4397 | 22.0436 | 93.8042 | 11432.0027 | 0.0088235 | 27.6959 | 57.4131 | 14.0997 | 13.1434 | 0.013918 | 38.1524 | 0.0087817 | 27.6101 | 0.0087127 | 23.6234 | 75.1652 | 62.1241 | 23.2454 | 51294.9173 | 49105.8745 | 7966 | 0.53003 | 47006.2768 | 44817.2341 | 4.919 | 0.18737 | -4.4504 | -17.7521 | 53.32 | 51294.9173 | 45949.5117 | 4356.4902 | 988.9154 | 51294.9173 | 100%
3 | 3-2000-82 | 75N0047 | 3-2000-82 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/12/2013 | 8:30:45 | 10 Ton | 0:30:00 | 75/62 - 82/68 | ENG 1 | TECH 1 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.8 | 1.2 | 25.6 | 0 | 32237 | 274 | 31175 | 339 | 8016 | 210 | 40261 | 454 | 5.6834 |  |  |  |  | 108.61 | 1.1 | -2.2 | [32 empty] | Lg rstrct CK1, 2000 cfm, clsd dmpr 75/62 ID, 82/68 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 75.01 | 0.016 | 62.004 | 0.029 | 81.988 | 0.024 | 67.997 | 0.019 | 74.32 | 0.06 | 60.42 | 0.15 | 65 | 0.08 | 0.743 | 0.004 | 0.7688 | 0.0016 | 32237 | 274 | 8016 | 210 | 5.684 | 0.071 | 39387 | 224 | 5.561 | 0.042 | -2.2 | 0.93 | 230.8 | 1 | 230.9 | 1 | 229.2 | 1 | 25.6 | 0.1 | 21.8 | 0.1 | 25.3 | 0.1 | 5824.6 | 46.6 | 3374.1 | 55 | 1258.6 | 37.3 | 230 |  | 230 |  | 230 |  | 6.2 |  | 5.7 |  | 5.8 |  | 0.48 | 230 |  | 230 |  | 230 |  | 9.5 |  | 8.5 |  | 8 |  | 2490 |  | 0.72 | 230 | 230 | 230 | 9.5 | 8.2 | 8.8 | 2670 | 0.76 | [8 empty] | 7100 | [14 empty] | 178.02 | 0.31 | 85.07 | 0.05 |  |  | 8.44 | 0.1 | 182.21 | 0.32 | 211.3 | 4.19 | 95.05 | 0.11 | 116.26 | 4.08 | 111.98 | 0.28 | 84.98 | 0.06 | 65.22 | 0.14 | -19.75 | 0.12 | [8 empty] | 22.66 | 0.53 | 24.61 | 7.06 | -2.1 | 0.67 | 26.77 | 6.47 | 102.66 | 2.06 | 34.83 | 0.02 | 39387 | 224 | 7585 | 234 | [18 empty] | 93.51 | 0.11 | 67.23 | 0.12 | [16 empty] | 206.21 | 0.15 | 187.97 | 0.05 | 103.4 | 0.05 | 84.58 | 0.05 | 196.25 | 0.16 |  |  | 12.83 | 0.04 | 195.75 | 0.17 | 87.02 | 0.06 | 99.85 | 0.06 | 12.83 | 0.06 | [6 empty] | 54.97 | 0.02 | 71.23 | 0.03 | 29.78 | 0.02 | 41.45 | 0.04 | 87.39 | 0.06 | 476.48 | 0.35 | 35.45 | 0.02 | 114.53 | 0.01 | 39387 | 224 | 37677 | 30 | [14 empty] | 87.19 | 0.06 | 100.02 | 0.06 | [8 empty] | 60.87 | 0.16 | 59.89 | 0.14 | 59.66 | 0.15 | 61.51 | 0.16 | 61.43 | 0.16 | 61.44 | 0.15 | [18 empty] | 84.98 | 0.06 | [12 empty] | 69.28 | 0.13 | 87.1 | 0.06 | [20 empty] | 85.79 | 0.07 | 87.39 | 0.06 | 69.28 | 0.13 | 87.1 | 0.06 | 28.11 | 6.89 | 70.91 | 0.03 | [12 empty] | 85.41 | 0.05 | 87.67 | 0.05 | 87.53 | 0.05 | [6 empty] | 81.74 | 0.07 | 81.47 | 0.06 | 74.2 | 0.05 | 74.29 | 0.05 | 74.19 | 0.06 | 74.18 | 0.05 | 74.27 | 0.05 | 74.29 | 0.05 |  |  | 75.06 | 0.08 | 74.68 | 0.08 | 74.71 | 0.06 | 74.71 | 0.07 | 76.87 | 0.11 | 75.5 | 0.08 | 74.84 | 0.08 | 74.81 | 0.08 | 75.74 | 0.11 | 75.85 | 0.06 | 75.81 | 0.05 | 74.71 | 0.06 | 74.85 | 0.08 | 75.68 | 0.07 | 75.39 | 0.06 | 72.68 | 0.09 | [30 empty] | 81.61 | 0.06 | 81.36 | 0.07 | 81.39 | 0.07 | 81.49 | 0.07 | 81.38 | 0.06 | 81.36 | 0.07 | [50 empty] | C8-55-CE3 | 75.01 | 0.016 | 62.004 | 0.029 | 60.627 | 0.128 | 55.4 | 0.088 | 81.988 | 0.024 | 67.997 | 0.019 | 2047.6 | 2.1 | 1999.7 | 2 | 1.404 | 0.003 | -0.274 | 0.002 | 0.743 | 0.004 | 0.7688 | 0.0016 | 29.322 | 0.001 | 7084 | 31 | 1330 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5255 | 9320.8919 | 329.8352 | 18.2217 | 79.5226 | 9241.3693 | 0.0088028 | 27.6499 | 59.1015 | 13.7483 | 13.1807 | 0.011344 | 32.126 | 0.0087809 | 27.6114 | 0.0080964 | 23.3587 | 75.0698 | 62.0586 | 22.9871 | 43461.37 | 35721.3296 | 5754 | 0.45186 | 40047.8077 | 32307.7673 | 5.6533 | 0.36005 | -4.6628 | -15.9683 | 50.1173 | 43461.37 | 39638.6789 | 3463.6767 | 359.0144 | 43461.37 | 100%
3 | 3-2000-95 | 75N0048 | 3-2000-95 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/11/2013 | 7:26:26 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.6 | 1.2 | 27.3 | 0 | 29533 | 135 | 28465 | 191 | 4463 | 108 | 33999 | 210 | 4.2109 |  |  |  |  | 106.15 | 0.67 | 18.78 | [32 empty] | Lg rstrct CK1, 2000 cfm, clsd dmpr, 75/62 ID, 95/75 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 74.996 | 0.017 | 62.01 | 0.028 | 94.989 | 0.011 | 74.995 | 0.026 | 74.17 | 0.07 | 61.44 | 0.06 | 65.85 | 0.03 | 0.781 | 0.003 | 0.772 | 0.0019 | 29533 | 135 | 4463 | 108 | 4.211 | 0.032 | 41863 | 244 | 5.185 | 0.038 | 18.78 | 0.65 | 230.6 | 1 | 230.3 | 1 | 229.4 | 1 | 27.3 | 0.1 | 24.1 | 0.1 | 27.3 | 0.1 | 6264.6 | 44.2 | 3497.1 | 55.3 | 1808.7 | 36.3 | 230 |  | 230 |  | 230 |  | 6.2 |  | 5.9 |  | 5.9 |  | 0.49 | 230 |  | 230 |  | 230 |  | 10.2 |  | 9.4 |  | 8.9 |  | 2940 |  | 0.78 | 230 | 230 | 230 | 10.5 | 9.4 | 10 | 3200 | 0.81 | [8 empty] | 8100 | [14 empty] | 218.49 | 0.21 | 98.3 | 0.04 |  |  | 9.11 | 0.07 | 223.12 | 0.22 | 223.44 | 3.2 | 108.88 | 0.07 | 114.56 | 3.14 | 135.36 | 0.22 | 98.04 | 0.04 | 76.26 | 0.1 | -21.77 | 0.09 | [8 empty] | 27.04 | 0.41 | 11.2 | 4.26 | 3.24 | 0.47 | 8 | 3.82 | 116.79 | 1.92 | 38.86 | 0.01 | 41863 | 244 | 7860 | 177 | [18 empty] | 107.41 | 0.07 | 79.54 | 0.09 | [16 empty] | 250.73 | 0.16 | 204.08 | 0.04 | 117.26 | 0.05 | 86.82 | 0.06 | 240.44 | 0.17 |  |  | 13.26 | 0.04 | 239.87 | 0.16 | 100.6 | 0.04 | 114.05 | 0.05 | 13.44 | 0.07 | [6 empty] | 62.3 | 0.04 | 74.36 | 0.05 | 35.33 | 0.03 | 39.02 | 0.06 | 101.04 | 0.04 | 518.51 | 0.38 | 39.67 | 0.01 | 114.7 | 0.01 | 41863 | 244 | 38905 | 30 | [14 empty] | 100.96 | 0.04 | 114.22 | 0.05 | [8 empty] | 61.96 | 0.09 | 61.49 | 0.14 | 61.63 | 0.19 | 62.02 | 0.12 | 61.96 | 0.12 | 62.04 | 0.12 | [18 empty] | 98.04 | 0.04 | [12 empty] | 80.25 | 0.1 | 100.89 | 0.04 | [20 empty] | 98.31 | 0.04 | 101.04 | 0.04 | 80.25 | 0.1 | 100.89 | 0.04 | 16.83 | 4.45 | 74.12 | 0.03 | [12 empty] | 98.6 | 0.03 | 101.43 | 0.04 | 101.3 | 0.03 | [6 empty] | 94.75 | 0.07 | 94.44 | 0.05 | 74.3 | 0.05 | 74.39 | 0.05 | 73.99 | 0.04 | 74.04 | 0.04 | 74.19 | 0.04 | 74.21 | 0.04 |  |  | 75.14 | 0.08 | 74.41 | 0.07 | 74.59 | 0.06 | 74.73 | 0.06 | 83.19 | 0.2 | 76.69 | 0.09 | 74.49 | 0.06 | 74.5 | 0.06 | 80.24 | 0.15 | 77.89 | 0.06 | 77.87 | 0.07 | 75.48 | 0.06 | 78.6 | 0.1 | 79.23 | 0.07 | 77.96 | 0.08 | 74.03 | 0.1 | [30 empty] | 94.62 | 0.06 | 94.17 | 0.06 | 94.31 | 0.07 | 94.46 | 0.06 | 94.42 | 0.07 | 94.45 | 0.09 | [50 empty] | C8-55-CE3 | 74.996 | 0.017 | 62.01 | 0.028 | 61.781 | 0.052 | 56.501 | 0.042 | 94.989 | 0.011 | 74.995 | 0.026 | 2055.5 | 2.6 | 1999.8 | 2.5 | 1.43 | 0.003 | -0.264 | 0.002 | 0.781 | 0.003 | 0.772 | 0.0019 | 29.275 | 0.001 | 8074 | 31 | 1350 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5445 | 9334.0811 | 335.9601 | 18.1132 | 77.0793 | 9257.0018 | 0.0088305 | 27.7029 | 60.2365 | 14.0996 | 13.2129 | 0.013919 | 38.1525 | 0.0087882 | 27.6159 | 0.0084683 | 24.0446 | 75.1626 | 62.1338 | 23.6681 | 37661.0072 | 33437.1527 | 6724 | 0.60936 | 34200.089 | 29976.2345 | 4.2358 | 0.35546 | -4.0348 | -14.9261 | 52.0049 | 37661.0072 | 33334.7469 | 3514.1083 | 812.152 | 37661.0072 | 100%
3 | 3-2500-115 | 75N0049 | 3-2500-115 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/11/2013 | 12:58:15 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 1.1 | 31.9 | 0 | 29297 | 45 | 28636 | 91 | -639 | 75 | 28657 | 78 | 2.8081 |  |  |  |  | 117.07 | 0.01 | 34.88 | [32 empty] | Lg rstrct CK1, 2500 cfm, clsd dmpr 75/62 ID, 115/80 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 75 | 0.009 | 62.003 | 0.018 | 115.001 | 0.027 | 80.014 | 0.023 | 74.56 | 0.03 | 64.24 | 0.02 | 67.32 | 0.01 | 0.17 | 0.004 | 0.9218 | 0.002 | 29297 | 45 | -639 | 75 | 2.808 | 0.012 | 44003 | 90 | 4.312 | 0.016 | 34.88 | 0.21 | 230.4 | 1 | 230.1 | 1 | 229.5 | 1 | 31.9 | 0.1 | 28.7 | 0.1 | 32 | 0.1 | 7338 | 42.7 | 3663.3 | 51.1 | 2866.5 | 35.5 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.1 |  | 6.1 |  | 0.54 | 230 |  | 230 |  | 230 |  | 12.3 |  | 11.6 |  | 11.1 |  | 3940 |  | 0.85 | 230 | 230 | 230 | 12.7 | 11.5 | 12.2 | 4150 | 0.86 | [8 empty] | 10210 | [14 empty] | 298.36 | 0.26 | 119.46 | 0.06 |  |  | 10.83 | 0.03 | 303.19 | 0.26 | 297.47 | 0.11 | 131.53 | 0.07 | 165.93 | 0.11 | 183.14 | 0.27 | 119.45 | 0.05 | 95.36 | 0.1 | -24.08 | 0.09 | [8 empty] | 41.92 | 0.05 | 82.56 | 0.03 | 18.61 | 0.05 | 63.95 | 0.05 | 146.23 | 1.25 | 45.74 | 0.02 | 44003 | 90 | 10432 | 88 | [18 empty] | 130.29 | 0.07 | 98.61 | 0.05 | [16 empty] | 328.81 | 0.29 | 233.46 | 0.06 | 137.88 | 0.07 | 95.58 | 0.04 | 318.24 | 0.29 |  |  | 12.59 | 0.03 | 317.22 | 0.29 | 122.39 | 0.05 | 135.05 | 0.07 | 12.67 | 0.05 | [6 empty] | 73.78 | 0.05 | 81.1 | 0.04 | 43.29 | 0.03 | 37.82 | 0.05 | 122.99 | 0.07 | 575 | 0.41 | 46.72 | 0.02 | 115.31 | 0.01 | 44003 | 90 | 39443 | 27 | [14 empty] | 122.72 | 0.06 | 135.31 | 0.07 | [8 empty] | 64.74 | 0.03 | 64.26 | 0.03 | 64.16 | 0.04 | 64.72 | 0.04 | 64.61 | 0.04 | 64.52 | 0.03 | [18 empty] | 119.45 | 0.05 | [12 empty] | 99.77 | 0.05 | 122.79 | 0.06 | [20 empty] | 120.54 | 0.05 | 122.99 | 0.07 | 99.77 | 0.05 | 122.79 | 0.06 | 84.43 | 0.03 | 80.6 | 0.04 | [12 empty] | 119.95 | 0.06 | 123.37 | 0.07 | 123.12 | 0.07 | [6 empty] | 115.23 | 0.09 | 114.66 | 0.07 | 74.48 | 0.04 | 74.51 | 0.05 | 74.49 | 0.06 | 74.48 | 0.04 | 74.58 | 0.04 | 74.62 | 0.04 |  |  | 77.34 | 0.11 | 75.39 | 0.07 | 75.28 | 0.06 | 75.32 | 0.06 | 102.41 | 0.36 | 81.3 | 0.21 | 75.58 | 0.06 | 75.39 | 0.05 | 92.8 | 0.39 | 80.95 | 0.15 | 82.13 | 0.12 | 78.05 | 0.1 | 86.04 | 0.1 | 84.1 | 0.15 | 83.75 | 0.12 | 79.5 | 0.13 | [30 empty] | 115.05 | 0.11 | 114.8 | 0.09 | 114.88 | 0.1 | 114.98 | 0.1 | 114.76 | 0.1 | 114.62 | 0.13 | [50 empty] | C8-55-CE3 | 75 | 0.009 | 62.003 | 0.018 | 64.444 | 0.013 | 58.35 | 0.016 | 115.001 | 0.027 | 80.014 | 0.023 | 2587.5 | 2.9 | 2500 | 2.7 | 1.198 | 0.002 | -0.409 | 0.003 | 0.17 | 0.004 | 0.9218 | 0.002 | 29.223 | 0.002 | 10205 | 31 | 1510 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4088 | 11686.8371 | 351.8535 | 22.9474 | 94.2581 | 11592.579 | 0.0088229 | 27.7343 | 63.0352 | 14.6071 | 13.2842 | 0.01378 | 42.925 | 0.0087826 | 27.6108 | 0.0089535 | 25.2224 | 75.3255 | 62.1805 | 24.8787 | 33373.4743 | 34472.5625 | 8695 | 0.88921 | 29420.7205 | 30519.8087 | 2.883 | 0.41262 | -2.8556 | -12.2904 | 54.4014 | 33373.4743 | 27912.9395 | 4017.0497 | 1443.485 | 33373.4743 | 100%
3 | 3-2500-82 | 75N0050 | 3-2500-82 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/12/2013 | 7:43:04 | 10 Ton | 0:30:00 | 75/62 - 82/68 | ENG 1 | TECH 1 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.8 | 1.2 | 25.9 | 0 | 36518 | 61 | 35810 | 106 | 7394 | 88 | 43919 | 88 | 6.0662 |  |  |  |  | 115.09 | 0.06 | -8.36 | [32 empty] | Lg rstrct CK1, 2500 cfm, clsd dmpr 75/62 ID, 82/68 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 75.007 | 0.013 | 61.999 | 0.028 | 81.996 | 0.024 | 67.999 | 0.019 | 74.46 | 0.05 | 61.65 | 0.04 | 65.42 | 0.02 | 0.149 | 0.003 | 0.9143 | 0.0019 | 36518 | 61 | 7394 | 88 | 6.066 | 0.028 | 40532 | 163 | 5.598 | 0.032 | -8.36 | 0.51 | 230.8 | 1.1 | 230.8 | 1.1 | 229.2 | 1.1 | 25.9 | 0.1 | 22.2 | 0.1 | 25.5 | 0.1 | 5898.1 | 47.6 | 3370.2 | 57.7 | 1341.9 | 37.5 | 230 |  | 230 |  | 230 |  | 6.5 |  | 6.1 |  | 6 |  | 0.54 | 230 |  | 230 |  | 230 |  | 9.4 |  | 8.5 |  | 8 |  | 2460 |  | 0.71 | 230 | 230 | 230 | 9.6 | 8.2 | 8.8 | 2680 | 0.76 | [8 empty] | 7280 | [14 empty] | 180.03 | 0.16 | 85.26 | 0.05 |  |  | 8.99 | 0.03 | 184.34 | 0.16 | 231.83 | 0.24 | 95.81 | 0.06 | 136.02 | 0.25 | 113.83 | 0.12 | 85.12 | 0.05 | 66.15 | 0.06 | -18.97 | 0.05 | [8 empty] | 25.81 | 0.05 | 66.07 | 0.36 | 1.79 | 0.06 | 64.29 | 0.33 | 106.57 | 2 | 34.87 | 0.01 | 40532 | 163 | 8551 | 159 | [18 empty] | 94.25 | 0.06 | 68.11 | 0.06 | [16 empty] | 206.67 | 0.18 | 189.09 | 0.03 | 103.55 | 0.06 | 85.53 | 0.06 | 196.69 | 0.18 |  |  | 12.87 | 0.04 | 196.19 | 0.19 | 87.17 | 0.04 | 99.99 | 0.06 | 12.82 | 0.06 | [6 empty] | 55.31 | 0.02 | 72.74 | 0.03 | 30.04 | 0.02 | 42.7 | 0.03 | 87.4 | 0.06 | 477.52 | 0.37 | 35.5 | 0.01 | 114.77 | 0.01 | 40532 | 163 | 37854 | 29 | [14 empty] | 87.3 | 0.04 | 100.17 | 0.06 | [8 empty] | 62.41 | 0.05 | 61.49 | 0.04 | 60.48 | 0.04 | 62.58 | 0.06 | 62.47 | 0.05 | 62.42 | 0.04 | [18 empty] | 85.12 | 0.05 | [12 empty] | 70.03 | 0.06 | 87.12 | 0.05 | [20 empty] | 86.02 | 0.06 | 87.4 | 0.06 | 70.03 | 0.06 | 87.12 | 0.05 | 67.31 | 0.34 | 72.35 | 0.04 | [12 empty] | 85.57 | 0.05 | 87.68 | 0.05 | 87.55 | 0.05 | [6 empty] | 81.72 | 0.08 | 81.43 | 0.07 | 74.32 | 0.04 | 74.43 | 0.05 | 74.28 | 0.06 | 74.28 | 0.05 | 74.4 | 0.05 | 74.42 | 0.05 |  |  | 75.09 | 0.13 | 74.7 | 0.11 | 74.77 | 0.08 | 74.83 | 0.06 | 79.03 | 0.1 | 75.68 | 0.12 | 74.87 | 0.11 | 74.88 | 0.1 | 76.49 | 0.12 | 75.86 | 0.06 | 75.99 | 0.05 | 75.2 | 0.04 | 75.9 | 0.05 | 76.26 | 0.05 | 75.87 | 0.05 | 72.58 | 0.1 | [30 empty] | 81.62 | 0.06 | 81.34 | 0.06 | 81.37 | 0.07 | 81.48 | 0.07 | 81.36 | 0.06 | 81.37 | 0.09 | [50 empty] | C8-55-CE3 | 75.007 | 0.013 | 61.999 | 0.028 | 61.94 | 0.019 | 56.275 | 0.028 | 81.996 | 0.024 | 67.999 | 0.019 | 2568.4 | 2.7 | 2499.9 | 2.6 | 1.17 | 0.003 | -0.406 | 0.002 | 0.149 | 0.003 | 0.9143 | 0.0019 | 29.303 | 0.001 | 7240 | 31 | 1530 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4464 | 11660.8041 | 343.6162 | 22.1809 | 96.8 | 11564.0041 | 0.0087996 | 27.6453 | 60.4936 | 13.7485 | 13.2156 | 0.011344 | 32.1275 | 0.0087783 | 27.6078 | 0.0082974 | 23.8973 | 75.0653 | 62.0522 | 23.5448 | 47815.2836 | 40780.2764 | 5710 | 0.40757 | 43766.1556 | 36731.1484 | 6.045 | 0.39362 | -4.1005 | -14.5717 | 51.0346 | 47815.2836 | 43267.6986 | 4110.078 | 437.507 | 47815.2836 | 100%
3 | 3-2500-95 Rerun | 75N0051 | 3-2500-95 Rerun | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/11/2013 | 6:44:58 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.6 | 1.1 | 27.7 | 0 | 33364 | 94 | 32652 | 119 | 3130 | 99 | 36497 | 113 | 4.4287 |  |  |  |  | 115.4 | 0.05 | 15.51 | [32 empty] | Lg rstrct CK1, 2500 cfm, clsd dmpr, 75/62 ID, 95/75 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 74.995 | 0.017 | 62.005 | 0.025 | 94.998 | 0.009 | 74.995 | 0.028 | 74.37 | 0.05 | 62.65 | 0.05 | 66.22 | 0.02 | 0.168 | 0.003 | 1.2068 | 0.0025 | 33364 | 94 | 3130 | 99 | 4.429 | 0.023 | 43200 | 135 | 5.242 | 0.025 | 15.51 | 0.42 | 230.6 | 0.9 | 230.3 | 0.9 | 229.3 | 0.9 | 27.7 | 0.1 | 24.4 | 0.1 | 27.6 | 0.1 | 6357.7 | 39.9 | 3481 | 47.3 | 1883.3 | 32.4 | 230 |  | 230 |  | 230 |  | 6.5 |  | 6.2 |  | 6.1 |  | 0.53 | 230 |  | 230 |  | 230 |  | 10.1 |  | 9.3 |  | 9 |  | 2950 |  | 0.79 | 230 | 230 | 230 | 10.6 | 9.4 | 9.9 | 3200 | 0.82 | [8 empty] | 8300 | [14 empty] | 221.26 | 0.16 | 98.48 | 0.04 |  |  | 9.81 | 0.03 | 226.02 | 0.15 | 251.13 | 0.19 | 109.79 | 0.05 | 141.34 | 0.18 | 138.63 | 0.11 | 98.22 | 0.04 | 77.7 | 0.05 | -20.52 | 0.04 | [8 empty] | 31.58 | 0.05 | 69.62 | 0.33 | 8.32 | 0.05 | 61.3 | 0.29 | 120.39 | 1.73 | 38.92 | 0.01 | 43200 | 135 | 9208 | 131 | [18 empty] | 108.29 | 0.05 | 80.65 | 0.04 | [16 empty] | 251.54 | 0.16 | 205.49 | 0.05 | 117.49 | 0.05 | 87.99 | 0.05 | 241.26 | 0.16 |  |  | 13.42 | 0.04 | 240.66 | 0.15 | 100.79 | 0.04 | 114.28 | 0.04 | 13.48 | 0.05 | [6 empty] | 62.89 | 0.05 | 76.41 | 0.03 | 35.76 | 0.03 | 40.65 | 0.04 | 101.1 | 0.05 | 520.35 | 0.38 | 39.73 | 0.01 | 115.03 | 0.01 | 43200 | 135 | 39181 | 31 | [14 empty] | 101.04 | 0.04 | 114.46 | 0.05 | [8 empty] | 63.3 | 0.05 | 62.78 | 0.04 | 62.64 | 0.04 | 63.23 | 0.04 | 63.15 | 0.04 | 63.13 | 0.04 | [18 empty] | 98.22 | 0.04 | [12 empty] | 81.37 | 0.04 | 100.94 | 0.05 | [20 empty] | 98.55 | 0.04 | 101.1 | 0.05 | 81.37 | 0.04 | 100.94 | 0.05 | 71.6 | 0.3 | 76.05 | 0.03 | [12 empty] | 98.83 | 0.04 | 101.48 | 0.04 | 101.35 | 0.03 | [6 empty] | 94.78 | 0.07 | 94.47 | 0.07 | 74.45 | 0.05 | 74.52 | 0.05 | 74.16 | 0.05 | 74.2 | 0.04 | 74.36 | 0.04 | 74.39 | 0.05 |  |  | 75.4 | 0.09 | 74.6 | 0.08 | 74.75 | 0.07 | 74.89 | 0.07 | 87.01 | 0.22 | 77.22 | 0.14 | 74.68 | 0.09 | 74.71 | 0.08 | 81.66 | 0.24 | 77.72 | 0.09 | 78.14 | 0.08 | 76.01 | 0.05 | 79.59 | 0.05 | 79.63 | 0.06 | 78.72 | 0.07 | 74.84 | 0.08 | [30 empty] | 94.64 | 0.06 | 94.2 | 0.07 | 94.32 | 0.07 | 94.48 | 0.07 | 94.39 | 0.07 | 94.4 | 0.09 | [50 empty] | C8-55-CE3 | 74.995 | 0.017 | 62.005 | 0.025 | 63.017 | 0.025 | 57.3 | 0.022 | 94.998 | 0.009 | 74.995 | 0.028 | 2577.9 | 2.7 | 2500 | 2.6 | 1.175 | 0.002 | -0.395 | 0.002 | 0.168 | 0.003 | 1.2068 | 0.0025 | 29.255 | 0.004 | 8241 | 31 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4547 | 11677.3506 | 345.0984 | 22.1561 | 94.2825 | 11583.0681 | 0.0088265 | 27.6974 | 61.5623 | 14.0998 | 13.2456 | 0.013917 | 38.1523 | 0.0087851 | 27.6123 | 0.0086529 | 24.5469 | 75.158 | 62.1261 | 24.1921 | 40932.3322 | 38102.9354 | 6701 | 0.55874 | 36854.1331 | 34024.7364 | 4.472 | 0.39002 | -3.5053 | -13.5957 | 52.869 | 40932.3322 | 35796.3257 | 4142.268 | 993.7384 | 40932.3322 | 100%
3 | 3-3000-115 | 75N0052 | 3-3000-115 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/11/2013 | 11:38:03 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 1 | 32.3 | 0 | 28660 | 491 | 28167 | 202 | -3859 | 320 | 24799 | 326 | 2.3868 |  |  |  |  | 117.17 | 0.01 | 44.13 | [32 empty] | Lg rstrct CK1, 3000 cfm, clsd dmpr 75/62 ID, 115/80 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 75 | 0.01 | 61.997 | 0.052 | 115.001 | 0.018 | 80.08 | 0.274 | 74.57 | 0.03 | 66.08 | 0.07 | 68.43 | 0.05 | -0.49 | 0.006 | 1.3279 | 0.0036 | 28660 | 491 | -3859 | 320 | 2.387 | 0.066 | 44419 | 346 | 4.274 | 0.076 | 44.13 | 1.46 | 230.4 | 1 | 230.1 | 1 | 229.5 | 1 | 32.3 | 0.1 | 29.1 | 0.1 | 32.4 | 0.1 | 7436.5 | 39.5 | 3660 | 47.9 | 2953.6 | 33.9 | 230 |  | 230 |  | 230 |  | 6.7 |  | 6.5 |  | 6.4 |  | 0.56 | 230 |  | 230 |  | 230 |  | 12.3 |  | 11.6 |  | 11.1 |  | 3930 |  | 0.85 | 230 | 230 | 230 | 12.7 | 11.5 | 12.2 | 4160 | 0.86 | [8 empty] | 10400 | [14 empty] | 298.66 | 0.26 | 119.42 | 0.06 |  |  | 10.96 | 0.03 | 303.53 | 0.26 | 297.18 | 0.15 | 131.63 | 0.07 | 165.56 | 0.16 | 184.19 | 0.25 | 119.42 | 0.06 | 95.75 | 0.09 | -23.67 | 0.08 | [8 empty] | 42.31 | 0.05 | 83.26 | 0.04 | 18.99 | 0.04 | 64.27 | 0.06 | 147.45 | 1.23 | 45.73 | 0.02 | 44419 | 346 | 10533 | 88 | [18 empty] | 130.38 | 0.07 | 99 | 0.06 | [16 empty] | 329.87 | 0.23 | 234.63 | 0.05 | 138.14 | 0.05 | 96.49 | 0.05 | 319.3 | 0.22 |  |  | 12.94 | 0.03 | 318.27 | 0.22 | 122.35 | 0.05 | 135.32 | 0.05 | 12.97 | 0.05 | [6 empty] | 74.5 | 0.05 | 82.91 | 0.07 | 43.77 | 0.03 | 39.14 | 0.07 | 122.91 | 0.07 | 577.04 | 4.7 | 46.7 | 0.02 | 115.6 | 0.01 | 44419 | 346 | 39736 | 17 | [14 empty] | 122.63 | 0.06 | 135.57 | 0.05 | [8 empty] | 66.36 | 0.05 | 66.13 | 0.06 | 66.07 | 0.06 | 66.28 | 0.06 | 66.18 | 0.05 | 66.18 | 0.06 | [18 empty] | 119.42 | 0.06 | [12 empty] | 100.02 | 0.06 | 122.7 | 0.07 | [20 empty] | 120.49 | 0.06 | 122.91 | 0.07 | 100.02 | 0.06 | 122.7 | 0.07 | 85.01 | 0.04 | 82.43 | 0.08 | [12 empty] | 119.95 | 0.06 | 123.32 | 0.06 | 123.08 | 0.06 | [6 empty] | 115.2 | 0.09 | 114.62 | 0.07 | 74.49 | 0.04 | 74.58 | 0.03 | 74.44 | 0.04 | 74.45 | 0.03 | 74.57 | 0.03 | 74.63 | 0.03 |  |  | 77.34 | 0.11 | 75.39 | 0.07 | 75.31 | 0.06 | 75.37 | 0.06 | 100.91 | 0.37 | 81.3 | 0.21 | 75.6 | 0.06 | 75.44 | 0.07 | 93.43 | 0.35 | 80.76 | 0.11 | 82.02 | 0.14 | 80.14 | 0.12 | 86.23 | 0.08 | 84.23 | 0.11 | 84.87 | 0.1 | 81.03 | 0.11 | [30 empty] | 115.12 | 0.1 | 114.82 | 0.1 | 114.88 | 0.11 | 115.02 | 0.11 | 114.79 | 0.11 | 114.67 | 0.11 | [50 empty] | C8-55-CE3 | 75 | 0.01 | 61.997 | 0.052 | 66.356 | 0.068 | 59.379 | 0.101 | 115.001 | 0.018 | 80.08 | 0.274 | 3113.8 | 4.2 | 3000 | 4 | 0.975 | 0.003 | -0.557 | 0.003 | -0.49 | 0.006 | 1.3279 | 0.0036 | 29.26 | 0.002 | 10390 | 30 | 1700 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.3763 | 14011.2835 | 343.6299 | 26.7798 | 109.9959 | 13901.2876 | 0.0088184 | 27.7273 | 64.9797 | 14.6077 | 13.3341 | 0.013845 | 42.9967 | 0.0087786 | 27.6065 | 0.0091396 | 25.8918 | 75.3169 | 62.1706 | 25.5559 | 30424.121 | 34760.8318 | 8690 | 0.97485 | 25794.8299 | 30131.5407 | 2.4827 | 0.47745 | -2.1714 | -10.3372 | 55.5349 | 30424.121 | 24025.0761 | 4706.1847 | 1692.8602 | 30424.121 | 100%
3 | 3-3000-82 | 75N0053 | 3-3000-82 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/12/2013 | 6:44:04 | 10 Ton | 0:30:00 | 75/62 - 82/68 | ENG 1 | TECH 1 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.8 | 1.2 | 26.2 | 0 | 38744 | 89 | 38174 | 127 | 5443 | 115 | 44192 | 128 | 5.955 |  |  |  |  | 115.99 | 0.01 | -7.9 | [32 empty] | Lg rstrct CK1, 3000 cfm, clsd dmpr 75/62 ID, 82/68 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 75 | 0.017 | 62 | 0.025 | 81.998 | 0.027 | 68.003 | 0.017 | 74.5 | 0.05 | 63.09 | 0.03 | 66.12 | 0.01 | -0.499 | 0.006 | 1.3187 | 0.0039 | 38744 | 89 | 5443 | 115 | 5.955 | 0.031 | 40957 | 177 | 5.519 | 0.032 | -7.9 | 0.58 | 230.8 | 1 | 230.8 | 1 | 229.2 | 1 | 26.2 | 0.1 | 22.5 | 0.1 | 25.9 | 0.1 | 5979.9 | 46.7 | 3375.6 | 55 | 1441.5 | 36.4 | 230 |  | 230 |  | 230 |  | 6.8 |  | 6.4 |  | 6.4 |  | 0.56 | 230 |  | 230 |  | 230 |  | 9.2 |  | 8.4 |  | 7.9 |  | 2460 |  | 0.73 | 230 | 230 | 230 | 9.6 | 8.2 | 8.8 | 2680 | 0.76 | [8 empty] | 7450 | [14 empty] | 180.29 | 0.17 | 85.29 | 0.06 |  |  | 9.05 | 0.03 | 184.84 | 0.17 | 234.68 | 0.05 | 95.99 | 0.06 | 138.69 | 0.05 | 114.55 | 0.13 | 85.13 | 0.06 | 66.5 | 0.07 | -18.63 | 0.05 | [8 empty] | 26.46 | 0.05 | 71.78 | 0.09 | 2.56 | 0.05 | 69.22 | 0.07 | 108.77 | 2.15 | 34.88 | 0.02 | 40957 | 177 | 8820 | 176 | [18 empty] | 94.34 | 0.06 | 68.46 | 0.06 | [16 empty] | 206.94 | 0.18 | 189.87 | 0.03 | 103.64 | 0.06 | 86.23 | 0.05 | 196.97 | 0.19 |  |  | 12.96 | 0.04 | 196.47 | 0.2 | 87.19 | 0.05 | 100.09 | 0.07 | 12.9 | 0.06 | [6 empty] | 55.59 | 0.03 | 73.9 | 0.03 | 30.26 | 0.02 | 43.64 | 0.03 | 87.38 | 0.07 | 478.42 | 0.39 | 35.51 | 0.01 | 114.95 | 0 | 40957 | 177 | 38009 | 32 | [14 empty] | 87.3 | 0.06 | 100.26 | 0.06 | [8 empty] | 63.69 | 0.03 | 62.93 | 0.03 | 62.09 | 0.04 | 63.79 | 0.04 | 63.7 | 0.03 | 63.68 | 0.03 | [18 empty] | 85.13 | 0.06 | [12 empty] | 70.36 | 0.06 | 87.08 | 0.06 | [20 empty] | 86.05 | 0.06 | 87.38 | 0.07 | 70.36 | 0.06 | 87.08 | 0.06 | 72.64 | 0.09 | 73.51 | 0.02 | [12 empty] | 85.59 | 0.05 | 87.67 | 0.05 | 87.54 | 0.06 | [6 empty] | 81.68 | 0.07 | 81.38 | 0.06 | 74.38 | 0.04 | 74.51 | 0.04 | 74.34 | 0.05 | 74.35 | 0.04 | 74.49 | 0.04 | 74.51 | 0.04 |  |  | 75.03 | 0.08 | 74.66 | 0.07 | 74.77 | 0.06 | 74.86 | 0.05 | 79.34 | 0.09 | 75.69 | 0.07 | 74.82 | 0.07 | 74.86 | 0.06 | 77.01 | 0.08 | 75.84 | 0.05 | 76.04 | 0.05 | 75.46 | 0.05 | 76.44 | 0.04 | 76.41 | 0.05 | 76.28 | 0.05 | 73.76 | 0.07 | [30 empty] | 81.66 | 0.09 | 81.37 | 0.07 | 81.39 | 0.08 | 81.51 | 0.08 | 81.39 | 0.08 | 81.41 | 0.1 | [50 empty] | C8-55-CE3 | 75 | 0.017 | 62 | 0.025 | 63.419 | 0.013 | 57.239 | 0.021 | 81.998 | 0.027 | 68.003 | 0.017 | 3094.1 | 4.6 | 3000 | 4.5 | 0.957 | 0.003 | -0.554 | 0.004 | -0.499 | 0.006 | 1.3187 | 0.0039 | 29.288 | 0.001 | 7421 | 31 | 1700 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.3832 | 14005.9539 | 337.286 | 25.9103 | 113.0748 | 13892.879 | 0.0088013 | 27.6451 | 62.0358 | 13.7486 | 13.2548 | 0.011346 | 32.1308 | 0.0087806 | 27.6086 | 0.0085212 | 24.5015 | 75.0568 | 62.0517 | 24.1643 | 48752.3795 | 43769.0798 | 5721 | 0.40051 | 44101.4366 | 39118.1368 | 5.9428 | 0.43204 | -3.4808 | -13.021 | 52.1308 | 48752.3795 | 43518.1617 | 4722.8774 | 511.3404 | 48752.3795 | 100%
3 | 3-3000-95 Rerun | 75N0054 | 3-3000-95 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/11/2013 | 5:35:26 | 10 Ton | 0:30:00 | 75/62 - 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.6 | 0.9 | 28.1 | 0 | 34656 | 62 | 34119 | 114 | 142 | 107 | 34798 | 123 | 4.1264 |  |  |  |  | 116.11 | 0.02 | 20.26 | [32 empty] | Lg rstrct CK1, 3000 cfm, clsd dmpr, 75/62 ID, 95/75 OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: No econo Meriam set @ 75%: Horiz airflow disch config. set on floor. | 75.004 | 0.005 | 61.998 | 0.022 | 94.999 | 0.014 | 75 | 0.025 | 74.46 | 0.04 | 64.23 | 0.03 | 67.06 | 0.02 | -0.493 | 0.006 | 1.3248 | 0.0035 | 34656 | 62 | 142 | 107 | 4.127 | 0.021 | 43640 | 124 | 5.175 | 0.023 | 20.26 | 0.35 | 230.6 | 0.8 | 230.5 | 0.8 | 229.4 | 0.8 | 28.1 | 0.1 | 24.7 | 0.1 | 28 | 0.1 | 6455.8 | 38.6 | 3475.7 | 44.9 | 1976.7 | 33.8 | 230 |  | 230 |  | 230 |  | 6.8 |  | 6.5 |  | 6.4 |  | 0.56 | 230 |  | 230 |  | 230 |  | 10.2 |  | 9.4 |  | 8.9 |  | 2950 |  | 0.78 | 230 | 230 | 230 | 10.6 | 9.4 | 9.9 | 3210 | 0.81 | [8 empty] | 8490 | [14 empty] | 221.83 | 0.14 | 98.46 | 0.04 |  |  | 10.01 | 0.03 | 226.65 | 0.14 | 253.31 | 0.05 | 109.99 | 0.04 | 143.32 | 0.05 | 139.49 | 0.1 | 98.21 | 0.03 | 78.07 | 0.04 | -20.14 | 0.04 | [8 empty] | 32.22 | 0.04 | 74.1 | 0.1 | 8.99 | 0.04 | 65.11 | 0.08 | 122.03 | 1.54 | 38.92 | 0.01 | 43640 | 124 | 9421 | 118 | [18 empty] | 108.47 | 0.04 | 81.06 | 0.06 | [16 empty] | 252.13 | 0.16 | 206.49 | 0.03 | 117.66 | 0.05 | 88.82 | 0.04 | 241.82 | 0.19 |  |  | 13.66 | 0.05 | 241.23 | 0.17 | 100.86 | 0.03 | 114.45 | 0.05 | 13.59 | 0.06 | [6 empty] | 63.29 | 0.04 | 77.77 | 0.03 | 36.04 | 0.03 | 41.73 | 0.05 | 101.12 | 0.06 | 521.98 | 0.36 | 39.75 | 0.01 | 115.24 | 0.01 | 43640 | 124 | 39407 | 28 | [14 empty] | 100.96 | 0.04 | 114.62 | 0.06 | [8 empty] | 64.7 | 0.04 | 64.31 | 0.04 | 64.24 | 0.03 | 64.67 | 0.05 | 64.57 | 0.05 | 64.59 | 0.05 | [18 empty] | 98.21 | 0.03 | [12 empty] | 81.73 | 0.05 | 100.92 | 0.04 | [20 empty] | 98.6 | 0.04 | 101.12 | 0.06 | 81.73 | 0.05 | 100.92 | 0.04 | 75.63 | 0.07 | 77.33 | 0.03 | [12 empty] | 98.91 | 0.05 | 101.53 | 0.05 | 101.41 | 0.05 | [6 empty] | 94.73 | 0.08 | 94.44 | 0.07 | 74.51 | 0.04 | 74.68 | 0.04 | 74.25 | 0.06 | 74.31 | 0.05 | 74.5 | 0.05 | 74.56 | 0.05 |  |  | 75.47 | 0.09 | 74.66 | 0.06 | 74.86 | 0.05 | 75.02 | 0.05 | 87.73 | 0.19 | 77.28 | 0.15 | 74.71 | 0.09 | 74.77 | 0.07 | 82.7 | 0.18 | 77.84 | 0.07 | 78.3 | 0.09 | 76.83 | 0.09 | 80.13 | 0.06 | 79.83 | 0.06 | 79.61 | 0.07 | 76.41 | 0.11 | [30 empty] | 94.76 | 0.07 | 94.24 | 0.09 | 94.35 | 0.09 | 94.56 | 0.08 | 94.49 | 0.08 | 94.53 | 0.09 | [50 empty] | C8-55-CE3 | 75.004 | 0.005 | 61.998 | 0.022 | 64.603 | 0.011 | 58.288 | 0.019 | 94.999 | 0.014 | 75 | 0.025 | 3107.2 | 4.2 | 3000 | 4 | 0.955 | 0.003 | -0.545 | 0.003 | -0.493 | 0.006 | 1.3248 | 0.0035 | 29.233 | 0.001 | 8433 | 30 | 1720 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4018 | 14030.5154 | 336.5811 | 26.0252 | 110.7465 | 13919.7689 | 0.008819 | 27.6904 | 63.2012 | 14.0999 | 13.2876 | 0.013921 | 38.1571 | 0.0087784 | 27.6071 | 0.0088778 | 25.1787 | 75.1633 | 62.1165 | 24.8368 | 40037.7895 | 40280.1449 | 6713 | 0.57225 | 35316.1808 | 35558.5363 | 4.1879 | 0.43381 | -2.8536 | -11.9621 | 54.036 | 40037.7895 | 34071.6632 | 4797.7501 | 1168.3761 | 40037.7895 | 100%
3 | 3-NC-2500-115 | 75N0055 | 3-NC-2500-115 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/15/2013 | 18:32:20 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.6 | 1.1 | 34.3 | 0 | 38521 | 71 | 37934 | 140 | 1883 | 101 | 40405 | 100 | 3.6228 | 900 |  |  |  | 114.06 | 0.01 | 34.36 | [32 empty] | Same as above at 115/80F OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with AX49 (notched) belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor. Added 0.4 o | 75.001 | 0.022 | 61.999 | 0.018 | 115.008 | 0.019 | 80.001 | 0.025 | 74.39 | 0.07 | 60.77 | 0.05 | 64.88 | 0.02 | 0.196 | 0.005 | 1.201 | 0.0032 | 38521 | 71 | 1883 | 101 | 3.623 | 0.011 | 61563 | 622 | 5.52 | 0.057 | 34.36 | 0.7 | 230.6 | 0.9 | 230.3 | 0.9 | 229.4 | 0.9 | 34.3 | 0.1 | 30.9 | 0.1 | 34.1 | 0.1 | 7908.4 | 34.2 | 3734.7 | 44.1 | 3244.3 | 28.6 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.1 |  | 6.1 |  | 0.54 | 230 |  | 230 |  | 230 |  | 14.7 |  | 13.9 |  | 13.4 |  | 4900 |  | 0.88 | 230 | 230 | 230 | 12.7 | 11.4 | 12 | 4120 | 0.86 | [8 empty] | 11170 | [14 empty] | 374.93 | 0.34 | 120.26 | 0.08 |  |  | 28.22 | 0.03 | 386.41 | 0.35 | 247.42 | 0.07 | 150.96 | 0.07 | 96.46 | 0.07 | 370.64 | 0.38 | 120.39 | 0.07 | 147.53 | 0.08 | 27.14 | 0.06 | [8 empty] | 75.48 | 0.09 | 74.58 | 0.07 | 44.44 | 0.06 | 30.14 | 0.09 | 413.13 | 9.02 | 46.05 | 0.02 | 61563 | 622 | 28087 | 611 | [18 empty] | 148.47 | 0.07 | 120.74 | 0.08 | [16 empty] | 326.72 | 0.36 | 236.42 | 0.06 | 137.39 | 0.09 | 99.03 | 0.05 | 316.33 | 0.35 |  |  | 11.68 | 0.04 | 315.31 | 0.34 | 123.44 | 0.05 | 134.59 | 0.08 | 11.15 | 0.09 | [6 empty] | 72.87 | 0.07 | 82.86 | 0.03 | 42.72 | 0.04 | 40.14 | 0.05 | 123.5 | 0.09 | 563.53 | 0.81 | 47.07 | 0.02 | 115.67 | 0.01 | 61563 | 622 | 38657 | 58 | [14 empty] | 123.17 | 0.07 | 134.85 | 0.09 | [8 empty] | 60.49 | 0.06 | 60.77 | 0.05 | 61.16 | 0.04 | 60.92 | 0.05 | 60.88 | 0.05 | 61.03 | 0.04 | [18 empty] | 120.39 | 0.07 | [12 empty] | 122.23 | 0.07 | 123.24 | 0.07 | [20 empty] | 120.83 | 0.07 | 123.5 | 0.09 | 122.23 | 0.07 | 123.24 | 0.07 | 76.9 | 0.06 | 82.79 | 0.04 | [12 empty] | 120.64 | 0.08 | 123.87 | 0.08 | 123.75 | 0.06 | [6 empty] | 115.2 | 0.14 | 114.53 | 0.11 | 74.41 | 0.06 | 74.6 | 0.07 | 74.03 | 0.06 | 74.12 | 0.05 | 74.34 | 0.06 | 74.44 | 0.06 |  |  | 76.27 | 0.14 | 74.83 | 0.1 | 74.88 | 0.09 | 75.22 | 0.09 | 98.75 | 0.36 | 82.63 | 0.2 | 74.71 | 0.12 | 74.8 | 0.1 | 92.1 | 0.28 | 81.29 | 0.15 | 79.3 | 0.16 | 77.51 | 0.1 | 86.36 | 0.14 | 84.36 | 0.16 | 81.13 | 0.16 | 78.45 | 0.27 | [30 empty] | 115.41 | 0.13 | 114.77 | 0.12 | 114.92 | 0.14 | 115.16 | 0.13 | 115.08 | 0.13 | 115.05 | 0.18 | [50 empty] | C8-55-CE3 | 75.001 | 0.022 | 61.999 | 0.018 | 61.169 | 0.014 | 56.751 | 0.016 | 115.008 | 0.019 | 80.001 | 0.025 | 2565.4 | 3.4 | 2500 | 3.3 | 1.23 | 0.002 | -0.422 | 0.003 | 0.196 | 0.005 | 1.201 | 0.0032 | 29.325 | 0.001 | 11153 | 21 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4371 | 11661.2084 | 361.252 | 23.3092 | 95.7442 | 11565.4642 | 0.0088207 | 27.7335 | 59.7319 | 14.6072 | 13.1997 | 0.013766 | 42.9107 | 0.0087797 | 27.6079 | 0.0087613 | 24.2143 | 75.3324 | 62.1795 | 23.8638 | 45125.9947 | 43660.9492 | 9613 | 0.72706 | 41102.9276 | 39637.8821 | 3.6854 | 0.2863 | -3.8698 | -15.6005 | 53.4739 | 45125.9947 | 39573.7606 | 4087.0769 | 1465.1572 | 45125.9947 | 100%
3 | 3-NC-2500-82 | 75N0056 | 3-NC-2500-82 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/15/2013 | 10:36:11 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 1.2 | 27.3 | 0 | 45784 | 78 | 45020 | 188 | 11504 | 128 | 57298 | 133 | 7.0808 | 899.6 |  |  |  | 114.6 | 0.01 | -9.79 | [32 empty] | NC (add 0.4 oz. Nitrogen) CK1, 2500 cfm, 75/62 ID, 82/68F OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with AX49 (notched) belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor. Added 0.4 o | 75 | 0.024 | 62.003 | 0.027 | 81.988 | 0.026 | 67.97 | 0.018 | 74.42 | 0.09 | 58.35 | 0.05 | 62.97 | 0.02 | 0.224 | 0.004 | 1.1951 | 0.0031 | 45784 | 78 | 11504 | 128 | 7.081 | 0.02 | 52201 | 795 | 6.451 | 0.098 | -9.79 | 1.66 | 230.5 | 1 | 230.5 | 1 | 229.5 | 1 | 27.3 | 0.1 | 24 | 0.1 | 27.4 | 0.1 | 6254.4 | 43.5 | 3501.8 | 54.4 | 1837.4 | 33.2 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.1 |  | 6.1 |  | 0.53 | 230 |  | 230 |  | 230 |  | 11 |  | 10.2 |  | 9.7 |  | 3310 |  | 0.81 | 230 | 230 | 230 | 9.4 | 8.2 | 8.9 | 2670 | 0.76 | [8 empty] | 8100 | [14 empty] | 249.17 | 0.23 | 84.85 | 0.05 |  |  | 31.96 | 0.05 | 259.93 | 0.22 | 211.38 | 0.06 | 119.91 | 0.06 | 91.47 | 0.1 | 245.88 | 0.39 | 85.09 | 0.05 | 115.84 | 0.11 | 30.75 | 0.11 | [8 empty] | 55.79 | 0.11 | 71.9 | 0.04 | 30.42 | 0.08 | 41.49 | 0.1 | 254.21 | 9.92 | 34.86 | 0.01 | 52201 | 795 | 20251 | 787 | [18 empty] | 116.81 | 0.07 | 86.38 | 0.04 | [16 empty] | 204.98 | 0.2 | 190.67 | 0.04 | 102.99 | 0.07 | 87.69 | 0.06 | 195.11 | 0.21 |  |  | 11.74 | 0.06 | 194.69 | 0.22 | 88.11 | 0.04 | 99.48 | 0.07 | 11.36 | 0.07 | [6 empty] | 54.61 | 0.05 | 73.58 | 0.04 | 29.49 | 0.04 | 44.09 | 0.06 | 87.62 | 0.06 | 468.91 | 0.43 | 35.79 | 0.01 | 114.95 | 0.01 | 52201 | 795 | 37118 | 34 | [14 empty] | 87.88 | 0.04 | 99.62 | 0.07 | [8 empty] | 58.67 | 0.05 | 58.4 | 0.05 | 58.01 | 0.04 | 58.81 | 0.04 | 58.74 | 0.04 | 58.81 | 0.04 | [18 empty] | 85.09 | 0.05 | [14 empty] | 87.33 | 0.05 | [20 empty] | 85.62 | 0.05 | 87.62 | 0.06 | 86.38 | 0.04 | 87.33 | 0.05 | 72.32 | 0.04 | 73.18 | 0.04 | [12 empty] | 84.94 | 0.06 | 87.88 | 0.05 | 87.82 | 0.05 | [6 empty] | 81.56 | 0.08 | 81.49 | 0.07 | 74.34 | 0.09 | 74.49 | 0.09 | 74.16 | 0.09 | 74.17 | 0.09 | 74.36 | 0.09 | 74.42 | 0.09 |  |  | 74.66 | 0.14 | 74.41 | 0.12 | 74.59 | 0.1 | 74.73 | 0.1 | 78.48 | 0.1 | 75.65 | 0.13 | 74.44 | 0.13 | 74.55 | 0.12 | 77.13 | 0.08 | 75.78 | 0.09 | 75.43 | 0.1 | 74.89 | 0.09 | 76.19 | 0.07 | 76.17 | 0.08 | 75.49 | 0.09 | 72.29 | 0.19 | [30 empty] | 81.43 | 0.09 | 81 | 0.09 | 81.01 | 0.1 | 81.21 | 0.09 | 81.1 | 0.09 | 81.14 | 0.12 | [50 empty] | C8-55-CE3 | 75 | 0.024 | 62.003 | 0.027 | 58.661 | 0.019 | 54.404 | 0.022 | 81.988 | 0.026 | 67.97 | 0.018 | 2554.7 | 3.3 | 2500 | 3.2 | 1.249 | 0.002 | -0.416 | 0.003 | 0.224 | 0.004 | 1.1951 | 0.0031 | 29.302 | 0.001 | 8092 | 18 | 1510 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.3921 | 11674.119 | 366.8323 | 22.4521 | 97.9861 | 11576.1329 | 0.0088039 | 27.6485 | 57.2689 | 13.7481 | 13.1301 | 0.011324 | 32.1038 | 0.0087826 | 27.6108 | 0.0079892 | 22.7632 | 75.0589 | 62.0564 | 22.4242 | 60989.3849 | 49843.9998 | 6582 | 0.36833 | 57087.7535 | 45942.3684 | 7.0548 | 0.29096 | -5.2243 | -17.7901 | 49.9684 | 60989.3849 | 56591 | 3958.1374 | 440.2475 | 60989.3849 | 100%
3 | 3-NC-2500-95 | 75N0057 | 3-NC-2500-95 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/15/2013 | 8:39:17 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.6 | 1.4 | 29.7 | 0 | 41965 | 80 | 41309 | 147 | 6462 | 91 | 48433 | 92 | 5.2915 | 899.6 |  |  |  | 114.56 | 0.01 | 13.46 | [32 empty] | NC (add 0.4 oz. Nitrogen) CK1, 2500 cfm, 75/62 ID, 95/75F OD | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: Unsealed cabinet/Economizer: Sealed ductwork: 7` blower pulley with AX49 (notched) belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 75%: Horiz airflow disch config. set on floor. Added 0.4 o | 75.001 | 0.015 | 62.001 | 0.024 | 94.996 | 0.017 | 75.005 | 0.025 | 74.53 | 0.06 | 59.74 | 0.04 | 63.95 | 0.02 | 0.211 | 0.003 | 1.1995 | 0.0026 | 41965 | 80 | 6462 | 91 | 5.292 | 0.014 | 55979 | 850 | 6.116 | 0.093 | 13.46 | 1.32 | 230.6 | 1.1 | 230.5 | 1.1 | 229.5 | 1.1 | 29.7 | 0.1 | 26.3 | 0.1 | 29.6 | 0.1 | 6829.4 | 43.7 | 3562.8 | 54.4 | 2323.3 | 34 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.1 |  | 6.1 |  | 0.54 | 230 |  | 230 |  | 230 |  | 12.3 |  | 11.4 |  | 10.9 |  | 3860 |  | 0.84 | 230 | 230 | 230 | 10.5 | 9.2 | 9.9 | 3180 | 0.81 | [8 empty] | 9160 | [14 empty] | 293.68 | 0.25 | 98.78 | 0.05 |  |  | 30.31 | 0.04 | 304.78 | 0.22 | 225.45 | 0.06 | 131.95 | 0.05 | 93.51 | 0.08 | 290.23 | 0.35 | 98.99 | 0.04 | 128.19 | 0.09 | 29.2 | 0.08 | [8 empty] | 62.96 | 0.1 | 73.76 | 0.04 | 35.82 | 0.07 | 37.94 | 0.08 | 303.38 | 11.2 | 39.16 | 0.01 | 55979 | 850 | 22878 | 847 | [18 empty] | 129.09 | 0.06 | 99.1 | 0.07 | [16 empty] | 249.32 | 0.21 | 207.92 | 0.04 | 116.85 | 0.06 | 91.07 | 0.05 | 239.19 | 0.21 |  |  | 12.06 | 0.04 | 238.6 | 0.21 | 102.07 | 0.03 | 113.66 | 0.06 | 11.59 | 0.06 | [6 empty] | 61.83 | 0.05 | 77.81 | 0.04 | 35 | 0.04 | 42.81 | 0.05 | 101.72 | 0.06 | 509.31 | 0.4 | 40.13 | 0.01 | 115.32 | 0.01 | 55979 | 850 | 38296 | 29 | [14 empty] | 101.78 | 0.04 | 113.84 | 0.06 | [8 empty] | 59.74 | 0.06 | 59.65 | 0.05 | 59.55 | 0.04 | 59.95 | 0.08 | 59.87 | 0.07 | 59.93 | 0.06 | [18 empty] | 98.99 | 0.04 | [12 empty] | 100.47 | 0.06 | 101.47 | 0.05 | [20 empty] | 99.53 | 0.05 | 101.72 | 0.06 | 100.47 | 0.06 | 101.47 | 0.05 | 74.38 | 0.05 | 77.41 | 0.03 | [12 empty] | 98.96 | 0.07 | 101.96 | 0.07 | 101.85 | 0.06 | [6 empty] | 94.83 | 0.12 | 94.55 | 0.08 | 74.3 | 0.07 | 74.4 | 0.06 | 74.23 | 0.1 | 74.23 | 0.09 | 74.39 | 0.07 | 74.44 | 0.07 |  |  | 75.65 | 0.17 | 74.84 | 0.13 | 74.87 | 0.11 | 75.02 | 0.08 | 86.49 | 0.19 | 78.76 | 0.21 | 74.86 | 0.16 | 74.88 | 0.14 | 83.26 | 0.16 | 77.96 | 0.1 | 77.15 | 0.11 | 76 | 0.08 | 80.34 | 0.1 | 79.39 | 0.09 | 77.71 | 0.1 | 74.81 | 0.24 | [30 empty] | 94.65 | 0.11 | 94.33 | 0.11 | 94.35 | 0.12 | 94.5 | 0.11 | 94.34 | 0.1 | 94.3 | 0.12 | [50 empty] | C8-55-CE3 | 75.001 | 0.015 | 62.001 | 0.024 | 59.98 | 0.022 | 55.653 | 0.024 | 94.996 | 0.017 | 75.005 | 0.025 | 2563.1 | 2.8 | 2500 | 2.7 | 1.239 | 0.002 | -0.418 | 0.002 | 0.211 | 0.003 | 1.1995 | 0.0026 | 29.281 | 0.001 | 9153 | 17 | 1510 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.395 | 11679.9475 | 363.8953 | 22.7921 | 96.9885 | 11582.959 | 0.0088238 | 27.697 | 58.585 | 14.0999 | 13.1667 | 0.013926 | 38.162 | 0.008781 | 27.6093 | 0.008396 | 23.5269 | 75.1686 | 62.1257 | 23.1869 | 52677.0674 | 46486.9387 | 7643 | 0.4952 | 48765.4119 | 42575.2833 | 5.3278 | 0.28859 | -4.51 | -16.5836 | 51.8578 | 52677.0674 | 47682.3283 | 3971.2496 | 1023.4895 | 52677.0674 | 100%
3 | 3-282 | 75N0062 | 3-282 | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 6:33:09 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 26 | 0 | 52216 | 105 | 52972 | 261 | 13243 | 143 | 65471 | 132 | 8.4533 |  |  |  |  | 111.92 | 0.04 | 17.53 | [32 empty] | 83% Airflow Both Stages, Economizer, Closed Damper | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.001 | 0.016 | 62 | 0.032 | 81.992 | 0.024 | 68.004 | 0.019 | 74.86 | 0.11 | 56.14 | 0.05 | 61.09 | 0.03 | 0.068 | 0.002 | 0.9245 | 0.0018 | 52216 | 105 | 13243 | 143 | 8.454 | 0.037 | 79387 | 55 | 10.251 | 0.04 | 17.53 | 0.17 | 230.2 | 0.8 | 229.7 | 0.8 | 229.8 | 0.8 | 26 | 0.1 | 23.7 | 0.1 | 26.8 | 0.1 | 5948.5 | 35.4 | 3592.4 | 42.4 | 1796.3 | 29.2 | 230.6 |  | 229.4 |  | 230.2 |  | 6.4 |  | 6.3 |  | 6.2 |  | 0.55 | 228.7 |  | 228.5 |  | 229.3 |  | 9.8 |  | 9.4 |  | 9 |  | 2890 |  | 0.77 | 229.7 | 228.7 | 228.2 | 9.4 | 8.5 | 9 | 2720 | 0.77 | [8 empty] | 7810 | [22 empty] | 226.94 | 0.18 | 171.49 | 0.09 | 110.08 | 0.06 | 61.41 | 0.11 | 208.06 | 0.17 | 87.77 | 0.06 | 104 | 0.06 | 16.23 | 0.03 | [8 empty] | 69.35 | 0.06 | 60.65 | 0.21 | 40.31 | 0.04 | 20.33 | 0.22 | 601.07 | 0.45 | 35.68 | 0.02 | 79387 | 55 | 45821 | 41 | [38 empty] | 210.07 | 0.21 | 188.81 | 0.04 | 104.66 | 0.07 | 84.15 | 0.07 | [6 empty] | 198.98 | 0.21 | 89.04 | 0.04 | 100.94 | 0.07 | 11.91 | 0.07 | [6 empty] | 58.02 | 0.06 | 73.78 | 0.06 | 32.12 | 0.05 | 41.66 | 0.08 | 88.15 | 0.05 | 493.03 | 0.46 | 36.07 | 0.01 | 114.81 | 0.01 | 79387 | 55 | 38822 | 37 | [26 empty] | 56.02 | 0.05 | 56.02 | 0.04 | 56.46 | 0.04 | 56.36 | 0.05 | 56.34 | 0.06 | 56.43 | 0.05 | [18 empty] | 87.77 | 0.06 | [12 empty] | 88.7 | 0.05 | 88.01 | 0.06 | [20 empty] | 87.99 | 0.05 | 88.15 | 0.05 |  |  |  |  | 62.13 | 0.19 | 73.64 | 0.05 | [24 empty] | 81.35 | 0.1 | 81.89 | 0.09 | 75.23 | 0.07 | 75.4 | 0.07 | 75.01 | 0.07 | 74.99 | 0.08 | 75.11 | 0.07 | 75.16 | 0.07 |  |  | 75.59 | 0.06 | 75.32 | 0.07 | 75.43 | 0.07 | 75.3 | 0.06 | 79.26 | 0.06 | 75.62 | 0.07 | 75.23 | 0.07 | 75.32 | 0.07 | 76.91 | 0.06 | 76.86 | 0.06 | 75.75 | 0.07 | 75.82 | 0.07 | 77.2 | 0.05 | 76.46 | 0.07 | 75.84 | 0.06 | 75.44 | 0.07 | [30 empty] | 81.81 | 0.1 | 81.45 | 0.09 | 81.58 | 0.1 | 81.61 | 0.1 | 81.96 | 0.07 | 82.01 | 0.11 | [50 empty] | C8-55-CE3 | 75.001 | 0.016 | 62 | 0.032 | 56.545 | 0.028 | 53.315 | 0.03 | 81.992 | 0.024 | 68.004 | 0.019 | 2575.3 | 2.6 | 2522.8 | 2.5 | 1.211 | 0.002 | -0.522 | 0.003 | 0.068 | 0.002 | 0.9245 | 0.0018 | 29.234 | 0.001 | 7745 | 31 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.481 | 11817.2881 | 358.9154 | 25.1507 | 109.7611 | 11707.527 | 0.0088042 | 27.6506 | 55.064 | 13.7484 | 13.0756 | 0.011348 | 32.1317 | 0.0087804 | 27.6086 | 0.0078762 | 22.1251 | 75.0662 | 62.0595 | 21.7645 | 69557.9753 | 56729.4438 | 6155 | 0.30201 | 65356.2834 | 52527.752 | 8.4385 | 0.20486 | -5.8861 | -20.0023 | 49.9107 | 69557.9753 | 64799.8521 | 4261.6652 | 496.4579 | 69557.9753 | 100%
3 | 3-2821 | 75N0063 | 3-2821. | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 7:38:23 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 26 | 0 | 50907 | 88 | 51832 | 223 | 11375 | 200 | 62293 | 191 | 8.0337 |  |  |  |  | 112.26 | 0.03 | 21.88 | [32 empty] | 83% Airflow Both Stages, Economizer, Damper 1 finger open (0.74in.) | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% : Damper | 75.001 | 0.015 | 61.995 | 0.04 | 81.996 | 0.02 | 68.012 | 0.021 | 74.95 | 0.1 | 56.69 | 0.05 | 61.48 | 0.03 | 0.109 | 0.005 | 0.9334 | 0.002 | 50907 | 88 | 11375 | 200 | 8.034 | 0.038 | 79744 | 50 | 10.285 | 0.04 | 21.88 | 0.23 | 230.2 | 0.8 | 229.6 | 0.8 | 229.8 | 0.8 | 26 | 0.1 | 23.8 | 0.1 | 26.9 | 0.1 | 5936.6 | 38 | 3604.1 | 46.9 | 1817.2 | 30.9 | 230.6 |  | 229.4 |  | 230.2 |  | 6.4 |  | 6.3 |  | 6.2 |  | 0.55 | 228.7 |  | 228.5 |  | 229.3 |  | 9.8 |  | 9.4 |  | 9 |  | 2890 |  | 0.77 | 229.7 | 228.7 | 228.2 | 9.4 | 8.5 | 9 | 2720 | 0.77 | [8 empty] | 7810 | [22 empty] | 227.61 | 0.18 | 173.03 | 0.08 | 110.29 | 0.05 | 62.75 | 0.1 | 208.62 | 0.16 | 87.79 | 0.06 | 104.19 | 0.05 | 16.4 | 0.03 | [8 empty] | 70.01 | 0.05 | 62.77 | 0.16 | 40.77 | 0.04 | 22 | 0.17 | 602.95 | 0.45 | 35.69 | 0.02 | 79744 | 50 | 46165 | 34 | [38 empty] | 210.06 | 0.16 | 188.97 | 0.04 | 104.67 | 0.05 | 84.3 | 0.06 | [6 empty] | 198.97 | 0.16 | 89.05 | 0.04 | 100.94 | 0.06 | 11.89 | 0.06 | [6 empty] | 58.04 | 0.04 | 74.03 | 0.04 | 32.13 | 0.04 | 41.9 | 0.06 | 88.18 | 0.05 | 492.95 | 0.37 | 36.08 | 0.01 | 114.86 | 0.01 | 79744 | 50 | 38835 | 30 | [26 empty] | 56.65 | 0.05 | 56.58 | 0.05 | 56.94 | 0.04 | 56.96 | 0.05 | 56.92 | 0.05 | 56.99 | 0.05 | [18 empty] | 87.79 | 0.06 | [12 empty] | 88.76 | 0.05 | 88.03 | 0.06 | [20 empty] | 88.04 | 0.06 | 88.18 | 0.05 |  |  |  |  | 63.89 | 0.15 | 73.9 | 0.04 | [24 empty] | 81.43 | 0.08 | 81.93 | 0.08 | 75.25 | 0.06 | 75.39 | 0.06 | 75.17 | 0.06 | 75.09 | 0.06 | 75.18 | 0.06 | 75.21 | 0.06 |  |  | 75.83 | 0.09 | 75.52 | 0.08 | 75.53 | 0.08 | 75.51 | 0.08 | 78.06 | 0.06 | 76.88 | 0.11 | 75.67 | 0.1 | 75.6 | 0.09 | 76.88 | 0.06 | 77.29 | 0.06 | 77.41 | 0.06 | 77.47 | 0.06 | 76.78 | 0.05 | 76.55 | 0.05 | 77.21 | 0.05 | 77.16 | 0.06 | [30 empty] | 80.4 | 0.07 | 80.08 | 0.07 | 80.39 | 0.07 | 80.47 | 0.08 | 80.7 | 0.08 | 80.73 | 0.1 | [50 empty] | C8-55-1FE3 | 75.001 | 0.015 | 61.995 | 0.04 | 57.068 | 0.023 | 53.798 | 0.032 | 81.996 | 0.02 | 68.012 | 0.021 | 2588.1 | 2.8 | 2534.3 | 2.8 | 1.162 | 0.002 | -0.427 | 0.005 | 0.109 | 0.005 | 0.9334 | 0.002 | 29.248 | 0 | 7754 | 30 | 1590 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4909 | 11862.9683 | 345.9627 | 253.597 | 1106.7206 | 10756.2477 | 0.0090174 | 28.0279 | 55.5771 | 13.7486 | 13.09 | 0.011353 | 32.1382 | 0.0087771 | 27.605 | 0.0080227 | 22.4117 | 75.6564 | 62.5907 | 22.0486 | 70932.4445 | 57167.7814 | 6164 | 0.29659 | 66686.5451 | 52921.882 | 8.6003 | 0.20685 | -5.9793 | -20.0792 | 50.3407 | 70932.4445 | 61607.7893 | 4307.6548 | 5017.0004 | 70932.4445 | 100%
3 | 3-2822 | 75N0064 | 3-2822. | 2 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 20:37:33 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 25.8 | 0 | 49727 | 56 | 50729 | 205 | 10167 | 98 | 59904 | 118 | 7.7707 |  |  |  |  | 112.76 | 0.01 | 24.24 | [32 empty] | 83.3% Airflow Both Stages 2 Fingers (1.289") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.997 | 0.011 | 61.979 | 0.012 | 81.994 | 0.015 | 67.993 | 0.018 | 74.99 | 0.08 | 57.13 | 0.05 | 61.76 | 0.02 | 0.128 | 0.003 | 0.9383 | 0.0019 | 49727 | 56 | 10167 | 98 | 7.771 | 0.033 | 79070 | 62 | 10.257 | 0.039 | 24.24 | 0.17 | 230.2 | 0.8 | 229.6 | 0.8 | 229.8 | 0.8 | 25.8 | 0.1 | 23.7 | 0.1 | 26.8 | 0.1 | 5905.7 | 35.3 | 3606.6 | 43 | 1803.4 | 29.7 | 231 |  | 228 |  | 228 |  | 6.3 |  | 6.4 |  | 6.3 |  | 0.55 | 227 |  | 229 |  | 230 |  | 9.8 |  | 9.3 |  | 9 |  | 2880 |  | 0.78 | 229 | 228 | 230 | 9.3 | 8.4 | 8.9 | 2690 | 0.77 | [8 empty] | 7740 | [22 empty] | 226.51 | 0.18 | 175.18 | 0.05 | 109.94 | 0.06 | 65.24 | 0.04 | 207.83 | 0.18 | 87.81 | 0.06 | 103.92 | 0.06 | 16.11 | 0.05 | [8 empty] | 70 | 0.05 | 65.62 | 0.06 | 40.74 | 0.03 | 24.87 | 0.07 | 598.85 | 0.55 | 35.7 | 0.02 | 79070 | 62 | 46153 | 43 | [38 empty] | 207.61 | 0.16 | 189.62 | 0.05 | 103.85 | 0.05 | 85.78 | 0.04 | [6 empty] | 196.72 | 0.18 | 89.21 | 0.05 | 100.16 | 0.06 | 10.95 | 0.06 | [6 empty] | 56.88 | 0.05 | 74.43 | 0.03 | 31.23 | 0.04 | 43.2 | 0.04 | 88.37 | 0.05 | 484.49 | 0.37 | 36.12 | 0.01 | 114.98 | 0.01 | 79070 | 62 | 38206 | 30 | [26 empty] | 57.02 | 0.04 | 56.99 | 0.04 | 57.02 | 0.03 | 57.54 | 0.04 | 57.49 | 0.04 | 57.55 | 0.04 | [18 empty] | 87.81 | 0.06 | [12 empty] | 88.77 | 0.05 | 88.21 | 0.07 | [20 empty] | 88.04 | 0.07 | 88.37 | 0.05 |  |  |  |  | 66.83 | 0.05 | 74.27 | 0.03 | [24 empty] | 81.24 | 0.09 | 81.98 | 0.08 | 75.26 | 0.06 | 75.41 | 0.05 | 75.11 | 0.06 | 75.06 | 0.06 | 75.16 | 0.05 | 75.2 | 0.05 |  |  | 75.85 | 0.1 | 75.51 | 0.08 | 75.52 | 0.06 | 75.5 | 0.06 | 77.27 | 0.05 | 76.2 | 0.12 | 75.8 | 0.11 | 75.75 | 0.09 | 77.48 | 0.07 | 77.34 | 0.06 | 77.84 | 0.07 | 78.15 | 0.06 | 77.04 | 0.05 | 77.05 | 0.06 | 77.55 | 0.06 | 77.73 | 0.06 | [30 empty] | 80.46 | 0.08 | 80.05 | 0.07 | 80.43 | 0.08 | 80.55 | 0.08 | 80.83 | 0.08 | 80.92 | 0.1 | [50 empty] | C8-55-2FE3 | 74.997 | 0.011 | 61.979 | 0.012 | 57.492 | 0.01 | 54.137 | 0.013 | 81.994 | 0.015 | 67.993 | 0.018 | 2597.6 | 2.7 | 2537.9 | 2.6 | 1.144 | 0.002 | -0.381 | 0.004 | 0.128 | 0.003 | 0.9383 | 0.0019 | 29.202 | 0.001 | 7709 | 29 | 1560 |  | 0.1172 | 290.407 | 13.03 | 0.325 | 1.4567 | 11896.1074 | 341.0874 | 322.9847 | 1409.5512 | 10486.5562 | 0.0090722 | 28.1302 | 56.0353 | 13.7484 | 13.1014 | 0.01134 | 32.1226 | 0.0087675 | 27.5935 | 0.0081137 | 22.6138 | 75.8295 | 62.7339 | 22.259 | 69844.5316 | 56513.6519 | 6149 | 0.30048 | 65684.3828 | 52353.5031 | 8.5205 | 0.21417 | -5.8712 | -19.7942 | 50.6408 | 69844.5316 | 59239.2141 | 4221.3568 | 6383.9608 | 69844.5316 | 100%
3 | 3-2823 | 75N0065 | 3-2823. | 3 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 18:46:02 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 25.9 | 0 | 48533 | 67 | 49561 | 182 | 8856 | 56 | 57398 | 92 | 7.4417 |  |  |  |  | 112.97 | 0.01 | 27.67 | [32 empty] | 83.3% Airflow Both Stages 3 Fingers (1.972") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.002 | 0.01 | 62.04 | 0.006 | 81.997 | 0.015 | 67.99 | 0.013 | 74.98 | 0.07 | 57.58 | 0.02 | 62.12 | 0.02 | 0.161 | 0.002 | 0.9463 | 0.0019 | 48533 | 67 | 8856 | 56 | 7.441 | 0.031 | 79353 | 58 | 10.288 | 0.039 | 27.67 | 0.14 | 230.2 | 0.8 | 229.6 | 0.8 | 229.7 | 0.8 | 25.9 | 0.1 | 23.7 | 0.1 | 26.7 | 0.1 | 5925.1 | 36.8 | 3591.3 | 46.8 | 1788.4 | 30 | 228 |  | 229 |  | 229 |  | 6.3 |  | 6.4 |  | 6.3 |  | 0.55 | 229 |  | 230 |  | 230 |  | 9.9 |  | 9.2 |  | 9.1 |  | 2880 |  | 0.78 | 230 | 229 | 229 | 9.3 | 8.4 | 8.9 | 2690 | 0.76 | [8 empty] | 7730 | [22 empty] | 226.69 | 0.17 | 176.02 | 0.05 | 109.99 | 0.05 | 66.02 | 0.05 | 207.96 | 0.17 | 87.71 | 0.05 | 103.96 | 0.06 | 16.26 | 0.03 | [8 empty] | 70.37 | 0.04 | 66.87 | 0.05 | 41 | 0.03 | 25.87 | 0.06 | 599.98 | 0.49 | 35.66 | 0.02 | 79353 | 58 | 46380 | 37 | [38 empty] | 207.56 | 0.19 | 189.71 | 0.04 | 103.83 | 0.06 | 85.88 | 0.06 | [6 empty] | 196.65 | 0.2 | 89.13 | 0.04 | 100.14 | 0.07 | 11.01 | 0.06 | [6 empty] | 56.96 | 0.05 | 74.69 | 0.03 | 31.29 | 0.04 | 43.4 | 0.06 | 88.27 | 0.06 | 484.8 | 0.42 | 36.1 | 0.01 | 115.02 | 0.01 | 79353 | 58 | 38263 | 33 | [26 empty] | 57.43 | 0.03 | 57.46 | 0.03 | 57.52 | 0.03 | 57.91 | 0.02 | 57.87 | 0.02 | 57.94 | 0.03 | [18 empty] | 87.71 | 0.05 | [12 empty] | 88.67 | 0.05 | 88.11 | 0.06 | [20 empty] | 87.93 | 0.05 | 88.27 | 0.06 |  |  |  |  | 68.13 | 0.04 | 74.49 | 0.03 | [24 empty] | 81.13 | 0.07 | 81.89 | 0.07 | 75.2 | 0.05 | 75.37 | 0.05 | 75.09 | 0.04 | 75.05 | 0.04 | 75.14 | 0.04 | 75.18 | 0.04 |  |  | 75.9 | 0.05 | 75.52 | 0.05 | 75.5 | 0.05 | 75.46 | 0.05 | 77.04 | 0.04 | 76.45 | 0.06 | 76.17 | 0.06 | 75.9 | 0.06 | 77.8 | 0.05 | 78 | 0.05 | 78.56 | 0.06 | 78.96 | 0.06 | 77.25 | 0.04 | 77.28 | 0.05 | 78.25 | 0.05 | 78.36 | 0.06 | [30 empty] | 80.35 | 0.08 | 79.97 | 0.08 | 80.33 | 0.08 | 80.45 | 0.08 | 80.87 | 0.08 | 80.97 | 0.1 | [50 empty] | C8-55-3FE3 | 75.002 | 0.01 | 62.04 | 0.006 | 57.965 | 0.012 | 54.59 | 0.009 | 81.997 | 0.015 | 67.99 | 0.013 | 2610.3 | 2.6 | 2547.1 | 2.6 | 1.118 | 0.002 | -0.318 | 0.002 | 0.161 | 0.002 | 0.9463 | 0.0019 | 29.188 | 0 | 7713 | 29 | 1550 |  | 0.17753 | 447.8183 | 13.029 | 0.274 | 1.4469 | 11942.3111 | 334.5437 | 495.5774 | 2162.7625 | 9779.5486 | 0.0092647 | 28.4493 | 56.5181 | 13.7485 | 13.1145 | 0.011337 | 32.1201 | 0.0088065 | 27.6375 | 0.0082593 | 22.8872 | 76.2736 | 63.176 | 22.5347 | 70634.2217 | 56622.3416 | 6163 | 0.29779 | 66485.8694 | 52473.9894 | 8.62 | 0.21613 | -5.9146 | -19.7555 | 51.071 | 70634.2217 | 56728.9151 | 4210.5035 | 9694.8031 | 70634.2217 | 100%
3 | 3-282OD | 75N0066 | 3-282OD | open | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/24/2013 | 17:24:20 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.2 | 25.8 | 0 | 42929 | 102 | 44001 | 176 | 939 | 130 | 43868 | 192 | 5.7135 |  |  |  |  | 113.69 | 0.01 | 45.23 | [32 empty] | 83.3% airflow both stages economizer fully open (5.047") | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.999 | 0.01 | 62.009 | 0.012 | 81.98 | 0.03 | 67.991 | 0.012 | 75.04 | 0.06 | 59.15 | 0.04 | 63.31 | 0.02 | 0.084 | 0.004 | 0.9082 | 0.0023 | 42929 | 102 | 939 | 130 | 5.714 | 0.034 | 80102 | 68 | 10.432 | 0.04 | 45.23 | 0.25 | 230.3 | 0.8 | 229.6 | 0.8 | 229.7 | 0.8 | 25.8 | 0.1 | 23.7 | 0.1 | 26.6 | 0.1 | 5904.8 | 39.4 | 3593.3 | 46.8 | 1773.2 | 31.4 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.4 |  | 6.1 |  | 0.54 | 230 |  | 230 |  | 230 |  | 9.8 |  | 9.3 |  | 8.9 |  | 2870 |  | 0.77 | 230 | 230 | 230 | 9.3 | 8.4 | 8.9 | 2680 | 0.77 | [8 empty] | 7680 | [22 empty] | 226.7 | 0.26 | 178.84 | 0.06 | 110 | 0.08 | 68.85 | 0.05 | 207.83 | 0.25 | 87.36 | 0.07 | 103.92 | 0.08 | 16.56 | 0.04 | [8 empty] | 71.48 | 0.07 | 71.28 | 0.06 | 41.75 | 0.05 | 29.53 | 0.06 | 602.29 | 0.58 | 35.56 | 0.02 | 80102 | 68 | 47058 | 41 | [38 empty] | 207.1 | 0.24 | 189.43 | 0.08 | 103.67 | 0.08 | 85.76 | 0.06 | [6 empty] | 196.26 | 0.25 | 88.87 | 0.06 | 100 | 0.09 | 11.13 | 0.07 | [6 empty] | 56.97 | 0.06 | 74.77 | 0.05 | 31.29 | 0.05 | 43.48 | 0.06 | 88.12 | 0.08 | 485.13 | 0.49 | 36.02 | 0.02 | 115.04 | 0.01 | 80102 | 68 | 38335 | 38 | [26 empty] | 59.35 | 0.04 | 59.2 | 0.05 | 59.37 | 0.05 | 59.44 | 0.05 | 59.4 | 0.04 | 59.46 | 0.05 | [18 empty] | 87.36 | 0.07 | [12 empty] | 88.4 | 0.07 | 87.91 | 0.08 | [20 empty] | 87.61 | 0.07 | 88.12 | 0.08 |  |  |  |  | 72.3 | 0.06 | 74.57 | 0.05 | [24 empty] | 80.83 | 0.09 | 81.94 | 0.1 | 75.14 | 0.04 | 75.3 | 0.04 | 75.07 | 0.05 | 75.1 | 0.05 | 75.19 | 0.04 | 75.22 | 0.04 |  |  | 75.85 | 0.11 | 76.29 | 0.08 | 76.97 | 0.08 | 77.08 | 0.08 | 77.35 | 0.1 | 78.61 | 0.13 | 79.16 | 0.14 | 79.56 | 0.16 | 78.06 | 0.09 | 78.34 | 0.08 | 79.27 | 0.1 | 80.77 | 0.11 | 78.67 | 0.09 | 78.68 | 0.08 | 78.78 | 0.09 | 79.66 | 0.1 | [30 empty] | 79.07 | 0.1 | 78.73 | 0.1 | 79.89 | 0.11 | 79.87 | 0.11 | 80.78 | 0.12 | 80.95 | 0.16 | [50 empty] | C8-55-OE3 | 74.999 | 0.01 | 62.009 | 0.012 | 59.501 | 0.026 | 56.25 | 0.026 | 81.98 | 0.03 | 67.991 | 0.012 | 2560.4 | 3.2 | 2489.6 | 3.1 | 0.784 | 0.002 | -0.085 | 0.007 | 0.084 | 0.004 | 0.9082 | 0.0023 | 29.187 | 0.001 | 7678 | 30 | 1520 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.5717 | 11675.1953 | 229.3035 | 909.1447 | 3967.7357 | 7707.4596 | 0.0096549 | 29.1465 | 57.9293 | 13.7481 | 13.1582 | 0.011341 | 32.1212 | 0.0087868 | 27.6151 | 0.008859 | 23.9137 | 77.3787 | 64.1303 | 23.5303 | 65570.0396 | 54498.0576 | 6158 | 0.32053 | 61164.8926 | 50092.9106 | 7.9663 | 0.19376 | -5.6162 | -19.4494 | 53.2553 | 65570.0396 | 43215.2424 | 4476.0319 | 17878.7653 | 65570.0396 | 100%
3 | 1-1CH Retest | 75N0067 | 1-1CH Retest | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/1/2013 | 9:33:46 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.4 | 15.7 | 0 | 34837 | 60 | 33993 | 159 | 14331 | 126 | 49182 | 134 | 11.7128 |  |  |  |  | 113.36 | 0.01 | -29.94 | [32 empty] | Econo Closed 1st Stage 55/51 Ambient | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor:VFD at 25.02% | 75 | 0.009 | 61.998 | 0.047 | 54.998 | 0.016 | 50.996 | 0.015 | 74.45 | 0.05 | 62.47 | 0.03 | 65.77 | 0.01 | 0.142 | 0.002 | 0.9322 | 0.002 | 34837 | 60 | 14331 | 126 | 11.713 | 0.085 | 37851 | 42 | 9.015 | 0.061 | -29.94 | 0.36 | 230.5 | 0.9 | 231.8 | 0.9 | 229.5 | 0.9 | 15.7 | 0.1 | 12.9 | 0.1 | 16.5 | 0.1 | 3563.9 | 32.1 | 2198.2 | 34.8 | 634.7 | 25.1 | 230.2 |  | 229.8 |  | 230.9 |  | 6.5 |  | 6.1 |  | 6.3 |  | 0.52 | 231.4 |  | 228.7 |  | 230.1 |  | 8.5 |  | 7.8 |  | 6.8 |  | 2003 |  | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4183 | [22 empty] | 148.36 | 0.19 | 149.7 | 0.03 | 81.87 | 0.08 | 67.83 | 0.07 | 130.15 | 0.18 | 58.61 | 0.05 | 73.92 | 0.08 | 15.31 | 0.04 | [8 empty] | 55.95 | 0.07 | 64.72 | 0.04 | 30.54 | 0.05 | 34.19 | 0.07 | 500.28 | 0.55 | 26.99 | 0.02 | 37851 | 42 | 43210 | 42 | [112 empty] | 61.34 | 0.05 | 62.07 | 0.05 | 63.25 | 0.05 | 62.69 | 0.04 | 62.59 | 0.04 | 62.6 | 0.05 | [18 empty] | 58.61 | 0.05 | [12 empty] | 60.25 | 0.06 | [22 empty] | 59.08 | 0.06 | 56.18 | 0.09 | 60.25 | 0.06 | 60.89 | 0.04 | 64.74 | 0.03 | 69.89 | 0.03 | [24 empty] | 54.79 | 0.09 | 54.67 | 0.08 | 74.56 | 0.05 | 74.45 | 0.05 | 74.16 | 0.04 | 73.2 | 0.08 | 65.8 | 0.1 | 68.66 | 0.1 |  |  | 73.59 | 0.07 | 74.11 | 0.06 | 74.13 | 0.06 | 73.29 | 0.06 | 59.48 | 0.14 | 68.65 | 0.18 | 74.25 | 0.05 | 74.27 | 0.05 | 67.94 | 0.35 | 69.33 | 0.17 | 73.52 | 0.1 | 73.54 | 0.07 | 68.6 | 0.13 | 70.03 | 0.11 | 72.4 | 0.17 | 71.57 | 0.1 | [30 empty] | 53.91 | 0.1 | 53.71 | 0.1 | 53.95 | 0.09 | 54.75 | 0.1 | 54.11 | 0.09 | 54.07 | 0.1 | [50 empty] | C8-55-CE3 | 75 | 0.009 | 61.998 | 0.047 | 62.716 | 0.016 | 55.619 | 0.044 | 54.998 | 0.016 | 50.996 | 0.015 | 2594.7 | 2.9 | 2524.7 | 2.8 | 1.205 | 0.002 | -0.446 | 0.002 | 0.142 | 0.002 | 0.9322 | 0.002 | 29.288 | 0.001 | 4199 | 29 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4651 | 11766.677 | 357.4061 | 22.6318 | 104.2183 | 11662.4586 | 0.0087634 | 27.5467 | 61.2509 | 13.0294 | 13.2308 | 0.0069797 | 20.7754 | 0.0087793 | 27.6072 | 0.0077308 | 23.4695 | 74.8234 | 61.9105 | 23.1129 | 52171.2251 | 38328.7433 | 2629 | 0.17199 | 48032.642 | 34190.1602 | 11.4391 | 0.531 | -4.4338 | -13.5725 | 45.8841 | 52171.2251 | 48686.6795 | 4196.5433 | -711.9977 | 52171.2251 | 100%
3 | 1-1EH | 75N0068 | 1-1EH | open | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/27/2013 | 12:08:16 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 0.2 | 15.2 | 0 | 55897 | 102 | 57035 | 317 | 27721 | 228 | 83644 | 275 | 19.8916 |  |  |  |  | 111.66 | 0.02 | -130.85 | [32 empty] | Econo Open 1st Stage 55/51 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.001 | 0.018 | 62 | 0.041 | 55.162 | 0.014 | 51.018 | 0.018 | 75.1 | 0.09 | 54.96 | 0.05 | 60.06 | 0.03 | 0.093 | 0.002 | 0.9126 | 0.002 | 55897 | 102 | 27721 | 228 | 19.89 | 0.153 | 36234 | 77 | 8.616 | 0.061 | -130.85 | 0.95 | 230.4 | 0.7 | 230.5 | 0.7 | 229.6 | 0.7 | 15.2 | 0.1 | 13.4 | 0.1 | 16.4 | 0.1 | 3460.6 | 25 | 2288.4 | 25.7 | 744.8 | 20.8 | 230 |  | 230 |  | 230 |  | 6.5 |  | 6.3 |  | 6.4 |  | 0.53 | 230 |  | 230 |  | 230 |  | 8.3 |  | 7.7 |  | 7.1 |  | 2040 |  | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4200 | [22 empty] | 147.17 | 0.24 | 142.28 | 0.06 | 81.36 | 0.1 | 60.91 | 0.09 | 129.56 | 0.21 | 58.84 | 0.08 | 73.65 | 0.1 | 14.81 | 0.04 | [8 empty] | 53.09 | 0.09 | 53.98 | 0.08 | 28.26 | 0.07 | 25.71 | 0.12 | 490.78 | 0.98 | 27.05 | 0.02 | 36234 | 77 | 41525 | 77 | [112 empty] | 53.77 | 0.07 | 54.2 | 0.07 | 55.53 | 0.07 | 56.03 | 0.05 | 55.79 | 0.06 | 55.62 | 0.06 | [18 empty] | 58.84 | 0.08 | [12 empty] | 59.39 | 0.07 | 59.96 | 0.06 | [20 empty] | 59.05 | 0.08 | 62.86 | 0.83 |  |  |  |  | 54.26 | 0.07 | 69.46 | 0.18 | [24 empty] | 55.19 | 0.15 | 54.72 | 0.06 | 75.19 | 0.07 | 75.05 | 0.07 | 74.8 | 0.07 | 74.86 | 0.07 | 74.83 | 0.07 | 74.83 | 0.08 |  |  | 73.17 | 0.09 | 70.36 | 0.12 | 68.26 | 0.14 | 67.05 | 0.23 | 66.49 | 0.26 | 59.72 | 0.27 | 59.16 | 0.27 | 60.86 | 0.53 | 60.34 | 0.23 | 59.85 | 0.16 | 57.61 | 0.14 | 55.95 | 0.21 | 57.66 | 0.17 | 58.1 | 0.22 | 58.99 | 0.2 | 57.63 | 0.19 | [30 empty] | 58.26 | 0.19 | 58.46 | 0.19 | 56.42 | 0.15 | 56.49 | 0.18 | 55.17 | 0.14 | 55.36 | 0.19 | [50 empty] | C8-55-OE3 | 75.001 | 0.018 | 62 | 0.041 | 55.273 | 0.032 | 50.544 | 0.034 | 55.162 | 0.014 | 51.018 | 0.018 | 2553.5 | 2.8 | 2514.3 | 2.8 | 0.784 | 0.002 | -0.085 | 0.002 | 0.093 | 0.002 | 0.9126 | 0.002 | 29.267 | 0.001 | 4205 | 29 | 1550 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.5946 | 11754.6083 | 231.5785 | 885.1988 | 4075.0688 | 7679.5395 | 0.0081468 | 25.2434 | 53.6784 | 13.0334 | 13.034 | 0.0069528 | 20.7861 | 0.0087804 | 27.6086 | 0.0066761 | 20.5127 | 68.1382 | 58.4575 | 20.1252 | 60162.1344 | 40792.5852 | 2655 | 0.15062 | 55662.3619 | 36292.8127 | 13.2372 | 0.48549 | -5.1182 | -14.4598 | 40.0345 | 60162.1344 | 83410.2524 | 4554.0132 | -27802.1312 | 60162.1344 | 100%
3 | 1-2CH Retest | 75N0069 | 1-2CH retest | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/1/2013 | 14:26:06 | 10 Ton | 0:30:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230.8 | 0.2 | 23.4 | 0 | 58384 | 122 | 57669 | 344 | 21618 | 253 | 80023 | 282 | 13.2226 |  |  |  |  | 113.46 | 0.02 | -10.73 | [32 empty] | Econo Closed 2 Stages 55/51 Ambient | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor:VFD at 25.02% | 74.977 | 0.046 | 61.979 | 0.062 | 54.993 | 0.02 | 51.01 | 0.015 | 74.47 | 0.14 | 54.32 | 0.07 | 59.55 | 0.05 | 0.12 | 0.003 | 0.9348 | 0.0023 | 58384 | 122 | 21618 | 253 | 13.223 | 0.081 | 72263 | 167 | 11.941 | 0.063 | -10.73 | 0.29 | 230.8 | 0.8 | 230.7 | 0.8 | 229.2 | 0.8 | 23.4 | 0.1 | 20 | 0.1 | 23.4 | 0.1 | 5274.8 | 39.6 | 3351.3 | 46.5 | 777.1 | 32.1 | 230 |  | 230 |  | 230 |  | 6.6 |  | 6.2 |  | 6.2 |  | 0.52 | 230 |  | 230 |  | 230 |  | 8.4 |  | 7.6 |  | 7.2 |  | 2010 |  | 0.67 | 230 | 230 | 230 | 8 | 6.7 | 7.3 | 1880 | 0.64 | [8 empty] | 6060 | [22 empty] | 148.69 | 0.12 | 150.36 | 0.07 | 82 | 0.05 | 68.37 | 0.08 | 130.75 | 0.11 | 59.34 | 0.04 | 74.19 | 0.05 | 14.84 | 0.03 | [8 empty] | 55.82 | 0.06 | 65.31 | 0.08 | 30.42 | 0.05 | 34.89 | 0.1 | 495.66 | 0.37 | 27.2 | 0.01 | 72263 | 167 | 42758 | 31 | [38 empty] | 134.57 | 0.24 | 151.62 | 0.64 | 75.9 | 0.11 | 75.69 | 0.57 | [6 empty] | 124.46 | 0.18 | 60.36 | 0.04 | 71.27 | 0.09 | 10.91 | 0.08 | [6 empty] | 43.95 | 0.2 | 59.81 | 1.43 | 20.43 | 0.17 | 39.31 | 1.24 | 58.88 | 0.05 | 407.11 | 0.86 | 27.5 | 0.01 | 113.14 | 0.23 | 72263 | 167 | 34866 | 160 | [26 empty] | 54.91 | 0.07 | 53.81 | 0.08 | 52.62 | 0.15 | 55.76 | 0.09 | 55.67 | 0.08 | 55.65 | 0.08 | [18 empty] | 59.34 | 0.04 | [12 empty] | 60.89 | 0.04 | 59.34 | 0.05 | [20 empty] | 59.6 | 0.05 | 58.88 | 0.05 | 60.89 | 0.04 | 59.34 | 0.05 | 65.25 | 0.08 | 59.52 | 1.42 | [26 empty] | 54.54 | 0.06 | 74.53 | 0.1 | 74.42 | 0.1 | 74.11 | 0.09 | 73.06 | 0.11 | 65.65 | 0.11 | 68.44 | 0.11 |  |  | 73.42 | 0.11 | 74.02 | 0.11 | 74.07 | 0.1 | 72.92 | 0.12 | 59.17 | 0.12 | 68.61 | 0.21 | 74.14 | 0.1 | 74.17 | 0.11 | 66.45 | 0.6 | 68.46 | 0.22 | 73.22 | 0.13 | 73.28 | 0.12 | 67.34 | 0.33 | 69.29 | 0.14 | 71.57 | 0.33 | 70.68 | 0.18 | [30 empty] | 54.12 | 0.03 | 53.94 | 0.03 | 54.07 | 0.03 | 54.1 | 0.03 | 54.14 | 0.03 | 54.12 | 0.04 | [50 empty] | C8-55-CE3 | 74.977 | 0.046 | 61.979 | 0.062 | 54.57 | 0.054 | 51.241 | 0.056 | 54.993 | 0.02 | 51.01 | 0.015 | 2585.2 | 3.2 | 2543.1 | 3.2 | 1.198 | 0.003 | -0.457 | 0.002 | 0.12 | 0.003 | 0.9348 | 0.0023 | 29.234 | 0.001 | 6052 | 29 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4345 | 11912.9994 | 357.9195 | 22.9091 | 105.496 | 11807.5034 | 0.0087564 | 27.5335 | 53.1355 | 13.0294 | 13.0204 | 0.0069883 | 20.7835 | 0.0087722 | 27.5938 | 0.0072108 | 20.9222 | 74.8006 | 61.8917 | 20.5733 | 82916.8351 | 61943.2107 | 4492 | 0.1849 | 78814.1343 | 57840.51 | 13.0228 | 0.2302 | -6.9602 | -21.6651 | 46.6569 | 82916.8351 | 79479.0798 | 4156.2128 | -718.4575 | 82916.8351 | 100%
3 | 2-1CH | 75N0070 | 2-1CH | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/26/2013 | 4:13:24 | 10 Ton | 0:30:00 | 75/62 70/60 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 70 | 60 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.2 | 15.8 | 0 | 29896 | 49 | 29562 | 82 | 11277 | 90 | 41183 | 90 | 8.9606 |  |  |  |  | 113.01 | 0.01 | -2.65 | [32 empty] | Economizer Closed 1st Stage 70/60 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.995 | 0.006 | 62.006 | 0.022 | 70.003 | 0.018 | 60.042 | 0.014 | 74.48 | 0.03 | 63.9 | 0.03 | 67.14 | 0.02 | 0.077 | 0.003 | 0.9132 | 0.002 | 29896 | 49 | 11277 | 90 | 8.961 | 0.059 | 40118 | 28 | 8.729 | 0.054 | -2.65 | 0.23 | 230.3 | 0.7 | 229.8 | 0.7 | 229.7 | 0.7 | 15.8 | 0.1 | 14.4 | 0.1 | 17.1 | 0.1 | 3599.7 | 25.3 | 2353.5 | 28.7 | 996.5 | 21.3 | 230 |  | 231 |  | 229 |  | 6.4 |  | 6.3 |  | 6.1 |  | 0.53 | 231 |  | 229 |  | 228 |  | 9 |  | 8.5 |  | 8.1 |  | 2460 |  | 0.72 | [16 empty] | 4650 | [22 empty] | 188.75 | 0.14 | 162.57 | 0.04 | 97.37 | 0.05 | 65.2 | 0.05 | 170.11 | 0.13 | 73.99 | 0.04 | 90.52 | 0.05 | 16.52 | 0.03 | [8 empty] | 63.86 | 0.04 | 65.11 | 0.04 | 36.43 | 0.03 | 28.68 | 0.06 | 557.24 | 0.38 | 31.52 | 0.01 | 40118 | 28 | 45408 | 28 | [38 empty] | 122.16 | 0.08 | 81.27 | 0.05 | 70.17 | 0.04 | 11.1 | 0.08 | [6 empty] | 121.75 | 0.08 | 82.58 | 0.02 | 69.97 | 0.04 | -12.61 | 0.04 | [6 empty] | 121.5 | 0.08 | 86.95 | 0.02 | 69.85 | 0.04 | 17.09 | 0.04 | 76.45 | 0.58 | -3 | 0 | 34.1 | 0.01 | 113.91 | 0.01 | 40118 | 28 | 0 | 0 | [26 empty] | 62.44 | 0.03 | 62.86 | 0.04 | 64.45 | 0.03 | 63.9 | 0.03 | 63.85 | 0.03 | 64.02 | 0.03 | [18 empty] | 73.99 | 0.04 | [12 empty] | 74.7 | 0.04 | 74.39 | 0.04 | [20 empty] | 74.22 | 0.04 | 76.45 | 0.58 |  |  |  |  | 65.56 | 0.04 | 86.44 | 0.03 | [24 empty] | 69.56 | 0.06 | 69.28 | 0.04 | 74.51 | 0.03 | 74.59 | 0.03 | 74.23 | 0.02 | 74.35 | 0.03 | 74.42 | 0.03 | 74.45 | 0.02 |  |  | 74.16 | 0.05 | 74.46 | 0.04 | 74.63 | 0.05 | 74.34 | 0.04 | 70.54 | 0.05 | 74.01 | 0.06 | 74.49 | 0.06 | 74.61 | 0.06 | 72.24 | 0.05 | 73.71 | 0.04 | 74.57 | 0.04 | 74.69 | 0.03 | 72.38 | 0.05 | 73.52 | 0.04 | 74.18 | 0.04 | 73.62 | 0.05 | [30 empty] | 69.28 | 0.08 | 68.87 | 0.07 | 69.13 | 0.08 | 69.23 | 0.08 | 69.43 | 0.08 | 69.49 | 0.08 | [50 empty] | C8-55-CE3 | 74.995 | 0.006 | 62.006 | 0.022 | 64.294 | 0.015 | 56.665 | 0.021 | 70.003 | 0.018 | 60.042 | 0.014 | 2577.6 | 2.8 | 2488.6 | 2.7 | 1.206 | 0.002 | -0.519 | 0.003 | 0.077 | 0.003 | 0.9132 | 0.002 | 29.153 | 0.001 | 4596 | 28 | 1580 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4975 | 11652.2505 | 352.588 | 24.7798 | 110.7639 | 11541.4866 | 0.0087849 | 27.6005 | 62.7965 | 13.423 | 13.2726 | 0.0086951 | 26.2965 | 0.0087858 | 27.613 | 0.0079724 | 24.1168 | 74.9476 | 61.9877 | 23.7521 | 44842.7088 | 33981.0234 | 3016 | 0.22955 | 40653.5515 | 29791.8662 | 8.8454 | 0.55939 | -3.8484 | -12.1511 | 47.3698 | 44842.7088 | 40738.837 | 4249.697 | -145.8253 | 44842.7088 | 100%
3 | 2-1EH | 75N0071 | 2-1EH | open | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/25/2013 | 22:37:38 | 10 Ton | 0:30:00 | 75/62 70/60 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 70 | 60 | 7.6 | 8.1 | 7.6 | 8.1 | 230.2 | 0.2 | 15.7 | 0 | 35264 | 122 | 35273 | 171 | 12173 | 442 | 47449 | 528 | 10.3465 |  |  |  |  | 112.53 | 0.02 | -19.49 | [32 empty] | Economizer Opened 1st Stage 70/60 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 75.003 | 0.006 | 61.994 | 0.046 | 69.992 | 0.019 | 60.214 | 0.129 | 74.62 | 0.04 | 61.93 | 0.06 | 65.57 | 0.03 | 0.089 | 0.002 | 0.903 | 0.002 | 35264 | 122 | 12173 | 442 | 10.348 | 0.138 | 39713 | 53 | 8.662 | 0.055 | -19.49 | 1.42 | 230.2 | 0.8 | 229.8 | 0.8 | 229.8 | 0.8 | 15.7 | 0.1 | 14.4 | 0.1 | 17.1 | 0.1 | 3579.5 | 25.7 | 2374.6 | 29.6 | 1005.8 | 21.6 | 228 |  | 228 |  | 227 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.52 | 228 |  | 231 |  | 231 |  | 9 |  | 8.5 |  | 8.1 |  | 2450 |  | 0.72 | [16 empty] | 4620 | [22 empty] | 188.53 | 0.21 | 160.47 | 0.08 | 97.29 | 0.07 | 63.18 | 0.07 | 169.92 | 0.2 | 73.97 | 0.06 | 90.44 | 0.07 | 16.47 | 0.04 | [8 empty] | 63.17 | 0.09 | 62.2 | 0.13 | 35.93 | 0.06 | 26.27 | 0.11 | 555.46 | 0.64 | 31.51 | 0.02 | 39713 | 53 | 45003 | 53 | [38 empty] | 120.85 | 0.16 | 82.01 | 0.07 | 69.55 | 0.08 | 12.47 | 0.12 | [6 empty] | 120.18 | 0.08 | 82.3 | 0.07 | 69.22 | 0.04 | -13.09 | 0.08 | [6 empty] | 121.12 | 0.08 | 86.78 | 0.03 | 69.67 | 0.04 | 17.11 | 0.04 | 76.14 | 1.49 | -3 | 0 | 34.02 | 0.02 | 113.9 | 0.01 | 39713 | 53 | 0 | 0 | [26 empty] | 60.72 | 0.07 | 60.73 | 0.07 | 62.38 | 0.06 | 62.07 | 0.06 | 61.99 | 0.06 | 62 | 0.06 | [18 empty] | 73.97 | 0.06 | [12 empty] | 74.78 | 0.04 | 74.5 | 0.05 | [20 empty] | 74.19 | 0.05 | 76.14 | 1.49 |  |  |  |  | 63.35 | 0.12 | 86.3 | 0.03 | [24 empty] | 69.43 | 0.09 | 69.18 | 0.05 | 74.63 | 0.03 | 74.77 | 0.03 | 74.47 | 0.03 | 74.53 | 0.03 | 74.6 | 0.03 | 74.64 | 0.02 |  |  | 73.79 | 0.06 | 73.11 | 0.05 | 72.6 | 0.06 | 72.34 | 0.08 | 72.98 | 0.07 | 70.73 | 0.09 | 70.03 | 0.09 | 70.37 | 0.14 | 70.38 | 0.07 | 70.64 | 0.09 | 70.18 | 0.09 | 69.89 | 0.11 | 69.91 | 0.09 | 70.11 | 0.1 | 70.56 | 0.1 | 70.14 | 0.1 | [30 empty] | 69.95 | 0.11 | 69.73 | 0.1 | 69.38 | 0.09 | 69.46 | 0.09 | 69.4 | 0.1 | 69.49 | 0.13 | [50 empty] | C8-55-OE3 | 75.003 | 0.006 | 61.994 | 0.046 | 62.311 | 0.041 | 55.728 | 0.085 | 69.992 | 0.019 | 60.214 | 0.129 | 2558.9 | 2.9 | 2478.7 | 2.7 | 0.777 | 0.002 | -0.077 | 0.002 | 0.089 | 0.002 | 0.903 | 0.002 | 29.158 | 0 | 4586 | 29 | 1560 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.6329 | 11612.2333 | 226.2612 | 855.0334 | 3821.7692 | 7790.4641 | 0.0087862 | 27.2132 | 60.6781 | 13.4236 | 13.2217 | 0.008807 | 26.416 | 0.008776 | 27.6043 | 0.0078896 | 23.5438 | 73.3537 | 61.4151 | 23.1462 | 47226.8616 | 35326.1217 | 3026 | 0.21868 | 42674.8111 | 30774.0712 | 9.3055 | 0.51128 | -4.067 | -12.6756 | 47.4174 | 47226.8616 | 47150.9832 | 4617.1382 | -4541.2597 | 47226.8616 | 100%
3 | 2-2CH Retest | 75N0072 | 2-2CH Retest | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/30/2013 | 17:50:24 | 10 Ton | 0:30:00 | 75/62 70/60 | ENG 1 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 70 | 60 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 0.2 | 24.6 | 0 | 57495 | 121 | 56550 | 251 | 19919 | 154 | 77433 | 142 | 11.0793 |  |  |  |  | 112.98 | 0.01 | 1.66 | [32 empty] | Economizer Closed 2 Stage 70/60 Ambient | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.999 | 0.023 | 61.993 | 0.033 | 70.003 | 0.019 | 60.017 | 0.024 | 74.39 | 0.09 | 54.43 | 0.05 | 59.74 | 0.02 | 0.076 | 0.002 | 0.9195 | 0.002 | 57495 | 121 | 19919 | 154 | 11.079 | 0.053 | 78741 | 53 | 11.266 | 0.049 | 1.66 | 0.2 | 230.4 | 0.8 | 230 | 0.8 | 229.6 | 0.8 | 24.6 | 0.1 | 22.1 | 0.1 | 25.2 | 0.1 | 5599.3 | 37.9 | 3493.1 | 44 | 1389.9 | 30.5 | 228 |  | 230 |  | 229 |  | 6.5 |  | 6.3 |  | 6.2 |  | 0.55 | 229 |  | 228 |  | 228 |  | 9 |  | 8.4 |  | 9 |  | 2460 |  | 0.73 | 230 | 229 | 228 | 8.7 | 7.7 | 8.2 | 2370 | 0.73 | [8 empty] | 7030 | [22 empty] | 189.36 | 0.15 | 162.92 | 0.03 | 97.58 | 0.05 | 65.34 | 0.06 | 170.8 | 0.14 | 75.38 | 0.05 | 90.78 | 0.06 | 15.4 | 0.03 | [8 empty] | 63.94 | 0.06 | 65.01 | 0.06 | 36.49 | 0.04 | 28.52 | 0.07 | 556.78 | 0.42 | 31.93 | 0.02 | 78741 | 53 | 45127 | 30 | [38 empty] | 179.13 | 0.16 | 172.12 | 0.03 | 93.89 | 0.06 | 78.23 | 0.05 | [6 empty] | 167.95 | 0.17 | 76.4 | 0.04 | 89.69 | 0.06 | 13.28 | 0.06 | [6 empty] | 54.52 | 0.04 | 68.95 | 0.05 | 29.37 | 0.03 | 39.58 | 0.06 | 75.33 | 0.05 | 474.9 | 0.42 | 32.24 | 0.01 | 114.16 | 0.01 | 78741 | 53 | 38903 | 35 | [26 empty] | 54.48 | 0.04 | 54.26 | 0.04 | 53.86 | 0.04 | 55.05 | 0.03 | 54.97 | 0.03 | 54.98 | 0.04 | [18 empty] | 75.38 | 0.05 | [12 empty] | 76.92 | 0.05 | 75.64 | 0.04 | [20 empty] | 75.94 | 0.06 | 75.33 | 0.05 | 76.92 | 0.05 | 75.64 | 0.04 | 65.63 | 0.04 | 68.68 | 0.04 | [24 empty] | 69.88 | 0.09 | 69.75 | 0.06 | 74.53 | 0.05 | 74.44 | 0.06 | 74.11 | 0.05 | 73.99 | 0.05 | 72.51 | 0.05 | 72.86 | 0.05 |  |  | 74.08 | 0.07 | 74.22 | 0.08 | 74.24 | 0.08 | 73.47 | 0.07 | 69.71 | 0.06 | 73.83 | 0.08 | 74.37 | 0.08 | 74.39 | 0.07 | 71.35 | 0.05 | 72.9 | 0.08 | 73.56 | 0.08 | 73.83 | 0.08 | 71.23 | 0.06 | 72.38 | 0.07 | 72.57 | 0.07 | 72.14 | 0.09 | [30 empty] | 68.9 | 0.1 | 68.65 | 0.09 | 68.92 | 0.1 | 68.9 | 0.15 | 69.06 | 0.09 | 69.03 | 0.1 | [50 empty] | C8-55-CE3 | 74.999 | 0.023 | 61.993 | 0.033 | 54.699 | 0.03 | 51.551 | 0.037 | 70.003 | 0.019 | 60.017 | 0.024 | 2567.7 | 2.8 | 2517.9 | 2.8 | 1.221 | 0.002 | -0.538 | 0.003 | 0.076 | 0.002 | 0.9195 | 0.002 | 29.162 | 0.001 | 6989 | 30 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4769 | 11828.4317 | 361.1763 | 25.2291 | 112.7737 | 11715.658 | 0.0087753 | 27.591 | 53.2221 | 13.4229 | 13.0247 | 0.0086793 | 26.2792 | 0.0087762 | 27.6036 | 0.0073466 | 21.1009 | 74.9514 | 61.9745 | 20.7416 | 81017.3135 | 61685.669 | 5399 | 0.22744 | 76823.3382 | 57491.6937 | 10.992 | 0.20809 | -6.8494 | -21.7293 | 47.5124 | 81017.3135 | 76916.9417 | 4249.7307 | -149.3589 | 81017.3135 | 100%
3 | 3-1CH Retest | 75N0074 | 3-1CH Retest | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/1/2013 | 4:11:18 | 10 Ton | 0:30:00 | 75/62 65/57 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 65 | 57 | 7.6 | 8.1 | 7.6 | 8.1 | 230.7 | 0.2 | 15.9 | 0 | 32385 | 63 | 31378 | 139 | 12839 | 125 | 45236 | 116 | 10.1563 |  |  |  |  | 113 | 0.01 | -13.67 | [32 empty] | Econo Closed 1st Stage 65/57 Ambient | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor:VFD at 25.02% | 75.005 | 0.01 | 61.997 | 0.045 | 64.999 | 0.013 | 57.015 | 0.016 | 74.37 | 0.04 | 63.26 | 0.03 | 66.4 | 0.02 | 0.142 | 0.002 | 0.929 | 0.0019 | 32385 | 63 | 12839 | 125 | 10.157 | 0.069 | 39797 | 28 | 8.935 | 0.057 | -13.67 | 0.29 | 230.7 | 0.8 | 230.6 | 0.8 | 229.3 | 0.8 | 15.9 | 0.1 | 13.9 | 0.1 | 16.6 | 0.1 | 3627.9 | 27.1 | 2268 | 29.8 | 826.1 | 22.2 | 230 |  | 231 |  | 229 |  | 6.6 |  | 6.2 |  | 6.2 |  | 0.52 | 228 |  | 228 |  | 229 |  | 9.1 |  | 8.2 |  | 7.6 |  | 2310 |  | 0.71 | [16 empty] | 4500 | [22 empty] | 175.47 | 0.11 | 157.36 | 0.03 | 92.54 | 0.04 | -64.82 | 0.04 | 156.65 | 0.1 | 69.01 | 0.03 | 85.26 | 0.04 | 16.24 | 0.03 | [8 empty] | 61.98 | 0.03 | 64.51 | 0.04 | 35.07 | 0.02 | 29.44 | 0.04 | 544.28 | 0.34 | 30.04 | 0.01 | 39797 | 28 | 45156 | 28 | [112 empty] | 61.88 | 0.04 | 62.93 | 0.04 | 64.44 | 0.03 | 63.29 | 0.03 | 63.18 | 0.03 | 63.21 | 0.03 | [18 empty] | 69.01 | 0.03 | [12 empty] | 70.77 | 0.04 | [22 empty] | 69.31 | 0.04 | 66.18 | 0.04 | 70.77 | 0.04 | 71.29 | 0.03 | 64.95 | 0.03 | 81.11 | 0.02 | [24 empty] | 64.68 | 0.07 | 64.61 | 0.06 | 74.48 | 0.03 | 74.39 | 0.04 | 74.1 | 0.03 | 73.66 | 0.04 | 69.98 | 0.05 | 71.38 | 0.06 |  |  | 73.97 | 0.04 | 74.2 | 0.05 | 74.21 | 0.04 | 73.68 | 0.04 | 66.71 | 0.06 | 71.52 | 0.07 | 74.35 | 0.04 | 74.35 | 0.04 | 71.25 | 0.16 | 71.75 | 0.08 | 73.8 | 0.05 | 73.74 | 0.05 | 71.28 | 0.05 | 72.1 | 0.06 | 73.36 | 0.08 | 72.41 | 0.08 | [30 empty] | 63.88 | 0.06 | 63.67 | 0.06 | 63.92 | 0.06 | 64.61 | 0.06 | 64.04 | 0.06 | 64.02 | 0.07 | [50 empty] | C8-55-CE3 | 75.005 | 0.01 | 61.997 | 0.045 | 63.533 | 0.018 | 56.15 | 0.039 | 64.999 | 0.013 | 57.015 | 0.016 | 2596.1 | 2.6 | 2514.3 | 2.6 | 1.2 | 0.002 | -0.444 | 0.002 | 0.142 | 0.002 | 0.929 | 0.0019 | 29.192 | 0.001 | 4454 | 28 | 1580 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4823 | 11753.8206 | 354.4569 | 22.8063 | 102.9568 | 11650.8637 | 0.0087708 | 27.5777 | 62.0507 | 13.2908 | 13.2524 | 0.0080142 | 24.3342 | 0.0087775 | 27.6064 | 0.0078481 | 23.7962 | 74.9175 | 61.9555 | 23.4352 | 48690.0615 | 36296.2079 | 2874 | 0.20146 | 44507.2829 | 32113.4293 | 9.9927 | 0.54574 | -4.1425 | -12.8668 | 46.5925 | 48690.0615 | 44784.6958 | 4242.2652 | -336.8996 | 48690.0615 | 100%
3 | 3-1EH | 75N0075 | 3-1EH | open | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/26/2013 | 10:46:05 | 10 Ton | 0:30:00 | 75/62 65/57 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 65 | 57 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 0.2 | 15.3 | 0 | 43053 | 172 | 42493 | 416 | 18607 | 313 | 61677 | 293 | 13.8725 |  |  |  |  | 112.24 | 0.01 | -60 | [32 empty] | Econo Open 1st Stage 65/57 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.979 | 0.083 | 61.988 | 0.045 | 65.006 | 0.017 | 57.001 | 0.018 | 74.44 | 0.17 | 59.32 | 0.06 | 63.5 | 0.04 | 0.094 | 0.005 | 0.911 | 0.002 | 43053 | 172 | 18607 | 313 | 13.872 | 0.118 | 38547 | 44 | 8.669 | 0.057 | -60 | 0.78 | 230.1 | 0.8 | 229.7 | 0.8 | 229.9 | 0.8 | 15.3 | 0.1 | 14.1 | 0.1 | 16.9 | 0.1 | 3483.6 | 26.3 | 2356.5 | 29.6 | 962.7 | 22.7 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.4 |  | 6.3 |  | 0.53 | 230 |  | 230 |  | 230 |  | 8.5 |  | 8.3 |  | 7.8 |  | 2290 |  | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4440 | [22 empty] | 173.86 | 0.18 | 154.35 | 0.05 | 91.95 | 0.07 | 62.4 | 0.06 | 155.66 | 0.17 | 68.97 | 0.06 | 84.86 | 0.07 | 15.89 | 0.05 | [8 empty] | 59.61 | 0.06 | 59.39 | 0.06 | 33.32 | 0.04 | 26.06 | 0.08 | 533.22 | 0.59 | 30.03 | 0.02 | 38547 | 44 | 43837 | 44 | [112 empty] | 57.73 | 0.05 | 58.87 | 0.06 | 60.59 | 0.06 | 59.36 | 0.06 | 59.23 | 0.06 | 59.24 | 0.06 | [18 empty] | 68.97 | 0.06 | [12 empty] | 69.8 | 0.05 | 69.76 | 0.06 | [20 empty] | 69.24 | 0.05 | 73.49 | 0.08 |  |  |  |  | 60.01 | 0.05 | 80.91 | 0.03 | [24 empty] | 64.64 | 0.09 | 64.33 | 0.05 | 74.34 | 0.16 | 74.48 | 0.16 | 74.16 | 0.14 | 74.24 | 0.15 | 74.31 | 0.15 | 74.35 | 0.16 |  |  | 72.79 | 0.13 | 71.83 | 0.12 | 70.56 | 0.14 | 70.31 | 0.14 | 70.03 | 0.15 | 67.17 | 0.11 | 65.85 | 0.1 | 66.17 | 0.2 | 66.53 | 0.11 | 66.93 | 0.11 | 66.3 | 0.1 | 65.31 | 0.1 | 65.81 | 0.1 | 66.05 | 0.12 | 66.61 | 0.12 | 66.07 | 0.11 | [30 empty] | 66.03 | 0.11 | 65.86 | 0.11 | 64.99 | 0.09 | 65.13 | 0.09 | 64.69 | 0.08 | 64.82 | 0.11 | [50 empty] | C8-55-OE3 | 74.979 | 0.083 | 61.988 | 0.045 | 59.659 | 0.037 | 53.745 | 0.024 | 65.006 | 0.017 | 57.001 | 0.018 | 2561.4 | 2.8 | 2499.9 | 2.7 | 0.792 | 0.002 | -0.076 | 0.009 | 0.094 | 0.005 | 0.911 | 0.002 | 29.237 | 0 | 4446 | 29 | 1540 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.5905 | 11686.4654 | 232.6017 | 845.2537 | 3815.7803 | 7870.6852 | 0.0085251 | 26.5309 | 58.0685 | 13.2909 | 13.1506 | 0.0080042 | 24.325 | 0.0087777 | 27.6003 | 0.0073826 | 22.3466 | 71.7258 | 60.4144 | 21.9597 | 53420.7644 | 38305.1573 | 2906 | 0.18566 | 48958.6141 | 33843.007 | 11.0118 | 0.49576 | -4.5712 | -13.6572 | 44.641 | 53420.7644 | 61396.9177 | 4521.768 | -12497.9213 | 53420.7644 | 100%
3 | 3-2CH Retest | 75N0076 | 3-2CH Retest | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/1/2013 | 2:57:26 | 10 Ton | 0:30:00 | 75/62 65/57 | ENG 1 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 65 | 57 | 7.6 | 8.1 | 7.6 | 8.1 | 230.6 | 0.3 | 24.4 | 0 | 59145 | 94 | 58106 | 288 | 21159 | 98 | 80323 | 122 | 12.0768 |  |  |  |  | 113.07 | 0.01 | -4.03 | [32 empty] | Economizer Closed 2 Stage 65/57 | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor:VFD at 25.02% | 74.999 | 0.018 | 61.994 | 0.023 | 64.986 | 0.012 | 57.033 | 0.015 | 74.36 | 0.12 | 54.14 | 0.04 | 59.43 | 0.03 | 0.147 | 0.003 | 0.9436 | 0.002 | 59145 | 94 | 21159 | 98 | 12.078 | 0.055 | 77209 | 63 | 11.61 | 0.05 | -4.03 | 0.17 | 230.6 | 0.5 | 230.4 | 0.5 | 229.4 | 0.5 | 24.4 | 0.1 | 21.2 | 0.1 | 24.5 | 0.1 | 5529.7 | 29.1 | 3414.2 | 30.5 | 1121 | 24.5 | 230 |  | 231 |  | 228 |  | 6.5 |  | 6.2 |  | 6.2 |  | 0.52 | 231 |  | 229 |  | 229 |  | 8.9 |  | 8.2 |  | 7.5 |  | 2310 |  | 0.7 | 229 | 228 | 229 | 8.5 | 7.3 | 7.9 | 2200 | 0.69 | [8 empty] | 6710 | [22 empty] | 174.92 | 0.13 | 158.12 | 0.05 | 92.33 | 0.05 | 65.78 | 0.05 | 156.49 | 0.12 | 69.84 | 0.04 | 85.18 | 0.05 | 15.34 | 0.03 | [8 empty] | 61.21 | 0.05 | 64.65 | 0.05 | 34.5 | 0.04 | 30.15 | 0.06 | 537.87 | 0.41 | 30.29 | 0.01 | 77209 | 63 | 44526 | 33 | [38 empty] | 164.62 | 0.16 | 166.3 | 0.04 | 88.41 | 0.06 | 77.9 | 0.06 | [6 empty] | 153.74 | 0.15 | 71.04 | 0.03 | 84.07 | 0.06 | 13.03 | 0.06 | [6 empty] | 51.24 | 0.04 | 67.75 | 0.04 | 26.72 | 0.04 | 41.02 | 0.05 | 69.78 | 0.05 | 455.71 | 0.47 | 30.64 | 0.01 | 114.12 | 0.01 | 77209 | 63 | 38042 | 40 | [26 empty] | 54.42 | 0.03 | 54.1 | 0.04 | 53.46 | 0.04 | 54.9 | 0.03 | 54.83 | 0.03 | 54.87 | 0.03 | [18 empty] | 69.84 | 0.04 | [12 empty] | 71.49 | 0.04 | 70.15 | 0.04 | [20 empty] | 70.08 | 0.04 | 69.78 | 0.05 | 71.49 | 0.04 | 70.15 | 0.04 | 65.08 | 0.04 | 67.44 | 0.04 | [24 empty] | 64.63 | 0.09 | 64.84 | 0.06 | 74.58 | 0.07 | 74.48 | 0.07 | 74.13 | 0.07 | 73.7 | 0.07 | 69.88 | 0.06 | 71.35 | 0.07 |  |  | 73.99 | 0.08 | 74.25 | 0.09 | 74.26 | 0.08 | 73.55 | 0.08 | 66.44 | 0.07 | 71.45 | 0.09 | 74.39 | 0.08 | 74.41 | 0.08 | 71.11 | 0.19 | 71.61 | 0.09 | 73.78 | 0.08 | 73.52 | 0.09 | 71.02 | 0.07 | 71.99 | 0.09 | 73.37 | 0.11 | 71.66 | 0.14 | [30 empty] | 63.53 | 0.08 | 63.27 | 0.07 | 63.58 | 0.08 | 64.32 | 0.08 | 63.79 | 0.07 | 63.78 | 0.09 | [50 empty] | C8-55-CE3 | 74.999 | 0.018 | 61.994 | 0.023 | 54.407 | 0.021 | 51.276 | 0.02 | 64.986 | 0.012 | 57.033 | 0.015 | 2599.1 | 2.8 | 2553.5 | 2.7 | 1.22 | 0.002 | -0.448 | 0.002 | 0.147 | 0.003 | 0.9436 | 0.002 | 29.191 | 0.001 | 6651 | 29 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4525 | 11980.4427 | 365.9829 | 22.9087 | 103.4204 | 11877.0223 | 0.0087704 | 27.5762 | 52.9545 | 13.2906 | 13.0167 | 0.0080281 | 24.346 | 0.0087769 | 27.6043 | 0.0072679 | 20.9445 | 74.9127 | 61.9533 | 20.5912 | 83683.6428 | 63136.4568 | 5061 | 0.20641 | 79506.0724 | 58958.8864 | 11.954 | 0.20983 | -6.985 | -21.9582 | 47.1235 | 83683.6428 | 79788.116 | 4232.4997 | -336.9729 | 83683.6428 | 100%
3 | 4-1CH Retest | 75N0078 | 4-1CH Retest | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/1/2013 | 7:17:37 | 10 Ton | 0:30:00 | 75/62 60/54 | ENG 1 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 60 | 54 | 7.6 | 8.1 | 7.6 | 8.1 | 230.8 | 0.3 | 15.7 | 0 | 33940 | 78 | 33017 | 169 | 13541 | 127 | 47494 | 101 | 10.9813 |  |  |  |  | 113.2 | 0.01 | -21.95 | [32 empty] | Econo Closed 1st Stage 60/54 Ambient | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor:VFD at 25.02% | 75.008 | 0.01 | 62.005 | 0.046 | 59.994 | 0.018 | 54.005 | 0.02 | 74.41 | 0.06 | 62.75 | 0.04 | 65.98 | 0.03 | 0.141 | 0.002 | 0.9312 | 0.0021 | 33940 | 78 | 13541 | 127 | 10.982 | 0.075 | 38947 | 30 | 9.005 | 0.058 | -21.95 | 0.26 | 230.8 | 0.8 | 230.8 | 0.8 | 229.2 | 0.8 | 15.7 | 0.1 | 13.5 | 0.1 | 16.3 | 0.1 | 3574.6 | 27.2 | 2239.6 | 28.8 | 750.6 | 22.2 | 229.8 |  | 228.9 |  | 230.2 |  | 6.6 |  | 6.2 |  | 6.2 |  | 0.53 | 230.3 |  | 228.9 |  | 230.3 |  | 8.7 |  | 7.9 |  | 7.4 |  | 2170 |  | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4350 | [22 empty] | 161.74 | 0.11 | 153.53 | 0.03 | 87.29 | 0.04 | 66.25 | 0.05 | 143.18 | 0.11 | 63.79 | 0.04 | 79.67 | 0.05 | 15.88 | 0.02 | [8 empty] | 59.1 | 0.05 | 64.79 | 0.05 | 32.94 | 0.04 | 31.85 | 0.06 | 523.06 | 0.37 | 28.5 | 0.01 | 38947 | 30 | 44305 | 30 | [38 empty] | 102.49 | 0.06 | 71.08 | 0.05 | 60.28 | 0.03 | 10.8 | 0.07 | [6 empty] | 101.9 | 0.07 | 73.13 | 0.03 | 59.97 | 0.04 | 13.16 | 0.05 | [6 empty] | 101.74 | 0.07 | 75.93 | 0.13 | 59.88 | 0.04 | 16.05 | 0.13 | 61.08 | 0.05 | 35.36 | 22.88 | 31.26 | 0.01 | 112.89 | 0.02 | 38947 | 30 | 0 | 0 | [26 empty] | 61.51 | 0.04 | 62.42 | 0.04 | 63.79 | 0.04 | 62.81 | 0.04 | 62.7 | 0.04 | 62.7 | 0.04 | [18 empty] | 63.79 | 0.04 | [12 empty] | 65.51 | 0.04 | 65.93 | 0.04 | [20 empty] | 64.21 | 0.04 | 61.08 | 0.05 | 65.51 | 0.04 | 65.93 | 0.04 | 64.98 | 0.04 | 74.58 | 0.36 | [24 empty] | 59.7 | 0.07 | 59.68 | 0.06 | 74.5 | 0.04 | 74.43 | 0.04 | 74.13 | 0.03 | 73.47 | 0.05 | 67.9 | 0.07 | 70.02 | 0.09 |  |  | 73.79 | 0.06 | 74.16 | 0.06 | 74.18 | 0.05 | 73.52 | 0.05 | 63.04 | 0.09 | 70.11 | 0.11 | 74.32 | 0.05 | 74.35 | 0.04 | 69.75 | 0.21 | 70.49 | 0.13 | 73.63 | 0.07 | 73.58 | 0.06 | 69.94 | 0.07 | 71.07 | 0.07 | 72.95 | 0.1 | 71.89 | 0.1 | [30 empty] | 58.87 | 0.07 | 58.66 | 0.07 | 58.9 | 0.07 | 59.6 | 0.07 | 59.01 | 0.07 | 59.02 | 0.08 | [50 empty] | C8-55-CE3 | 75.008 | 0.01 | 62.005 | 0.046 | 63.017 | 0.029 | 55.856 | 0.043 | 59.994 | 0.018 | 54.005 | 0.02 | 2595.8 | 2.9 | 2520.8 | 2.8 | 1.204 | 0.002 | -0.446 | 0.002 | 0.141 | 0.002 | 0.9312 | 0.0021 | 29.245 | 0.001 | 4325 | 28 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4664 | 11764.4171 | 356.5578 | 22.7445 | 103.7016 | 11660.7155 | 0.0087703 | 27.5671 | 61.5506 | 13.1596 | 13.2389 | 0.0074496 | 22.501 | 0.008782 | 27.6121 | 0.0077978 | 23.6157 | 74.876 | 61.9399 | 23.2587 | 50685.4347 | 37623.599 | 2755 | 0.18551 | 46543.9566 | 33482.1208 | 10.7616 | 0.53191 | -4.3084 | -13.3254 | 46.4084 | 50685.4347 | 47015.4731 | 4199.9918 | -530.0302 | 50685.4347 | 100%
3 | 4-1EH | 75N0079 | 4-1EH | open | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 9/26/2013 | 21:02:21 | 10 Ton | 0:30:00 | 75/62 60/54 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 60 | 54 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 0.2 | 15.1 | 0 | 49245 | 92 | 49953 | 269 | 24220 | 117 | 73488 | 172 | 16.9249 |  |  |  |  | 111.9 | 0.01 | -49.0638 | [32 empty] | Economizer Open 1st Stage 60/54 Ambient | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor: VFD 25.02% | 74.997 | 0.019 | 62.108 | 0.02 | 59.989 | 0.016 | 53.931 | 0.02 | 74.98 | 0.09 | 57.25 | 0.03 | 61.84 | 0.02 | 0.1 | 0.004 | 0.9097 | 0.0021 | 49245 | 92 | 24220 | 117 | 16.924 | 0.118 | -5290 | 1 | 8.6209 | 0 | 0 | 0 | 230.1 | 0.5 | 229.7 | 0.5 | 229.8 | 0.5 | 15.1 | 0.1 | 13.9 | 0.1 | 16.6 | 0.1 | 3425.5 | 21.9 | 2354.2 | 21.9 | 916.9 | 20 | 230 |  | 228 |  | 227 |  | 6.1 |  | 6.2 |  | 6.3 |  | 0.54 | 228 |  | 229 |  | 231 |  | 8.3 |  | 8 |  | 7.5 |  | 2150 |  | 0.68 | [16 empty] | 4280 | [22 empty] | 160.02 | 0.15 | 147.85 | 0.06 | 86.6 | 0.06 | 61.25 | 0.07 | 142.1 | 0.15 | 63.88 | 0.05 | 79.2 | 0.06 | 15.32 | 0.04 | [8 empty] | 56.3 | 0.06 | 56.4 | 0.07 | 30.78 | 0.04 | 25.62 | 0.08 | 512.37 | 0.56 | 28.52 | 0.01 | 37432 | 1 | 42721.4106 | 0 | [38 empty] | 102.28 | 0.07 | 71.43 | 0.04 | 60.16 | 0.04 | 11.27 | 0.06 | [6 empty] | 101.62 | 0.07 | 72.72 | 0.03 | 59.81 | 0.04 | -12.91 | 0.05 | [6 empty] | 101.49 | 0.07 | 75.74 | 0.03 | 59.73 | 0.04 | 16.01 | 0.04 | 68.84 | 0.09 | 3.04 | 1.19 | 31.14 | 0.01 | 112.87 | 0.01 | -5290 | 1 | 0 | 0 | [26 empty] | 56.34 | 0.04 | 55.83 | 0.05 | 57.24 | 0.05 | 57.95 | 0.03 | 57.79 | 0.03 | 57.57 | 0.04 | [18 empty] | 63.88 | 0.05 | [12 empty] | 64.46 | 0.04 | 64.79 | 0.03 | [20 empty] | 64.1 | 0.04 | 68.84 | 0.09 |  |  |  |  | 56.88 | 0.06 | 75.18 | 0.03 | [24 empty] | 59.93 | 0.09 | 59.69 | 0.05 | 75.13 | 0.07 | 74.98 | 0.07 | 74.75 | 0.07 | 74.79 | 0.07 | 74.77 | 0.07 | 74.79 | 0.07 |  |  | 72.9 | 0.07 | 71.47 | 0.07 | 69.42 | 0.12 | 68.84 | 0.15 | 68.17 | 0.18 | 64.38 | 0.15 | 62.64 | 0.2 | 63.26 | 0.41 | 63.13 | 0.15 | 63.38 | 0.12 | 62.11 | 0.1 | 60.28 | 0.13 | 61.53 | 0.11 | 61.77 | 0.14 | 62.51 | 0.13 | 61.71 | 0.12 | [30 empty] | 62.45 | 0.15 | 62.42 | 0.13 | 60.81 | 0.14 | 60.9 | 0.13 | 59.63 | 0.11 | 59.66 | 0.17 | [50 empty] | C8-55-OE3 | 74.997 | 0.019 | 62.108 | 0.02 | 57.523 | 0.018 | 52.172 | 0.023 | 59.989 | 0.016 | 53.931 | 0.02 | 2557.1 | 3 | 2501.8 | 3 | 0.778 | 0.002 | -0.08 | 0.008 | 0.1 | 0.004 | 0.9097 | 0.0021 | 29.197 | 0 | 4342 | 29 | 1520 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.5667 | 11717.5795 | 228.6637 | 862.9028 | 3934.4579 | 7783.1215 | 0.008368 | 25.9303 | 55.9563 | 13.1592 | 13.0937 | 0.0074092 | 22.4558 | 0.0088526 | 27.6867 | 0.0070178 | 21.4307 | 69.9665 | 59.5095 | 21.0498 | 57187.9672 | 39399.9062 | 2822 | 0.16842 | 52780.6365 | 34992.5756 | 12.1558 | 0.49956 | -4.8805 | -14.0103 | 41.9706 | 57187.9672 | 73305.3232 | 4463.243 | -20580.599 | 57187.9672 | 100%
3 | 4-2CH Retest | 75N0080 | 4-2CH Retest | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/1/2013 | 5:51:59 | 10 Ton | 0:30:00 | 75/62 60/54 | ENG 1 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 60 | 54 | 7.6 | 8.1 | 7.6 | 8.1 | 230.7 | 0.2 | 23.9 | 0 | 57990 | 104 | 56992 | 250 | 21319 | 78 | 79328 | 144 | 12.5103 |  |  |  |  | 113.33 | 0.02 | -7.66 | [32 empty] | . | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: With econo Meriam set to 75%: Horiz airflow disch config. set on floor:VFD at 25.02% | 75.003 | 0.018 | 62.006 | 0.014 | 59.938 | 0.069 | 54.002 | 0.049 | 74.4 | 0.09 | 54.51 | 0.03 | 59.73 | 0.03 | 0.132 | 0.004 | 0.9375 | 0.0021 | 57990 | 104 | 21319 | 78 | 12.509 | 0.063 | 73686 | 140 | 11.619 | 0.054 | -7.66 | 0.21 | 230.7 | 0.7 | 230.7 | 0.7 | 229.4 | 0.7 | 23.9 | 0.1 | 20.5 | 0.1 | 23.9 | 0.1 | 5391.9 | 34.1 | 3374.7 | 37.4 | 949.6 | 29.1 | 229.9 |  | 228.5 |  | 229.4 |  | 6.5 |  | 6.2 |  | 6.2 |  | 0.53 | 230 |  | 229.6 |  | 229.9 |  | 8.7 |  | 7.9 |  | 7.3 |  | 2180 |  | 0.68 | 228.9 | 228.8 | 230 | 8.7 | 7.9 | 7.3 | 2004 | 0.67 | [8 empty] | 6364 | [22 empty] | 161.34 | 0.7 | 154.57 | 0.11 | 87.14 | 0.29 | 67.45 | 0.18 | 143.14 | 0.66 | 64.64 | 0.21 | 79.66 | 0.29 | 15.02 | 0.08 | [8 empty] | 58.47 | 0.19 | 65.35 | 0.05 | 32.46 | 0.15 | 32.9 | 0.17 | 517.07 | 1.47 | 28.76 | 0.06 | 73686 | 140 | 43740 | 91 | [38 empty] | 147.86 | 0.6 | 159.45 | 0.45 | 81.65 | 0.26 | 77.79 | 0.46 | [6 empty] | 137.77 | 0.59 | 65.72 | 0.15 | 77.32 | 0.27 | 11.6 | 0.13 | [6 empty] | 45.38 | 0.16 | 61.89 | 0.84 | 21.74 | 0.15 | 40.12 | 0.75 | 64.41 | 0.23 | 418.53 | 1.16 | 29.07 | 0.05 | 113.42 | 0.14 | 73686 | 140 | 35309 | 97 | [26 empty] | 55.13 | 0.06 | 54.15 | 0.04 | 53.01 | 0.05 | 55.95 | 0.09 | 55.86 | 0.09 | 55.87 | 0.09 | [18 empty] | 64.64 | 0.21 | [12 empty] | 66.19 | 0.21 | 64.77 | 0.2 | [20 empty] | 64.94 | 0.21 | 64.41 | 0.23 | 66.19 | 0.21 | 64.77 | 0.2 | 65.51 | 0.05 | 61.55 | 0.84 | [24 empty] | 59.69 | 0.26 | 59.84 | 0.24 | 74.54 | 0.07 | 74.47 | 0.07 | 74.13 | 0.07 | 73.46 | 0.07 | 67.82 | 0.11 | 69.87 | 0.11 |  |  | 73.74 | 0.09 | 74.19 | 0.09 | 74.21 | 0.08 | 73.31 | 0.07 | 62.78 | 0.18 | 69.92 | 0.13 | 74.34 | 0.08 | 74.36 | 0.07 | 69.25 | 0.31 | 69.9 | 0.14 | 73.58 | 0.09 | 73.46 | 0.08 | 69.52 | 0.12 | 70.7 | 0.1 | 72.74 | 0.15 | 71.16 | 0.17 | [30 empty] | 58.64 | 0.29 | 58.41 | 0.28 | 58.71 | 0.27 | 59.43 | 0.27 | 58.85 | 0.26 | 58.87 | 0.27 | [50 empty] | C8-55-CE3 | 75.003 | 0.018 | 62.006 | 0.014 | 54.755 | 0.019 | 51.394 | 0.02 | 59.938 | 0.069 | 54.002 | 0.049 | 2590.1 | 2.9 | 2545.7 | 2.9 | 1.201 | 0.002 | -0.447 | 0.003 | 0.132 | 0.004 | 0.9375 | 0.0021 | 29.221 | 0 | 6341 | 31 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4428 | 11931.0143 | 359.1826 | 22.7689 | 103.8231 | 11827.1912 | 0.0087724 | 27.5684 | 53.3122 | 13.1583 | 13.0254 | 0.0074611 | 22.4999 | 0.0087839 | 27.6129 | 0.0072492 | 21.0088 | 74.8722 | 61.9417 | 20.6579 | 82449.9482 | 61735.8248 | 4771 | 0.19749 | 78317.4285 | 57603.3052 | 12.351 | 0.23146 | -6.9106 | -21.56 | 46.8192 | 82449.9482 | 78794.0847 | 4186.7135 | -530.85 | 82449.9482 | 100%
3 | 3-421151CF | 75N0082 | 3-421151CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 15:29:05 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.4 | 0.1 | 33.4 | 0 | 40970 | 63 | 40173 | 142 | -6462 | 75 | 34502 | 96 | 3.1831 |  |  |  |  | 109.67 | 0 | 56.41 | [32 empty] | 100% airflow, both stages, 1-finger (0.74") open | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 100%: Horiz airflow disch config. set on floor: | 74.999 | 0.007 | 62.027 | 0.009 | 115.008 | 0.017 | 80.01 | 0.028 | 74.45 | 0.05 | 62.34 | 0.04 | 65.32 | 0.01 | -0.266 | 0.005 | 1.7296 | 0.0043 | 40970 | 63 | -6462 | 75 | 3.183 | 0.013 | 79143 | 63 | 7.302 | 0.021 | 56.41 | 0.13 | 230.4 | 0.8 | 230 | 0.8 | 229.6 | 0.8 | 33.4 | 0.1 | 30.1 | 0.1 | 33.5 | 0.1 | 7691.2 | 32.5 | 3715.8 | 38.2 | 3147.7 | 28.3 | 230 |  | 230 |  | 230 |  | 6.7 |  | 6.6 |  | 6.4 |  | 0.56 | 230 |  | 230 |  | 230 |  | 13.4 |  | 12.6 |  | 12.2 |  | 4340 |  | 0.86 | 230 | 230 | 230 | 12.8 | 11.7 | 12.2 | 4200 | [9 empty] | 10850 | [22 empty] | 347.86 | 0.24 | 198.92 | 0.05 | 142.38 | 0.06 | 56.53 | 0.06 | 328.35 | 0.23 | 123.54 | 0.06 | 137.78 | 0.06 | 14.24 | 0.04 | [8 empty] | 83.61 | 0.04 | 52.99 | 0.03 | 49.56 | 0.02 | 3.43 | 0.02 | 705.26 | 0.48 | 47.1 | 0.02 | 79143 | 63 | 44126 | 32 | [38 empty] | 332.52 | 0.33 | 236.12 | 0.05 | 138.78 | 0.08 | 97.33 | 0.05 | [6 empty] | 320.94 | 0.32 | 123.72 | 0.05 | 135.98 | 0.08 | 12.27 | 0.07 | [6 empty] | 75.11 | 0.04 | 83.78 | 0.03 | 44.2 | 0.03 | 39.58 | 0.03 | 123.41 | 0.08 | 577.97 | 0.58 | 47.16 | 0.02 | 115.72 | 0.01 | 79143 | 63 | 39624 | 42 | [26 empty] | 61.98 | 0.05 | 62.38 | 0.05 | 62.89 | 0.05 | 62.51 | 0.05 | 62.48 | 0.05 | 62.73 | 0.04 | [18 empty] | 123.54 | 0.06 | [12 empty] | 125.51 | 0.06 | 124.09 | 0.06 | [20 empty] | 123.68 | 0.07 | 123.41 | 0.08 | 125.51 | 0.06 | 124.09 | 0.06 | 54.88 | 0.04 | 83.76 | 0.04 | [24 empty] | 115.25 | 0.11 | 114.73 | 0.08 | 74.62 | 0.04 | 74.73 | 0.05 | 74.43 | 0.05 | 74.44 | 0.04 | 74.6 | 0.05 | 74.64 | 0.04 |  |  | 75.89 | 0.1 | 75.22 | 0.09 | 75.22 | 0.08 | 75.23 | 0.08 | 96.26 | 0.28 | 79.62 | 0.25 | 78.68 | 0.21 | 76.51 | 0.15 | 92.23 | 0.35 | 89.6 | 0.11 | 93.33 | 0.2 | 94.04 | 0.16 | 88.99 | 0.09 | 88.98 | 0.1 | 91.8 | 0.12 | 92.4 | 0.21 | [30 empty] | 115.4 | 0.11 | 115.02 | 0.1 | 115 | 0.12 | 115.17 | 0.12 | 115 | 0.12 | 114.93 | 0.15 | [50 empty] | C8-55-1FE3 | 74.999 | 0.007 | 62.027 | 0.009 | 62.646 | 0.006 | 58.32 | 0.012 | 115.008 | 0.017 | 80.01 | 0.028 | 3084.1 | 3.9 | 3000 | 3.7 | 0.883 | 0.002 | -0.261 | 0.002 | -0.266 | 0.005 | 1.7296 | 0.0043 | 29.359 | 0.001 | 10839 | 31 | 1700 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4129 | 13974.3797 | 311.2054 | 204.3649 | 839.4376 | 13134.9421 | 0.0090976 | 28.5467 | 61.2331 | 14.6073 | 13.2418 | 0.013775 | 42.9205 | 0.0087987 | 27.6281 | 0.0093607 | 25.2272 | 77.4228 | 63.3307 | 24.8822 | 51209.971 | 54297.6974 | 9139 | 0.60909 | 46470.0149 | 49557.7413 | 4.2873 | 0.25859 | -3.6646 | -16.1897 | 55.5864 | 51209.971 | 33552.3587 | 4820.6268 | 12836.9854 | 51209.971 | 100%
3 | 3-42821CF | 75N0083 | 3-42821CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 11:18:29 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.3 | 0.2 | 26.6 | 0 | 55800 | 97 | 54930 | 232 | 10615 | 122 | 66426 | 139 | 8.4062 |  |  |  |  | 112.9 | 0.01 | 16.8 | [32 empty] | 100% airflow, both stages, 1-finger (0.74") open | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 100%: Horiz airflow disch config. set on floor: | 75.001 | 0.018 | 61.997 | 0.023 | 81.998 | 0.023 | 67.997 | 0.02 | 74.55 | 0.07 | 58.16 | 0.05 | 61.95 | 0.02 | -0.216 | 0.005 | 1.7073 | 0.0047 | 55800 | 97 | 10615 | 122 | 8.406 | 0.038 | 79842 | 51 | 10.104 | 0.04 | 16.8 | 0.18 | 230.3 | 0.8 | 230.1 | 0.8 | 229.7 | 0.8 | 26.6 | 0.1 | 23.8 | 0.1 | 27.1 | 0.1 | 6086.5 | 38.2 | 3524.1 | 45.4 | 1815.8 | 31.8 | 230 |  | 230 |  | 230 |  | 6.7 |  | 6.6 |  | 6.4 |  | 0.57 | 230 |  | 230 |  | 230 |  | 10 |  | 9.3 |  | 8.9 |  | 2890 |  | 0.78 | 230 | 230 | 230 | 9.4 | 8.3 | 9 | 2700 | 0.77 | [8 empty] | 7910 | [22 empty] | 227.22 | 0.14 | 173.78 | 0.04 | 110.2 | 0.04 | 63.58 | 0.05 | 208.25 | 0.14 | 88.28 | 0.03 | 104.1 | 0.05 | 15.82 | 0.04 | [8 empty] | 70.64 | 0.04 | 66.6 | 0.05 | 41.27 | 0.03 | 25.33 | 0.06 | 602.46 | 0.37 | 35.84 | 0.01 | 79842 | 51 | 46425 | 27 | [38 empty] | 209.46 | 0.18 | 191.13 | 0.04 | 104.5 | 0.06 | 86.63 | 0.05 | [6 empty] | 199.06 | 0.19 | 88.82 | 0.03 | 101.01 | 0.06 | 12.18 | 0.07 | [6 empty] | 56.4 | 0.04 | 74.74 | 0.04 | 30.95 | 0.03 | 43.78 | 0.05 | 87.88 | 0.04 | 481.04 | 0.41 | 36.01 | 0.01 | 115.05 | 0.01 | 79842 | 51 | 38025 | 33 | [26 empty] | 58.2 | 0.04 | 57.97 | 0.03 | 58.27 | 0.04 | 58.74 | 0.06 | 58.62 | 0.06 | 58.61 | 0.06 | [18 empty] | 88.28 | 0.03 | [12 empty] | 90.04 | 0.04 | 88.43 | 0.04 | [20 empty] | 88.61 | 0.04 | 87.88 | 0.04 | 90.04 | 0.04 | 88.43 | 0.04 | 67.42 | 0.05 | 74.66 | 0.03 | [24 empty] | 81.95 | 0.08 | 81.76 | 0.06 | 74.59 | 0.07 | 74.66 | 0.06 | 74.76 | 0.06 | 74.74 | 0.06 | 74.81 | 0.06 | 74.81 | 0.06 |  |  | 75.46 | 0.08 | 75.22 | 0.09 | 75.18 | 0.08 | 75.01 | 0.08 | 78.01 | 0.08 | 75.76 | 0.09 | 75.64 | 0.08 | 75.41 | 0.08 | 77.32 | 0.13 | 76.68 | 0.07 | 77.69 | 0.07 | 77.9 | 0.07 | 76.41 | 0.06 | 76.47 | 0.07 | 77.28 | 0.06 | 77.09 | 0.08 | [30 empty] | 81.94 | 0.08 | 81.77 | 0.07 | 81.72 | 0.09 | 81.77 | 0.09 | 81.53 | 0.09 | 81.49 | 0.12 | [50 empty] | C8-55-1FE3 | 75.001 | 0.018 | 61.997 | 0.023 | 58.351 | 0.024 | 54.618 | 0.02 | 81.998 | 0.023 | 67.997 | 0.02 | 3048.2 | 4.2 | 3000 | 4.1 | 0.919 | 0.003 | -0.265 | 0.002 | -0.216 | 0.005 | 1.7073 | 0.0047 | 29.452 | 0.001 | 7902 | 31 | 1710 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.414 | 13935.9667 | 323.8932 | 199.7802 | 871.8619 | 13064.1048 | 0.0089388 | 27.8892 | 56.937 | 13.7485 | 13.1237 | 0.011342 | 32.1258 | 0.0087784 | 27.6065 | 0.0081841 | 22.8996 | 75.4407 | 62.3961 | 22.5551 | 74335.6022 | 61888.0216 | 6192 | 0.2843 | 69604.8198 | 57157.2392 | 8.8085 | 0.24506 | -5.3341 | -18.5037 | 50.9305 | 74335.6022 | 65594.3268 | 4801.0023 | 3940.2731 | 74335.6022 | 100%
3 | 3-42951CF | 75N0084 | 3-42951CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 3:25:55 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.1 | 29.2 | 0 | 50032 | 79 | 48962 | 170 | 2595 | 93 | 52629 | 99 | 5.8902 |  |  |  |  | 111.48 | 0.07 | 33.76 | [32 empty] | 100% Airflow, Both Stages, 1 Finger opened (0.74") | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 100%: Horiz airflow disch config. set on floor: | 75.003 | 0.015 | 61.99 | 0.011 | 94.996 | 0.015 | 75.034 | 0.02 | 74.33 | 0.05 | 59.66 | 0.03 | 63.31 | 0.01 | -0.241 | 0.003 | 1.3052 | 0.0028 | 50032 | 79 | 2595 | 93 | 5.89 | 0.024 | 79454 | 77 | 8.893 | 0.032 | 33.76 | 0.14 | 230.5 | 0.8 | 230.3 | 0.8 | 229.5 | 0.8 | 29.2 | 0.1 | 25.8 | 0.1 | 29.2 | 0.1 | 6699.1 | 36.8 | 3530.1 | 42.6 | 2236.1 | 30.6 | 228 |  | 229 |  | 230 |  | 6.8 |  | 6.5 |  | 6.4 |  | 0.57 | 231 |  | 231 |  | 230 |  | 11.2 |  | 10.4 |  | 10.1 |  | 3410 |  | 0.82 | 229 | 228 | 229 | 10.7 | 9.5 | 10 | 3240 | 0.82 | [8 empty] | 8980 | [22 empty] | 270.94 | 0.19 | 183.37 | 0.06 | 123.01 | 0.05 | 60.36 | 0.08 | 251.7 | 0.19 | 102.02 | 0.05 | 117.56 | 0.06 | 15.55 | 0.04 | [8 empty] | 76.03 | 0.04 | 60.39 | 0.4 | 44.82 | 0.03 | 15.57 | 0.41 | 646.16 | 0.46 | 40.11 | 0.01 | 79454 | 77 | 46117 | 57 | [38 empty] | 254.45 | 0.22 | 208 | 0.03 | 118.36 | 0.06 | 89.64 | 0.05 | [6 empty] | 243.57 | 0.22 | 102.44 | 0.04 | 115.18 | 0.07 | 12.74 | 0.05 | [6 empty] | 63.75 | 0.05 | 78.48 | 0.02 | 36.45 | 0.04 | 42.03 | 0.05 | 101.65 | 0.06 | 523.03 | 0.45 | 40.25 | 0.01 | 115.34 | 0.01 | 79454 | 77 | 39276 | 34 | [26 empty] | 59.35 | 0.04 | 59.71 | 0.04 | 59.93 | 0.04 | 59.82 | 0.04 | 59.78 | 0.04 | 59.91 | 0.04 | [18 empty] | 102.02 | 0.05 | [12 empty] | 103.82 | 0.05 | 102.28 | 0.05 | [20 empty] | 102.23 | 0.05 | 101.65 | 0.06 | 103.82 | 0.05 | 102.28 | 0.05 | 62.76 | 0.17 | 78.51 | 0.03 | [24 empty] | 94.83 | 0.1 | 94.55 | 0.07 | 74.55 | 0.04 | 74.7 | 0.05 | 74.39 | 0.05 | 74.42 | 0.04 | 74.54 | 0.04 | 74.56 | 0.04 |  |  | 75.48 | 0.1 | 75.02 | 0.09 | 75.03 | 0.08 | 75.01 | 0.08 | 84.77 | 0.16 | 76.55 | 0.1 | 76.21 | 0.12 | 75.47 | 0.1 | 83.55 | 0.3 | 80.49 | 0.07 | 82.59 | 0.1 | 83.55 | 0.09 | 80.73 | 0.06 | 80.83 | 0.07 | 82.05 | 0.08 | 82.14 | 0.11 | [30 empty] | 94.9 | 0.08 | 94.53 | 0.08 | 94.54 | 0.08 | 94.66 | 0.08 | 94.5 | 0.08 | 94.53 | 0.11 | [50 empty] | C8-55-1FE3 | 75.003 | 0.015 | 61.99 | 0.011 | 60.016 | 0.011 | 56.229 | 0.012 | 94.996 | 0.015 | 75.034 | 0.02 | 3062.1 | 3.3 | 3000 | 3.2 | 0.912 | 0.002 | -0.271 | 0.002 | -0.241 | 0.003 | 1.3052 | 0.0028 | 29.422 | 0 | 8935 | 32 | 1720 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4253 | 13950.1774 | 321.4261 | 204.5958 | 870.6164 | 13079.561 | 0.0090965 | 28.2622 | 58.5907 | 14.1001 | 13.1702 | 0.013952 | 38.1901 | 0.0087733 | 27.6014 | 0.0087248 | 23.8934 | 76.2618 | 62.9223 | 23.5458 | 65794.9426 | 59163.4449 | 7215 | 0.37427 | 61021.6101 | 54390.1123 | 6.8295 | 0.23783 | -4.7164 | -17.6711 | 53.0765 | 65794.9426 | 51727.2866 | 4848.9575 | 9218.6985 | 65794.9426 | 100%
3 | 3-621151CF | 75N0085 | 3-621151CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 20:18:11 | 10 Ton | 0:30:00 | 75/62 115/80 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.2 | 32.6 | 0 | 28478 | 73 | 27779 | 148 | -5277 | 145 | 23197 | 178 | 2.2256 |  |  |  |  | 109.44 | 0.01 | 70.51 | [32 empty] | 66.7% Airflow, Both Stages, 1 Finger (0.74") | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 53%: Horiz airflow disch config. set on floor: | 75 | 0.014 | 61.985 | 0.021 | 114.989 | 0.031 | 80.005 | 0.046 | 74.36 | 0.07 | 61.82 | 0.06 | 65.85 | 0.02 | 0.568 | 0.007 | 0.7725 | 0.0021 | 28478 | 73 | -5277 | 145 | 2.225 | 0.018 | 78651 | 85 | 7.546 | 0.024 | 70.51 | 0.24 | 230.5 | 0.8 | 230 | 0.8 | 229.5 | 0.8 | 32.6 | 0.1 | 29.3 | 0.1 | 32.5 | 0.1 | 7503.2 | 36 | 3695.3 | 42.2 | 2919.6 | 29.9 | 230 |  | 230 |  | 229 |  | 6.1 |  | 6.2 |  | 5.9 |  | 0.51 | 231 |  | 228 |  | 228 |  | 13.3 |  | 12.4 |  | 11.9 |  | 4270 |  | 0.86 | 230 | 230 | 231 | 12.7 | 11.5 | 12.1 | 4150 | 0.86 | [8 empty] | 10440 | [22 empty] | 343.35 | 0.44 | 189.59 | 0.29 | 141.34 | 0.1 | 48.25 | 0.29 | 324.34 | 0.42 | 123.17 | 0.09 | 136.81 | 0.1 | 13.64 | 0.09 | [8 empty] | 80.02 | 0.27 | 50.49 | 0.16 | 47.33 | 0.17 | 3.15 | 0.05 | 695.66 | 1.03 | 46.98 | 0.03 | 78651 | 85 | 43449 | 77 | [38 empty] | 331.26 | 0.51 | 237.39 | 0.11 | 138.48 | 0.13 | 98.9 | 0.1 | [6 empty] | 319.7 | 0.5 | 123.37 | 0.07 | 135.68 | 0.12 | 12.31 | 0.1 | [6 empty] | 75.2 | 0.11 | 86.06 | 0.14 | 44.26 | 0.07 | 41.8 | 0.13 | 123.17 | 0.12 | 576.32 | 0.8 | 47.04 | 0.03 | 116.12 | 0.02 | 78651 | 85 | 39810 | 60 | [26 empty] | 61.55 | 0.08 | 61.93 | 0.06 | 62.22 | 0.07 | 62.01 | 0.08 | 61.96 | 0.08 | 62.04 | 0.07 | [18 empty] | 123.17 | 0.09 | [12 empty] | 125.14 | 0.09 | 123.8 | 0.1 | [20 empty] | 123.23 | 0.1 | 123.17 | 0.12 | 125.14 | 0.09 | 123.8 | 0.1 | 52.36 | 0.16 | 86.07 | 0.15 | [24 empty] | 115.06 | 0.12 | 114.62 | 0.14 | 79.54 | 0.09 | 80.94 | 0.12 | 79.54 | 0.1 | 81.1 | 0.12 | 76.01 | 0.06 | 75.72 | 0.06 |  |  | 91.83 | 0.24 | 82.74 | 2.33 | 77.98 | 0.11 | 76.63 | 0.09 | 103.92 | 0.66 | 100.35 | 0.7 | 99.31 | 1.76 | 91.21 | 2.01 | 95.87 | 0.55 | 90.05 | 0.49 | 95.58 | 2.05 | 92.59 | 2.58 | 89.66 | 0.39 | 89.89 | 0.34 | 92.68 | 1.64 | 89.03 | 2.23 | [30 empty] | 115.2 | 0.16 | 114.9 | 0.14 | 114.78 | 0.16 | 114.93 | 0.16 | 114.82 | 0.16 | 114.58 | 0.2 | [50 empty] | C8-55-1FE3 | 75 | 0.014 | 61.985 | 0.021 | 62.144 | 0.017 | 58.274 | 0.028 | 114.989 | 0.031 | 80.005 | 0.046 | 2054.6 | 2.8 | 2000.1 | 2.7 | 1.431 | 0.003 | -0.477 | 0.01 | 0.568 | 0.007 | 0.7725 | 0.0021 | 29.353 | 0.001 | 10423 | 33 | 1410 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.6382 | 9318.0624 | 336.2455 | 276.2728 | 1134.8399 | 8183.2225 | 0.0093801 | 29.4633 | 60.5058 | 14.6068 | 13.2298 | 0.013775 | 42.9154 | 0.0087707 | 27.5978 | 0.0094514 | 25.2033 | 79.9091 | 64.5982 | 24.8033 | 43422.9052 | 43392.4734 | 9013 | 0.70841 | 39758.181 | 39727.7492 | 3.8145 | 0.20074 | -4.6601 | -19.4034 | 55.6326 | 43422.9052 | 22312.1452 | 3727.7099 | 17383.05 | 43422.9052 | 100%
3 | 3-62821CF | 75N0086 | 3-62821CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 7:04:39 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 1 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.1 | 26.2 | 0 | 46207 | 71 | 45462 | 202 | 13520 | 94 | 59739 | 125 | 7.9208 |  |  |  |  | 110.53 | 0.12 | 22.83 | [32 empty] | 66.7% airflow, both stages, 1-finger (0.74") open | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 53%: Horiz airflow disch config. set on floor: | 75.001 | 0.021 | 62.004 | 0.021 | 81.987 | 0.024 | 68.004 | 0.023 | 74.34 | 0.11 | 54.13 | 0.05 | 60.24 | 0.03 | 0.64 | 0.003 | 0.7581 | 0.0017 | 46207 | 71 | 13520 | 94 | 7.921 | 0.037 | 77411 | 84 | 10.264 | 0.044 | 22.83 | 0.16 | 230.5 | 0.8 | 230.4 | 0.8 | 229.5 | 0.8 | 26.2 | 0.1 | 22.9 | 0.1 | 26.3 | 0.1 | 5981.7 | 36.6 | 3459.8 | 43.5 | 1560.5 | 29.5 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6 |  | 5.9 |  | 0.51 | 230 |  | 230 |  | 230 |  | 10.1 |  | 9.3 |  | 8.8 |  | 2860 |  | 0.77 | 230 | 230 | 230 | 9.5 | 8.3 | 8.9 | 2700 | 0.77 | [8 empty] | 7590 | [22 empty] | 223.87 | 0.16 | 166.18 | 0.05 | 109.15 | 0.05 | 57.03 | 0.08 | 205.38 | 0.16 | 87.97 | 0.06 | 103.14 | 0.05 | 15.17 | 0.05 | [8 empty] | 67.41 | 0.04 | 52.25 | 0.67 | 39.04 | 0.03 | 13.2 | 0.68 | 592.74 | 0.41 | 35.75 | 0.02 | 77411 | 84 | 44327 | 77 | [38 empty] | 208.41 | 0.18 | 189.3 | 0.03 | 104.15 | 0.06 | 85.15 | 0.05 | [6 empty] | 198.04 | 0.18 | 88.57 | 0.05 | 100.65 | 0.06 | 12.08 | 0.06 | [6 empty] | 55.82 | 0.04 | 72.27 | 0.04 | 30.49 | 0.03 | 41.78 | 0.05 | 87.6 | 0.07 | 478.73 | 0.48 | 35.93 | 0.02 | 114.66 | 0.01 | 77411 | 84 | 37691 | 39 | [26 empty] | 53.94 | 0.05 | 53.93 | 0.04 | 54.04 | 0.04 | 54.63 | 0.05 | 54.58 | 0.05 | 54.64 | 0.05 | [18 empty] | 87.97 | 0.06 | [12 empty] | 89.63 | 0.06 | 88.19 | 0.07 | [20 empty] | 88.17 | 0.07 | 87.6 | 0.07 | 89.63 | 0.06 | 88.19 | 0.07 | 56.36 | 0.35 | 72.23 | 0.05 | [24 empty] | 81.64 | 0.1 | 81.53 | 0.07 | 75.13 | 0.08 | 75.48 | 0.07 | 75.03 | 0.08 | 75.28 | 0.07 | 74.56 | 0.09 | 74.55 | 0.09 |  |  | 77.43 | 0.12 | 75.69 | 0.13 | 75.13 | 0.12 | 74.89 | 0.11 | 79.26 | 0.11 | 78.7 | 0.14 | 78.46 | 0.14 | 77.18 | 0.14 | 76.27 | 0.18 | 74.88 | 0.09 | 77.85 | 0.08 | 77.64 | 0.08 | 75.37 | 0.08 | 75.16 | 0.08 | 76.89 | 0.08 | 76.03 | 0.11 | [30 empty] | 81.71 | 0.1 | 81.41 | 0.11 | 81.42 | 0.12 | 81.52 | 0.1 | 81.37 | 0.1 | 81.37 | 0.12 | [50 empty] | C8-55-1FE3 | 75.001 | 0.021 | 62.004 | 0.021 | 54.463 | 0.012 | 51.851 | 0.016 | 81.987 | 0.024 | 68.004 | 0.023 | 2020.2 | 2.3 | 2000 | 2.2 | 1.506 | 0.002 | -0.484 | 0.003 | 0.64 | 0.003 | 0.7581 | 0.0017 | 29.434 | 0 | 7542 | 31 | 1420 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.6282 | 9309.3702 | 353.8507 | 269.9907 | 1178.2863 | 8131.0839 | 0.0091079 | 28.1836 | 52.8348 | 13.7483 | 13.0204 | 0.011349 | 32.1318 | 0.008783 | 27.6115 | 0.0075639 | 21.2793 | 75.8888 | 62.8079 | 20.883 | 67963.935 | 51508.3231 | 6122 | 0.30743 | 64325.1675 | 47869.5556 | 8.5289 | 0.153 | -7.3006 | -23.054 | 48.6706 | 67963.935 | 58949.1559 | 3688.6042 | 5326.1749 | 67963.935 | 100%
3 | 3-62951CF | 75N0087 | 3-62951CF | 1 finger | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 10 | 10/8/2013 | 5:15:35 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | ck1: 7.6 lbs / ck2: 8.1 lbs | 230/208/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.5 | 0.1 | 28.5 | 0 | 37728 | 59 | 36993 | 183 | 3691 | 110 | 41422 | 116 | 4.8294 |  |  |  |  | 109.1 | 0.01 | 47.37 | [32 empty] | 66.7% airflow, both stages, 1 finger (0.74'') | New R22 CK 1 : 7.6 lbs /Ck 2 : 8.1 lbs: No tape: Sealed ductwork: 7` blower pulley with A49 belt : motor pulley 4.5 turns opened from closed: With econo Meriam set @ 53%: Horiz airflow disch config. set on floor: | 74.998 | 0.016 | 62.001 | 0.018 | 94.998 | 0.014 | 75.042 | 0.019 | 74.37 | 0.09 | 57.83 | 0.06 | 62.92 | 0.02 | 0.612 | 0.002 | 0.7644 | 0.0016 | 37728 | 59 | 3691 | 110 | 4.83 | 0.022 | 78714 | 87 | 9.178 | 0.035 | 47.37 | 0.17 | 230.5 | 0.8 | 230.3 | 0.8 | 229.5 | 0.8 | 28.5 | 0.1 | 25.1 | 0.1 | 28.4 | 0.1 | 6529.8 | 37.8 | 3522 | 44.6 | 2046.8 | 31.9 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 5.9 |  | 0.5 | 230 |  | 230 |  | 230 |  | 11.2 |  | 10.4 |  | 9.9 |  | 3380 |  | 0.81 | 230 | 230 | 230 | 10.6 | 9.4 | 10 | 3210 | 0.81 | [8 empty] | 8610 | [22 empty] | 268.41 | 0.17 | 175.51 | 0.07 | 122.31 | 0.05 | 53.2 | 0.08 | 249.53 | 0.16 | 101.82 | 0.06 | 116.93 | 0.05 | 15.11 | 0.05 | [8 empty] | 72.97 | 0.04 | 46.2 | 0.05 | 42.82 | 0.03 | 3.38 | 0.06 | 640.13 | 0.44 | 40.05 | 0.02 | 78714 | 87 | 44198 | 30 | [38 empty] | 253.62 | 0.2 | 207.79 | 0.04 | 118.12 | 0.06 | 89.67 | 0.05 | [6 empty] | 242.77 | 0.2 | 102.36 | 0.04 | 114.94 | 0.06 | 12.58 | 0.06 | [6 empty] | 63.47 | 0.05 | 78.32 | 0.04 | 36.24 | 0.03 | 42.08 | 0.05 | 101.63 | 0.07 | 521.07 | 0.44 | 40.22 | 0.01 | 115.33 | 0.01 | 78714 | 87 | 39135 | 34 | [26 empty] | 57.68 | 0.06 | 57.86 | 0.05 | 58.17 | 0.04 | 58.08 | 0.08 | 58.02 | 0.07 | 58.09 | 0.06 | [18 empty] | 101.82 | 0.06 | [12 empty] | 103.65 | 0.05 | 102.22 | 0.06 | [20 empty] | 101.99 | 0.06 | 101.63 | 0.07 | 103.65 | 0.05 | 102.22 | 0.06 | 47.44 | 0.05 | 78.36 | 0.04 | [24 empty] | 94.88 | 0.1 | 94.54 | 0.08 | 76.8 | 0.07 | 77.53 | 0.07 | 76.75 | 0.07 | 77.49 | 0.07 | 75.14 | 0.07 | 74.99 | 0.07 |  |  | 82.75 | 0.12 | 77.9 | 0.12 | 76.21 | 0.1 | 75.58 | 0.09 | 89.78 | 0.16 | 87.23 | 0.12 | 87 | 0.14 | 83.07 | 0.16 | 84.05 | 0.22 | 80.88 | 0.11 | 85.45 | 0.08 | 84.59 | 0.09 | 81.34 | 0.1 | 81.05 | 0.09 | 83.81 | 0.09 | 82.39 | 0.12 | [30 empty] | 95.03 | 0.1 | 94.73 | 0.1 | 94.71 | 0.11 | 94.82 | 0.1 | 94.65 | 0.09 | 94.57 | 0.12 | [50 empty] | C8-55-1FE3 | 74.998 | 0.016 | 62.001 | 0.018 | 58.124 | 0.014 | 55.175 | 0.015 | 94.998 | 0.014 | 75.042 | 0.019 | 2035 | 2.1 | 2000.1 | 2.1 | 1.473 | 0.002 | -0.481 | 0.003 | 0.612 | 0.002 | 0.7644 | 0.0016 | 29.422 | 0.001 | 8577 | 31 | 1410 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.6253 | 9305.7633 | 346.1143 | 272.5751 | 1159.8802 | 8145.8831 | 0.0094269 | 28.9291 | 56.4987 | 14.1002 | 13.1209 | 0.013958 | 38.1978 | 0.0087818 | 27.6094 | 0.0085574 | 23.25 | 77.5114 | 63.8445 | 22.8537 | 56536.4461 | 46929.3803 | 7167 | 0.43266 | 52905.4043 | 43298.3384 | 6.1683 | 0.16383 | -6.0754 | -21.0127 | 52.3817 | 56536.4461 | 40567.7271 | 3687.4446 | 12281.2744 | 56536.4461 | 100%
3 | 5-2115 recalc | 75N0088 | 5-2115 | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/20/2013 | 2:36:05 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 8.59 lbs ck2: 10.35 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 8.59 | 10.35 | 7.6 | 8.1 | 230.4 | 1.3 | 32.9 | 0 | 38728 | 46 | 39736 | 146 | -3579 | 0 | 35146 | 46 | 3.2476 | 896.7 |  |  |  | 109.94 | 0.01 | 56.09 | [32 empty] | 83.3% air flow both stages closed | 2511.4 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper close 28% (set to 72% on Meriam M334 damper controller) with Both Stages Cooling, with Econo fully closed, The unit has NO Tape around the Unit. -0.488 Inlet static. | 74.999 | 0.01 | 62.002 | 0.032 | 115 | 0.043 | 80.01 | 0.026 | 74.74 | 0.05 | 60.55 | 0.02 | 63.77 | 0.02 | -0.034 | 0.003 | 0.9236 | 0.0019 | 39066 | 46 | 0 | 0 | 3.609 | 0.011 | 80047 | 69 | 7.397 | 0.021 | 51.2 | 0.08 | 230.4 | 0.9 | 230.2 | 0.9 | 229.6 | 0.9 | 32.9 | 0.1 | 30.8 | 0.1 | 33 | 0.1 | 7573.3 | 34.5 | 3810.3 | 42.9 | 3248.4 | 31.4 | 229 |  | 228 |  | 227 |  | 6.3 |  | 6.4 |  | 6 |  | 0.55 | 227 |  | 228 |  | 228 |  | 13 |  | 12.3 |  | 12.8 |  | 4290 |  | 0.86 | 227 | 228 | 229 | 13.2 | 12.5 | 12.3 | 4330 | 0.87 | [8 empty] | 10730 | [22 empty] | 346.4 | 0.41 | 184.83 | 0.09 | 142.04 | 0.1 | 42.79 | 0.08 | 327.7 | 0.41 | 126.24 | 0.14 | 137.62 | 0.1 | 11.38 | 0.09 | [8 empty] | 78.1 | 0.08 | 52.55 | 0.05 | 46.1 | 0.05 | 6.46 | 0.03 | 689.05 | 0.64 | 48.01 | 0.05 | 80047 | 69 | 42674 | 41 | [38 empty] | 350.35 | 0.41 | 226.82 | 0.08 | 142.95 | 0.09 | 83.86 | 0.07 | [6 empty] | 336.84 | 0.41 | 125.59 | 0.09 | 139.8 | 0.1 | 14.21 | 0.05 | [6 empty] | 84.24 | 0.06 | 78.93 | 0.09 | 49.92 | 0.04 | 29.01 | 0.11 | 124.58 | 0.11 | 649.27 | 0.69 | 47.79 | 0.03 | 114.39 | 0.02 | 80047 | 69 | 43243 | 48 | [26 empty] | 60.16 | 0.03 | 60.96 | 0.03 | 60.97 | 0.03 | 59.99 | 0.03 | 60.45 | 0.04 | 60.75 | 0.04 | [32 empty] | 125.43 | 0.11 | 125.32 | 0.1 | [16 empty] | 125.26 | 0.08 | 125.2 | 0.1 | 125.02 | 0.12 | 124.58 | 0.11 |  |  |  |  | 53.07 | 0.1 | 80.63 | 0.08 | [24 empty] | 114.63 | 0.22 |  |  | 77.02 | 0.06 | 75.4 | 0.05 | 75.25 | 0.04 | 76.42 | 0.06 | 75.21 | 0.04 | 75.28 | 0.04 |  |  | 89.56 | 0.1 | 90.11 | 0.2 | 88.72 | 0.19 | 96.54 | 0.17 | 80.18 | 0.1 | 80.23 | 0.06 | 79.45 | 0.04 | 88.3 | 0.12 | 76.68 | 0.05 | 76.44 | 0.04 | 76.91 | 0.04 | 82.81 | 0.1 | 76.67 | 0.06 | 75.9 | 0.04 | 76.91 | 0.06 | 77.6 | 0.08 | [30 empty] | 114.76 | 0.11 | 114.42 | 0.1 | 114.29 | 0.11 | 114.44 | 0.13 | 114.48 | 0.1 | 113.94 | 0.16 | [38 empty] | 126.12 | 0.11 | 125.94 | 0.1 | 125.68 | 0.1 | 125.75 | 0.11 |  |  |  |  | C8-55-CE3 | 74.999 | 0.01 | 62.002 | 0.032 | 61.041 | 0.01 | 57.463 | 0.012 | 115 | 0.043 | 80.01 | 0.026 | 2580.5 | 2.7 | 2511.4 | 2.6 | 1.142 | 0.002 | -0.488 | 0.003 | -0.034 | 0.003 | 0.9236 | 0.0019 | 29.263 | 0.002 | 10822 | 30 | 1500 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4097 | 11729.5445 | 336.9358 | 25.0657 | 102.9598 | 11626.5847 | 0.008826 | 27.7445 | 59.6313 | 14.6071 | 13.2 | 0.013777 | 42.9207 | 0.0087822 | 27.6101 | 0.0092186 | 24.6806 | 75.3533 | 62.1951 | 24.3366 | 39973.5078 | 44258.7575 | 9322 | 0.79593 | 36003.9696 | 40289.2192 | 3.3269 | 0.2187 | -3.4079 | -15.722 | 55.2304 | 39973.5078 | 34361.0817 | 4036.0537 | 1576.3724 | 39973.5078 | 100%
3 | 5-21151 recalc | 75N0089 | 5-21151 | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/20/2013 | 3:51:42 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 8.59 lbs ck2: 10.35 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 8.59 | 10.35 | 7.6 | 8.1 | 230.4 | 1.1 | 33 | 0 | 34326 | 60 | 35192 | 138 | -7603 | 0 | 26716 | 59 | 2.4607 | 896.8 |  |  | 3.1616 | 109.94 | 0.01 | 67 | [32 empty] | 83.3% air flow both stages 1 finger (0.74'') | 2522.2 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper close 28% (set to 72% on Meriam M334 damper controller) with Both Stages Cooling, with Econo open 1 finger (0.74''), The unit has NO Tape around the Unit. -0.428 Inlet static. | 75.012 | 0.022 | 62.006 | 0.032 | 115.01 | 0.039 | 80.001 | 0.032 | 74.74 | 0.05 | 62.17 | 0.02 | 65.07 | 0.02 | 0.013 | 0.003 | 0.9347 | 0.0021 | 34621 | 60 | 0 | 0 | 3.188 | 0.01 | 80966 | 67 | 7.456 | 0.02 | 57.25 | 0.08 | 230.4 | 0.9 | 230.1 | 0.9 | 229.6 | 0.9 | 33 | 0.1 | 30.9 | 0.1 | 33.1 | 0.1 | 7586 | 34.2 | 3814.3 | 45.4 | 3272 | 30 | 229 |  | 227 |  | 226 |  | 6.4 |  | 6.4 |  | 6.1 |  | 0.55 | 230 |  | 229 |  | 228 |  | 13 |  | 12.3 |  | 12.4 |  | 4310 |  | 0.86 | 227 | 226 | 230 | 13.3 | 12.5 | 12.4 | 4360 | 0.87 | [8 empty] | 10800 | [22 empty] | 346.78 | 0.38 | 184.83 | 0.1 | 142.12 | 0.09 | 42.71 | 0.09 | 328.04 | 0.37 | 126.38 | 0.11 | 137.7 | 0.09 | 11.32 | 0.07 | [8 empty] | 78.14 | 0.08 | 52.57 | 0.04 | 46.13 | 0.05 | 6.45 | 0.03 | 689.32 | 0.6 | 48.05 | 0.04 | 80966 | 67 | 42659 | 37 | [38 empty] | 352.98 | 0.34 | 230.63 | 0.08 | 143.55 | 0.08 | 87.08 | 0.07 | [6 empty] | 339.32 | 0.33 | 125.69 | 0.07 | 140.38 | 0.08 | 14.7 | 0.05 | [6 empty] | 86.21 | 0.07 | 84.26 | 0.05 | 51.1 | 0.04 | 33.16 | 0.07 | 124.65 | 0.09 | 655.11 | 0.7 | 47.82 | 0.02 | 115.26 | 0.01 | 80966 | 67 | 44178 | 48 | [26 empty] | 61.9 | 0.03 | 62.45 | 0.04 | 62.41 | 0.04 | 61.82 | 0.03 | 62.08 | 0.04 | 62.33 | 0.04 | [32 empty] | 125.56 | 0.1 | 125.43 | 0.08 | [16 empty] | 125.38 | 0.06 | 125.31 | 0.08 | 125.12 | 0.1 | 124.65 | 0.09 |  |  |  |  | 53.06 | 0.12 | 85.8 | 0.05 | [24 empty] | 114.92 | 0.23 | 116.29 | 0.08 | 76.8 | 0.06 | 75.42 | 0.05 | 75.26 | 0.05 | 76.18 | 0.05 | 75.21 | 0.05 | 75.3 | 0.05 |  |  | 85.79 | 0.13 | 83.53 | 0.1 | 91.06 | 0.2 | 102.54 | 0.14 | 80.61 | 0.1 | 80.05 | 0.07 | 81.09 | 0.07 | 101.28 | 0.15 | 76.98 | 0.05 | 76.35 | 0.05 | 77.27 | 0.06 | 85.4 | 0.17 | 77.29 | 0.06 | 76.15 | 0.04 | 77.12 | 0.07 | 79.61 | 0.14 | [30 empty] | 114.88 | 0.13 | 114.58 | 0.11 | 114.41 | 0.11 | 114.54 | 0.15 | 114.51 | 0.1 | 114.11 | 0.16 | [38 empty] | 126.23 | 0.09 | 126.07 | 0.08 | 125.79 | 0.07 | 125.83 | 0.09 |  |  |  |  | C8-55-1FE3 | 75.012 | 0.022 | 62.006 | 0.032 | 62.642 | 0.018 | 58.601 | 0.017 | 115.01 | 0.039 | 80.001 | 0.032 | 2599.6 | 2.9 | 2522.2 | 2.8 | 1.134 | 0.002 | -0.428 | 0.003 | 0.013 | 0.003 | 0.9347 | 0.0021 | 29.257 | 0.001 | 10857 | 29 | 1520 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4291 | 11777.933 | 336.0142 | 261.7023 | 1074.9555 | 10702.9775 | 0.0092366 | 29.009 | 61.2129 | 14.6072 | 13.2431 | 0.013766 | 42.9107 | 0.0087817 | 27.6128 | 0.0095349 | 25.4158 | 78.6926 | 63.9745 | 25.0668 | 46431.2273 | 49410.1513 | 9337 | 0.68633 | 42390.2838 | 45369.2079 | 3.9044 | 0.22736 | -3.9422 | -17.4798 | 56.0693 | 46431.2273 | 25875.6401 | 4111.0192 | 16444.5679 | 46431.2273 | 100%
3 | 5-282 recalc | 75N0090 | 5-282 | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/20/2013 | 0:14:52 | 10 Ton | 0:30:00 | 82/68 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 8.59 lbs ck2: 10.35 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 82 | 68 | 75 | 62 | 8.59 | 10.35 | 7.6 | 8.1 | 230.5 | 1.4 | 26.2 | 0 | 53494 | 64 | 54712 | 204 | 13404 | 184 | 66909 | 192 | 8.5158 | 896.3 |  |  |  | 109.64 | 0.06 | 17.32 | [32 empty] | 83.3% air flow both stages closed | 2543.1 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper close 28% (set to 72% on Meriam M334 damper controller) with Both Stages Cooling, with Econo fully closed, The unit has NO Tape around the Unit. -0.496 Inlet static. | 74.89 | 0.01 | 62.001 | 0.031 | 82.004 | 0.018 | 67.996 | 0.028 | 74.63 | 0.07 | 55.52 | 0.03 | 59.75 | 0.01 | -0.024 | 0.002 | 0.9354 | 0.002 | 53947 | 64 | 13404 | 184 | 8.574 | 0.041 | 80931 | 76 | 10.301 | 0.039 | 16.76 | 0.23 | 230.5 | 1 | 230.2 | 1 | 229.6 | 1 | 26.2 | 0.1 | 24.2 | 0.1 | 26.6 | 0.1 | 5980.5 | 42.7 | 3582.7 | 56.7 | 1876.3 | 33 | 227 |  | 228 |  | 228 |  | 6.3 |  | 6.4 |  | 6.1 |  | 0.53 | 228 |  | 230 |  | 227 |  | 9.7 |  | 9.2 |  | 9.1 |  | 2910 |  | 0.77 | 230 | 228 | 231 | 9.6 | 8.9 | 8.7 | 2780 | 0.76 | [8 empty] | 7830 | [22 empty] | 229.88 | 0.18 | 165.46 | 0.07 | 111 | 0.06 | 54.46 | 0.08 | 210.84 | 0.17 | 88 | 0.09 | 104.93 | 0.06 | 16.93 | 0.08 | [8 empty] | 68.73 | 0.07 | 47.7 | 0.3 | 39.91 | 0.04 | 7.79 | 0.32 | 605.34 | 0.53 | 35.75 | 0.03 | 80931 | 76 | 44727 | 58 | [38 empty] | 220.84 | 0.18 | 183.16 | 0.04 | 108.16 | 0.06 | 75 | 0.04 | [6 empty] | 208.73 | 0.17 | 89.22 | 0.05 | 104.23 | 0.06 | 15.01 | 0.04 | [6 empty] | 64.21 | 0.05 | 71.54 | 0.03 | 36.73 | 0.04 | 34.81 | 0.06 | 87.64 | 0.06 | 539.55 | 0.52 | 36.13 | 0.02 | 114.11 | 0.01 | 80931 | 76 | 42075 | 38 | [26 empty] | 55.44 | 0.03 | 55.86 | 0.03 | 55.83 | 0.03 | 55.32 | 0.04 | 55.6 | 0.03 | 55.81 | 0.03 | [32 empty] | 88.5 | 0.05 | 88.7 | 0.05 | [16 empty] | 89.03 | 0.04 | 88.49 | 0.05 | 87.98 | 0.06 | 87.64 | 0.06 |  |  |  |  | 48.45 | 0.33 | 72.67 | 0.04 | [24 empty] | 81.23 | 0.14 | 81.92 | 0.12 | 75.19 | 0.04 | 74.98 | 0.05 | 74.53 | 0.04 | 74.52 | 0.04 | 74.51 | 0.05 | 74.55 | 0.05 |  |  | 76.52 | 0.02 | 76.63 | 0.03 | 76.55 | 0.04 | 77.58 | 0.02 | 75.17 | 0.03 | 75.47 | 0.04 | 75.36 | 0.03 | 76.59 | 0.02 | 74.96 | 0.03 | 74.75 | 0.04 | 74.77 | 0.05 | 75.57 | 0.04 | 74.81 | 0.05 | 74.7 | 0.05 | 74.76 | 0.05 | 74.81 | 0.05 | [30 empty] | 79.46 | 0.05 | 79.03 | 0.05 | 79.15 | 0.06 | 79.33 | 0.07 | 79.13 | 0.05 | 79.33 | 0.07 | [38 empty] | 89.15 | 0.05 | 89.17 | 0.05 | 88.93 | 0.05 | 88.78 | 0.06 |  |  |  |  | C8-55-CE3 | 74.89 | 0.01 | 62.001 | 0.031 | 56.043 | 0.008 | 53.131 | 0.017 | 82.004 | 0.018 | 67.996 | 0.028 | 2585.2 | 2.8 | 2543.1 | 2.7 | 1.145 | 0.002 | -0.496 | 0.003 | -0.024 | 0.002 | 0.9354 | 0.002 | 29.287 | 0.001 | 7857 | 29 | 1530 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4223 | 11874.1491 | 342.085 | 24.5165 | 106.9918 | 11767.1573 | 0.0088301 | 27.6516 | 54.6207 | 13.7487 | 13.063 | 0.011339 | 32.1249 | 0.0088073 | 27.611 | 0.0078924 | 22.0205 | 74.9544 | 62.0586 | 21.6742 | 70977.5013 | 57946.7749 | 6327 | 0.30424 | 66923.1474 | 53892.4209 | 8.5176 | 0.18297 | -5.9775 | -20.3337 | 50.0671 | 70977.5013 | 66382.2008 | 4112.3457 | 482.9548 | 70977.5013 | 100%
3 | 5-2821 recalc | 75N0091 | 5-2821 | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/19/2013 | 23:15:00 | 10 Ton | 0:30:00 | 82/68 75/62 | ENG 2 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 8.59 lbs ck2: 10.35 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 82 | 68 | 75 | 62 | 8.59 | 10.35 | 7.6 | 8.1 | 230.4 | 1.2 | 26.1 | 0 | 52649 | 55 | 53908 | 223 | 11655 | 196 | 64314 | 204 | 8.172 | 896.4 |  |  |  | 109.91 | 0.07 | 20.89 | [32 empty] | 83.3% air flow both stages 1 finger (0.74'') | 2558 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper close 28% (set to 72% on Meriam M334 damper controller) with Both Stages Cooling, with Econo open 1 finger (0.74''), The unit has NO Tape around the Unit. -0.434 Inlet static. | 74.946 | 0.008 | 62.002 | 0.028 | 82.001 | 0.018 | 67.995 | 0.029 | 74.69 | 0.08 | 55.94 | 0.03 | 60.11 | 0.02 | 0.024 | 0.003 | 0.9473 | 0.002 | 53093 | 55 | 11652 | 196 | 8.229 | 0.039 | 81298 | 69 | 10.331 | 0.038 | 20.35 | 0.24 | 230.4 | 0.8 | 230.1 | 0.8 | 229.7 | 0.8 | 26.1 | 0.1 | 24.2 | 0.1 | 26.7 | 0.1 | 5962.2 | 34.7 | 3605.6 | 42.5 | 1907.2 | 28.3 | 229.5 |  | 228.9 |  | 228.6 |  | 6.3 |  | 6.4 |  | 6.1 |  | 0.55 | 228.5 |  | 228.6 |  | 229.6 |  | 9.7 |  | 9.3 |  | 9.1 |  | 2900 |  | 0.078 | 228.2 | 228.7 | 230.2 | 9.6 | 9 | 8.7 | 2790 | 0.78 | [8 empty] | 7880 | [22 empty] | 230.13 | 0.16 | 166.09 | 0.07 | 111.08 | 0.05 | 55.01 | 0.08 | 211.07 | 0.15 | 87.94 | 0.07 | 105 | 0.05 | 17.06 | 0.07 | [8 empty] | 68.95 | 0.08 | 49.25 | 0.37 | 40.06 | 0.05 | 9.19 | 0.4 | 605.85 | 0.48 | 35.74 | 0.02 | 81298 | 69 | 44935 | 55 | [38 empty] | 221.35 | 0.16 | 183.69 | 0.04 | 108.32 | 0.05 | 75.36 | 0.05 | [6 empty] | 209.19 | 0.15 | 89.24 | 0.03 | 104.38 | 0.05 | 15.14 | 0.04 | [6 empty] | 64.53 | 0.05 | 72.24 | 0.03 | 36.95 | 0.04 | 35.29 | 0.05 | 87.68 | 0.04 | 540.9 | 0.52 | 36.14 | 0.01 | 114.22 | 0.01 | 81298 | 69 | 42234 | 39 | [26 empty] | 55.91 | 0.04 | 56.25 | 0.03 | 56.23 | 0.04 | 55.78 | 0.03 | 56.03 | 0.04 | 56.21 | 0.03 | [32 empty] | 88.55 | 0.04 | 88.72 | 0.04 | [16 empty] | 89.04 | 0.03 | 88.51 | 0.04 | 88.01 | 0.04 | 87.68 | 0.04 |  |  |  |  | 50.08 | 0.43 | 73.38 | 0.03 | [24 empty] | 81.38 | 0.14 | 81.81 | 0.12 | 75.19 | 0.05 | 75.03 | 0.06 | 74.59 | 0.05 | 74.55 | 0.05 | 74.57 | 0.06 | 74.61 | 0.05 |  |  | 76.16 | 0.04 | 75.76 | 0.04 | 76.79 | 0.04 | 78.38 | 0.04 | 75.28 | 0.04 | 75.49 | 0.04 | 75.62 | 0.04 | 78.28 | 0.03 | 75.01 | 0.04 | 74.77 | 0.05 | 74.89 | 0.06 | 76.06 | 0.04 | 74.94 | 0.04 | 74.75 | 0.06 | 74.84 | 0.06 | 75.22 | 0.05 | [30 empty] | 79.48 | 0.06 | 79.01 | 0.05 | 79.1 | 0.05 | 79.37 | 0.06 | 79.08 | 0.04 | 79.29 | 0.08 | [38 empty] | 89.21 | 0.04 | 89.21 | 0.04 | 88.95 | 0.04 | 88.8 | 0.05 |  |  |  |  | C8-55-1FE3 | 74.946 | 0.008 | 62.002 | 0.028 | 56.487 | 0.007 | 53.557 | 0.014 | 82.001 | 0.018 | 67.995 | 0.029 | 2602.7 | 2.7 | 2558 | 2.6 | 1.135 | 0.002 | -0.434 | 0.003 | 0.024 | 0.003 | 0.9473 | 0.002 | 29.284 | 0.001 | 7870 | 28 | 1580 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4747 | 11943.3038 | 341.0841 | 255.6674 | 1115.7546 | 10827.5492 | 0.0090324 | 28.0325 | 55.0123 | 13.7486 | 13.0753 | 0.011339 | 32.1241 | 0.0087947 | 27.6109 | 0.0080248 | 22.2724 | 75.6079 | 62.596 | 21.9132 | 73084.2944 | 59035.0538 | 6290 | 0.29374 | 68855.8745 | 54806.6339 | 8.7492 | 0.18052 | -6.1193 | -20.5956 | 50.4753 | 73084.2944 | 63758.6578 | 4289.937 | 5035.6996 | 73084.2944 | 100%
3 | 5-2951 recalc | 75N0092 | 5-2951 | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/19/2013 | 11:13:10 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 8.59 lbs ck2: 10.35 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 8.59 | 10.35 | 7.6 | 8.1 | 230.3 | 1.3 | 28.4 | 0 | 45000 | 73 | 46200 | 171 | 923 | 135 | 45924 | 128 | 5.1369 | 896.2 |  |  |  | 109.55 | 0.01 | 79.4987 | [32 empty] | 83.3% air flow both stages 1 finger (0.74") | 2547.9 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper close 28% (set to 72% on Meriam M334 damper controller) with Both Stages Cooling, with Econo open 1 finger, The unit has NO Tape around the Unit. -0.435 Inlet static. | 74.977 | 0.029 | 62.021 | 0.021 | 94.999 | 0.027 | 75.001 | 0.033 | 74.73 | 0.06 | 58.5 | 0.02 | 61.91 | 0.02 | 0.02 | 0.002 | 0.9441 | 0.0018 | 45384 | 73 | 927 | 135 | 5.18 | 0.022 | 82433 | 65 | 9.221 | 0.029 | 43.82 | 0.16 | 230.3 | 1.1 | 230.2 | 1.1 | 229.7 | 1.1 | 28.4 | 0.1 | 26.4 | 0.1 | 29.1 | 0.1 | 6516.5 | 43 | 3685.1 | 55.8 | 2423.5 | 33.5 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.3 |  | 6.1 |  | 0.56 | 228 |  | 228 |  | 229 |  | 10.8 |  | 10.4 |  | 10.3 |  | 3420 |  | 0.82 | 229 | 229 | 229 | 10.8 | 10.3 | 10 | 3350 | 0.82 | [8 empty] | 8930 | [22 empty] | 273.57 | 0.31 | 173.11 | 0.07 | 123.72 | 0.09 | 49.39 | 0.06 | 254.43 | 0.32 | 105.28 | 0.1 | 118.34 | 0.09 | 13.06 | 0.07 | [8 empty] | 73.18 | 0.05 | 48.72 | 0.04 | 42.93 | 0.04 | 5.79 | 0.03 | 647.68 | 0.6 | 41.15 | 0.03 | 82433 | 65 | 44300 | 35 | [38 empty] | 269.69 | 0.31 | 201.45 | 0.07 | 122.65 | 0.09 | 78.8 | 0.05 | [6 empty] | 256.82 | 0.3 | 103.36 | 0.07 | 119.02 | 0.08 | 15.67 | 0.05 | [6 empty] | 74.89 | 0.06 | 78.91 | 0.04 | 44.05 | 0.04 | 34.86 | 0.05 | 101.94 | 0.08 | 593.35 | 0.69 | 40.54 | 0.02 | 114.7 | 0.01 | 82433 | 65 | 44004 | 47 | [26 empty] | 58.37 | 0.04 | 58.71 | 0.02 | 58.68 | 0.03 | 58.22 | 0.04 | 58.42 | 0.04 | 58.62 | 0.03 | [32 empty] | 102.76 | 0.09 | 102.88 | 0.07 | [16 empty] | 103.11 | 0.07 | 102.69 | 0.08 | 102.27 | 0.08 | 101.94 | 0.08 |  |  |  |  | 49.61 | 0.04 | 77.94 | 0.05 | 103.63 | 0.08 | 103.64 | 0.07 | [20 empty] | 94.33 | 0.19 | 95.36 | 0.12 | 75.79 | 0.05 | 75.12 | 0.06 | 74.84 | 0.06 | 75.22 | 0.05 | 74.81 | 0.06 | 74.85 | 0.06 |  |  | 79.83 | 0.08 | 78.64 | 0.07 | 82.93 | 0.1 | 88.53 | 0.08 | 77.34 | 0.05 | 77.01 | 0.06 | 77.63 | 0.06 | 87.25 | 0.1 | 75.74 | 0.05 | 75.36 | 0.04 | 75.74 | 0.06 | 79.77 | 0.1 | 75.83 | 0.06 | 75.26 | 0.06 | 75.74 | 0.06 | 76.98 | 0.08 | [30 empty] | 93.24 | 0.08 | 92.82 | 0.09 | 92.82 | 0.09 | 93.05 | 0.1 | 92.84 | 0.09 | 92.81 | 0.1 | [38 empty] | 103.48 | 0.08 | 103.42 | 0.08 | 103.2 | 0.08 | 103.11 | 0.08 |  |  |  |  | C8-55-1FE3 | 74.977 | 0.029 | 62.021 | 0.021 | 59.038 | 0.008 | 56.093 | 0.019 | 94.999 | 0.027 | 75.001 | 0.033 | 2601.7 | 2.5 | 2547.9 | 2.5 | 1.13 | 0.002 | -0.435 | 0.003 | 0.02 | 0.002 | 0.9441 | 0.0018 | 29.321 | 0.001 | 8940 | 29 | 1550 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4508 | 11873.9885 | 338.2407 | 259.2114 | 1103.0353 | 10770.9532 | 0.0092757 | 28.6027 | 57.5872 | 14.0999 | 13.1466 | 0.013922 | 38.1581 | 0.0087999 | 27.6241 | 0.0088761 | 23.8193 | 76.8527 | 63.3944 | 23.4654 | 61000.0928 | 54901.9876 | 7390 | 0.41348 | 56864.3584 | 50766.2532 | 6.3607 | 0.16987 | -5.1373 | -19.2655 | 53.6449 | 61000.0928 | 45178.3294 | 4202.4146 | 11619.3488 | 61000.0928 | 100%
3 | 7-3B | 75N0093 | 7-3B | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/26/2013 | 9:55:57 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 5.55 lbs ck2: 7.11 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 5.55 | 7.11 | 7.6 | 8.1 | 230.3 | 1.3 | 24.3 | 0 | 36976 | 53 | 37624 | 128 | 4312 | 103 | 41291 | 110 | 5.8214 |  |  |  |  | 115.25 | 0.01 | 4.18 | [32 empty] | Closed Damper, -40% charge, both stages B-Test | 2539.4 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.412 Inlet static. | 75.006 | 0.014 | 61.998 | 0.013 | 81.993 | 0.037 | 67.994 | 0.027 | 74.77 | 0.05 | 61.55 | 0.02 | 64.94 | 0.02 | 0.037 | 0.002 | 0.9437 | 0.002 | 36976 | 53 | 4312 | 103 | 5.821 | 0.029 | 43097 | 311 | 6.076 | 0.05 | 4.18 | 0.72 | 230.3 | 1.1 | 230 | 1.1 | 229.7 | 1.1 | 24.3 | 0.1 | 22.7 | 0.1 | 25.2 | 0.1 | 5514.4 | 45.6 | 3588.7 | 59.3 | 1578.5 | 36.1 | 231.8 |  | 227.6 |  | 229.6 |  | 6.2 |  | 6.4 |  | 6.1 |  | 0.57 | 228.5 |  | 229.6 |  | 228.2 |  | 8.8 |  | 8.6 |  | 8.4 |  | 2540 |  | 0.75 | 228.3 | 228.9 | 229.7 | 8.6 | 8.2 | 7.9 | 2380 | 0.73 | [8 empty] | 7070 | [22 empty] | 198.05 | 0.23 | 193.31 | 0.07 | 100.63 | 0.08 | 92.68 | 0.09 | 183.45 | 0.29 | 91.29 | 0.12 | 95.49 | 0.1 | 4.2 | 0.1 | [8 empty] | 49.41 | 0.08 | 73.86 | 0.03 | 25.25 | 0.07 | 48.61 | 0.08 | 392.18 | 2.09 | 36.76 | 0.04 | 43097 | 311 | 30779 | 164 | [38 empty] | 184.39 | 0.19 | 208.34 | 0.09 | 95.83 | 0.07 | 112.51 | 0.11 | [6 empty] | 175.35 | 0.28 | 91.59 | 0.06 | 92.52 | 0.11 | 0.93 | 0.08 | [6 empty] | 37.49 | 0.12 | 76.25 | 0.03 | 14.41 | 0.11 | 61.83 | 0.12 | 91.24 | 0.07 | 221.89 | 3.31 | 36.86 | 0.02 | 116.22 | 0.01 | 43097 | 311 | 17607 | 264 | [26 empty] | 61.26 | 0.03 | 61.98 | 0.03 | 62 | 0.03 | 61.39 | 0.03 | 61.76 | 0.04 | 61.85 | 0.03 | [32 empty] | 94.32 | 0.07 | 91.21 | 0.06 | [16 empty] | 91.1 | 0.04 | 91.23 | 0.06 | 92.9 | 0.08 | 91.24 | 0.07 |  |  |  |  | 74.06 | 0.03 | 78.39 | 0.04 | 94.32 | 0.07 | 91.28 | 0.06 | [20 empty] | 81.1 | 0.14 | 81.93 | 0.13 | 75.19 | 0.04 | 74.83 | 0.31 | 74.58 | 0.04 | 74.54 | 0.03 | 74.53 | 0.04 | 74.59 | 0.04 |  |  | 76.28 | 0.03 | 76.7 | 0.04 | 76.61 | 0.04 | 77.27 | 0.03 | 75.23 | 0.03 | 75.59 | 0.03 | 75.72 | 0.04 | 76.05 | 0.03 | 75.11 | 0.03 | 74.88 | 0.03 | 74.91 | 0.05 | 75.56 | 0.04 | 74.81 | 0.05 | 74.74 | 0.04 | 74.87 | 0.04 | 75.44 | 0.05 | [30 empty] | 79.36 | 0.07 | 79.18 | 0.07 | 79.27 | 0.07 | 79.22 | 0.07 | 79.29 | 0.07 | 79.22 | 0.08 | [38 empty] | 94.38 | 0.07 | 94.03 | 0.07 | 91.1 | 0.07 | 91.59 | 0.07 |  |  |  |  | C8-55-CE3 | 75.006 | 0.014 | 61.998 | 0.013 | 62.01 | 0.014 | 56.742 | 0.012 | 81.993 | 0.037 | 67.994 | 0.027 | 2609.8 | 2.7 | 2539.4 | 2.6 | 1.121 | 0.002 | -0.412 | 0.002 | 0.037 | 0.002 | 0.9437 | 0.002 | 29.288 | 0.001 | 7093 | 29 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4469 | 11845.3443 | 334.4274 | 22.3441 | 97.513 | 11747.8314 | 0.008799 | 27.6443 | 60.5631 | 13.7484 | 13.2194 | 0.011341 | 32.1234 | 0.0087779 | 27.6071 | 0.0085572 | 24.1972 | 75.0638 | 62.0507 | 23.8444 | 45010.8198 | 41223.7906 | 5553 | 0.42106 | 40896.2005 | 37109.1712 | 5.7657 | 0.35747 | -3.7999 | -14.5007 | 52.4957 | 45010.8198 | 40391.8859 | 4178.5323 | 440.4016 | 45010.8198 | 100%
3 | 7-3F | 75N0094 | 7-3F | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/26/2013 | 3:38:51 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 5.55 lbs ck2: 7.11 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 5.55 | 7.11 | 7.6 | 8.1 | 230.4 | 1.5 | 30.3 | 0 | 18552 | 43 | 18921 | 76 | -5981 | 95 | 12565 | 91 | 1.2859 |  |  |  |  | 116.06 | 0.01 | 66.03 | [32 empty] | Damper Closed, -40% Charge, Both Stages 115 Ambient | 2502.9 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.41 Inlet static. | 75 | 0.013 | 62.003 | 0.01 | 114.984 | 0.035 | 80.007 | 0.033 | 74.73 | 0.03 | 67.89 | 0.01 | 69.84 | 0.01 | 0.032 | 0.002 | 0.931 | 0.0019 | 18552 | 43 | -5981 | 95 | 1.286 | 0.01 | 36988 | 245 | 3.785 | 0.028 | 66.03 | 0.35 | 230.4 | 1.1 | 230.1 | 1.1 | 229.5 | 1.1 | 30.3 | 0.1 | 28.4 | 0.1 | 30.5 | 0.1 | 6957.3 | 41.7 | 3694.1 | 55.5 | 2814.1 | 35.2 | 227 |  | 228 |  | 228 |  | 6.2 |  | 6.4 |  | 6.1 |  | 0.45 | 226 |  | 228 |  | 229 |  | 11.8 |  | 11.3 |  | 11.3 |  | 3860 |  | 0.85 | 227 | 228 | 229 | 11.6 | 11 | 10.9 | 3730 | 0.84 | [8 empty] | 9730 | [22 empty] | 308.43 | 0.35 | 246.23 | 0.09 | 132.86 | 0.09 | 113.38 | 0.07 | 293.6 | 0.42 | 127.6 | 0.11 | 129.06 | 0.11 | 1.46 | 0.07 | [8 empty] | 59.91 | 0.06 | 81.52 | 0.03 | 33.53 | 0.05 | 47.99 | 0.06 | 339.45 | 3.01 | 48.47 | 0.04 | 36988 | 245 | 22945 | 203 | [38 empty] | 296.72 | 0.4 | 267.4 | 0.1 | 129.87 | 0.1 | 137.53 | 0.11 | [6 empty] | 286.99 | 0.41 | 126.96 | 0.08 | 127.31 | 0.11 | 0.36 | 0.05 | [6 empty] | 51.72 | 0.12 | 90.19 | 0.04 | 27.12 | 0.1 | 63.07 | 0.11 | 126.54 | 0.1 | 277.47 | 2.5 | 48.25 | 0.03 | 117.93 | 0.01 | 36988 | 245 | 19333 | 172 | [26 empty] | 67.39 | 0.02 | 68.37 | 0.03 | 68.52 | 0.03 | 67.45 | 0.02 | 67.93 | 0.03 | 68.01 | 0.03 | [32 empty] | 128.92 | 0.08 | 126.48 | 0.08 | [16 empty] | 125.95 | 0.08 | 126.84 | 0.09 | 128.34 | 0.08 | 126.54 | 0.1 |  |  |  |  | 82.63 | 0.03 | 93.72 | 0.04 | [24 empty] | 114.14 | 0.14 | 116.33 | 0.12 | 76.36 | 0.03 | 75.34 | 0.03 | 75.23 | 0.03 | 75.88 | 0.03 | 75.07 | 0.03 | 75.21 | 0.02 |  |  | 86.41 | 0.14 | 90.7 | 0.13 | 89.23 | 0.16 | 92.82 | 0.17 | 79.61 | 0.05 | 80.39 | 0.06 | 81.41 | 0.06 | 83.42 | 0.08 | 77.19 | 0.05 | 76.61 | 0.03 | 77.16 | 0.04 | 81.63 | 0.1 | 75.81 | 0.03 | 75.59 | 0.03 | 76.76 | 0.04 | 81.09 | 0.09 | [30 empty] | 115.4 | 0.13 | 114.86 | 0.16 | 115.28 | 0.14 | 115.29 | 0.14 | 115.27 | 0.15 | 115.16 | 0.14 | [38 empty] | 128.85 | 0.08 | 128.16 | 0.08 | 126.36 | 0.11 | 127.04 | 0.11 |  |  |  |  | C8-55-CE3 | 75 | 0.013 | 62.003 | 0.01 | 68.288 | 0.009 | 60.464 | 0.013 | 114.984 | 0.035 | 80.007 | 0.033 | 2609 | 2.6 | 2502.9 | 2.5 | 1.127 | 0.002 | -0.41 | 0.002 | 0.032 | 0.002 | 0.931 | 0.0019 | 29.187 | 0.001 | 9771 | 28 | 1530 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.457 | 11695.2569 | 331.3847 | 22.975 | 94.3747 | 11600.8822 | 0.0088229 | 27.7343 | 66.831 | 14.6067 | 13.3849 | 0.013778 | 42.9177 | 0.0087826 | 27.6108 | 0.0093699 | 26.6147 | 75.3256 | 62.1805 | 26.2589 | 17255.3021 | 23843.1336 | 8241 | 1.63 | 13164.4283 | 19752.2598 | 1.3473 | 0.53354 | -1.4754 | -8.4946 | 57.1146 | 17255.3021 | 11650.1507 | 4160.5668 | 1444.5846 | 17255.3021 | 100%
3 | 7-4A | 75N0095 | 7-4A | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/24/2013 | 23:41:51 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 10.11 lbs ck2: 11.97 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 10.11 | 11.97 | 7.6 | 8.1 | 230.3 | 1.3 | 29 | 0 | 49959 | 67 | 50790 | 127 | 5323 | 148 | 55288 | 174 | 5.9933 |  |  |  |  | 109.45 | 0.01 | 37.52 | [32 empty] | Closed Damper, +20% Charge, Both Stages A-Test | 2543.5 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Closed Damper, The unit has NO Tape around the Unit. -0.413 Inlet static. | 75.003 | 0.008 | 62.004 | 0.023 | 95.015 | 0.02 | 75.007 | 0.025 | 74.76 | 0.04 | 56.96 | 0.01 | 61.43 | 0.02 | 0.007 | 0.002 | 0.9407 | 0.0019 | 49959 | 67 | 5323 | 148 | 5.993 | 0.026 | 88494 | 61 | 9.593 | 0.029 | 37.52 | 0.18 | 230.3 | 1 | 229.9 | 1 | 229.7 | 1 | 29 | 0.1 | 27.3 | 0.1 | 29.6 | 0.1 | 6665.4 | 38.1 | 3724.6 | 51.3 | 2559.4 | 32.5 | 228 |  | 229 |  | 229 |  | 6.2 |  | 6.4 |  | 6.1 |  | 0.57 | 227 |  | 227 |  | 228 |  | 11 |  | 10.6 |  | 10.6 |  | 3510 |  | 0.83 | 228 | 229 | 228 | 11.2 | 10.6 | 10.5 | 3530 | 0.83 | [8 empty] | 9210 | [22 empty] | 282.7 | 0.24 | 157.77 | 0.05 | 126.19 | 0.06 | 31.58 | 0.07 | 262.89 | 0.23 | 102.42 | 0.09 | 120.75 | 0.06 | 18.33 | 0.07 | [8 empty] | 74.46 | 0.04 | 48.63 | 0.04 | 43.76 | 0.03 | 4.87 | 0.03 | 686.55 | 0.58 | 40.24 | 0.03 | 88494 | 61 | 47516 | 41 | [38 empty] | 286.54 | 0.33 | 194.82 | 0.08 | 127.21 | 0.09 | 67.61 | 0.1 | [6 empty] | 272.74 | 0.31 | 102.67 | 0.07 | 123.49 | 0.09 | 20.82 | 0.05 | [6 empty] | 77.65 | 0.05 | 68.05 | 0.19 | 45.82 | 0.03 | 22.22 | 0.21 | 101.54 | 0.08 | 638.55 | 0.69 | 40.32 | 0.02 | 112.78 | 0.04 | 88494 | 61 | 46267 | 49 | [26 empty] | 56.69 | 0.02 | 57.39 | 0.02 | 57.45 | 0.02 | 56.55 | 0.02 | 57.01 | 0.03 | 57.22 | 0.03 | [32 empty] | 101.97 | 0.07 | 102.31 | 0.06 | [16 empty] | 102.65 | 0.05 | 102.08 | 0.07 | 101.38 | 0.07 | 101.54 | 0.08 |  |  |  |  | 49.81 | 0.04 | 69.36 | 0.17 | [24 empty] | 93.24 | 0.16 | 96.14 | 0.1 | 75.64 | 0.03 | 75.22 | 0.03 | 74.91 | 0.03 | 75.09 | 0.03 | 74.81 | 0.04 | 74.91 | 0.03 |  |  | 80.16 | 0.07 | 81.59 | 0.09 | 81.42 | 0.08 | 83.68 | 0.09 | 77.05 | 0.03 | 77.25 | 0.04 | 77.86 | 0.04 | 78.97 | 0.04 | 76 | 0.04 | 75.54 | 0.03 | 75.83 | 0.04 | 78.03 | 0.05 | 75.29 | 0.04 | 75.16 | 0.04 | 75.7 | 0.04 | 77.64 | 0.05 | [30 empty] | 93.66 | 0.08 | 93.22 | 0.1 | 93.61 | 0.08 | 93.6 | 0.08 | 93.57 | 0.09 | 93.5 | 0.08 | [38 empty] | 102.7 | 0.07 | 102.79 | 0.07 | 102.78 | 0.07 | 102.74 | 0.08 |  |  |  |  | C8-55-CE3 | 75.003 | 0.008 | 62.004 | 0.023 | 57.497 | 0.009 | 54.846 | 0.013 | 95.015 | 0.02 | 75.007 | 0.025 | 2597.5 | 2.6 | 2543.5 | 2.6 | 1.096 | 0.002 | -0.413 | 0.002 | 0.007 | 0.002 | 0.9407 | 0.0019 | 29.274 | 0.001 | 9225 | 28 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4733 | 11892.6866 | 327.4971 | 22.6557 | 96.4051 | 11796.2815 | 0.0088242 | 27.697 | 56.0237 | 14.1003 | 13.1047 | 0.013923 | 38.1636 | 0.0087826 | 27.6115 | 0.0085162 | 23.0524 | 75.1667 | 62.1257 | 22.6932 | 59508.5877 | 54639.0295 | 7665 | 0.43961 | 55302.0551 | 50432.4969 | 5.9948 | 0.15097 | -5.0038 | -19.1431 | 52.6198 | 59508.5877 | 54219.7523 | 4271.5546 | 1017.2808 | 59508.5877 | 100%
3 | 7-4B | 75N0096 | 7-4B | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/24/2013 | 21:29:28 | 10 Ton | 0:30:00 | 82/68 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 10.11 lbs ck2: 11.97 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 82 | 68 | 75 | 62 | 10.11 | 11.97 | 7.6 | 8.1 | 230.2 | 1.2 | 26.5 | 0 | 57321 | 67 | 58303 | 187 | 14171 | 138 | 71505 | 151 | 8.735 |  |  |  |  | 109.19 | 0.01 | 18.9 | [32 empty] | Closed Damper, +20% Charge, Both Stages B-Test | 2553.2 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Closed Damper, The unit has NO Tape around the Unit. -0.34 Inlet static. | 75.002 | 0.012 | 62.002 | 0.02 | 82.077 | 0.013 | 68.005 | 0.02 | 74.83 | 0.07 | 54.56 | 0.03 | 59.55 | 0.02 | 0.013 | 0.003 | 0.9439 | 0.002 | 57321 | 67 | 14171 | 138 | 8.736 | 0.033 | 88173 | 61 | 10.772 | 0.036 | 18.9 | 0.17 | 230.2 | 1 | 229.7 | 1 | 229.7 | 1 | 26.5 | 0.1 | 25.2 | 0.1 | 27.3 | 0.1 | 6065.9 | 41.7 | 3682.1 | 56.5 | 2119.7 | 32.4 | 231 |  | 228 |  | 227 |  | 6.3 |  | 6.6 |  | 6.1 |  | 0.56 | 228 |  | 227 |  | 227 |  | 10 |  | 9.5 |  | 9.1 |  | 3040 |  | 0.8 | 227 | 228 | 228 | 9.9 | 9.4 | 9.2 | 2960 | 0.79 | [8 empty] | 8210 | [22 empty] | 241.85 | 0.2 | 153.02 | 0.06 | 114.63 | 0.06 | 38.39 | 0.05 | 221.87 | 0.21 | 87.89 | 0.08 | 108.48 | 0.07 | 20.59 | 0.07 | [8 empty] | 71.27 | 0.04 | 46.07 | 0.04 | 41.62 | 0.03 | 4.45 | 0.04 | 652.58 | 0.5 | 35.72 | 0.02 | 88173 | 61 | 47943 | 36 | [38 empty] | 237.61 | 0.22 | 179.61 | 0.05 | 113.36 | 0.07 | 66.25 | 0.06 | [6 empty] | 224.37 | 0.21 | 88.84 | 0.06 | 109.27 | 0.06 | 20.44 | 0.06 | [6 empty] | 70.3 | 0.05 | 67.45 | 0.05 | 40.96 | 0.04 | 26.49 | 0.07 | 87.59 | 0.07 | 590.7 | 0.66 | 36.01 | 0.02 | 113.07 | 0.01 | 88173 | 61 | 45520 | 49 | [26 empty] | 54.34 | 0.03 | 54.89 | 0.03 | 54.93 | 0.03 | 54.29 | 0.03 | 54.65 | 0.03 | 54.8 | 0.04 | [32 empty] | 88.29 | 0.06 | 88.46 | 0.06 | [16 empty] | 89 | 0.05 | 88.19 | 0.07 | 87.66 | 0.06 | 87.59 | 0.07 |  |  |  |  | 47.44 | 0.04 | 68.39 | 0.06 | [24 empty] | 80.62 | 0.2 | 82.71 | 0.15 | 75.2 | 0.06 | 75.11 | 0.06 | 74.64 | 0.05 | 74.56 | 0.05 | 74.6 | 0.06 | 74.66 | 0.06 |  |  | 76.27 | 0.04 | 76.64 | 0.04 | 76.66 | 0.05 | 77.27 | 0.05 | 75.3 | 0.05 | 75.58 | 0.04 | 75.73 | 0.05 | 76.03 | 0.05 | 75.18 | 0.05 | 74.92 | 0.05 | 74.88 | 0.07 | 75.5 | 0.06 | 74.82 | 0.07 | 74.76 | 0.06 | 74.85 | 0.06 | 75.33 | 0.06 | [30 empty] | 79.59 | 0.08 | 79.34 | 0.09 | 79.53 | 0.08 | 79.5 | 0.09 | 79.54 | 0.08 | 79.4 | 0.09 | [38 empty] | 88.87 | 0.08 | 89.03 | 0.07 | 88.75 | 0.06 | 88.63 | 0.07 |  |  |  |  | C8-55-CE3 | 75.002 | 0.012 | 62.002 | 0.02 | 55.078 | 0.009 | 52.594 | 0.01 | 82.077 | 0.013 | 68.005 | 0.02 | 2598.8 | 2.7 | 2553.2 | 2.7 | 1.095 | 0.002 | -0.416 | 0.002 | 0.013 | 0.003 | 0.9439 | 0.002 | 29.233 | 0.001 | 8186 | 27 | 1600 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5115 | 11959.4822 | 328.4461 | 22.454 | 97.9779 | 11861.5043 | 0.0088023 | 27.6471 | 53.5665 | 13.7504 | 13.038 | 0.011329 | 32.1311 | 0.0087815 | 27.6101 | 0.0078237 | 21.711 | 75.0602 | 62.0545 | 21.343 | 75394.1675 | 61693.0473 | 6586 | 0.29814 | 71054.3539 | 57353.2337 | 8.68 | 0.14245 | -6.3041 | -21.4938 | 49.996 | 75394.1675 | 70549.8625 | 4401.3373 | 442.9677 | 75394.1675 | 100%
3 | 7-4F | 75N0097 | 7-4F | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 5:18:00 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 10.11 lbs ck2: 11.97 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 10.11 | 11.97 | 7.6 | 8.1 | 230.3 | 1.3 | 33.7 | 0 | 40213 | 72 | 40908 | 145 | -4427 | 95 | 35781 | 92 | 3.1999 |  |  |  |  | 109.83 | 0.02 | 57.28 | [32 empty] | Closed Damper, +20 Charge Both Stages, 115F Ambient | 2530.6 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.416 Inlet static. | 75.006 | 0.022 | 62.001 | 0.013 | 114.995 | 0.037 | 80.004 | 0.038 | 74.78 | 0.05 | 60.28 | 0.02 | 64.01 | 0.02 | 0.014 | 0.002 | 0.9377 | 0.002 | 40213 | 72 | -4427 | 95 | 3.2 | 0.012 | 83759 | 63 | 7.49 | 0.022 | 57.28 | 0.11 | 230.3 | 1.1 | 230 | 1.1 | 229.7 | 1.1 | 33.7 | 0.1 | 31.8 | 0.1 | 34 | 0.1 | 7746.9 | 40.2 | 3907.9 | 52.1 | 3435.3 | 34.2 | 227 |  | 229 |  | 227 |  | 6.2 |  | 6.4 |  | 6.1 |  | 0.57 | 228 |  | 227 |  | 229 |  | 13.2 |  | 12.6 |  | 12.6 |  | 4380 |  | 0.87 | 226 | 228 | 228 | 13.8 | 13.1 | 13 | 4590 | 0.88 | [8 empty] | 11170 | [22 empty] | 350.81 | 0.39 | 171.82 | 0.21 | 143.06 | 0.09 | 28.76 | 0.2 | 331.02 | 0.4 | 124.91 | 0.11 | 138.42 | 0.1 | 13.51 | 0.08 | [8 empty] | 78.22 | 0.04 | 51.99 | 0.1 | 46.18 | 0.03 | 5.81 | 0.1 | 720.34 | 0.77 | 47.56 | 0.04 | 83759 | 63 | 44853 | 52 | [38 empty] | 370.83 | 0.51 | 210.81 | 0.11 | 147.57 | 0.11 | 63.25 | 0.14 | [6 empty] | 356.16 | 0.49 | 124.04 | 0.09 | 144.28 | 0.11 | 20.24 | 0.05 | [6 empty] | 86.36 | 0.05 | 55.97 | 0.03 | 51.19 | 0.03 | 4.78 | 0.04 | 123.22 | 0.1 | 703.91 | 0.74 | 47.27 | 0.03 | 110.05 | 0.01 | 83759 | 63 | 44196 | 35 | [26 empty] | 59.9 | 0.02 | 60.68 | 0.02 | 60.67 | 0.03 | 59.73 | 0.02 | 60.22 | 0.03 | 60.49 | 0.02 | [32 empty] | 123.39 | 0.09 | 123.88 | 0.09 | [16 empty] | 123.92 | 0.07 | 123.71 | 0.09 | 122.96 | 0.09 | 123.22 | 0.1 |  |  |  |  | 54.08 | 0.05 | 54.86 | 0.05 | [24 empty] | 113.6 | 0.15 | 116.53 | 0.11 | 76.39 | 0.05 | 75.41 | 0.05 | 75.3 | 0.05 | 75.92 | 0.05 | 75.14 | 0.05 | 75.28 | 0.05 |  |  | 86.14 | 0.11 | 89.63 | 0.17 | 89.14 | 0.17 | 93.96 | 0.18 | 79.58 | 0.06 | 80 | 0.07 | 81.39 | 0.07 | 83.48 | 0.09 | 77.22 | 0.06 | 76.45 | 0.06 | 77.2 | 0.07 | 81.99 | 0.09 | 75.89 | 0.06 | 75.69 | 0.05 | 76.81 | 0.07 | 80.78 | 0.09 | [30 empty] | 114.68 | 0.12 | 114.06 | 0.14 | 114.61 | 0.12 | 114.61 | 0.12 | 114.5 | 0.13 | 114.51 | 0.12 | [38 empty] | 124.21 | 0.08 | 124.18 | 0.08 | 124.41 | 0.09 | 124.43 | 0.09 |  |  |  |  | C8-55-CE3 | 75.006 | 0.022 | 62.001 | 0.013 | 60.751 | 0.014 | 57.457 | 0.011 | 114.995 | 0.037 | 80.004 | 0.038 | 2600.2 | 2.8 | 2530.6 | 2.7 | 1.12 | 0.002 | -0.416 | 0.002 | 0.014 | 0.002 | 0.9377 | 0.002 | 29.277 | 0.001 | 11182 | 32 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5112 | 11825.2195 | 332.9712 | 23.1427 | 95.062 | 11730.1575 | 0.00882 | 27.7323 | 59.2398 | 14.6069 | 13.1932 | 0.013772 | 42.9142 | 0.0087799 | 27.6093 | 0.0092837 | 24.6807 | 75.3304 | 62.1778 | 24.3117 | 40449.1565 | 45665.9918 | 9592 | 0.80935 | 36158.9171 | 41375.7524 | 3.2337 | 0.19191 | -3.4206 | -16.0906 | 55.4184 | 40449.1565 | 34631.5907 | 4362.6449 | 1454.9209 | 40449.1565 | 100%
3 | 7-5B | 75N0098 | 8-5A | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 15:43:17 | 10 Ton | 0:30:00 | 75/62 82/68 | ENG 2 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 11.63 lbs ck2: 13.59 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 75 | 62 | 82 | 68 | 11.63 | 13.59 | 7.6 | 8.1 | 230.3 | 1.3 | 27.4 | 0 | 58794 | 93 | 59838 | 192 | 14940 | 109 | 73748 | 130 | 8.7234 | 896.4 |  |  |  | 109.16 | 0.01 | 20.43 | [32 empty] | Close damper, +40% charge, both stages B-Test | 2546.6 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.414 Inlet static. | 74.995 | 0.016 | 62.002 | 0.016 | 81.978 | 0.041 | 68.003 | 0.019 | 74.99 | 0.07 | 54.14 | 0.04 | 59.15 | 0.02 | -0.007 | 0.002 | 0.939 | 0.0019 | 58794 | 93 | 14940 | 109 | 8.723 | 0.035 | 92683 | 71 | 10.963 | 0.039 | 20.43 | 0.14 | 230.3 | 1 | 230.1 | 1 | 229.6 | 1 | 27.4 | 0.1 | 25.5 | 0.1 | 27.9 | 0.1 | 6280.8 | 40.1 | 3655.6 | 52.8 | 2173.3 | 32.6 | 229.3 |  | 228.9 |  | 228.6 |  | 6.2 |  | 6.4 |  | 6.1 |  | 0.56 | 227.7 |  | 228.8 |  | 228.7 |  | 10.2 |  | 9.5 |  | 9.6 |  | 3070 |  | 0.8 | 228.1 | 228.2 | 229.4 | 10.4 | 9.8 | 9.7 | 3180 | 0.8 | [8 empty] | 8430 | [22 empty] | 248.2 | 0.2 | 141.67 | 0.08 | 116.51 | 0.06 | 25.16 | 0.08 | 227.29 | 0.2 | 87.68 | 0.09 | 110.18 | 0.06 | 22.51 | 0.08 | [8 empty] | 72.37 | 0.04 | 46.31 | 0.04 | 42.35 | 0.03 | 3.96 | 0.04 | 680.36 | 0.57 | 35.65 | 0.03 | 92683 | 71 | 50012 | 48 | [38 empty] | 256.06 | 0.28 | 163.45 | 0.13 | 118.79 | 0.08 | 44.66 | 0.14 | [6 empty] | 241.29 | 0.27 | 87.71 | 0.08 | 114.46 | 0.08 | 26.75 | 0.06 | [6 empty] | 73.47 | 0.04 | 47.01 | 0.03 | 43.08 | 0.03 | 3.93 | 0.04 | 86.54 | 0.11 | 652.04 | 0.61 | 35.66 | 0.02 | 109.22 | 0.01 | 92683 | 71 | 47962 | 45 | [26 empty] | 53.73 | 0.03 | 54.48 | 0.02 | 54.54 | 0.03 | 53.66 | 0.03 | 54.16 | 0.03 | 54.33 | 0.03 | [32 empty] | 87.69 | 0.09 | 87.45 | 0.1 | [16 empty] | 87.97 | 0.08 | 87.13 | 0.09 | 87.15 | 0.1 | 86.54 | 0.11 |  |  |  |  | 47.35 | 0.06 | 46.11 | 0.06 | 88.92 | 0.07 | 88.45 | 0.08 | [20 empty] | 80.95 | 0.16 | 82.29 | 0.13 | 75.26 | 0.05 | 75.17 | 0.06 | 74.69 | 0.04 | 74.6 | 0.05 | 74.66 | 0.05 | 74.72 | 0.05 |  |  | 76.24 | 0.04 | 76.62 | 0.04 | 76.5 | 0.04 | 77.13 | 0.05 | 75.32 | 0.04 | 75.58 | 0.04 | 75.68 | 0.04 | 75.99 | 0.04 | 75.21 | 0.04 | 75.01 | 0.04 | 74.81 | 0.06 | 75.39 | 0.05 | 74.76 | 0.06 | 74.7 | 0.07 | 74.83 | 0.06 | 75.22 | 0.05 | [30 empty] | 78.91 | 0.1 | 78.74 | 0.1 | 78.87 | 0.1 | 78.79 | 0.11 | 78.89 | 0.1 | 78.76 | 0.12 | [38 empty] | 88.18 | 0.08 | 88.44 | 0.07 | 87.63 | 0.07 | 87.42 | 0.08 |  |  |  |  | C8-55-CE3 | 74.995 | 0.016 | 62.002 | 0.016 | 54.515 | 0.015 | 52.247 | 0.015 | 81.978 | 0.041 | 68.003 | 0.019 | 2591.9 | 2.6 | 2546.6 | 2.6 | 1.079 | 0.002 | -0.414 | 0.002 | -0.007 | 0.002 | 0.939 | 0.0019 | 29.21 | 0.001 | 8454 | 30 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4848 | 11941.195 | 322.8102 | 22.398 | 97.7504 | 11843.4446 | 0.0088041 | 27.6472 | 53.0302 | 13.7481 | 13.0233 | 0.011351 | 32.1311 | 0.0087831 | 27.6102 | 0.0077666 | 21.512 | 75.0524 | 62.0544 | 21.1505 | 77578.2181 | 63113.3545 | 6884 | 0.30286 | 73321.5594 | 58856.6958 | 8.673 | 0.12643 | -6.4967 | -22.0223 | 49.8429 | 77578.2181 | 72819.7392 | 4316.5542 | 441.9247 | 77578.2181 | 100%
3 | 7-5F | 75N0099 | 7-5F | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 7:12:59 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 11.63 lbs ck2: 13.59 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 11.63 | 13.59 | 7.6 | 8.1 | 230.3 | 1.4 | 34.4 | 0 | 39061 | 55 | 39750 | 121 | -5361 | 102 | 33695 | 114 | 2.9387 | 896 |  |  |  | 109.82 | 0.02 | 61.52 | [32 empty] | Closed Damper, +40 Charge Both Stages, 115F Ambient | 2533.1 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.416 Inlet static. | 74.998 | 0.005 | 61.999 | 0.015 | 115.008 | 0.026 | 80.005 | 0.034 | 74.78 | 0.04 | 60.69 | 0.02 | 64.29 | 0.02 | 0.016 | 0.003 | 0.9395 | 0.0021 | 39061 | 55 | -5361 | 102 | 2.939 | 0.014 | 87562 | 90 | 7.637 | 0.025 | 61.52 | 0.13 | 230.3 | 1 | 230 | 1 | 229.7 | 1 | 34.4 | 0.1 | 32.5 | 0.1 | 34.7 | 0.1 | 7922.9 | 40.4 | 3952 | 48.9 | 3543.2 | 34 | 228 |  | 228 |  | 227 |  | 6.2 |  | 6.4 |  | 5.9 |  | 0.55 | 227 |  | 228 |  | 229 |  | 13.1 |  | 12.6 |  | 12.6 |  | 4390 |  | 0.87 | 228 | 228 | 229 | 14.4 | 13.8 | 13.7 | 4870 | 0.88 | [8 empty] | 11420 | [22 empty] | 349.61 | 0.34 | 169 | 0.08 | 142.79 | 0.08 | 26.21 | 0.07 | 330.23 | 0.34 | 124.76 | 0.1 | 138.23 | 0.08 | 13.47 | 0.07 | [8 empty] | 78.92 | 0.03 | 52.18 | 0.1 | 46.63 | 0.02 | 5.55 | 0.1 | 716.52 | 0.92 | 47.51 | 0.04 | 87562 | 90 | 44644 | 56 | [38 empty] | 391.71 | 0.41 | 187.48 | 0.1 | 152.09 | 0.09 | 35.39 | 0.08 | [6 empty] | 375.82 | 0.4 | 123.01 | 0.07 | 148.66 | 0.09 | 25.65 | 0.05 | [6 empty] | 89.09 | 0.05 | 56.85 | 0.03 | 52.81 | 0.03 | 4.04 | 0.02 | 122.16 | 0.1 | 763.76 | 0.84 | 46.93 | 0.02 | 110.05 | 0.01 | 87562 | 90 | 48210 | 50 | [26 empty] | 60.32 | 0.02 | 61.08 | 0.03 | 61 | 0.03 | 60.18 | 0.03 | 60.61 | 0.03 | 60.94 | 0.04 | [32 empty] | 123.09 | 0.07 | 122.75 | 0.07 | [16 empty] | 122.95 | 0.05 | 122.66 | 0.08 | 122.81 | 0.09 | 122.16 | 0.1 |  |  |  |  | 54.27 | 0.05 | 55.28 | 0.03 | 124.25 | 0.06 | 123.83 | 0.06 | [20 empty] | 113.72 | 0.14 | 116.5 | 0.11 | 76.39 | 0.05 | 75.41 | 0.04 | 75.3 | 0.03 | 75.91 | 0.04 | 75.13 | 0.03 | 75.29 | 0.04 |  |  | 86.33 | 0.12 | 89.7 | 0.15 | 89.08 | 0.18 | 94.35 | 0.17 | 79.6 | 0.04 | 80 | 0.06 | 81.4 | 0.06 | 83.56 | 0.07 | 77.22 | 0.04 | 76.45 | 0.03 | 77.17 | 0.05 | 81.97 | 0.1 | 75.86 | 0.04 | 75.67 | 0.04 | 76.8 | 0.05 | 80.73 | 0.08 | [30 empty] | 114.64 | 0.11 | 114.02 | 0.14 | 114.55 | 0.11 | 114.57 | 0.12 | 114.48 | 0.12 | 114.46 | 0.13 | [38 empty] | 124.03 | 0.09 | 124.02 | 0.08 | 123.41 | 0.09 | 123.41 | 0.1 |  |  |  |  | C8-55-CE3 | 74.998 | 0.005 | 61.999 | 0.015 | 61.151 | 0.008 | 57.733 | 0.01 | 115.008 | 0.026 | 80.005 | 0.034 | 2602.3 | 2.9 | 2533.1 | 2.8 | 1.126 | 0.002 | -0.416 | 0.003 | 0.016 | 0.003 | 0.9395 | 0.0021 | 29.3 | 0.001 | 11466 | 38 | 1550 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4606 | 11825.1719 | 335.0856 | 23.143 | 95.061 | 11730.111 | 0.0088205 | 27.731 | 59.6904 | 14.6072 | 13.2039 | 0.01377 | 42.9151 | 0.0087804 | 27.6079 | 0.0093562 | 24.8572 | 75.3225 | 62.1758 | 24.5006 | 38200.2827 | 44364.6828 | 9916 | 0.88594 | 34053.78 | 40218.1801 | 2.97 | 0.20327 | -3.2304 | -15.6321 | 55.7022 | 38200.2827 | 32528.1334 | 4217.0384 | 1455.111 | 38200.2827 | 100%
3 | 8-3A | 75N0100 | 8-3A | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/26/2013 | 6:11:38 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 5.55 lbs ck2: 7.11 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 5.55 | 7.11 | 7.6 | 8.1 | 230.4 | 1.3 | 26.4 | 0 | 26050 | 51 | 26554 | 87 | -7299 | 96 | 18744 | 95 | 2.3369 |  |  |  |  | 115.59 | 0.01 | 51.67 | [32 empty] | 1 Finger Open, -40% Charge, Both Stages A-Test | 2535.1 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer One Finger Opened, The unit has NO Tape around the Unit. -0.349 Inlet static. | 75.002 | 0.011 | 61.999 | 0.011 | 94.96 | 0.044 | 74.99 | 0.023 | 74.75 | 0.02 | 65.29 | 0.02 | 67.84 | 0.01 | 0.084 | 0.003 | 0.95 | 0.0019 | 26050 | 51 | -7299 | 96 | 2.337 | 0.014 | 38784 | 243 | 4.835 | 0.034 | 51.67 | 0.38 | 230.4 | 1 | 230.1 | 1 | 229.6 | 1 | 26.4 | 0.1 | 24.6 | 0.1 | 26.8 | 0.1 | 6027 | 40.7 | 3596.1 | 53.7 | 1993.6 | 31.1 | 231 |  | 229 |  | 228 |  | 6.2 |  | 6.5 |  | 6.1 |  | 0.54 | 227 |  | 227 |  | 230 |  | 9.8 |  | 9.4 |  | 9.4 |  | 3000 |  | 0.79 | 226 | 229 | 229 | 9.6 | 9.1 | 9.8 | 2850 | 0.78 | [8 empty] | 7980 | [22 empty] | 237.99 | 0.22 | 212.85 | 0.09 | 113.47 | 0.07 | 99.38 | 0.08 | 223.36 | 0.27 | 105.89 | 0.08 | 108.95 | 0.09 | 3.06 | 0.08 | [8 empty] | 53.48 | 0.06 | 76.98 | 0.02 | 28.56 | 0.05 | 48.42 | 0.06 | 354.3 | 2.11 | 41.34 | 0.03 | 38784 | 243 | 26304 | 157 | [38 empty] | 224.62 | 0.32 | 231.37 | 0.12 | 109.35 | 0.1 | 122.02 | 0.14 | [6 empty] | 215.31 | 0.37 | 105.66 | 0.09 | 106.37 | 0.12 | 0.72 | 0.07 | [6 empty] | 43.13 | 0.14 | 83.88 | 0.03 | 19.72 | 0.13 | 64.16 | 0.13 | 105.32 | 0.1 | 233.91 | 2.76 | 41.27 | 0.03 | 117.24 | 0.01 | 38784 | 243 | 17769 | 207 | [26 empty] | 65.02 | 0.03 | 65.64 | 0.02 | 65.75 | 0.02 | 65.11 | 0.02 | 65.42 | 0.03 | 65.42 | 0.03 | [32 empty] | 108.29 | 0.06 | 105.23 | 0.08 | [16 empty] | 105.04 | 0.07 | 105.4 | 0.08 | 107.19 | 0.07 | 105.32 | 0.1 |  |  |  |  | 77.54 | 0.05 | 86.34 | 0.03 | [24 empty] | 94.44 | 0.13 | 94.96 | 0.09 | 75.61 | 0.03 | 75.19 | 0.05 | 74.86 | 0.03 | 75.04 | 0.02 | 74.76 | 0.03 | 74.85 | 0.03 |  |  | 84.18 | 0.17 | 79.59 | 0.06 | 80.89 | 0.06 | 87.18 | 0.06 | 77.36 | 0.07 | 78.02 | 0.05 | 78.75 | 0.04 | 87.12 | 0.11 | 76.46 | 0.03 | 75.66 | 0.02 | 75.82 | 0.03 | 78.79 | 0.07 | 75.54 | 0.03 | 75.38 | 0.03 | 75.81 | 0.03 | 78.64 | 0.06 | [30 empty] | 93.32 | 0.1 | 93.06 | 0.09 | 93.29 | 0.11 | 93.18 | 0.1 | 93.29 | 0.11 | 93.11 | 0.11 | [38 empty] | 108.23 | 0.06 | 107.75 | 0.07 | 105.18 | 0.09 | 105.72 | 0.1 |  |  |  |  | C8-55-1FE3 | 75.002 | 0.011 | 61.999 | 0.011 | 65.716 | 0.008 | 59.682 | 0.006 | 94.96 | 0.044 | 74.99 | 0.023 | 2629 | 2.6 | 2535.1 | 2.5 | 1.115 | 0.002 | -0.349 | 0.003 | 0.084 | 0.003 | 0.95 | 0.0019 | 29.226 | 0.002 | 8021 | 28 | 1520 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4262 | 11841.8166 | 332.0741 | 232.1704 | 988.0361 | 10853.7805 | 0.0092085 | 28.4873 | 64.2898 | 14.0989 | 13.3206 | 0.013922 | 38.1482 | 0.0087795 | 27.6079 | 0.0094818 | 26.1087 | 76.6815 | 63.2356 | 25.7604 | 32292.0466 | 35217.5364 | 6501 | 0.6871 | 28237.6556 | 31163.1454 | 3.5205 | 0.39563 | -2.727 | -12.3917 | 56.178 | 32292.0466 | 17753.5608 | 4124.3014 | 10414.1843 | 32292.0466 | 100%
3 | 8-3B | 75N0101 | 8-3B | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/26/2013 | 10:54:22 | 10 Ton | 0:30:06 | 95/75 75/62 | ENG 2 | TECH 5 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 5.55 lbs ck2: 7.11 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 5.55 | 7.11 | 7.6 | 8.1 | 230.3 | 1.4 | 24.3 | 0 | 36109 | 51 | 36816 | 133 | 2805 | 103 | 38916 | 105 | 5.4788 |  |  |  |  | 115.27 | 0.01 | 9.72 | [32 empty] | 1 Finger, -40% charge, both stages B-Test | 2552.5 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer 1 Finger Open, The unit has NO Tape around the Unit. -0.363 Inlet static. | 74.998 | 0.024 | 62 | 0.014 | 82.001 | 0.028 | 68.004 | 0.018 | 74.79 | 0.05 | 61.9 | 0.02 | 65.2 | 0.02 | 0.075 | 0.002 | 0.9542 | 0.0019 | 36109 | 51 | 2805 | 103 | 5.479 | 0.027 | 43111 | 319 | 6.07 | 0.05 | 9.72 | 0.72 | 230.3 | 1.1 | 229.9 | 1.1 | 229.7 | 1.1 | 24.3 | 0.1 | 22.8 | 0.1 | 25.1 | 0.1 | 5513.7 | 44.8 | 3592.9 | 58.3 | 1588.7 | 33.9 | 227.5 |  | 230.9 |  | 227.9 |  | 6.2 |  | 6.5 |  | 6.2 |  | 0.56 | 227.5 |  | 228.5 |  | 230.9 |  | 8.9 |  | 8.5 |  | 8.4 |  | 2540 |  | 0.75 | 230.5 | 228.7 | 227.8 | 8.8 | 8.2 | 7.9 | 2380 | 0.73 | [8 empty] | 7070 | [22 empty] | 198.29 | 0.15 | 193.46 | 0.03 | 100.71 | 0.05 | 92.74 | 0.06 | 183.67 | 0.21 | 91.38 | 0.08 | 95.57 | 0.08 | 4.18 | 0.08 | [8 empty] | 49.48 | 0.07 | 74 | 0.03 | 25.29 | 0.06 | 48.7 | 0.06 | 392.88 | 2.22 | 36.79 | 0.02 | 43111 | 319 | 30831 | 174 | [38 empty] | 184.59 | 0.2 | 208.63 | 0.06 | 95.9 | 0.07 | 112.73 | 0.1 | [6 empty] | 175.62 | 0.28 | 91.65 | 0.05 | 92.61 | 0.11 | 0.96 | 0.08 | [6 empty] | 37.56 | 0.12 | 76.65 | 0.02 | 14.49 | 0.12 | 62.16 | 0.12 | 91.33 | 0.06 | 221.26 | 3.06 | 36.88 | 0.02 | 116.28 | 0.01 | 43111 | 319 | 17570 | 243 | [26 empty] | 61.58 | 0.03 | 62.33 | 0.03 | 62.36 | 0.03 | 61.76 | 0.03 | 62.12 | 0.03 | 62.19 | 0.04 | [32 empty] | 94.4 | 0.04 | 91.3 | 0.05 | [16 empty] | 91.17 | 0.04 | 91.31 | 0.05 | 92.98 | 0.05 | 91.33 | 0.06 |  |  |  |  | 74.18 | 0.03 | 78.74 | 0.03 | 94.4 | 0.03 | 91.37 | 0.05 | [20 empty] | 81.2 | 0.13 | 81.91 | 0.11 | 75.18 | 0.05 | 74.82 | 0.44 | 74.59 | 0.05 | 74.54 | 0.05 | 74.55 | 0.05 | 74.58 | 0.05 |  |  | 76.61 | 0.05 | 75.99 | 0.04 | 76.46 | 0.04 | 78.26 | 0.04 | 75.32 | 0.05 | 75.54 | 0.04 | 75.91 | 0.04 | 77.63 | 0.04 | 75.19 | 0.05 | 74.86 | 0.05 | 74.86 | 0.05 | 75.72 | 0.05 | 74.83 | 0.05 | 74.75 | 0.05 | 74.87 | 0.05 | 75.62 | 0.04 | [30 empty] | 79.44 | 0.06 | 79.27 | 0.06 | 79.36 | 0.06 | 79.29 | 0.06 | 79.37 | 0.06 | 79.27 | 0.08 | [38 empty] | 94.42 | 0.05 | 94.07 | 0.05 | 91.15 | 0.07 | 91.65 | 0.07 |  |  |  |  | C8-55-1FE3 | 74.998 | 0.024 | 62 | 0.014 | 62.355 | 0.019 | 57.088 | 0.011 | 82.001 | 0.028 | 68.004 | 0.018 | 2625 | 2.6 | 2552.5 | 2.5 | 1.113 | 0.002 | -0.363 | 0.002 | 0.075 | 0.002 | 0.9542 | 0.0019 | 29.285 | 0 | 7103 | 29 | 1540 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4404 | 11905.5758 | 333.7536 | 233.8216 | 1020.4137 | 10885.1621 | 0.0090009 | 27.9963 | 60.9146 | 13.7486 | 13.2291 | 0.011346 | 32.1316 | 0.0087811 | 27.6087 | 0.0086821 | 24.4173 | 75.6008 | 62.5463 | 24.0661 | 46792.029 | 41963.388 | 5563 | 0.40576 | 42675.1102 | 37846.4691 | 6.008 | 0.35724 | -3.9303 | -14.6862 | 52.7522 | 46792.029 | 37994.9932 | 4181.8189 | 4615.2169 | 46792.029 | 100%
3 | 8-3F | 75N0102 | 8-3F | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/26/2013 | 4:53:56 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 5.55 lbs ck2: 7.11 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 5.55 | 7.11 | 7.6 | 8.1 | 230.4 | 1.4 | 30.3 | 0 | 11854 | 28 | 12184 | 64 | -10883 | 80 | 961 | 94 | 0.098081 |  |  |  |  | 116.15 | 0.01 | 97.43 | [32 empty] | One Finger Opened, -40% Charge, Both Stages 115 Ambient | 2511.4 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer One Finger Opened, The unit has NO Tape around the Unit. -0.347 Inlet static. | 74.995 | 0.011 | 62.016 | 0.011 | 114.982 | 0.039 | 80.005 | 0.031 | 74.73 | 0.02 | 70.26 | 0.02 | 71.66 | 0.01 | 0.078 | 0.002 | 0.9409 | 0.0019 | 11854 | 28 | -10883 | 80 | 0.098 | 0.01 | 37345 | 257 | 3.812 | 0.029 | 97.43 | 0.25 | 230.4 | 0.9 | 230 | 0.9 | 229.6 | 0.9 | 30.3 | 0.1 | 28.5 | 0.1 | 30.6 | 0.1 | 6961.2 | 37.5 | 3703.1 | 47.5 | 2836.6 | 30.2 | 228 |  | 229 |  | 228 |  | 6.2 |  | 6.4 |  | 5.9 |  | 0.55 | 227 |  | 228 |  | 230 |  | 11.8 |  | 11.3 |  | 11.4 |  | 3860 |  | 0.85 | 228 | 230 | 231 | 11.7 | 11 | 10.9 | 3740 | 0.84 | [8 empty] | 9760 | [22 empty] | 309.33 | 0.38 | 246.9 | 0.11 | 133.08 | 0.1 | 113.82 | 0.07 | 294.55 | 0.43 | 128.28 | 0.12 | 129.31 | 0.11 | 1.03 | 0.09 | [8 empty] | 60.1 | 0.06 | 82.07 | 0.03 | 33.68 | 0.05 | 48.39 | 0.05 | 341.14 | 2.77 | 48.7 | 0.04 | 37345 | 257 | 23009 | 188 | [38 empty] | 297.87 | 0.46 | 270.2 | 0.12 | 130.17 | 0.12 | 140.04 | 0.1 | [6 empty] | 288.17 | 0.47 | 127.26 | 0.1 | 127.63 | 0.13 | 0.37 | 0.05 | [6 empty] | 52.38 | 0.12 | 94.13 | 0.05 | 27.66 | 0.1 | 66.47 | 0.1 | 126.84 | 0.11 | 279.49 | 2.66 | 48.35 | 0.03 | 118.58 | 0.01 | 37345 | 257 | 19626 | 183 | [26 empty] | 69.85 | 0.03 | 70.57 | 0.04 | 70.78 | 0.03 | 69.99 | 0.03 | 70.24 | 0.03 | 70.18 | 0.04 | [32 empty] | 129.17 | 0.08 | 126.8 | 0.1 | [16 empty] | 126.28 | 0.08 | 127.16 | 0.11 | 128.58 | 0.09 | 126.84 | 0.11 |  |  |  |  | 83.1 | 0.03 | 97.34 | 0.04 | [24 empty] | 114.47 | 0.16 | 116.5 | 0.12 | 76.25 | 0.03 | 75.29 | 0.43 | 75.23 | 0.02 | 75.8 | 0.02 | 75.06 | 0.02 | 75.19 | 0.02 |  |  | 95.22 | 0.33 | 85.24 | 0.12 | 88.29 | 0.11 | 101.34 | 0.14 | 80.24 | 0.16 | 81.75 | 0.11 | 83.17 | 0.1 | 100.35 | 0.25 | 78.33 | 0.06 | 76.86 | 0.03 | 77.18 | 0.05 | 83.32 | 0.16 | 76.47 | 0.04 | 76.23 | 0.02 | 77.19 | 0.04 | 83.12 | 0.13 | [30 empty] | 115.89 | 0.16 | 115.27 | 0.2 | 115.79 | 0.17 | 115.72 | 0.16 | 115.75 | 0.19 | 115.57 | 0.17 | [38 empty] | 129.07 | 0.09 | 128.38 | 0.09 | 126.66 | 0.11 | 127.34 | 0.11 |  |  |  |  | C8-55-1FE3 | 74.995 | 0.011 | 62.016 | 0.011 | 70.64 | 0.013 | 61.923 | 0.01 | 114.982 | 0.039 | 80.005 | 0.031 | 2626.9 | 2.6 | 2511.4 | 2.5 | 1.113 | 0.002 | -0.347 | 0.003 | 0.078 | 0.002 | 0.9409 | 0.0019 | 29.201 | 0.001 | 9798 | 29 | 1550 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4818 | 11720.5469 | 328.3796 | 235.6358 | 967.9269 | 10752.62 | 0.0092039 | 28.8834 | 69.1582 | 14.6066 | 13.4477 | 0.013776 | 42.9156 | 0.0087924 | 27.6203 | 0.0097618 | 27.617 | 78.3247 | 63.7999 | 27.255 | 19086.1244 | 25784.8213 | 8248 | 1.4749 | 14916.7339 | 21615.4308 | 1.5224 | 0.54291 | -1.6284 | -9.1665 | 58.2705 | 19086.1244 | 37.9343 | 4243.443 | 14804.7471 | 19086.1244 | 100%
3 | 8-4A | 75N0103 | 8-4A | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 1:19:36 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 10.11 lbs ck2: 11.97 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 10.11 | 11.97 | 7.6 | 8.1 | 230.3 | 1.2 | 29.1 | 0 | 46974 | 72 | 47828 | 142 | 1010 | 146 | 47986 | 149 | 5.1815 |  |  |  |  | 109.45 | 0.01 | 46.39 | [32 empty] | 1 Finger Open, +20% Charge, Both Stages A-Test | 2557.2 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer One Finger Opened (0.74"), The unit has NO Tape around the Unit. -0.347 Inlet static. | 74.999 | 0.016 | 62.007 | 0.03 | 95.003 | 0.012 | 75.001 | 0.041 | 74.8 | 0.04 | 58.08 | 0.03 | 62.25 | 0.02 | 0.059 | 0.002 | 0.9532 | 0.0019 | 46974 | 72 | 1010 | 146 | 5.182 | 0.024 | 89506 | 76 | 9.665 | 0.031 | 46.39 | 0.16 | 230.3 | 1 | 230 | 1 | 229.7 | 1 | 29.1 | 0.1 | 27.4 | 0.1 | 29.7 | 0.1 | 6681.1 | 40.4 | 3725.9 | 53.7 | 2579.9 | 33.1 | 228 |  | 229 |  | 226 |  | 6.3 |  | 6.4 |  | 6.1 |  | 0.56 | 227 |  | 228 |  | 229 |  | 11 |  | 10.6 |  | 10.6 |  | 3510 |  | 0.83 | 228 | 227 | 229 | 11.2 | 10.6 | 10.2 | 3570 | 0.83 | [8 empty] | 9260 | [22 empty] | 283.25 | 0.25 | 157.9 | 0.07 | 126.34 | 0.07 | 31.56 | 0.07 | 263.37 | 0.24 | 102.46 | 0.1 | 120.88 | 0.07 | 18.42 | 0.09 | [8 empty] | 74.65 | 0.05 | 48.71 | 0.05 | 43.88 | 0.03 | 4.83 | 0.03 | 687.93 | 0.75 | 40.25 | 0.03 | 89506 | 76 | 47603 | 56 | [38 empty] | 288.94 | 0.28 | 198.16 | 0.06 | 127.84 | 0.07 | 70.32 | 0.06 | [6 empty] | 274.94 | 0.27 | 102.74 | 0.06 | 124.09 | 0.07 | 21.35 | 0.05 | [6 empty] | 79.42 | 0.05 | 72.77 | 0.07 | 46.94 | 0.03 | 25.83 | 0.09 | 101.54 | 0.07 | 644.8 | 0.72 | 40.34 | 0.02 | 113.53 | 0.01 | 89506 | 76 | 47192 | 52 | [26 empty] | 57.9 | 0.03 | 58.46 | 0.03 | 58.45 | 0.03 | 57.78 | 0.03 | 58.12 | 0.03 | 58.32 | 0.03 | [32 empty] | 102.03 | 0.06 | 102.39 | 0.06 | [16 empty] | 102.74 | 0.05 | 102.12 | 0.06 | 101.44 | 0.07 | 101.54 | 0.07 |  |  |  |  | 49.61 | 0.06 | 73.84 | 0.07 | [24 empty] | 93.54 | 0.16 | 95.96 | 0.12 | 75.62 | 0.03 | 75.21 | 0.04 | 74.92 | 0.03 | 75.07 | 0.03 | 74.83 | 0.04 | 74.88 | 0.04 |  |  | 84.77 | 0.2 | 79.42 | 0.05 | 80.88 | 0.06 | 87.41 | 0.08 | 78.06 | 0.13 | 77.99 | 0.06 | 78.72 | 0.05 | 87.23 | 0.13 | 76.53 | 0.04 | 75.6 | 0.03 | 75.85 | 0.04 | 78.86 | 0.07 | 75.58 | 0.04 | 75.44 | 0.03 | 75.81 | 0.04 | 78.53 | 0.06 | [30 empty] | 93.69 | 0.1 | 93.19 | 0.11 | 93.65 | 0.1 | 93.59 | 0.11 | 93.53 | 0.09 | 93.46 | 0.11 | [38 empty] | 102.76 | 0.06 | 102.85 | 0.06 | 102.82 | 0.06 | 102.73 | 0.07 |  |  |  |  | C8-55-1FE3 | 74.999 | 0.016 | 62.007 | 0.03 | 58.583 | 0.021 | 55.886 | 0.022 | 95.003 | 0.012 | 75.001 | 0.041 | 2617.3 | 2.6 | 2557.2 | 2.6 | 1.086 | 0.002 | -0.347 | 0.002 | 0.059 | 0.002 | 0.9532 | 0.0019 | 29.269 | 0.002 | 9261 | 29 | 1570 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4789 | 11955.7714 | 326.2568 | 231.5131 | 985.163 | 10970.6085 | 0.0092086 | 28.4826 | 57.1041 | 14.1 | 13.1349 | 0.013921 | 38.158 | 0.0087855 | 27.6137 | 0.0088623 | 23.6933 | 76.6615 | 63.2288 | 23.3325 | 61572.7569 | 56117.7482 | 7691 | 0.42631 | 57327.8615 | 51872.8528 | 6.1902 | 0.14948 | -5.15 | -19.5574 | 53.6669 | 61572.7569 | 46871.6436 | 4313.227 | 10387.8863 | 61572.7569 | 100%
3 | 8-4B | 75N0104 | 8-4B | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/24/2013 | 20:04:18 | 10 Ton | 0:30:00 | 82/68 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 10.11 lbs ck2: 11.97 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 82 | 68 | 75 | 62 | 10.11 | 11.97 | 7.6 | 8.1 | 230.3 | 1.3 | 26.6 | 0 | 55876 | 83 | 56947 | 152 | 11892 | 141 | 67779 | 162 | 8.2557 |  |  |  |  | 109.24 | 0.01 | 23.55 | [32 empty] | 1 Finger Open, +20% Charge, Both Stages B-Test | 2572.1 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer One Finger Opened (0.74"), The unit has NO Tape around the Unit. -0.34 Inlet static. | 75.003 | 0.018 | 62 | 0.017 | 82.005 | 0.026 | 68.029 | 0.014 | 74.94 | 0.08 | 55.26 | 0.07 | 59.99 | 0.02 | 0.071 | 0.002 | 0.9587 | 0.0019 | 55876 | 83 | 11892 | 141 | 8.255 | 0.035 | 88660 | 67 | 10.799 | 0.036 | 23.55 | 0.19 | 230.3 | 1 | 229.8 | 1 | 229.7 | 1.1 | 26.6 | 0.1 | 25.2 | 0.1 | 27.4 | 0.1 | 6090.6 | 41.7 | 3671.1 | 57.9 | 2119.5 | 32.2 | 229 |  | 228 |  | 228 |  | 6.3 |  | 6.6 |  | 6.1 |  | 0.55 | 227 |  | 228 |  | 230 |  | 9.9 |  | 9.5 |  | 9.6 |  | 3040 |  | 0.79 | 227 | 229 | 227 | 9.9 | 9.4 | 9.3 | 2990 | 0.8 | [8 empty] | 8210 | [22 empty] | 242.14 | 0.24 | 153.25 | 0.07 | 114.72 | 0.07 | 38.54 | 0.1 | 222.14 | 0.23 | 87.85 | 0.1 | 108.56 | 0.07 | 20.71 | 0.08 | [8 empty] | 71.42 | 0.04 | 46.39 | 0.03 | 41.72 | 0.03 | 4.67 | 0.03 | 653.59 | 0.6 | 35.71 | 0.03 | 88660 | 67 | 48058 | 42 | [38 empty] | 238.7 | 0.22 | 180.81 | 0.05 | 113.69 | 0.07 | 67.12 | 0.04 | [6 empty] | 225.34 | 0.22 | 88.8 | 0.06 | 109.58 | 0.07 | 20.77 | 0.06 | [6 empty] | 71.01 | 0.04 | 68.55 | 0.04 | 41.44 | 0.03 | 27.11 | 0.06 | 87.62 | 0.1 | 594.26 | 0.66 | 36 | 0.02 | 113.23 | 0.01 | 88660 | 67 | 45892 | 51 | [26 empty] | 54.97 | 0.03 | 55.49 | 0.03 | 55.49 | 0.02 | 54.93 | 0.03 | 55.25 | 0.04 | 55.38 | 0.04 | [32 empty] | 88.36 | 0.09 | 88.53 | 0.1 | [16 empty] | 89.01 | 0.07 | 88.2 | 0.09 | 87.73 | 0.1 | 87.62 | 0.1 |  |  |  |  | 47.6 | 0.08 | 69.58 | 0.07 | [24 empty] | 80.69 | 0.21 | 82.62 | 0.17 | 75.19 | 0.04 | 75.09 | 0.04 | 74.66 | 0.05 | 74.59 | 0.05 | 74.63 | 0.05 | 74.66 | 0.05 |  |  | 77.73 | 0.06 | 76.1 | 0.04 | 76.36 | 0.03 | 78.2 | 0.04 | 75.66 | 0.05 | 75.8 | 0.04 | 75.91 | 0.03 | 78.78 | 0.04 | 75.3 | 0.03 | 74.95 | 0.04 | 74.87 | 0.07 | 75.74 | 0.07 | 74.86 | 0.07 | 74.78 | 0.06 | 74.84 | 0.06 | 75.57 | 0.06 | [30 empty] | 79.75 | 0.08 | 79.42 | 0.08 | 79.75 | 0.08 | 79.67 | 0.08 | 79.67 | 0.09 | 79.54 | 0.09 | [38 empty] | 88.85 | 0.07 | 89.01 | 0.07 | 88.7 | 0.07 | 88.58 | 0.07 |  |  |  |  | C8-55-1FE3 | 75.003 | 0.018 | 62 | 0.017 | 55.69 | 0.007 | 53.191 | 0.011 | 82.005 | 0.026 | 68.029 | 0.014 | 2620.8 | 2.5 | 2571.1 | 2.5 | 1.079 | 0.002 | -0.34 | 0.003 | 0.071 | 0.002 | 0.9587 | 0.0019 | 29.22 | 0.001 | 8210 | 28 | 1570 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4684 | 12045.0739 | 325.9159 | 226.2948 | 987.5487 | 11057.5252 | 0.0089918 | 27.9811 | 54.2216 | 13.7489 | 13.055 | 0.011364 | 32.1521 | 0.0087799 | 27.6086 | 0.0080089 | 22.0611 | 75.5796 | 62.525 | 21.7034 | 75615.1314 | 61741.8978 | 6640 | 0.29971 | 71369.0723 | 57495.8387 | 8.6929 | 0.14459 | -6.2777 | -21.3579 | 50.6116 | 75615.1314 | 66820.4932 | 4307.7081 | 4486.9301 | 75615.1314 | 100%
3 | 8-4F | 75N0105 | 8-4F | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 4:26:05 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 4 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 10.11 lbs ck2: 11.97 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 10.11 | 11.97 | 7.6 | 8.1 | 230.3 | 1.4 | 33.9 | 0 | 35506 | 54 | 36204 | 133 | -10654 | 142 | 24841 | 126 | 2.2024 |  |  |  |  | 109.88 | 0.02 | 70.78 | [32 empty] | 1 Finger Open, +20% Charge, Both Stages 115F Ambient | 2540.5 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer One Finger Opened (0.74"), The unit has NO Tape around the Unit. -0.346 Inlet static. | 75.015 | 0.02 | 61.915 | 0.016 | 115.012 | 0.02 | 80.014 | 0.032 | 74.8 | 0.04 | 61.94 | 0.02 | 65.28 | 0.01 | 0.061 | 0.002 | 0.9483 | 0.0019 | 35506 | 54 | -10654 | 142 | 2.203 | 0.013 | 85016 | 84 | 7.538 | 0.021 | 70.78 | 0.14 | 230.3 | 1.3 | 230 | 1.3 | 229.7 | 1.3 | 33.9 | 0.1 | 32 | 0.1 | 34.2 | 0.1 | 7802.7 | 46.3 | 3910.2 | 60.9 | 3475.9 | 38.5 | 229 |  | 229 |  | 226 |  | 6.3 |  | 6.5 |  | 6.1 |  | 0.55 | 227 |  | 228 |  | 231 |  | 13.3 |  | 12.7 |  | 12.8 |  | 4400 |  | 0.87 | 226 | 229 | 231 | 13.9 | 13.3 | 13.2 | 4660 | 0.88 | [8 empty] | 11260 | [22 empty] | 352.47 | 0.34 | 172.86 | 0.22 | 143.44 | 0.08 | 29.42 | 0.21 | 332.76 | 0.35 | 125.17 | 0.1 | 138.83 | 0.08 | 13.66 | 0.08 | [8 empty] | 78.79 | 0.05 | 52.49 | 0.1 | 46.54 | 0.03 | 5.95 | 0.09 | 721.51 | 0.79 | 47.65 | 0.03 | 85016 | 84 | 44903 | 54 | [38 empty] | 376.72 | 0.45 | 217.99 | 0.14 | 148.86 | 0.1 | 69.13 | 0.16 | [6 empty] | 361.68 | 0.44 | 124.53 | 0.08 | 145.53 | 0.1 | 21 | 0.05 | [6 empty] | 90.03 | 0.07 | 62.52 | 0.29 | 53.35 | 0.04 | 9.17 | 0.29 | 123.73 | 0.1 | 713.67 | 0.76 | 47.43 | 0.03 | 111.05 | 0.05 | 85016 | 84 | 45403 | 59 | [26 empty] | 61.71 | 0.03 | 62.23 | 0.02 | 62.24 | 0.03 | 61.54 | 0.03 | 61.86 | 0.03 | 62.04 | 0.03 | [32 empty] | 123.84 | 0.08 | 124.44 | 0.08 | [16 empty] | 124.44 | 0.06 | 124.24 | 0.08 | 123.34 | 0.08 | 123.73 | 0.1 |  |  |  |  | 54.5 | 0.04 | 67.71 | 0.28 | [24 empty] | 113.87 | 0.16 | 116.75 | 0.12 | 76.24 | 0.04 | 75.41 | 0.04 | 75.3 | 0.04 | 75.82 | 0.04 | 75.14 | 0.04 | 75.29 | 0.04 |  |  | 95.19 | 0.4 | 84.66 | 0.11 | 88.05 | 0.11 | 101.63 | 0.15 | 81.33 | 0.19 | 81.46 | 0.11 | 83.31 | 0.08 | 100.94 | 0.23 | 78.36 | 0.05 | 76.73 | 0.04 | 77.27 | 0.05 | 83.51 | 0.14 | 76.55 | 0.04 | 76.32 | 0.04 | 77.18 | 0.06 | 82.99 | 0.13 | [30 empty] | 115.27 | 0.14 | 114.48 | 0.17 | 115.24 | 0.15 | 115.24 | 0.15 | 115.02 | 0.16 | 115.02 | 0.16 | [38 empty] | 124.59 | 0.08 | 124.59 | 0.1 | 124.89 | 0.08 | 124.93 | 0.09 |  |  |  |  | C8-55-1FE3 | 75.015 | 0.02 | 61.915 | 0.016 | 62.401 | 0.013 | 58.804 | 0.015 | 115.012 | 0.02 | 80.014 | 0.032 | 2618.4 | 2.7 | 2540.5 | 2.6 | 1.101 | 0.002 | -0.346 | 0.003 | 0.061 | 0.002 | 0.9483 | 0.0019 | 29.274 | 0.001 | 11279 | 30 | 1590 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.5111 | 11867.2986 | 328.6031 | 235.3022 | 966.5055 | 10900.7931 | 0.0091329 | 28.7995 | 60.8899 | 14.6074 | 13.2384 | 0.013778 | 42.9248 | 0.0087211 | 27.5471 | 0.0097179 | 25.5562 | 78.3 | 63.6875 | 25.187 | 42871.2742 | 49586.629 | 9689 | 0.77135 | 38566.1265 | 45281.4812 | 3.4193 | 0.19299 | -3.6126 | -17.4101 | 56.7265 | 42871.2742 | 23627.4499 | 4381.262 | 14862.5623 | 42871.2742 | 100%
3 | 8-5A | 75N0106 | 8-5A | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 12:55:47 | 10 Ton | 0:30:00 | 95/75 75/62 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 11.63 lbs ck2: 13.59 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 95 | 75 | 75 | 62 | 11.63 | 13.59 | 7.6 | 8.1 | 230.3 | 1.3 | 30 | 0 | 47649 | 62 | 48618 | 140 | 988 | 107 | 48638 | 111 | 5.0723 | 896 |  |  |  | 109.43 | 0.01 | 47.86 | [32 empty] | 1 Finger Open, +40 Charge Both Stages, 95F Ambient | 2552.5 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer 1 Finger Open, The unit has NO Tape around the Unit. -0.345 Inlet static. | 74.996 | 0.012 | 62.002 | 0.012 | 94.978 | 0.017 | 74.998 | 0.024 | 74.98 | 0.08 | 57.96 | 0.06 | 62.07 | 0.01 | 0.049 | 0.002 | 0.9495 | 0.0021 | 47649 | 62 | 988 | 107 | 5.072 | 0.026 | 93279 | 58 | 9.728 | 0.046 | 47.86 | 0.12 | 230.3 | 0.9 | 230.2 | 0.9 | 229.7 | 0.9 | 30 | 0.1 | 28 | 0.1 | 30.4 | 0.1 | 6897.9 | 41.3 | 3738.2 | 49.2 | 2691.6 | 35.1 | 229 |  | 229 |  | 228 |  | 6.3 |  | 6.5 |  | 6.1 |  | 0.54 | 228 |  | 230 |  | 229 |  | 11.1 |  | 10.7 |  | 10.5 |  | 3510 |  | 0.83 | 228 | 228 | 229 | 12 | 11.4 | 11.1 | 3840 | 0.84 | [8 empty] | 9540 | [22 empty] | 285.88 | 0.24 | 152.61 | 0.07 | 127.04 | 0.06 | 25.57 | 0.07 | 265.33 | 0.23 | 102.41 | 0.1 | 121.43 | 0.06 | 19.02 | 0.08 | [8 empty] | 75.33 | 0.03 | 48.8 | 0.05 | 44.32 | 0.02 | 4.48 | 0.05 | 699.6 | 0.59 | 40.24 | 0.03 | 93279 | 58 | 48404 | 43 | [38 empty] | 313.34 | 0.29 | 176.37 | 0.1 | 134.1 | 0.07 | 42.27 | 0.11 | [6 empty] | 297.47 | 0.28 | 101.64 | 0.07 | 130.07 | 0.07 | 28.43 | 0.06 | [6 empty] | 82.53 | 0.04 | 52.77 | 0.03 | 48.87 | 0.02 | 3.9 | 0.02 | 100.6 | 0.08 | 719.66 | 0.61 | 40 | 0.02 | 109.7 | 0.01 | 93279 | 58 | 50165 | 43 | [26 empty] | 57.63 | 0.02 | 58.18 | 0.02 | 58.13 | 0.02 | 57.51 | 0.02 | 57.85 | 0.02 | 58.06 | 0.03 | [32 empty] | 101.49 | 0.07 | 101.43 | 0.08 | [16 empty] | 101.85 | 0.05 | 101.17 | 0.07 | 101.04 | 0.08 | 100.6 | 0.08 |  |  |  |  | 49.79 | 0.07 | 51.55 | 0.06 | 102.74 | 0.06 | 102.42 | 0.06 | [20 empty] | 94.31 | 0.18 | 95.38 | 0.14 | 75.69 | 0.04 | 75.29 | 0.04 | 74.96 | 0.04 | 75.11 | 0.04 | 74.89 | 0.05 | 74.95 | 0.04 |  |  | 84.4 | 0.16 | 79.74 | 0.05 | 81.06 | 0.06 | 87.53 | 0.06 | 77.51 | 0.08 | 78.32 | 0.06 | 78.94 | 0.05 | 88.63 | 0.09 | 76.56 | 0.03 | 75.81 | 0.03 | 75.78 | 0.05 | 78.87 | 0.08 | 75.5 | 0.04 | 75.38 | 0.05 | 75.83 | 0.05 | 78.51 | 0.07 | [30 empty] | 93.63 | 0.12 | 93.19 | 0.1 | 93.71 | 0.14 | 93.48 | 0.13 | 93.6 | 0.12 | 93.41 | 0.14 | [38 empty] | 102.17 | 0.06 | 102.31 | 0.07 | 101.7 | 0.08 | 101.63 | 0.09 |  |  |  |  | C8-55-1FE3 | 74.996 | 0.012 | 62.002 | 0.012 | 58.316 | 0.005 | 55.78 | 0.008 | 94.978 | 0.017 | 74.998 | 0.024 | 2612 | 2.9 | 2552.5 | 2.9 | 1.076 | 0.002 | -0.345 | 0.003 | 0.049 | 0.002 | 0.9495 | 0.0021 | 29.264 | 0.002 | 9589 | 45 | 1580 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4974 | 11937.7033 | 322.6585 | 230.84 | 982.341 | 10955.3623 | 0.009206 | 28.4779 | 56.8186 | 14.0994 | 13.1282 | 0.013924 | 38.1556 | 0.0087829 | 27.6101 | 0.0088634 | 23.6294 | 76.6544 | 63.2223 | 23.2641 | 62240.5298 | 56830.489 | 8009 | 0.43918 | 57949.2233 | 52539.1824 | 6.0433 | 0.13619 | -5.2138 | -19.8358 | 53.6914 | 62240.5298 | 47520.9126 | 4360.3943 | 10359.223 | 62240.5298 | 100%
3 | 8-5B | 75N0107 | 8-5B | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 16:41:43 | 10 Ton | 0:30:00 | 0 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 11.63 lbs ck2: 13.59 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 0 |  |  |  | 11.63 | 13.59 | 7.6 | 8.1 | 230.4 | 1.2 | 27.5 | 0 | 57969 | 57 | 59108 | 170 | 13620 | 127 | 71602 | 135 | 8.4248 | 896.3 |  |  |  | 109.16 | 0.01 | 23.05 | [32 empty] | . | 2558.7 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer Fully Closed, The unit has NO Tape around the Unit. -0.36 Inlet static. | 74.992 | 0.01 | 62.001 | 0.016 | 81.983 | 0.028 | 67.997 | 0.024 | 75 | 0.06 | 54.49 | 0.02 | 59.39 | 0.01 | 0.035 | 0.003 | 0.9489 | 0.0017 | 57969 | 57 | 13620 | 127 | 8.425 | 0.033 | 93052 | 62 | 10.949 | 0.038 | 23.05 | 0.14 | 230.4 | 1 | 230.1 | 1 | 229.6 | 1 | 27.5 | 0.1 | 25.7 | 0.1 | 28 | 0.1 | 6304.3 | 40 | 3658.3 | 53 | 2194.7 | 31.7 | 229.8 |  | 227.5 |  | 228.8 |  | 6.2 |  | 6.5 |  | 6.1 |  | 0.55 | 228.5 |  | 228.6 |  | 230.7 |  | 10.7 |  | 9.8 |  | 9.6 |  | 3110 |  | 0.8 | 226.7 | 227.7 | 230.9 | 10.5 | 9.9 | 9.7 | 3200 | 0.81 | [8 empty] | 8490 | [22 empty] | 248.84 | 0.24 | 141.66 | 0.07 | 116.7 | 0.07 | -24.97 | 0.07 | 227.89 | 0.24 | 87.67 | 0.11 | 110.37 | 0.07 | 22.69 | 0.09 | [8 empty] | 72.58 | 0.04 | 46.36 | 0.05 | 42.49 | 0.03 | 3.87 | 0.04 | 682.03 | 0.61 | 35.65 | 0.03 | 93052 | 62 | 50133 | 48 | [38 empty] | 257.37 | 0.32 | 165.6 | 0.12 | 119.17 | 0.09 | 46.43 | 0.16 | [6 empty] | 242.49 | 0.31 | 87.84 | 0.07 | 114.82 | 0.09 | 26.98 | 0.06 | [6 empty] | 74.37 | 0.04 | 47.79 | 0.04 | 43.67 | 0.03 | 4.12 | 0.06 | 86.62 | 0.09 | 655.01 | 0.69 | 35.7 | 0.02 | 109.3 | 0.01 | 93052 | 62 | 48209 | 45 | [26 empty] | 54.14 | 0.02 | 54.84 | 0.02 | 54.9 | 0.02 | 54.09 | 0.02 | 54.57 | 0.03 | 54.71 | 0.02 | [32 empty] | 87.76 | 0.07 | 87.56 | 0.07 | [16 empty] | 88.1 | 0.06 | 87.25 | 0.07 | 87.22 | 0.08 | 86.62 | 0.09 |  |  |  |  | 47.31 | 0.06 | 47.01 | 0.14 | 89.01 | 0.07 | 88.55 | 0.07 | [20 empty] | 81.03 | 0.16 | 82.38 | 0.17 | 75.29 | 0.04 | 75.21 | 0.05 | 74.71 | 0.04 | 74.62 | 0.04 | 74.69 | 0.05 | 74.74 | 0.04 |  |  | 76.66 | 0.05 | 76.01 | 0.04 | 76.45 | 0.04 | 78.09 | 0.06 | 75.41 | 0.03 | 75.61 | 0.04 | 75.91 | 0.04 | 77.66 | 0.06 | 75.3 | 0.03 | 75 | 0.03 | 74.8 | 0.06 | 75.57 | 0.05 | 74.81 | 0.06 | 74.74 | 0.05 | 74.85 | 0.05 | 75.43 | 0.05 | [30 empty] | 78.97 | 0.11 | 78.76 | 0.12 | 78.92 | 0.13 | 78.81 | 0.11 | 78.91 | 0.13 | 78.78 | 0.13 | [38 empty] | 88.25 | 0.09 | 88.51 | 0.08 | 87.72 | 0.09 | 87.5 | 0.1 |  |  |  |  | C8-55-1FE3 | 74.992 | 0.01 | 62.001 | 0.016 | 54.879 | 0.012 | 52.607 | 0.015 | 81.983 | 0.028 | 67.997 | 0.024 | 2606.9 | 2.4 | 2558.7 | 2.4 | 1.068 | 0.002 | -0.36 | 0.003 | 0.035 | 0.003 | 0.9489 | 0.0017 | 29.197 | 0.001 | 8499 | 29 | 1570 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4795 | 12001.0112 | 321.0375 | 232.8495 | 1016.2055 | 10984.8057 | 0.0090001 | 27.9919 | 53.3995 | 13.7482 | 13.0334 | 0.011345 | 32.1261 | 0.0087832 | 27.6095 | 0.0078777 | 21.7212 | 75.5865 | 62.54 | 21.3609 | 79578.7501 | 63904.0875 | 6929 | 0.29717 | 75316.041 | 59641.3784 | 8.8618 | 0.12674 | -6.631 | -22.187 | 50.1795 | 79578.7501 | 70665.3878 | 4323.5659 | 4589.7964 | 79578.7501 | 100%
3 | 8-5F | 75N0108 | 8-5F | 1 finger | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 11 | 6/25/2013 | 10:57:48 | 10 Ton | 0:30:00 | 115/80 75/62 | ENG 2 | TECH 2 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. ck1: 11.63 lbs ck2: 13.59 lbs | 208/230/3 | TU2 | Ashrae 340/360 | 115 | 80 | 75 | 62 | 11.63 | 13.59 | 7.6 | 8.1 | 230.3 | 1.3 | 35 | 0 | 34342 | 33 | 35191 | 125 | -10509 | 350 | 23825 | 316 | 2.0431 | 896 |  |  |  | 109.84 | 0.02 | 73.27 | [32 empty] | 1 Finger Open, +40 Charge Both Stages, 115F Ambient | 2546.6 SCFM, VFD Setpoint 25.022%, (Manual Mode) Damper closed 28% (set to 72% on Meriam M334 damper controller) with 2 Stages ON, Economizer 1 Finger Open, The unit has NO Tape around the Unit. -0.346 Inlet static. | 75.002 | 0.03 | 62.002 | 0.014 | 115.001 | 0.032 | 80.002 | 0.035 | 74.86 | 0.05 | 62.39 | 0.04 | 65.57 | 0.01 | 0.075 | 0.002 | 0.9528 | 0.0018 | 34342 | 33 | -10509 | 350 | 2.044 | 0.056 | 89471 | 67 | 7.666 | 0.198 | 73.27 | 1.83 | 230.3 | 1 | 230.4 | 0.9 | 229.7 | 1 | 35 | 0.1 | 32.8 | 0.1 | 35.1 | 0.1 | 8060.8 | 36.8 | 3934.4 | 45.8 | 3600.1 | 32.3 | 230 |  | 228 |  | 229 |  | 6.3 |  | 6.5 |  | 5.9 |  | 0.56 | 228 |  | 228 |  | 229 |  | 13.3 |  | 12.7 |  | 12.8 |  | 4420 |  | 0.86 | 229 | 228 | 230 | 14.9 | 14.2 | 14 | 5000 | 0.88 | [8 empty] | 11600 | [22 empty] | 350.59 | 0.36 | 169.38 | 0.08 | 143.01 | 0.08 | 26.37 | 0.08 | 331.04 | 0.35 | 125.17 | 0.11 | 138.42 | 0.08 | 13.25 | 0.08 | [8 empty] | 79.07 | 0.04 | 52.38 | 0.13 | 46.73 | 0.02 | 5.65 | 0.12 | 717.21 | 0.76 | 47.65 | 0.04 | 89471 | 67 | 44608 | 47 | [38 empty] | 404.96 | 0.41 | 194.9 | 0.12 | 154.86 | 0.08 | 40.04 | 0.1 | [6 empty] | 387.92 | 0.39 | 123.34 | 0.07 | 151.28 | 0.08 | 27.94 | 0.04 | [6 empty] | 93.65 | 0.07 | 59.68 | 0.04 | 55.43 | 0.04 | 4.25 | 0.02 | 122.54 | 0.08 | 792.82 | 0.67 | 47.04 | 0.02 | 110.29 | 0.01 | 89471 | 67 | 50153 | 39 | [26 empty] | 62.08 | 0.04 | 62.7 | 0.05 | 62.64 | 0.04 | 61.99 | 0.04 | 62.3 | 0.05 | 62.56 | 0.05 | [32 empty] | 123.41 | 0.08 | 123.24 | 0.08 | [16 empty] | 123.38 | 0.06 | 123.08 | 0.08 | 123.07 | 0.09 | 122.54 | 0.08 |  |  |  |  | 54.42 | 0.13 | 57.91 | 0.04 | 124.53 | 0.08 | 124.19 | 0.07 | [20 empty] | 114.14 | 0.15 | 116.54 | 0.12 | 76.36 | 0.04 | 75.46 | 0.04 | 75.36 | 0.03 | 75.89 | 0.04 | 75.2 | 0.04 | 75.32 | 0.04 |  |  | 95.47 | 0.32 | 84.57 | 0.12 | 88.06 | 0.11 | 101.54 | 0.14 | 80.47 | 0.27 | 81.71 | 0.1 | 83.55 | 0.09 | 101.96 | 0.22 | 78.13 | 0.05 | 76.77 | 0.04 | 77.2 | 0.05 | 83.55 | 0.14 | 76.41 | 0.05 | 76.24 | 0.05 | 77.14 | 0.05 | 82.86 | 0.14 | [30 empty] | 114.88 | 0.23 | 114.16 | 0.21 | 114.81 | 0.25 | 114.78 | 0.23 | 114.64 | 0.21 | 114.58 | 0.23 | [38 empty] | 124.21 | 0.09 | 124.19 | 0.08 | 123.67 | 0.08 | 123.69 | 0.09 |  |  |  |  | C8-55-1FE3 | 75.002 | 0.03 | 62.002 | 0.014 | 62.812 | 0.013 | 59.032 | 0.013 | 115.001 | 0.032 | 80.002 | 0.035 | 2624.3 | 2.6 | 2546.6 | 2.5 | 1.12 | 0.002 | -0.346 | 0.003 | 0.075 | 0.002 | 0.9528 | 0.0018 | 29.296 | 0.001 | 11661 | 38 | 1570 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.4773 | 11884.3697 | 335.0764 | 235.2994 | 966.5173 | 10917.8524 | 0.0091871 | 28.8545 | 61.3347 | 14.607 | 13.2492 | 0.013769 | 42.912 | 0.0087815 | 27.6101 | 0.0097623 | 25.705 | 78.2821 | 63.7605 | 25.344 | 41719.6764 | 48338.1361 | 10091 | 0.82552 | 37504.8822 | 44123.3419 | 3.2163 | 0.20812 | -3.5105 | -16.9474 | 56.8806 | 41719.6764 | 22640.4643 | 4289.6576 | 14789.5545 | 41719.6764 | 100%
3 | C8-CB10-115-CE | 75N0111 | C8-CB10-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 10 | 0 | CUST 3 | 6/30/2015 | 17:35:35 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.9 | 33 | 0 | 41286 | 126 | 40747 | 150 | -288 | 170 | 40998 | 144 | 3.766 | 900 | [38 empty] | 10% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%:--Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage, Conden | 74.939 | 0.041 | 62 | 0.023 | 114.975 | 0.021 | 80.001 | 0.017 | 74.6 | 0.07 | 59.9 | 0.05 | 63.35 | 0.02 | 0.13 | 0.005 | 0.8811 | 0.0029 | 41286 | 126 | -288 | 170 | 3.766 | 0.016 | [6 empty] | 229.9 | 1.5 | 229.6 | 1.5 | 230.1 | 1.5 | 33 | 0.1 | 30.3 | 0.1 | 34.3 | 0.1 | 7583.4 | 50.8 | 3886.6 | 69.1 | 3303.3 | 40 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 12.5 |  | 12.6 |  | 11.6 |  | 4230 |  | 0.87 | 230 | 230 | 230 | 13.4 | 13.2 | 11.7 | 4390 | 0.76 | 228.3 |  | 2.4 |  | 519.6 |  | 115 |  | 10824.6 | [22 empty] | 333.91 | 0.47 | 223.83 | 0.1 | 139.09 | 0.11 | 84.74 | 0.06 | [16 empty] | 71.92 | 0.06 | 83.11 | 0.02 | 42.04 | 0.04 | 41.06 | 0.05 | [8 empty] | 322.07 | 0.47 | 126.46 | 0.15 | 136.24 | 0.12 | 9.78 | 0.06 | 319.03 | 0.48 | 135.5 | 0.12 | 8.27 | 0.06 | [24 empty] | 360.43 | 0.67 | 226.17 | 0.1 | 145.23 | 0.15 | 80.93 | 0.1 | [20 empty] | 84.67 | 0.07 | 75.28 | 0.17 | 50.15 | 0.04 | 25.14 | 0.2 | [12 empty] | 349.37 | 0.66 | 127.06 | 0.14 | 142.72 | 0.15 | 15.65 | 0.04 | 345.68 | 0.64 | 141.86 | 0.15 | 13.4 | 0.05 | [12 empty] | 60.48 | 0.05 | 59.85 | 0.06 | 59.51 | 0.05 | 58.81 | 0.06 | 60.04 | 0.05 |  |  | 126.13 | 0.14 |  |  | 76.14 | 0.03 | 80.73 | 0.03 | 220.33 | 0.1 |  |  | 128.16 | 0.14 | 77.58 | 0.43 | 82.45 | 0.15 |  |  | 129.11 | 0.11 | [28 empty] | 60.23 | 0.05 | [8 empty] | 128.46 | 0.14 | 127.23 | 0.12 | [8 empty] | 78.63 | 0.05 | 127.75 | 0.14 | 74.43 | 0.17 | 128.49 | 0.14 | [10 empty] | 223.5 | 0.13 | 115.65 | 0.21 | 115.5 | 0.21 | 74.96 | 0.07 | 74.91 | 0.07 | 75.07 | 0.07 | 75.08 | 0.07 | 75.04 | 0.07 | 75.05 | 0.07 |  |  | 80.54 | 0.13 | 80.53 | 0.16 | 74.87 | 0.07 | 93.86 | 0.31 | 75.93 | 0.08 | 78.52 | 0.19 | 75.37 | 0.08 | 75.9 | 0.11 | 77.47 | 0.22 | 82.03 | 0.16 | 81.96 | 0.13 | 87.2 | 0.15 | 74.96 | 0.07 | 79.2 | 0.19 | 75.36 | 0.08 | 92.42 | 0.21 | [78 empty] | 114.13 | 0.16 | [8 empty] | 60.21 | 0.05 | 60.01 | 0.05 | C8-55-CE3 | 74.939 | 0.041 | 62 | 0.023 | 60.049 | 0.006 | 56.662 | 0.017 | 114.975 | 0.021 | 80.001 | 0.017 | 2521.4 | 4.1 | 2451.8 | 4.1 | 1.146 | 0.002 | -0.421 | 0.003 | 0.13 | 0.005 | 0.8811 | 0.0029 | 29.192 | 0.001 | 10887 | 24 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5349 | 11484.4561 | 330.0918 | 23.281 | 95.6332 | 11388.8229 | 0.0088365 | 27.737 | 58.5141 | 14.6064 | 13.1729 | 0.013774 | 42.9114 | 0.008795 | 27.6095 | 0.0089733 | 24.1717 | 75.2754 | 62.1831 | 23.7972 | 45245.7778 | 46198.5824 | 9317 | 0.7028 | 41013.9712 | 41966.7758 | 3.7672 | 0.20132 | -3.9397 | -16.7613 | 54.289 | 45245.7778 | 39481.6177 | 4300.7969 | 1463.3632 | 45245.7778 | 100%
3 | C8-CB20-115-CE | 75N0112 | C8-CB20-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 20 | 0 | CUST 3 | 6/30/2015 | 19:00:48 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 33.7 | 0 | 41357 | 60 | 41070 | 151 | -1032 | 122 | 40325 | 137 | 3.615 | 900 | [38 empty] | 20% condenser coil block, economizer closed (2.0V), factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage 19" | 75.03 | 0.014 | 62.005 | 0.025 | 114.992 | 0.023 | 80.004 | 0.021 | 74.61 | 0.08 | 59.78 | 0.06 | 63.38 | 0.02 | 0.082 | 0.003 | 0.8796 | 0.0024 | 41357 | 60 | -1032 | 122 | 3.615 | 0.014 | [6 empty] | 229.9 | 1.4 | 229.7 | 1.5 | 230.2 | 1.5 | 33.7 | 0.1 | 30.8 | 0.1 | 34.9 | 0.1 | 7745.7 | 49.5 | 3903 | 68.1 | 3408.6 | 39.6 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.1 |  | 0.64 | 230 |  | 230 |  | 230 |  | 12.9 |  | 12.8 |  | 12 |  | 4360 |  | 0.87 | 230 | 230 | 230 | 13.8 | 13.5 | 12 | 4520 | 0.76 | 228.4 |  | 2.3 |  | 519.6 |  | 115 |  | 11084.6 | [22 empty] | 343.75 | 0.51 | 227.4 | 0.1 | 141.41 | 0.12 | 85.99 | 0.08 | [16 empty] | 73.14 | 0.08 | 82.31 | 0.06 | 42.86 | 0.05 | 39.45 | 0.09 | [8 empty] | 331.81 | 0.49 | 129.19 | 0.12 | 138.59 | 0.12 | 9.4 | 0.06 | 328.7 | 0.49 | 137.85 | 0.12 | 8.34 | 0.09 | [24 empty] | 370.75 | 0.46 | 225.29 | 0.1 | 147.54 | 0.1 | 77.75 | 0.13 | [20 empty] | 85.51 | 0.06 | 69.92 | 0.29 | 50.66 | 0.04 | 19.27 | 0.3 | [12 empty] | 359.61 | 0.45 | 129.04 | 0.1 | 145.05 | 0.1 | 16.01 | 0.04 | 355.77 | 0.46 | 144.18 | 0.1 | 14.21 | 0.05 | [12 empty] | 60.48 | 0.03 | 60.05 | 0.04 | 59.7 | 0.04 | 59 | 0.04 | 60.19 | 0.03 |  |  | 129.36 | 0.1 |  |  | 75.6 | 0.06 | 80.15 | 0.06 | 219.37 | 0.09 |  |  | 129.93 | 0.09 | 72.21 | 0.46 | 76.44 | 0.22 |  |  | 130.78 | 0.08 | [28 empty] | 60.33 | 0.03 | [8 empty] | 129.97 | 0.08 | 129.51 | 0.08 | [8 empty] | 77.92 | 0.06 | 129.92 | 0.12 | 66.16 | 1.24 | 130.26 | 0.08 | [10 empty] | 227.16 | 0.11 | 115.16 | 0.19 | 114.63 | 0.13 | 75.05 | 0.07 | 75.06 | 0.06 | 75.09 | 0.08 | 75.13 | 0.07 | 75.11 | 0.07 | 75.13 | 0.06 |  |  | 80.78 | 0.13 | 80.82 | 0.16 | 75.12 | 0.06 | 94.14 | 0.3 | 76.26 | 0.07 | 78.7 | 0.18 | 75.69 | 0.07 | 76.21 | 0.1 | 77.8 | 0.18 | 82.24 | 0.15 | 82.24 | 0.12 | 87.39 | 0.14 | 75.25 | 0.06 | 79.29 | 0.19 | 75.52 | 0.06 | 92.81 | 0.24 | [78 empty] | 114.35 | 0.19 | [8 empty] | 60.4 | 0.04 | 60.16 | 0.03 | C8-55-CE3 | 75.03 | 0.014 | 62.005 | 0.025 | 60.094 | 0.011 | 56.756 | 0.016 | 114.992 | 0.023 | 80.004 | 0.021 | 2519.2 | 3.4 | 2449.6 | 3.4 | 1.145 | 0.002 | -0.421 | 0.003 | 0.082 | 0.003 | 0.8796 | 0.0024 | 29.199 | 0.001 | 11154 | 23 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5371 | 11473.1335 | 329.5078 | 23.2813 | 95.6318 | 11377.5017 | 0.0088185 | 27.7394 | 58.5569 | 14.6069 | 13.1744 | 0.013773 | 42.9143 | 0.0087768 | 27.6118 | 0.0090186 | 24.232 | 75.3661 | 62.1882 | 23.8569 | 44544.1275 | 46285.0774 | 9584 | 0.73433 | 40310.3277 | 42051.2777 | 3.614 | 0.19574 | -3.8825 | -16.8092 | 54.4658 | 44544.1275 | 38777.5455 | 4303.1771 | 1463.4048 | 44544.1275 | 100%
3 | C8-CB30-115-CE | 75N0113 | C8-CB30-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 0 | CUST 3 | 6/30/2015 | 19:43:28 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.7 | 34.7 | 0 | 40656 | 96 | 40438 | 172 | -1901 | 91 | 38753 | 124 | 3.364 | 900 | [38 empty] | 30% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage 29" | 74.999 | 0.022 | 61.994 | 0.014 | 114.988 | 0.024 | 80.012 | 0.03 | 74.53 | 0.07 | 59.9 | 0.03 | 63.57 | 0.02 | 0.084 | 0.004 | 0.8774 | 0.0032 | 40656 | 96 | -1901 | 91 | 3.364 | 0.011 | [6 empty] | 229.9 | 1.2 | 229.7 | 1.2 | 230 | 1.2 | 34.7 | 0.1 | 31.6 | 0.1 | 35.7 | 0.1 | 7961.9 | 40.3 | 3928.1 | 56.7 | 3559 | 33.1 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 13.3 |  | 13.2 |  | 12.4 |  | 4520 |  | 0.88 | 230 | 230 | 230 | 14.2 | 14 | 12.5 | 4720 | 0.77 | 228.3 |  | 2.4 |  | 529.7 |  | 115 |  | 11444.7 | [22 empty] | 355.71 | 0.29 | 232.77 | 0.07 | 144.17 | 0.07 | 88.6 | 0.06 | [16 empty] | 74.01 | 0.04 | 82.19 | 0.06 | 43.44 | 0.03 | 38.75 | 0.06 | [8 empty] | 343.77 | 0.3 | 133.14 | 0.08 | 141.42 | 0.07 | 8.28 | 0.05 | 340.64 | 0.3 | 140.69 | 0.07 | 7.47 | 0.06 | [24 empty] | 385.1 | 0.28 | 227.75 | 0.11 | 150.66 | 0.06 | 77.08 | 0.1 | [20 empty] | 86.46 | 0.04 | 66.61 | 0.16 | 51.23 | 0.02 | 15.37 | 0.17 | [12 empty] | 373.92 | 0.27 | 132.88 | 0.07 | 148.24 | 0.06 | 15.35 | 0.04 | 370 | 0.27 | 147.38 | 0.06 | 14.21 | 0.04 | [12 empty] | 60.61 | 0.03 | 60.3 | 0.04 | 59.98 | 0.03 | 59.24 | 0.03 | 60.43 | 0.03 |  |  | 133.39 | 0.08 |  |  | 75.53 | 0.05 | 79.4 | 0.06 | 222.35 | 0.1 |  |  | 133.14 | 0.06 | 61.42 | 0.18 | 75.22 | 0.15 |  |  | 133.4 | 0.05 | [28 empty] | 60.54 | 0.02 | [8 empty] | 133.17 | 0.06 | 133.22 | 0.06 | [8 empty] | 78.41 | 0.05 | 133.63 | 0.08 | 58.43 | 0.1 | 133.53 | 0.06 | [10 empty] | 231.19 | 0.09 | 114.76 | 0.14 | 114.81 | 0.09 | 74.89 | 0.08 | 74.96 | 0.07 | 74.85 | 0.08 | 74.91 | 0.08 | 74.93 | 0.08 | 74.97 | 0.08 |  |  | 80.81 | 0.12 | 80.77 | 0.15 | 75.11 | 0.06 | 94.14 | 0.28 | 76.29 | 0.06 | 78.92 | 0.17 | 75.7 | 0.07 | 76.24 | 0.11 | 77.89 | 0.18 | 82.4 | 0.12 | 82.24 | 0.11 | 87.34 | 0.18 | 75.29 | 0.07 | 79.53 | 0.17 | 75.55 | 0.07 | 92.64 | 0.19 | [78 empty] | 114.26 | 0.11 | [8 empty] | 60.63 | 0.02 | 60.39 | 0.02 | C8-55-CE3 | 74.999 | 0.022 | 61.994 | 0.014 | 60.29 | 0.004 | 56.953 | 0.009 | 114.988 | 0.024 | 80.012 | 0.03 | 2516 | 4.6 | 2446.6 | 4.4 | 1.145 | 0.002 | -0.42 | 0.003 | 0.084 | 0.004 | 0.8774 | 0.0032 | 29.214 | 0.001 | 11521 | 17 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5278 | 11453.7563 | 329.1043 | 23.2536 | 95.5183 | 11358.238 | 0.0088186 | 27.7321 | 58.7622 | 14.6068 | 13.18 | 0.013782 | 42.9231 | 0.0087769 | 27.6043 | 0.0090898 | 24.3572 | 75.3355 | 62.1776 | 23.9844 | 42925.0563 | 45558.4133 | 9961 | 0.79201 | 38724.0092 | 41357.3662 | 3.3612 | 0.19581 | -3.7477 | -16.5733 | 54.7269 | 42925.0563 | 37191.3966 | 4270.441 | 1463.2187 | 42925.0563 | 100%
3 | C8-CB40-115-CE | 75N0114 | C8-CB40-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 40 | 0 | CUST 3 | 6/30/2015 | 20:57:12 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.7 | 35.5 | 0 | 40036 | 75 | 39768 | 173 | -2725 | 103 | 37308 | 119 | 3.14 | 90 | [38 empty] | 40% condenser coil block, economizer closed (2.0V), factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 115F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage 40" | 74.996 | 0.016 | 62.011 | 0.017 | 114.997 | 0.011 | 80.002 | 0.016 | 74.53 | 0.07 | 60.18 | 0.03 | 63.57 | 0.01 | 0.085 | 0.003 | 0.8824 | 0.0022 | 40036 | 75 | -2725 | 103 | 3.14 | 0.011 | [6 empty] | 229.9 | 1.2 | 229.6 | 1.2 | 230.1 | 1.2 | 35.5 | 0.1 | 32.6 | 0.1 | 36.6 | 0.1 | 8150.8 | 39 | 3980.5 | 56.5 | 3730.1 | 33.3 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 13.6 |  | 13.4 |  | 12.8 |  | 4650 |  | 0.88 | 230 | 230 | 230 | 14.9 | 14.6 | 13.2 | 4950 | 0.77 | 228.2 |  | 2.4 |  | 530.1 |  | 115 |  | 11805.1 | [22 empty] | 364.43 | 0.18 | 235.54 | 0.05 | 146.14 | 0.04 | 89.4 | 0.04 | [16 empty] | 74.5 | 0.04 | 82.23 | 0.03 | 43.77 | 0.02 | 38.46 | 0.04 | [8 empty] | 352.6 | 0.2 | 135.86 | 0.05 | 143.46 | 0.05 | 7.6 | 0.05 | 349.47 | 0.2 | 142.75 | 0.05 | 7.28 | 0.05 | [24 empty] | 402.45 | 0.21 | 228.55 | 0.06 | 154.34 | 0.04 | 74.21 | 0.08 | [20 empty] | 87.94 | 0.03 | 57.04 | 0.28 | 52.12 | 0.02 | 4.92 | 0.29 | [12 empty] | 391.11 | 0.21 | 135.77 | 0.04 | 151.95 | 0.05 | 16.18 | 0.04 | 387.03 | 0.22 | 151.08 | 0.05 | 14.67 | 0.04 | [12 empty] | 60.91 | 0.04 | 60.54 | 0.04 | 60.21 | 0.03 | 59.46 | 0.03 | 60.64 | 0.03 |  |  | 136.02 | 0.05 |  |  | 76.23 | 0.06 | 79.86 | 0.04 | 222.86 | 0.06 |  |  | 136.49 | 0.04 | 60.86 | 0.04 | 63.6 | 0.09 |  |  | 135.96 | 0.04 | [28 empty] | 60.78 | 0.03 | [8 empty] | 136.41 | 0.04 | 135.47 | 0.05 | [8 empty] | 79.11 | 0.04 | 136 | 0.14 | 58.53 | 0.05 | 136.56 | 0.04 | [10 empty] | 233.92 | 0.06 | 115.1 | 0.1 | 114.68 | 0.09 | 74.84 | 0.07 | 74.93 | 0.07 | 74.75 | 0.07 | 74.82 | 0.07 | 74.85 | 0.07 | 74.93 | 0.07 |  |  | 80.78 | 0.12 | 80.81 | 0.14 | 75.04 | 0.07 | 94.62 | 0.33 | 76.32 | 0.07 | 78.9 | 0.16 | 75.75 | 0.08 | 76.27 | 0.13 | 77.95 | 0.19 | 82.41 | 0.11 | 82.34 | 0.1 | 87.55 | 0.15 | 75.32 | 0.08 | 79.47 | 0.14 | 75.55 | 0.07 | 92.85 | 0.2 | [78 empty] | 114.58 | 0.09 | [8 empty] | 60.85 | 0.03 | 60.6 | 0.03 | C8-55-CE3 | 74.996 | 0.016 | 62.011 | 0.017 | 60.55 | 0.01 | 57.184 | 0.005 | 114.997 | 0.011 | 80.002 | 0.016 | 2521.7 | 3.2 | 2454.7 | 3.1 | 1.145 | 0.002 | -0.422 | 0.002 | 0.085 | 0.003 | 0.8824 | 0.0022 | 29.247 | 0.001 | 11881 | 15 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5238 | 11473.4434 | 330.1939 | 23.309 | 95.745 | 11377.6984 | 0.0088304 | 27.7443 | 59.0262 | 14.607 | 13.1871 | 0.01377 | 42.912 | 0.0087888 | 27.6166 | 0.0091668 | 24.5044 | 75.3328 | 62.1943 | 24.1325 | 41439.9588 | 44902.4247 | 10321 | 0.85004 | 37242.6305 | 40705.0964 | 3.1346 | 0.19795 | -3.6118 | -16.3067 | 55.0016 | 41439.9588 | 35708.2431 | 4267.2581 | 1464.4576 | 41439.9588 | 100%
3 | C8-CB5-115-CE | 75N0115 | C8-CB5-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 5 | 0 | CUST 3 | 6/30/2015 | 16:23:38 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 32.7 | 0 | 41681 | 121 | 41328 | 220 | -44 | 179 | 41639 | 138 | 3.879 | 900 | [38 empty] | 5% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.Condenser coil block 7" | 75.026 | 0.048 | 61.996 | 0.026 | 114.985 | 0.02 | 80.005 | 0.021 | 74.69 | 0.08 | 59.76 | 0.03 | 63.55 | 0.03 | 0.137 | 0.005 | 0.8776 | 0.0027 | 41681 | 121 | -44 | 179 | 3.879 | 0.014 | [6 empty] | 229.9 | 1.5 | 229.8 | 1.5 | 230.2 | 1.5 | 32.7 | 0.1 | 29.9 | 0.1 | 33.9 | 0.1 | 7511.5 | 51.1 | 3861.9 | 70.2 | 3222.3 | 40.6 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.3 |  | 0.63 | 230 |  | 230 |  | 230 |  | 12.3 |  | 12.4 |  | 11.6 |  | 4160 |  | 0.87 | 230 | 230 | 230 | 13.1 | 13 | 11.5 | 4310 | 0.76 | 228.4 |  | 2.4 |  | 521 |  | 115 |  | 10676 | [22 empty] | 329.01 | 0.32 | 221.88 | 0.06 | 137.92 | 0.08 | 83.95 | 0.07 | [16 empty] | 71.46 | 0.05 | 83.68 | 0.04 | 41.74 | 0.04 | 41.94 | 0.06 | [8 empty] | 317.2 | 0.3 | 125.12 | 0.08 | 135.05 | 0.07 | 9.93 | 0.05 | 314.16 | 0.32 | 134.29 | 0.08 | 8.41 | 0.07 | [24 empty] | 353.59 | 0.34 | 225.99 | 0.08 | 143.68 | 0.08 | 82.31 | 0.06 | [20 empty] | 83.96 | 0.05 | 76.75 | 0.06 | 49.73 | 0.03 | 27.02 | 0.08 | [12 empty] | 342.57 | 0.32 | 126.31 | 0.08 | 141.14 | 0.08 | 14.83 | 0.04 | 338.94 | 0.35 | 140.29 | 0.08 | 13.63 | 0.05 | [12 empty] | 60.3 | 0.05 | 59.8 | 0.05 | 59.47 | 0.04 | 58.75 | 0.04 | 59.96 | 0.04 |  |  | 125.01 | 0.08 |  |  | 76.19 | 0.04 | 80.85 | 0.04 | 220.47 | 0.07 |  |  | 126.71 | 0.08 | 78.75 | 0.07 | 83.91 | 0.1 |  |  | 127.71 | 0.06 | [28 empty] | 60.11 | 0.04 | [8 empty] | 126.66 | 0.07 | 125.88 | 0.06 | [8 empty] | 78.72 | 0.04 | 126.11 | 0.09 | 75.65 | 0.07 | 126.67 | 0.08 | [10 empty] | 222.5 | 0.06 | 115.53 | 0.15 | 115.8 | 0.13 | 74.99 | 0.09 | 75 | 0.09 | 75 | 0.08 | 75.04 | 0.09 | 75.03 | 0.09 | 75.07 | 0.09 |  |  | 80.43 | 0.14 | 80.5 | 0.14 | 75 | 0.08 | 93.67 | 0.27 | 76.15 | 0.09 | 78.34 | 0.18 | 75.56 | 0.09 | 76.14 | 0.12 | 77.69 | 0.21 | 81.9 | 0.15 | 81.89 | 0.11 | 86.94 | 0.16 | 75.17 | 0.09 | 78.92 | 0.17 | 75.45 | 0.09 | 92.46 | 0.22 | [78 empty] | 113.5 | 0.11 | [8 empty] | 60.12 | 0.04 | 59.91 | 0.04 | C8-55-CE3 | 75.026 | 0.048 | 61.996 | 0.026 | 59.966 | 0.016 | 56.556 | 0.016 | 114.985 | 0.02 | 80.005 | 0.021 | 2516.2 | 3.9 | 2447 | 3.8 | 1.152 | 0.002 | -0.421 | 0.002 | 0.137 | 0.005 | 0.8776 | 0.0027 | 29.204 | 0 | 10734 | 20 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5364 | 11462.8966 | 331.1704 | 23.2812 | 95.6323 | 11367.2643 | 0.0088136 | 27.7331 | 58.4296 | 14.6067 | 13.1705 | 0.013776 | 42.9155 | 0.0087718 | 27.6054 | 0.00893 | 24.1043 | 75.3624 | 62.1795 | 23.7295 | 45892.8894 | 46583.793 | 9164 | 0.68152 | 41664.764 | 42355.6677 | 3.8816 | 0.20194 | -4.0036 | -16.9328 | 54.1449 | 45892.8894 | 40132.0279 | 4296.7168 | 1464.1446 | 45892.8894 | 100%
3 | C8-CB50-115-CE | 75N0116 | C8-CB50-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 50 | 0 | CUST 3 | 6/30/2015 | 22:00:05 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.7 | 36.2 | 0 | 39850 | 65 | 39576 | 122 | -3160 | 137 | 36687 | 130 | 3.024 | 900 | [38 empty] | 50% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage 44.5" | 75.01 | 0.005 | 62.011 | 0.029 | 114.99 | 0.02 | 79.999 | 0.035 | 74.57 | 0.05 | 60.24 | 0.03 | 63.58 | 0.02 | 0.071 | 0.003 | 0.8759 | 0.0021 | 39850 | 65 | -3160 | 137 | 3.024 | 0.011 | [6 empty] | 229.9 | 1.1 | 229.8 | 1.1 | 230.1 | 1.1 | 36.2 | 0.1 | 33 | 0.1 | 37.2 | 0.1 | 8318.2 | 36.6 | 3988.4 | 50.3 | 3812.4 | 30.9 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 13.9 |  | 13.8 |  | 13.1 |  | 4770 |  | 0.89 | 230 | 230 | 230 | 15.2 | 14.9 | 13.4 | 5080 | 0.77 | 228.3 |  | 2.4 |  | 529.8 |  | 115 |  | 12064.8 | [22 empty] | 373.32 | 0.29 | 238.34 | 0.05 | 148.11 | 0.06 | 90.22 | 0.06 | [16 empty] | 75.42 | 0.05 | 81.78 | 0.04 | 44.37 | 0.03 | 37.4 | 0.05 | [8 empty] | 361.44 | 0.32 | 137.52 | 0.08 | 145.47 | 0.07 | 7.96 | 0.05 | 358.23 | 0.3 | 144.75 | 0.07 | 8.01 | 0.07 | [24 empty] | 411.62 | 0.22 | 228.41 | 0.09 | 156.23 | 0.05 | 72.18 | 0.09 | [20 empty] | 88.78 | 0.03 | 56.57 | 0.04 | 52.62 | 0.02 | 3.95 | 0.04 | [12 empty] | 400.31 | 0.21 | 137.29 | 0.05 | 153.89 | 0.04 | 16.6 | 0.04 | 396.15 | 0.24 | 153.02 | 0.05 | 14.98 | 0.04 | [12 empty] | 60.96 | 0.03 | 60.57 | 0.03 | 60.18 | 0.03 | 59.44 | 0.03 | 60.64 | 0.03 |  |  | 137.35 | 0.08 |  |  | 75.93 | 0.09 | 79.32 | 0.04 | 222.08 | 0.07 |  |  | 138.26 | 0.06 | 60.79 | 0.06 | 63.02 | 0.08 |  |  | 137.56 | 0.05 | [28 empty] | 60.81 | 0.03 | [8 empty] | 138.04 | 0.05 | 136.74 | 0.07 | [8 empty] | 78.94 | 0.03 | 138.15 | 0.19 | 58.92 | 0.06 | 138.45 | 0.05 | [10 empty] | 237.48 | 0.06 | 114.8 | 0.12 | 114.86 | 0.08 | 74.84 | 0.05 | 74.95 | 0.05 | 74.73 | 0.06 | 74.81 | 0.06 | 74.84 | 0.05 | 74.93 | 0.05 |  |  | 80.75 | 0.11 | 80.75 | 0.16 | 75.02 | 0.05 | 94.52 | 0.28 | 76.37 | 0.04 | 78.97 | 0.2 | 75.8 | 0.05 | 76.34 | 0.11 | 77.99 | 0.2 | 82.43 | 0.13 | 82.32 | 0.09 | 87.51 | 0.16 | 75.37 | 0.05 | 79.52 | 0.17 | 75.58 | 0.06 | 92.81 | 0.25 | [78 empty] | 114.36 | 0.12 | [8 empty] | 60.87 | 0.03 | 60.61 | 0.03 | C8-55-CE3 | 75.01 | 0.005 | 62.011 | 0.029 | 60.578 | 0.012 | 57.252 | 0.019 | 114.99 | 0.02 | 79.999 | 0.035 | 2511.8 | 3 | 2446.2 | 2.9 | 1.15 | 0.001 | -0.421 | 0.002 | 0.071 | 0.003 | 0.8759 | 0.0021 | 29.263 | 0.001 | 12131 | 17 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.542 | 11427.552 | 330.4874 | 23.2813 | 95.6321 | 11331.9199 | 0.0088272 | 27.7444 | 59.036 | 14.6068 | 13.1881 | 0.013768 | 42.9089 | 0.0087855 | 27.6164 | 0.009201 | 24.5485 | 75.3476 | 62.1948 | 24.1721 | 40822.6599 | 44736.4629 | 10561 | 0.88296 | 36592.2034 | 40506.0064 | 3.0164 | 0.19357 | -3.5723 | -16.3116 | 55.1207 | 40822.6599 | 35059.0017 | 4301.2064 | 1462.4519 | 40822.6599 | 100%
3 | C8-CB10-82-CE | 75N0119 | C8-CB10-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 10 | 0 | CUST 3 | 7/1/2015 | 4:15:58 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.9 | 26 | 0 | 49754 | 95 | 49273 | 169 | 11539 | 156 | 61303 | 151 | 7.844 | 899 | [38 empty] | 10% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage 13" | 74.965 | 0.023 | 61.991 | 0.025 | 82.003 | 0.015 | 67.983 | 0.016 | 74.65 | 0.08 | 57.12 | 0.04 | 61.27 | 0.03 | 0.157 | 0.005 | 0.8878 | 0.0028 | 49754 | 95 | 11539 | 156 | 7.844 | 0.029 | [6 empty] | 229.9 | 1.4 | 229.8 | 1.4 | 230.1 | 1.4 | 26 | 0.1 | 23.7 | 0.1 | 27.4 | 0.1 | 5948.2 | 57.8 | 3628.6 | 75.7 | 1867.4 | 42.2 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.4 |  | 0.67 | 230 |  | 230 |  | 230 |  | 9.4 |  | 9.2 |  | 8.5 |  | 2770 |  | 0.77 | 230 | 230 | 230 | 9.8 | 9.5 | 8.4 | 2830 | 0.69 | 228.5 |  | 2.4 |  | 534.2 |  | 115 |  | 7809.2 | [22 empty] | 214 | 0.19 | 179.66 | 0.04 | 105.96 | 0.06 | 73.7 | 0.05 | [16 empty] | 57.91 | 0.05 | 75.89 | 0.03 | 32.04 | 0.04 | 43.85 | 0.05 | [8 empty] | 202.11 | 0.19 | 89.97 | 0.07 | 102.01 | 0.06 | 12.04 | 0.05 | 199.69 | 0.21 | 101.19 | 0.07 | 10.15 | 0.07 | [24 empty] | 230.53 | 0.32 | 184.04 | 0.05 | 111.2 | 0.1 | 72.84 | 0.06 | [20 empty] | 65.78 | 0.08 | 71.11 | 0.03 | 37.83 | 0.05 | 33.28 | 0.06 | [12 empty] | 220.27 | 0.28 | 90.86 | 0.09 | 107.98 | 0.09 | 17.11 | 0.05 | 217.57 | 0.31 | 107.11 | 0.1 | 15.25 | 0.07 | [12 empty] | 57.96 | 0.03 | 56.89 | 0.04 | 56.33 | 0.04 | 56.29 | 0.04 | 57.04 | 0.04 |  |  | 89.77 | 0.07 |  |  | 72.42 | 0.04 | 75.19 | 0.04 | 178.64 | 0.06 |  |  | 91.77 | 0.08 | 72.03 | 0.04 | 74.8 | 0.06 |  |  | 93.03 | 0.07 | [28 empty] | 57.77 | 0.04 | [8 empty] | 91.86 | 0.08 | 91.04 | 0.05 | [8 empty] | 73.64 | 0.04 | 91.06 | 0.07 | 70.5 | 0.04 | 91.99 | 0.08 | [10 empty] | 178.84 | 0.06 | 82.6 | 0.14 | 82.68 | 0.17 | 75.14 | 0.07 | 75.1 | 0.07 | 75.27 | 0.07 | 75.27 | 0.07 | 75.21 | 0.08 | 75.2 | 0.07 |  |  | 75.73 | 0.06 | 75.88 | 0.06 | 74.94 | 0.07 | 78.61 | 0.07 | 75.53 | 0.07 | 75.82 | 0.08 | 75.2 | 0.08 | 75.08 | 0.07 | 75.82 | 0.08 | 76.44 | 0.06 | 76.26 | 0.06 | 76.77 | 0.06 | 74.92 | 0.07 | 75.81 | 0.07 | 75.14 | 0.07 | 77.87 | 0.06 | [78 empty] | 81.46 | 0.1 | [8 empty] | 57.41 | 0.03 | 57.63 | 0.03 | C8-55-CE3 | 74.965 | 0.023 | 61.991 | 0.025 | 57.264 | 0.014 | 53.802 | 0.015 | 82.003 | 0.015 | 67.983 | 0.016 | 2522.7 | 4 | 2472 | 4 | 1.16 | 0.002 | -0.423 | 0.003 | 0.157 | 0.005 | 0.8878 | 0.0028 | 29.251 | 0.001 | 7815 | 23 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5043 | 11559.1153 | 336.8772 | 22.6406 | 98.8055 | 11460.3098 | 0.0088047 | 27.6412 | 55.7597 | 13.7486 | 13.0946 | 0.01133 | 32.1142 | 0.008783 | 27.6027 | 0.0079788 | 22.4117 | 75.0254 | 62.0457 | 22.0453 | 64683.7412 | 53446.8528 | 6255 | 0.33004 | 60509.2229 | 49272.3345 | 7.7427 | 0.2216 | -5.5959 | -19.2658 | 50.2749 | 64683.7412 | 60003.0776 | 4234.8959 | 445.7677 | 64683.7412 | 100%
3 | C8-CB20-82-CE | 75N0120 | C8-CB20-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 20 | 0 | CUST 3 | 7/1/2015 | 5:00:42 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 26.4 | 0 | 50438 | 111 | 50244 | 176 | 11529 | 134 | 61977 | 174 | 7.753 | 899 | [38 empty] | 20% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage 19" | 74.983 | 0.01 | 61.99 | 0.03 | 81.991 | 0.018 | 68.007 | 0.01 | 74.5 | 0.06 | 56.7 | 0.04 | 60.88 | 0.02 | 0.095 | 0.005 | 0.8953 | 0.0033 | 50438 | 111 | 11529 | 134 | 7.753 | 0.032 | [6 empty] | 229.9 | 1.4 | 229.6 | 1.4 | 230 | 1.4 | 26.4 | 0.1 | 24.1 | 0.1 | 27.7 | 0.1 | 6034.1 | 54.7 | 3638.9 | 72.9 | 1959.6 | 41.1 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 9.4 |  | 9.5 |  | 8.7 |  | 2840 |  | 0.78 | 230 | 230 | 230 | 9.9 | 9.7 | 8.6 | 2920 | 0.68 | 228.4 |  | 2.4 |  | 530.5 |  | 115 |  | 7965.5 | [22 empty] | 221.22 | 0.43 | 181.73 | 0.09 | 108.28 | 0.14 | 73.45 | 0.08 | [16 empty] | 59.29 | 0.11 | 75.68 | 0.04 | 33.09 | 0.08 | 42.59 | 0.09 | [8 empty] | 209.15 | 0.4 | 91.68 | 0.09 | 104.36 | 0.13 | 12.69 | 0.08 | 206.66 | 0.4 | 103.54 | 0.13 | 10.84 | 0.13 | [24 empty] | 238.97 | 0.32 | 185.67 | 0.06 | 113.77 | 0.1 | 71.89 | 0.07 | [20 empty] | 67.5 | 0.07 | 70.23 | 0.05 | 39.04 | 0.05 | 31.18 | 0.08 | [12 empty] | 228.42 | 0.32 | 92.34 | 0.07 | 110.54 | 0.1 | 18.2 | 0.05 | 225.67 | 0.31 | 109.68 | 0.1 | 16.25 | 0.07 | [12 empty] | 57.94 | 0.03 | 57.38 | 0.03 | 56.34 | 0.04 | 56.18 | 0.04 | 56.65 | 0.03 |  |  | 91.52 | 0.09 |  |  | 72.21 | 0.03 | 74.85 | 0.04 | 180.04 | 0.06 |  |  | 93.56 | 0.07 | 71.19 | 0.03 | 73.98 | 0.07 |  |  | 94.66 | 0.06 | [28 empty] | 57.86 | 0.03 | [8 empty] | 93.43 | 0.07 | 92.7 | 0.07 | [8 empty] | 73.48 | 0.04 | 92.7 | 0.08 | 69.66 | 0.04 | 93.68 | 0.07 | [10 empty] | 180.89 | 0.07 | 81.55 | 0.12 | 81.51 | 0.1 | 74.9 | 0.07 | 75.04 | 0.06 | 74.7 | 0.07 | 74.81 | 0.07 | 74.84 | 0.07 | 74.96 | 0.06 |  |  | 75.88 | 0.05 | 76.01 | 0.05 | 75.09 | 0.06 | 79.01 | 0.07 | 75.88 | 0.06 | 76.15 | 0.06 | 75.56 | 0.07 | 75.42 | 0.07 | 76.26 | 0.07 | 76.71 | 0.05 | 76.47 | 0.05 | 76.88 | 0.05 | 75.29 | 0.06 | 76.11 | 0.05 | 75.4 | 0.07 | 77.85 | 0.06 | [78 empty] | 81.41 | 0.09 | [8 empty] | 57.79 | 0.02 | 57.61 | 0.04 | C8-55-CE3 | 74.983 | 0.01 | 61.99 | 0.03 | 57.118 | 0.016 | 53.743 | 0.024 | 81.991 | 0.018 | 68.007 | 0.01 | 2532.6 | 4.7 | 2483.5 | 4.6 | 1.159 | 0.002 | -0.428 | 0.003 | 0.095 | 0.005 | 0.8953 | 0.0033 | 29.255 | 0 | 7994 | 23 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4965 | 11607.7468 | 338.1526 | 22.7739 | 99.3883 | 11508.3585 | 0.0088001 | 27.6405 | 55.6215 | 13.7484 | 13.0909 | 0.011351 | 32.1342 | 0.008778 | 27.6017 | 0.0079801 | 22.3776 | 75.0433 | 62.045 | 22.0131 | 65321.0679 | 54106.2578 | 6434 | 0.33617 | 61150.9026 | 49936.0926 | 7.6496 | 0.2145 | -5.6274 | -19.4217 | 50.3178 | 65321.0679 | 60640.0987 | 4230.4902 | 450.479 | 65321.0679 | 100%
3 | C8-CB30-82-CE | 75N0121 | C8-CB30-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 0 | CUST 3 | 7/1/2015 | 5:59:51 | 10 Ton | 0:15:00 | 75/62 - 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.5 | 26.8 | 0 | 50559 | 94 | 50277 | 206 | 11403 | 158 | 61971 | 197 | 7.521 | 900 | [38 empty] | 30% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75%--Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage. 29" | 75 | 0.01 | 62.004 | 0.029 | 81.991 | 0.016 | 68.001 | 0.017 | 74.55 | 0.07 | 56.73 | 0.04 | 61.01 | 0.02 | 0.092 | 0.005 | 0.8942 | 0.0029 | 50559 | 94 | 11403 | 158 | 7.521 | 0.03 | [6 empty] | 229.9 | 1.2 | 229.6 | 1.2 | 230.1 | 1.2 | 26.8 | 0.1 | 24.6 | 0.1 | 28.3 | 0.1 | 6148.8 | 47.4 | 3670.1 | 65.2 | 2091 | 34.9 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 9.6 |  | 9.6 |  | 8.9 |  | 2930 |  | 0.8 | 230 | 230 | 230 | 10.1 | 10 | 8.9 | 3060 | 0.7 | 228.3 |  | 2.4 |  | 543 |  | 115 |  | 8218 | [22 empty] | 230.04 | 0.27 | 186.6 | 0.05 | 111.04 | 0.08 | 75.55 | 0.05 | [16 empty] | 60.19 | 0.07 | 75.4 | 0.03 | 33.77 | 0.05 | 41.63 | 0.05 | [8 empty] | 217.98 | 0.29 | 95.79 | 0.08 | 107.24 | 0.09 | 11.45 | 0.05 | 215.47 | 0.26 | 106.43 | 0.09 | 10.15 | 0.07 | [24 empty] | 250.06 | 0.21 | 189.31 | 0.07 | 117.06 | 0.06 | 72.25 | 0.04 | [20 empty] | 69.1 | 0.04 | 69.51 | 0.03 | 40.15 | 0.03 | 29.36 | 0.04 | [12 empty] | 239.44 | 0.2 | 96.38 | 0.07 | 113.91 | 0.06 | 17.53 | 0.03 | 236.56 | 0.21 | 113.04 | 0.06 | 16.3 | 0.04 | [12 empty] | 57.93 | 0.03 | 57.24 | 0.03 | 56.08 | 0.03 | 56.02 | 0.04 | 56.38 | 0.04 |  |  | 96.04 | 0.08 |  |  | 72.23 | 0.04 | 74.3 | 0.04 | 184.1 | 0.07 |  |  | 96.68 | 0.06 | 70.77 | 0.04 | 74.09 | 0.05 |  |  | 97.33 | 0.05 | [28 empty] | 57.8 | 0.04 | [8 empty] | 96.74 | 0.06 | 96.28 | 0.06 | [8 empty] | 73.73 | 0.04 | 96.14 | 0.08 | 69.28 | 0.04 | 96.96 | 0.06 | [10 empty] | 185.08 | 0.07 | 81.51 | 0.11 | 81.72 | 0.1 | 74.88 | 0.08 | 75.01 | 0.08 | 74.7 | 0.08 | 74.81 | 0.08 | 74.84 | 0.08 | 74.96 | 0.07 |  |  | 75.74 | 0.06 | 75.87 | 0.06 | 74.98 | 0.08 | 78.89 | 0.07 | 75.84 | 0.08 | 76.12 | 0.08 | 75.52 | 0.08 | 75.38 | 0.08 | 76.22 | 0.08 | 76.66 | 0.06 | 76.42 | 0.06 | 76.83 | 0.05 | 75.25 | 0.08 | 76.08 | 0.07 | 75.38 | 0.08 | 77.77 | 0.06 | [78 empty] | 81.26 | 0.1 | [8 empty] | 57.67 | 0.03 | 57.51 | 0.03 | C8-55-CE3 | 75 | 0.01 | 62.004 | 0.029 | 57.079 | 0.013 | 53.754 | 0.018 | 81.991 | 0.016 | 68.001 | 0.017 | 2531.1 | 4.1 | 2481.9 | 4.1 | 1.159 | 0.002 | -0.428 | 0.002 | 0.092 | 0.005 | 0.8942 | 0.0029 | 29.26 | 0.001 | 8240 | 20 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5098 | 11601.6412 | 337.9347 | 22.7738 | 99.3884 | 11502.2528 | 0.0088052 | 27.6502 | 55.5692 | 13.7484 | 13.09 | 0.011346 | 32.1292 | 0.0087833 | 27.6115 | 0.0079955 | 22.3848 | 75.0602 | 62.0588 | 22.0171 | 65354.0031 | 54270.4587 | 6670 | 0.34833 | 61148.9643 | 50065.4199 | 7.421 | 0.20958 | -5.6332 | -19.4909 | 50.4013 | 65354.0031 | 60639.0064 | 4265.9877 | 449.009 | 65354.0031 | 100%
3 | C8-CB40-82-CE | 75N0122 | C8-CB40-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 40 | 0 | CUST 3 | 7/1/2015 | 7:37:53 | 10 Ton | 0:15:00 | 75/62 - 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.7 | 27.2 | 0 | 50841 | 113 | 50468 | 200 | 11352 | 191 | 62204 | 171 | 7.364 | 900 | [38 empty] | 40% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75%--Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage. 40" | 74.993 | 0.016 | 62.004 | 0.035 | 82.009 | 0.012 | 68.001 | 0.025 | 74.56 | 0.09 | 56.57 | 0.05 | 60.88 | 0.02 | 0.094 | 0.004 | 0.8834 | 0.0026 | 50841 | 113 | 11352 | 191 | 7.364 | 0.027 | [6 empty] | 229.8 | 1.3 | 229.5 | 1.3 | 230.1 | 1.3 | 27.2 | 0.1 | 25 | 0.1 | 28.8 | 0.1 | 6244 | 48.8 | 3696 | 67.4 | 2203.6 | 35.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 9.8 |  | 9.8 |  | 9.1 |  | 3020 |  | 0.8 | 230 | 230 | 230 | 10.4 | 10.3 | 9.1 | 3160 | 0.71 | 228.2 |  | 2.5 |  | 543.4 |  | 115 |  | 8378.4 | [22 empty] | 238.02 | 0.22 | 188.9 | 0.05 | 113.49 | 0.07 | 75.41 | 0.06 | [16 empty] | 61.25 | 0.06 | 74.86 | 0.04 | 34.57 | 0.04 | 40.29 | 0.06 | [8 empty] | 225.92 | 0.24 | 98.28 | 0.06 | 109.77 | 0.08 | 11.48 | 0.05 | 223.34 | 0.22 | 108.95 | 0.07 | 10.71 | 0.06 | [24 empty] | 260.38 | 0.24 | 190.83 | 0.06 | 120.04 | 0.07 | 70.8 | 0.05 | [20 empty] | 70.78 | 0.05 | 68.51 | 0.06 | 41.31 | 0.03 | 27.21 | 0.06 | [12 empty] | 249.68 | 0.25 | 98.44 | 0.07 | 116.95 | 0.07 | 18.52 | 0.05 | 246.72 | 0.23 | 116.08 | 0.07 | 16.83 | 0.05 | [12 empty] | 57.57 | 0.05 | 56.86 | 0.04 | 55.99 | 0.04 | 55.78 | 0.04 | 56.23 | 0.04 |  |  | 98.43 | 0.06 |  |  | 72.34 | 0.05 | 73.99 | 0.04 | 185.43 | 0.07 |  |  | 99.11 | 0.06 | 70.44 | 0.05 | 72.87 | 0.05 |  |  | 99.12 | 0.04 | [28 empty] | 57.39 | 0.05 | [8 empty] | 99.26 | 0.06 | 98.24 | 0.05 | [8 empty] | 73.81 | 0.04 | 98.56 | 0.05 | 69.04 | 0.05 | 99.39 | 0.06 | [10 empty] | 187.78 | 0.05 | 81.9 | 0.1 | 81.85 | 0.12 | 74.85 | 0.09 | 74.98 | 0.08 | 74.67 | 0.08 | 74.78 | 0.09 | 74.82 | 0.09 | 74.94 | 0.08 |  |  | 75.67 | 0.07 | 75.81 | 0.07 | 74.89 | 0.08 | 78.92 | 0.07 | 75.76 | 0.08 | 76.07 | 0.08 | 75.46 | 0.08 | 75.33 | 0.08 | 76.15 | 0.08 | 76.65 | 0.06 | 76.44 | 0.06 | 76.92 | 0.06 | 75.19 | 0.08 | 76.05 | 0.07 | 75.33 | 0.08 | 77.93 | 0.06 | [78 empty] | 81.64 | 0.1 | [8 empty] | 57.22 | 0.05 | 57.1 | 0.04 | C8-55-CE3 | 74.993 | 0.016 | 62.004 | 0.035 | 56.869 | 0.023 | 53.666 | 0.028 | 82.009 | 0.012 | 68.001 | 0.025 | 2514.6 | 3.7 | 2467.6 | 3.8 | 1.162 | 0.002 | -0.424 | 0.002 | 0.094 | 0.004 | 0.8834 | 0.0026 | 29.275 | 0.001 | 8447 | 20 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.4834 | 11530.6957 | 336.8573 | 22.6675 | 98.9214 | 11431.7743 | 0.0088069 | 27.6504 | 55.3856 | 13.7488 | 13.0847 | 0.011342 | 32.129 | 0.0087849 | 27.6116 | 0.0079957 | 22.3338 | 75.0535 | 62.0589 | 21.9726 | 65469.2493 | 54428.2182 | 6907 | 0.36007 | 61362.9233 | 50321.8922 | 7.2645 | 0.20098 | -5.6778 | -19.6679 | 50.4384 | 65469.2493 | 60856.5435 | 4165.8457 | 446.8601 | 65469.2493 | 100%
3 | C8-CB5-82-CE | 75N0123 | C8-CB5-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 5 | 0 | CUST 3 | 7/1/2015 | 3:33:44 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 2 | 25.9 | 0 | 50084 | 98 | 49774 | 246 | 11088 | 205 | 61182 | 185 | 7.911 | 899 | [38 empty] | 5% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs,--CK2 8.1 lbs) 82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage. 7" | 74.982 | 0.032 | 62 | 0.03 | 82.011 | 0.011 | 68.036 | 0.017 | 74.69 | 0.09 | 57.14 | 0.05 | 61.1 | 0.02 | 0.208 | 0.005 | 0.9038 | 0.0032 | 50084 | 98 | 11088 | 205 | 7.911 | 0.033 | [6 empty] | 229.9 | 1.6 | 229.8 | 1.6 | 230 | 1.6 | 25.9 | 0.1 | 23.4 | 0.1 | 27.2 | 0.1 | 5920.4 | 61.9 | 3601 | 83.2 | 1813.4 | 44.8 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 9.3 |  | 9.1 |  | 8.5 |  | 2720 |  | 0.76 | 230 | 230 | 230 | 9.6 | 9.3 | 9.2 | 2780 | 0.69 | 228.6 |  | 2.4 |  | 534.7 |  | 115 |  | 7719.7 | [22 empty] | 210.66 | 0.17 | 178.61 | 0.04 | 104.86 | 0.06 | 73.75 | 0.05 | [16 empty] | 57.4 | 0.05 | 76.06 | 0.03 | 31.65 | 0.04 | 44.4 | 0.05 | [8 empty] | 198.84 | 0.18 | 88.79 | 0.07 | 100.9 | 0.06 | 12.11 | 0.06 | 196.42 | 0.17 | 100.07 | 0.06 | 10.18 | 0.06 | [24 empty] | 225.96 | 0.18 | 183.49 | 0.06 | 109.77 | 0.06 | 73.71 | 0.06 | [20 empty] | 64.86 | 0.05 | 71.19 | 0.05 | 37.18 | 0.03 | 34.01 | 0.05 | [12 empty] | 215.82 | 0.18 | 90.12 | 0.07 | 106.55 | 0.06 | 16.43 | 0.05 | 213.19 | 0.17 | 105.69 | 0.06 | 15.23 | 0.05 | [12 empty] | 58.13 | 0.03 | 57.06 | 0.04 | 56.48 | 0.04 | 56.36 | 0.04 | 57.21 | 0.03 |  |  | 88.72 | 0.06 |  |  | 72.57 | 0.05 | 75.31 | 0.03 | 178.5 | 0.05 |  |  | 90.69 | 0.05 | 72.09 | 0.04 | 74.46 | 0.04 |  |  | 92.04 | 0.04 | [28 empty] | 57.95 | 0.03 | [8 empty] | 90.46 | 0.06 | 89.89 | 0.06 | [8 empty] | 73.7 | 0.05 | 89.95 | 0.05 | 70.5 | 0.05 | 90.57 | 0.04 | [10 empty] | 179.06 | 0.04 | 82.75 | 0.12 | 83.13 | 0.12 | 75.28 | 0.09 | 75.22 | 0.08 | 75.42 | 0.09 | 75.42 | 0.09 | 75.35 | 0.09 | 75.34 | 0.08 |  |  | 75.8 | 0.07 | 75.96 | 0.07 | 75.07 | 0.08 | 78.66 | 0.06 | 75.66 | 0.08 | 75.95 | 0.08 | 75.32 | 0.09 | 75.2 | 0.09 | 75.94 | 0.09 | 76.55 | 0.07 | 76.36 | 0.06 | 76.82 | 0.06 | 75.05 | 0.08 | 75.88 | 0.07 | 75.23 | 0.08 | 77.88 | 0.06 | [78 empty] | 81.29 | 0.09 | [8 empty] | 57.56 | 0.04 | 57.75 | 0.04 | C8-55-CE3 | 74.982 | 0.032 | 62 | 0.03 | 57.32 | 0.027 | 53.911 | 0.015 | 82.011 | 0.011 | 68.036 | 0.017 | 2544.7 | 4.6 | 2495.1 | 4.5 | 1.143 | 0.002 | -0.43 | 0.003 | 0.208 | 0.005 | 0.9038 | 0.0032 | 29.257 | 0.001 | 7734 | 22 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.506 | 11658.3237 | 335.042 | 22.8275 | 99.6179 | 11558.7058 | 0.0088069 | 27.6478 | 55.814 | 13.7491 | 13.0964 | 0.011368 | 32.1578 | 0.0087849 | 27.6089 | 0.0080268 | 22.4775 | 75.0423 | 62.0551 | 22.1107 | 64552.5664 | 53800.7465 | 6164 | 0.3259 | 60337.6549 | 49585.835 | 7.8016 | 0.21637 | -5.537 | -19.2283 | 50.5047 | 64552.5664 | 59823.1697 | 4276.248 | 453.1487 | 64552.5664 | 100%
3 | C8-CB50-82-CE | 75N0124 | C8-CB50-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 50 | 0 | CUST 3 | 7/1/2015 | 9:02:03 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1.6 | 27.7 | 0 | 50929 | 90 | 50542 | 215 | 11179 | 130 | 62119 | 150 | 7.17 | 900 | [38 empty] | 50% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%:--Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage. 44.5" | 74.996 | 0.019 | 62.005 | 0.021 | 82.039 | 0.016 | 67.993 | 0.017 | 74.64 | 0.07 | 56.62 | 0.04 | 60.89 | 0.02 | 0.096 | 0.004 | 0.8827 | 0.0031 | 50929 | 90 | 11179 | 130 | 7.17 | 0.025 | [6 empty] | 229.7 | 1.3 | 229.5 | 1.3 | 230.2 | 1.3 | 27.7 | 0.1 | 25.4 | 0.1 | 29.4 | 0.1 | 6342.6 | 49.9 | 3725.1 | 67.2 | 2320.4 | 37.9 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.3 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.1 |  | 10.1 |  | 9.3 |  | 3130 |  | 0.81 | 230 | 230 | 230 | 10.6 | 10.6 | 9.3 | 3300 | 0.72 | 228.2 |  | 2.4 |  | 540.8 |  | 115 |  | 8655.8 | [22 empty] | 245.63 | 0.24 | 191.24 | 0.06 | 115.76 | 0.07 | 75.47 | 0.06 | [16 empty] | 62.03 | 0.05 | 75.39 | 0.03 | 35.14 | 0.04 | 40.25 | 0.04 | [8 empty] | 233.52 | 0.25 | 100.67 | 0.07 | 112.12 | 0.08 | 11.45 | 0.05 | 230.92 | 0.25 | 111.32 | 0.08 | 10.95 | 0.06 | [24 empty] | 271.14 | 0.33 | 192.76 | 0.08 | 123.04 | 0.09 | 69.72 | 0.05 | [20 empty] | 72.17 | 0.05 | 68.19 | 0.04 | 42.24 | 0.04 | 25.95 | 0.06 | [12 empty] | 260.3 | 0.32 | 101.26 | 0.09 | 120.01 | 0.09 | 18.75 | 0.04 | 257.24 | 0.31 | 119.14 | 0.09 | 17.12 | 0.05 | [12 empty] | 57.43 | 0.03 | 56.82 | 0.02 | 56.05 | 0.02 | 55.82 | 0.03 | 56.26 | 0.02 |  |  | 100.44 | 0.09 |  |  | 72.57 | 0.04 | 74.44 | 0.04 | 186.68 | 0.07 |  |  | 102.1 | 0.09 | 70.21 | 0.05 | 72.7 | 0.05 |  |  | 101.76 | 0.07 | [28 empty] | 57.3 | 0.03 | [8 empty] | 102.01 | 0.08 | 100.37 | 0.06 | [8 empty] | 74.09 | 0.05 | 101.35 | 0.07 | 68.82 | 0.05 | 102.35 | 0.09 | [10 empty] | 190.34 | 0.06 | 82.1 | 0.11 | 82.25 | 0.12 | 74.99 | 0.09 | 75.02 | 0.08 | 74.92 | 0.09 | 75.01 | 0.09 | 75.02 | 0.09 | 75.07 | 0.08 |  |  | 75.71 | 0.06 | 75.84 | 0.07 | 74.94 | 0.08 | 78.76 | 0.06 | 75.69 | 0.07 | 76 | 0.08 | 75.37 | 0.09 | 75.22 | 0.08 | 75.99 | 0.08 | 76.54 | 0.06 | 76.34 | 0.06 | 76.88 | 0.06 | 75.06 | 0.08 | 76.02 | 0.07 | 75.31 | 0.08 | 77.87 | 0.05 | [78 empty] | 81.47 | 0.07 | [8 empty] | 57.13 | 0.02 | 57.04 | 0.03 | C8-55-CE3 | 74.996 | 0.019 | 62.005 | 0.021 | 56.833 | 0.013 | 53.676 | 0.012 | 82.039 | 0.016 | 67.993 | 0.017 | 2513.7 | 4.4 | 2466.7 | 4.4 | 1.161 | 0.002 | -0.424 | 0.002 | 0.096 | 0.004 | 0.8827 | 0.0031 | 29.277 | 0.001 | 8663 | 20 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5214 | 11527.2754 | 336.4447 | 22.668 | 98.919 | 11428.3564 | 0.0088067 | 27.651 | 55.3116 | 13.7495 | 13.0839 | 0.011329 | 32.1219 | 0.0087849 | 27.6123 | 0.0080097 | 22.3404 | 75.0567 | 62.0598 | 21.9698 | 65488.2552 | 54625.6401 | 7093 | 0.36966 | 61278.1309 | 50415.5158 | 7.0735 | 0.1952 | -5.6812 | -19.7451 | 50.5224 | 65488.2552 | 60770.9145 | 4271.2583 | 446.0824 | 65488.2552 | 100%
3 | C8-CB60-82-CE | 75N0125 | C8-CB60-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 60 | 0 | CUST 3 | 7/1/2015 | 10:39:47 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.5 | 28.1 | 0 | 51531 | 107 | 50928 | 168 | 10966 | 167 | 62507 | 155 | 7.046 | 900 | [38 empty] | 60% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%:--Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage. 47.5" | 74.997 | 0.02 | 62.003 | 0.036 | 81.909 | 0.066 | 68.044 | 0.037 | 74.55 | 0.08 | 56.47 | 0.04 | 60.73 | 0.02 | 0.179 | 0.003 | 0.8909 | 0.0021 | 51531 | 107 | 10966 | 167 | 7.046 | 0.027 | [6 empty] | 229.8 | 1.2 | 229.5 | 1.2 | 230.2 | 1.2 | 28.1 | 0.1 | 25.9 | 0.1 | 29.8 | 0.1 | 6457.6 | 46.3 | 3735.1 | 61.4 | 2413.5 | 34.9 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.3 |  | 10.2 |  | 9.5 |  | 3220 |  | 0.81 | 230 | 230 | 230 | 10.9 | 10.8 | 9.6 | 3400 | 0.72 | 228.2 |  | 2.5 |  | 544 |  | 115 |  | 8849 | [22 empty] | 253.28 | 0.46 | 193.65 | 0.11 | 118 | 0.14 | 75.65 | 0.08 | [16 empty] | 63.04 | 0.06 | 75.42 | 0.03 | 35.88 | 0.04 | 39.54 | 0.05 | [8 empty] | 241.09 | 0.47 | 102.65 | 0.14 | 114.41 | 0.14 | 11.76 | 0.05 | 238.45 | 0.44 | 113.62 | 0.14 | 10.95 | 0.07 | [24 empty] | 280.14 | 0.57 | 194.2 | 0.14 | 125.49 | 0.16 | 68.7 | 0.05 | [20 empty] | 73.55 | 0.07 | 67.31 | 0.06 | 43.15 | 0.05 | 24.15 | 0.07 | [12 empty] | 269.25 | 0.57 | 103.57 | 0.14 | 122.52 | 0.16 | 18.95 | 0.05 | 266.14 | 0.56 | 121.65 | 0.16 | 17.52 | 0.06 | [12 empty] | 57.3 | 0.05 | 56.71 | 0.04 | 55.94 | 0.04 | 55.76 | 0.04 | 56.11 | 0.04 |  |  | 102.13 | 0.14 |  |  | 72.46 | 0.04 | 74.34 | 0.04 | 187.85 | 0.13 |  |  | 104.2 | 0.16 | 69.55 | 0.06 | 72.78 | 0.07 |  |  | 103.77 | 0.12 | [28 empty] | 57.15 | 0.04 | [8 empty] | 104.13 | 0.14 | 102.67 | 0.13 | [8 empty] | 74.12 | 0.04 | 103.51 | 0.15 | 67.99 | 0.07 | 104.2 | 0.15 | [10 empty] | 192.67 | 0.12 | 82.04 | 0.15 | 82.13 | 0.17 | 74.87 | 0.07 | 74.94 | 0.07 | 74.81 | 0.08 | 74.89 | 0.08 | 74.89 | 0.07 | 74.95 | 0.07 |  |  | 75 | 0.07 | 75.59 | 0.07 | 74.85 | 0.07 | 78.81 | 0.06 | 75.57 | 0.07 | 75.44 | 0.08 | 75.26 | 0.08 | 75.22 | 0.08 | 75.9 | 0.08 | 75.29 | 0.07 | 75.64 | 0.08 | 77.49 | 0.05 | 74.99 | 0.08 | 75.37 | 0.07 | 75.19 | 0.08 | 77.83 | 0.06 | [78 empty] | 81.72 | 0.13 | [8 empty] | 56.99 | 0.03 | 56.93 | 0.03 | C8-55-CE3 | 74.997 | 0.02 | 62.003 | 0.036 | 56.704 | 0.015 | 53.66 | 0.03 | 81.909 | 0.066 | 68.044 | 0.037 | 2524.5 | 2.9 | 2478.8 | 2.9 | 1.156 | 0.002 | -0.429 | 0.002 | 0.179 | 0.003 | 0.8909 | 0.0021 | 29.28 | 0.001 | 8872 | 23 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5142 | 11579.546 | 336.639 | 22.799 | 99.5104 | 11480.0356 | 0.0088058 | 27.65 | 55.1898 | 13.7467 | 13.0808 | 0.011398 | 32.166 | 0.0087833 | 27.6108 | 0.0080312 | 22.3323 | 75.0567 | 62.0584 | 21.9635 | 65847.4523 | 55211.995 | 7302 | 0.37848 | 61637.9912 | 51002.5339 | 6.9475 | 0.18601 | -5.6865 | -19.8669 | 50.6498 | 65847.4523 | 61123.4123 | 4270.7525 | 453.2874 | 65847.4523 | 100%
3 | C8-CB70-82-CE | 75N0126 | C8-CB70-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 70 | 0 | CUST 3 | 7/1/2015 | 12:31:12 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.5 | 28.9 | 0 | 51213 | 102 | 50730 | 237 | 10530 | 208 | 61755 | 278 | 6.716 | 900 | [38 empty] | 70% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%:--Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage 50" | 74.996 | 0.009 | 61.999 | 0.021 | 82.272 | 0.177 | 68.005 | 0.079 | 74.61 | 0.07 | 56.54 | 0.04 | 60.72 | 0.02 | 0.169 | 0.007 | 0.8848 | 0.0034 | 51213 | 102 | 10530 | 208 | 6.716 | 0.06 | [6 empty] | 229.8 | 1.2 | 229.6 | 1.2 | 230.3 | 1.2 | 28.9 | 0.1 | 26.5 | 0.1 | 30.5 | 0.1 | 6644.8 | 54.9 | 3754.5 | 60.4 | 2551.1 | 42.8 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.5 |  | 9.8 |  | 3360 |  | 0.82 | 230 | 230 | 230 | 10.7 | 10.9 | 9.5 | 3590 | 0.73 | 228.3 |  | 2.5 |  | 548 |  | 115 |  | 9183 | [22 empty] | 264.48 | 1.75 | 197.39 | 0.52 | 121.19 | 0.49 | 76.2 | 0.26 | [16 empty] | 64.12 | 0.19 | 75.83 | 0.09 | 36.66 | 0.14 | 39.18 | 0.13 | [8 empty] | 252.35 | 1.77 | 106.58 | 0.6 | 117.73 | 0.51 | 11.14 | 0.13 | 249.66 | 1.75 | 116.94 | 0.52 | 10.72 | 0.22 | [24 empty] | 295.8 | 2.68 | 197.07 | 0.48 | 129.63 | 0.7 | 67.44 | 0.31 | [20 empty] | 75.16 | 0.32 | 65.75 | 0.45 | 44.21 | 0.21 | 21.54 | 0.64 | [12 empty] | 284.76 | 2.67 | 107.97 | 0.68 | 126.73 | 0.71 | 18.76 | 0.12 | 281.55 | 2.64 | 125.87 | 0.71 | 17.57 | 0.2 | [12 empty] | 57.4 | 0.04 | 56.75 | 0.04 | 55.92 | 0.04 | 55.77 | 0.04 | 56.15 | 0.05 |  |  | 105.89 | 0.58 |  |  | 72.83 | 0.07 | 74.71 | 0.08 | 190.54 | 0.47 |  |  | 108.6 | 0.71 | 68.02 | 0.36 | 73.06 | 0.36 |  |  | 107.85 | 0.63 | [28 empty] | 57.24 | 0.04 | [8 empty] | 108.3 | 0.69 | 106.22 | 0.58 | [8 empty] | 74.6 | 0.1 | 107.41 | 0.62 | 66.23 | 0.42 | 108.34 | 0.68 | [10 empty] | 196.36 | 0.55 | 82.83 | 0.58 | 81.62 | 0.24 | 74.98 | 0.08 | 75 | 0.07 | 74.95 | 0.07 | 75.02 | 0.07 | 75.01 | 0.08 | 75.04 | 0.07 |  |  | 75.08 | 0.07 | 75.75 | 0.07 | 74.92 | 0.07 | 79.19 | 0.16 | 75.58 | 0.07 | 75.45 | 0.07 | 75.26 | 0.08 | 75.21 | 0.08 | 75.89 | 0.07 | 75.34 | 0.06 | 75.7 | 0.07 | 77.69 | 0.12 | 74.97 | 0.08 | 75.36 | 0.07 | 75.18 | 0.08 | 78.34 | 0.18 | [78 empty] | 82.26 | 0.35 | [8 empty] | 57.06 | 0.03 | 56.99 | 0.04 | C8-55-CE3 | 74.996 | 0.009 | 61.999 | 0.021 | 56.747 | 0.026 | 53.736 | 0.038 | 82.272 | 0.177 | 68.005 | 0.079 | 2516.2 | 4.8 | 2469.8 | 4.7 | 1.156 | 0.002 | -0.425 | 0.003 | 0.169 | 0.007 | 0.8848 | 0.0034 | 29.271 | 0.001 | 9196 | 59 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5209 | 11540.2911 | 335.4167 | 22.6993 | 99.0156 | 11441.2754 | 0.0088024 | 27.6468 | 55.2261 | 13.755 | 13.0822 | 0.011282 | 32.128 | 0.0087809 | 27.608 | 0.0080637 | 22.378 | 75.0587 | 62.054 | 22.0075 | 65078.1761 | 54929.789 | 7626 | 0.39994 | 60864.5435 | 50716.1563 | 6.6186 | 0.18249 | -5.6392 | -19.8326 | 50.7991 | 65078.1761 | 60355.3859 | 4275.2378 | 447.5525 | 65078.1761 | 100%
3 | C8-CB80-82-CE | 75N0127 | C8-CB80-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 80 | 0 | CUST 3 | 7/1/2015 | 14:11:53 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.7 | 30 | 0 | 50290 | 75 | 49732 | 159 | 9782 | 144 | 60082 | 169 | 6.22 | 900 | [38 empty] | 80% condenser coil block, economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%:--Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage. 51.5" | 74.996 | 0.01 | 61.999 | 0.022 | 82.018 | 0.036 | 67.988 | 0.014 | 74.62 | 0.06 | 56.78 | 0.04 | 61.03 | 0.02 | 0.128 | 0.004 | 0.8742 | 0.0027 | 50290 | 75 | 9782 | 144 | 6.22 | 0.025 | [6 empty] | 229.8 | 1.4 | 229.6 | 1.4 | 230.3 | 1.4 | 30 | 0.1 | 27.5 | 0.1 | 31.6 | 0.1 | 6896.6 | 53.9 | 3803.8 | 73 | 2762.9 | 41.5 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.6 |  | 10.6 |  | 9.9 |  | 3430 |  | 0.83 | 230 | 230 | 230 | 12.3 | 12.2 | 10.8 | 3990 | 0.75 | 228.2 |  | 2.4 |  | 540.2 |  | 115 |  | 9645.2 | [22 empty] | 269.85 | 0.7 | 200.23 | 0.08 | 122.69 | 0.19 | 77.54 | 0.18 | [16 empty] | 63.58 | 0.17 | 75.58 | 0.04 | 36.25 | 0.13 | 39.32 | 0.11 | [8 empty] | 258.1 | 0.66 | 110.01 | 0.2 | 119.38 | 0.19 | 9.37 | 0.11 | 255.43 | 0.69 | 118.62 | 0.2 | 8.74 | 0.17 | [24 empty] | 329.02 | 1.11 | 194.12 | 0.2 | 137.93 | 0.27 | 56.18 | 0.35 | [20 empty] | 77.49 | 0.12 | 49.16 | 0.25 | 45.7 | 0.08 | 3.46 | 0.29 | [12 empty] | 317.36 | 1.06 | 115.01 | 0.23 | 135.09 | 0.26 | 20.08 | 0.12 | 313.8 | 1.07 | 134.21 | 0.27 | 19.1 | 0.18 | [12 empty] | 57.79 | 0.03 | 57 | 0.03 | 55.94 | 0.03 | 55.82 | 0.03 | 56.18 | 0.03 |  |  | 109.69 | 0.19 |  |  | 73.08 | 0.04 | 74.41 | 0.04 | 189.09 | 0.18 |  |  | 115.54 | 0.23 | 53.19 | 0.05 | 57.9 | 0.15 |  |  | 113.75 | 0.15 | [28 empty] | 57.57 | 0.03 | [8 empty] | 115.11 | 0.22 | 109.87 | 0.17 | [8 empty] | 74.57 | 0.04 | 110.83 | 0.18 | 50.53 | 0.04 | 115.61 | 0.24 | [10 empty] | 197.83 | 0.08 | 90.05 | 0.87 | 80.56 | 0.11 | 74.96 | 0.07 | 74.99 | 0.06 | 74.96 | 0.07 | 75.03 | 0.07 | 75 | 0.07 | 75.03 | 0.06 |  |  | 74.97 | 0.06 | 75.43 | 0.05 | 74.89 | 0.06 | 77.91 | 0.06 | 75.54 | 0.06 | 75.4 | 0.06 | 75.23 | 0.06 | 75.14 | 0.06 | 75.79 | 0.06 | 75.18 | 0.06 | 75.54 | 0.05 | 76.82 | 0.05 | 74.96 | 0.06 | 75.3 | 0.06 | 75.15 | 0.07 | 77.1 | 0.06 | [78 empty] | 79.42 | 0.14 | [8 empty] | 57.42 | 0.03 | 57.3 | 0.03 | C8-55-CE3 | 74.996 | 0.01 | 61.999 | 0.022 | 56.953 | 0.009 | 53.926 | 0.011 | 82.018 | 0.036 | 67.988 | 0.014 | 2503 | 3.9 | 2452.9 | 3.8 | 1.149 | 0.002 | -0.418 | 0.003 | 0.128 | 0.004 | 0.8742 | 0.0027 | 29.247 | 0.001 | 9659 | 32 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5349 | 11474.7759 | 331.1044 | 22.5067 | 98.2185 | 11376.5574 | 0.0088027 | 27.6466 | 55.4181 | 13.7489 | 13.0878 | 0.01133 | 32.1181 | 0.0087809 | 27.608 | 0.0081218 | 22.4914 | 75.0564 | 62.0537 | 22.1175 | 63445.4694 | 54082.8504 | 8089 | 0.43514 | 59217.1187 | 49854.4998 | 6.1308 | 0.18245 | -5.5291 | -19.6383 | 51.0355 | 63445.4694 | 58711.8661 | 4290.6258 | 442.9775 | 63445.4694 | 100%
3 | C8-CB10-95-CE | 75N0131 | C8-CB10-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 10 | 0 | CUST 3 | 6/27/2015 | 11:21:58 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1.2 | 28.3 | 0 | 44241 | 75 | 43788 | 199 | 3106 | 163 | 47349 | 170 | 5.251 | 900 | [38 empty] | 10% condenser coil block(~10 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 13` | 75.012 | 0.011 | 62.004 | 0.034 | 95.007 | 0.015 | 75.007 | 0.014 | 74.67 | 0.07 | 59.07 | 0.05 | 62.62 | 0.02 | 0.146 | 0.006 | 0.895 | 0.003 | 44241 | 75 | 3106 | 163 | 5.251 | 0.022 | [6 empty] | 229.7 | 1 | 229.4 | 1 | 230.3 | 1 | 28.3 | 0.1 | 26.3 | 0.1 | 30.1 | 0.1 | 6499.6 | 39.7 | 3780 | 55.7 | 2516.5 | 30.9 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.4 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.6 |  | 9.9 |  | 3400 |  | 0.82 | 230 | 230 | 230 | 10.8 | 10.8 | 9.6 | 3390 | 0.73 | 228.2 |  | 2.4 |  | 527.4 |  | 115 |  | 9022.4 | [22 empty] | 266.65 | 0.22 | 195.33 | 0.03 | 121.81 | 0.06 | 73.53 | 0.05 | [16 empty] | 66.57 | 0.05 | 78.25 | 0.04 | 38.42 | 0.04 | 39.83 | 0.07 | [8 empty] | 254.26 | 0.22 | 103.96 | 0.06 | 118.29 | 0.06 | 14.33 | 0.05 | 251.47 | 0.22 | 117.48 | 0.06 | 12.4 | 0.06 | [24 empty] | 279.07 | 0.25 | 203.94 | 0.05 | 125.22 | 0.07 | 78.72 | 0.04 | [20 empty] | 73.55 | 0.06 | 76.81 | 0.03 | 43.17 | 0.04 | 33.64 | 0.05 | [12 empty] | 268.52 | 0.25 | 104.91 | 0.06 | 122.33 | 0.07 | 17.42 | 0.04 | 265.47 | 0.23 | 121.48 | 0.07 | 15.66 | 0.05 | [12 empty] | 59.71 | 0.04 | 58.79 | 0.04 | 58.66 | 0.04 | 58.24 | 0.05 | 59.06 | 0.05 |  |  | 103.81 | 0.05 |  |  | 74.58 | 0.04 | 78.55 | 0.03 | 197.99 | 0.05 |  |  | 105.74 | 0.06 | 77.82 | 0.03 | 83.52 | 0.02 |  |  | 107.24 | 0.04 | [28 empty] | 59.53 | 0.05 | [8 empty] | 105.82 | 0.05 | 105.08 | 0.06 | [8 empty] | 76.01 | 0.04 | 104.94 | 0.05 | 76.93 | 0.04 | 105.82 | 0.05 | [10 empty] | 196.08 | 0.04 | 95.71 | 0.09 | 95.45 | 0.07 | 75.05 | 0.07 | 75.04 | 0.07 | 75.32 | 0.07 | 75.28 | 0.07 | 75.16 | 0.07 | 75.16 | 0.06 |  |  | 80.96 | 0.09 | 80.56 | 0.11 | 75.48 | 0.09 | 86.89 | 0.13 | 75.61 | 0.06 | 82.29 | 0.09 | 77.18 | 0.13 | 79.36 | 0.14 | 85.83 | 0.21 | 82.26 | 0.09 | 81.26 | 0.08 | 83.84 | 0.07 | 75 | 0.07 | 82.52 | 0.09 | 77.78 | 0.11 | 82.19 | 0.1 | [78 empty] | 93.85 | 0.1 | [8 empty] | 59.2 | 0.04 | 59.33 | 0.04 | C8-55-CE3 | 75.012 | 0.011 | 62.004 | 0.034 | 59.257 | 0.014 | 55.829 | 0.021 | 95.007 | 0.015 | 75.007 | 0.014 | 2534.1 | 4.3 | 2479.2 | 4.2 | 1.149 | 0.002 | -0.394 | 0.003 | 0.146 | 0.006 | 0.895 | 0.003 | 29.313 | 0.001 | 9017 | 17 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5436 | 11562.0046 | 334.6545 | 22.1283 | 94.1621 | 11467.8425 | 0.0088223 | 27.6973 | 57.7134 | 14.1001 | 13.1505 | 0.013925 | 38.1638 | 0.0087804 | 27.6113 | 0.0086695 | 23.6481 | 75.1764 | 62.1263 | 23.2717 | 51168.4525 | 48457.553 | 7427 | 0.49539 | 46883.9584 | 44173.0589 | 5.1995 | 0.20745 | -4.4256 | -17.4629 | 53.1424 | 51168.4525 | 45822.8787 | 4351.9359 | 993.638 | 51168.4525 | 100%
3 | C8-CB20-95-CE | 75N0132 | C8-CB20-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 20 | 0 | CUST 3 | 6/27/2015 | 12:12:48 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 0.9 | 28.9 | 0 | 44871 | 90 | 44424 | 170 | 3086 | 172 | 47960 | 176 | 5.17 | 900 | [38 empty] | 20% condenser coil block(~20 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 19` | 74.996 | 0.009 | 62.001 | 0.03 | 95.016 | 0.011 | 74.991 | 0.018 | 74.67 | 0.06 | 58.81 | 0.05 | 62.44 | 0.02 | 0.136 | 0.006 | 0.8913 | 0.0032 | 44871 | 90 | 3086 | 172 | 5.17 | 0.02 | [6 empty] | 229.7 | 0.6 | 229.4 | 0.6 | 230.3 | 0.6 | 28.9 | 0.1 | 26.8 | 0.1 | 30.7 | 0.1 | 6642.1 | 25.7 | 3802.4 | 31.5 | 2635.6 | 21.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.8 |  | 10.9 |  | 10.2 |  | 3500 |  | 0.83 | 230 | 230 | 230 | 11.1 | 11.1 | 9.9 | 3540 | 0.73 | 228.2 |  | 2.4 |  | 524.3 |  | 115 |  | 9269.3 | [22 empty] | 276.51 | 0.4 | 198.44 | 0.09 | 124.52 | 0.11 | 73.92 | 0.08 | [16 empty] | 68.24 | 0.09 | 78.13 | 0.05 | 39.57 | 0.06 | 38.56 | 0.1 | [8 empty] | 263.96 | 0.39 | 106.45 | 0.08 | 121.05 | 0.11 | 14.6 | 0.08 | 261.09 | 0.38 | 120.24 | 0.11 | 12.43 | 0.1 | [24 empty] | 291.07 | 0.32 | 205.98 | 0.07 | 128.41 | 0.09 | 77.57 | 0.05 | [20 empty] | 75.63 | 0.06 | 75.47 | 0.06 | 44.53 | 0.04 | 30.94 | 0.09 | [12 empty] | 280.29 | 0.33 | 107.22 | 0.07 | 125.54 | 0.09 | 18.32 | 0.06 | 277.13 | 0.3 | 124.69 | 0.08 | 16.33 | 0.07 | [12 empty] | 59.39 | 0.03 | 58.54 | 0.04 | 58.4 | 0.04 | 58.02 | 0.04 | 58.81 | 0.03 |  |  | 106.31 | 0.07 |  |  | 74.34 | 0.04 | 78.47 | 0.05 | 199.88 | 0.06 |  |  | 108.37 | 0.06 | 77.18 | 0.05 | 82.01 | 0.11 |  |  | 109.71 | 0.05 | [28 empty] | 59.17 | 0.03 | [8 empty] | 108.36 | 0.07 | 107.81 | 0.06 | [8 empty] | 75.88 | 0.03 | 107.43 | 0.07 | 76.02 | 0.06 | 108.39 | 0.07 | [10 empty] | 199.42 | 0.08 | 95.74 | 0.1 | 95.45 | 0.08 | 75.05 | 0.06 | 75.04 | 0.06 | 75.3 | 0.06 | 75.27 | 0.06 | 75.16 | 0.06 | 75.16 | 0.06 |  |  | 80.91 | 0.09 | 80.51 | 0.09 | 75.45 | 0.08 | 86.93 | 0.14 | 75.63 | 0.06 | 82.29 | 0.07 | 77.18 | 0.11 | 79.34 | 0.14 | 85.79 | 0.21 | 82.27 | 0.07 | 81.27 | 0.08 | 83.84 | 0.07 | 75 | 0.06 | 82.52 | 0.07 | 77.81 | 0.11 | 82.2 | 0.09 | [78 empty] | 94.06 | 0.1 | [8 empty] | 58.86 | 0.03 | 58.97 | 0.04 | C8-55-CE3 | 74.996 | 0.009 | 62.001 | 0.03 | 58.984 | 0.012 | 55.728 | 0.014 | 95.016 | 0.011 | 74.991 | 0.018 | 2528.6 | 4.6 | 2474.2 | 4.5 | 1.149 | 0.002 | -0.392 | 0.002 | 0.136 | 0.006 | 0.8913 | 0.0032 | 29.307 | 0 | 9278 | 18 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.547 | 11542.945 | 333.9796 | 22.0721 | 93.9225 | 11449.0225 | 0.0088239 | 27.6952 | 57.437 | 14.1002 | 13.1436 | 0.013909 | 38.1481 | 0.0087822 | 27.6094 | 0.008675 | 23.5876 | 75.1604 | 62.123 | 23.2103 | 51768.0308 | 49099.1503 | 7688 | 0.50686 | 47481.2332 | 44812.3526 | 5.1176 | 0.19395 | -4.4848 | -17.7234 | 53.1725 | 51768.0308 | 46423.8885 | 4354.3196 | 989.8227 | 51768.0308 | 100%
3 | C8-CB40-95-CE | 75N0133 | C8-CB40-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 40 | 0 | CUST 3 | 6/27/2015 | 13:37:44 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.2 | 30.3 | 0 | 44942 | 100 | 44394 | 173 | 2238 | 156 | 47183 | 157 | 4.789 | 900 | [38 empty] | 40% condenser coil block(~40 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 40` | 75 | 0.011 | 61.998 | 0.039 | 95.044 | 0.007 | 75 | 0.017 | 74.72 | 0.05 | 58.79 | 0.05 | 62.35 | 0.02 | 0.122 | 0.006 | 0.8816 | 0.0036 | 44942 | 100 | 2238 | 156 | 4.789 | 0.018 | [6 empty] | 229.8 | 0.6 | 229.4 | 0.6 | 230.2 | 0.6 | 30.3 | 0 | 28.1 | 0 | 32 | 0 | 6960.3 | 23.6 | 3843.2 | 30.3 | 2892.7 | 18.8 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 11.4 |  | 11.4 |  | 10.7 |  | 3740 |  | 0.84 | 230 | 230 | 230 | 12 | 11.9 | 10.6 | 3840 | 0.74 | 228.1 |  | 2.4 |  | 537 |  | 115 |  | 9822 | [22 empty] | 295.6 | 0.19 | 205.8 | 0.04 | 129.59 | 0.05 | 76.21 | 0.06 | [16 empty] | 70.21 | 0.04 | 77.68 | 0.04 | 40.93 | 0.03 | 36.76 | 0.04 | [8 empty] | 283.07 | 0.21 | 112.81 | 0.05 | 126.29 | 0.06 | 13.48 | 0.04 | 280.1 | 0.19 | 125.49 | 0.05 | 12.54 | 0.06 | [24 empty] | 317.49 | 0.22 | 211.48 | 0.06 | 135.13 | 0.05 | 76.34 | 0.04 | [20 empty] | 79.22 | 0.05 | 73.26 | 0.03 | 46.82 | 0.03 | 26.43 | 0.03 | [12 empty] | 306.45 | 0.21 | 113.81 | 0.05 | 132.37 | 0.05 | 18.57 | 0.04 | 303.1 | 0.21 | 131.52 | 0.05 | 16.91 | 0.05 | [12 empty] | 59.35 | 0.03 | 58.31 | 0.04 | 58.27 | 0.03 | 57.92 | 0.04 | 58.64 | 0.03 |  |  | 112.76 | 0.06 |  |  | 74.58 | 0.04 | 77.51 | 0.04 | 205.16 | 0.05 |  |  | 114.67 | 0.04 | 75.62 | 0.05 | 79.84 | 0.04 |  |  | 114.66 | 0.03 | [28 empty] | 59.06 | 0.03 | [8 empty] | 114.62 | 0.05 | 112.95 | 0.05 | [8 empty] | 76.35 | 0.04 | 113.54 | 0.04 | 74.92 | 0.06 | 114.71 | 0.04 | [10 empty] | 206.18 | 0.05 | 95.85 | 0.1 | 95.41 | 0.07 | 75.09 | 0.06 | 75.06 | 0.05 | 75.27 | 0.06 | 75.25 | 0.06 | 75.2 | 0.05 | 75.21 | 0.05 |  |  | 81.01 | 0.08 | 80.6 | 0.1 | 75.45 | 0.07 | 87.01 | 0.11 | 75.66 | 0.05 | 82.4 | 0.07 | 77.25 | 0.1 | 79.4 | 0.13 | 85.96 | 0.18 | 82.39 | 0.07 | 81.36 | 0.07 | 83.9 | 0.06 | 75.03 | 0.05 | 82.64 | 0.07 | 77.88 | 0.12 | 82.33 | 0.08 | [78 empty] | 94.32 | 0.1 | [8 empty] | 58.77 | 0.04 | 58.9 | 0.03 | C8-55-CE3 | 75 | 0.011 | 61.998 | 0.039 | 58.866 | 0.017 | 55.799 | 0.028 | 95.044 | 0.007 | 75 | 0.017 | 2515 | 5.2 | 2460.2 | 5.1 | 1.149 | 0.002 | -0.388 | 0.002 | 0.122 | 0.006 | 0.8816 | 0.0036 | 29.299 | 0.001 | 9853 | 16 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5574 | 11483.001 | 332.0898 | 21.9598 | 93.4397 | 11389.5613 | 0.0088211 | 27.693 | 57.3086 | 14.1009 | 13.1412 | 0.01391 | 38.1563 | 0.0087793 | 27.6072 | 0.0087444 | 23.6342 | 75.1646 | 62.1202 | 23.2544 | 50968.8933 | 49209.6679 | 8263 | 0.55331 | 46675.6458 | 44916.4204 | 4.7372 | 0.1779 | -4.4386 | -17.856 | 53.4446 | 50968.8933 | 45621.7633 | 4361.4218 | 985.7082 | 50968.8933 | 100%
3 | C8-CB5-95-CE | 75N0134 | C8-CB5-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 5 | 0 | CUST 3 | 6/27/2015 | 10:32:08 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1.3 | 28.1 | 0 | 44197 | 103 | 43721 | 179 | 2884 | 160 | 47082 | 175 | 5.309 | 900 | [38 empty] | 5% condenser coil block(~5 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Condenser coil block 7` | 75.022 | 0.007 | 62.006 | 0.035 | 95.022 | 0.011 | 74.99 | 0.031 | 74.68 | 0.07 | 59.04 | 0.06 | 62.57 | 0.02 | 0.136 | 0.006 | 0.8872 | 0.0037 | 44197 | 103 | 2884 | 160 | 5.309 | 0.021 | [6 empty] | 229.7 | 1 | 229.6 | 1 | 230.2 | 1 | 28.1 | 0.1 | 25.9 | 0.1 | 29.8 | 0.1 | 6444 | 36.2 | 3751.9 | 51.1 | 2423.9 | 28.4 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.3 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.5 |  | 9.7 |  | 3330 |  | 0.82 | 230 | 230 | 230 | 10.7 | 10.6 | 9.4 | 3300 | 0.73 | 228.3 |  | 2.4 |  | 528 |  | 115 |  | 8843 | [22 empty] | 261.48 | 0.19 | 193.68 | 0.04 | 120.35 | 0.05 | 73.33 | 0.05 | [16 empty] | 65.78 | 0.04 | 78.18 | 0.04 | 37.85 | 0.03 | 40.33 | 0.05 | [8 empty] | 249.2 | 0.2 | 102.42 | 0.07 | 116.82 | 0.06 | 14.39 | 0.03 | 246.41 | 0.19 | 116 | 0.06 | 12.25 | 0.03 | [24 empty] | 272.54 | 0.24 | 202.75 | 0.05 | 123.43 | 0.07 | 79.31 | 0.05 | [20 empty] | 72.35 | 0.04 | 77 | 0.04 | 42.37 | 0.03 | 34.63 | 0.05 | [12 empty] | 262.14 | 0.23 | 103.78 | 0.07 | 120.54 | 0.07 | 16.76 | 0.04 | 259.13 | 0.24 | 119.68 | 0.07 | 15.53 | 0.04 | [12 empty] | 59.8 | 0.05 | 58.82 | 0.06 | 58.61 | 0.05 | 58.12 | 0.05 | 59.07 | 0.05 |  |  | 102.35 | 0.07 |  |  | 74.35 | 0.05 | 78.48 | 0.04 | 197 | 0.05 |  |  | 104.29 | 0.05 | 77.94 | 0.05 | 83.2 | 0.05 |  |  | 105.94 | 0.05 | [28 empty] | 59.57 | 0.04 | [8 empty] | 104.15 | 0.06 | 103.74 | 0.05 | [8 empty] | 75.88 | 0.04 | 103.48 | 0.06 | 76.87 | 0.06 | 104.12 | 0.05 | [10 empty] | 195.52 | 0.05 | 95.9 | 0.08 | 95.26 | 0.09 | 75.09 | 0.06 | 75.08 | 0.06 | 75.35 | 0.06 | 75.3 | 0.07 | 75.19 | 0.06 | 75.2 | 0.06 |  |  | 81.19 | 0.08 | 80.75 | 0.11 | 75.51 | 0.09 | 87.36 | 0.13 | 75.69 | 0.07 | 82.61 | 0.08 | 77.29 | 0.11 | 79.54 | 0.14 | 86.2 | 0.22 | 82.59 | 0.08 | 81.53 | 0.09 | 84.16 | 0.09 | 75.06 | 0.07 | 82.83 | 0.08 | 77.85 | 0.11 | 82.5 | 0.09 | [78 empty] | 94.9 | 0.16 | [8 empty] | 59.27 | 0.05 | 59.38 | 0.05 | C8-55-CE3 | 75.022 | 0.007 | 62.006 | 0.035 | 59.212 | 0.027 | 55.841 | 0.025 | 95.022 | 0.011 | 74.99 | 0.031 | 2523.2 | 5.3 | 2468.1 | 5.2 | 1.149 | 0.002 | -0.39 | 0.002 | 0.136 | 0.006 | 0.8872 | 0.0037 | 29.306 | 0.001 | 8868 | 17 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5273 | 11513.1502 | 333.1562 | 22.0159 | 93.6822 | 11419.4681 | 0.0088211 | 27.6984 | 57.6847 | 14.1004 | 13.1495 | 0.013907 | 38.1471 | 0.0087794 | 27.6126 | 0.0086872 | 23.6563 | 75.1862 | 62.128 | 23.2839 | 50824.3298 | 48359.4454 | 7298 | 0.49008 | 46602.9819 | 44138.0975 | 5.2552 | 0.20344 | -4.4145 | -17.5015 | 53.2147 | 50824.3298 | 45549.5096 | 4287.9335 | 986.8867 | 50824.3298 | 100%
3 | C8-CB50-95-CE | 75N0135 | C8-CB50-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 50 | 0 | CUST 3 | 6/27/2015 | 16:12:57 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.2 | 31 | 0 | 45167 | 73 | 44594 | 179 | 2006 | 143 | 47175 | 141 | 4.658 | 900 | [38 empty] | 50% condenser coil block(~50 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 44.5` | 74.994 | 0.01 | 62.001 | 0.029 | 94.985 | 0.016 | 74.999 | 0.023 | 74.6 | 0.05 | 58.52 | 0.04 | 62.24 | 0.02 | 0.114 | 0.004 | 0.8744 | 0.003 | 45167 | 73 | 2006 | 143 | 4.658 | 0.016 | [6 empty] | 229.8 | 1 | 229.4 | 1 | 230.2 | 1 | 31 | 0.1 | 28.7 | 0.1 | 32.6 | 0.1 | 7114.7 | 38.4 | 3861.3 | 51.3 | 3012.8 | 30.1 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 11.7 |  | 11.7 |  | 11 |  | 3890 |  | 0.85 | 230 | 230 | 230 | 12.3 | 12.2 | 10.9 | 3990 | 0.75 | 228.1 |  | 2.4 |  | 534.4 |  | 115 |  | 10119.4 | [22 empty] | 307.51 | 0.29 | 208.81 | 0.05 | 132.64 | 0.07 | 76.17 | 0.06 | [16 empty] | 71.84 | 0.05 | 77.19 | 0.03 | 42.01 | 0.03 | 35.18 | 0.03 | [8 empty] | 294.8 | 0.28 | 115.36 | 0.07 | 129.38 | 0.07 | 14.01 | 0.04 | 291.72 | 0.28 | 128.58 | 0.07 | 13.4 | 0.05 | [24 empty] | 327.88 | 0.37 | 212.92 | 0.08 | 137.66 | 0.09 | 75.26 | 0.05 | [20 empty] | 80.45 | 0.05 | 72.2 | 0.07 | 47.58 | 0.03 | 24.61 | 0.08 | [12 empty] | 316.78 | 0.37 | 116.07 | 0.08 | 134.95 | 0.09 | 18.88 | 0.04 | 313.3 | 0.35 | 134.09 | 0.09 | 17.17 | 0.06 | [12 empty] | 59.04 | 0.02 | 57.86 | 0.02 | 58.15 | 0.03 | 57.86 | 0.03 | 58.32 | 0.02 |  |  | 114.92 | 0.07 |  |  | 74.18 | 0.04 | 76.78 | 0.03 | 206.21 | 0.07 |  |  | 117.05 | 0.09 | 74.45 | 0.06 | 80.83 | 0.17 |  |  | 116.83 | 0.07 | [28 empty] | 58.84 | 0.02 | [8 empty] | 116.92 | 0.09 | 115.17 | 0.06 | [8 empty] | 76.01 | 0.04 | 116.5 | 0.08 | 73.56 | 0.07 | 117.13 | 0.08 | [10 empty] | 208.94 | 0.06 | 95.74 | 0.12 | 95.49 | 0.08 | 75.06 | 0.06 | 75.01 | 0.05 | 75.26 | 0.05 | 75.21 | 0.05 | 75.14 | 0.06 | 75.14 | 0.05 |  |  | 80.95 | 0.07 | 80.62 | 0.1 | 75.46 | 0.07 | 86.85 | 0.11 | 75.53 | 0.05 | 82.25 | 0.08 | 77.13 | 0.1 | 79.31 | 0.14 | 85.7 | 0.18 | 82.29 | 0.07 | 81.21 | 0.07 | 83.7 | 0.06 | 74.9 | 0.06 | 82.61 | 0.08 | 77.76 | 0.1 | 82.39 | 0.08 | [78 empty] | 94.18 | 0.1 | [8 empty] | 58.47 | 0.02 | 58.65 | 0.02 | C8-55-CE3 | 74.994 | 0.01 | 62.001 | 0.029 | 58.704 | 0.009 | 55.779 | 0.017 | 94.985 | 0.016 | 74.999 | 0.023 | 2505.7 | 4.4 | 2448.8 | 4.3 | 1.149 | 0.002 | -0.384 | 0.002 | 0.114 | 0.004 | 0.8744 | 0.003 | 29.267 | 0.001 | 10127 | 17 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5646 | 11443.9333 | 330.551 | 21.8452 | 92.9614 | 11350.9719 | 0.0088245 | 27.6951 | 57.1394 | 14.0996 | 13.1373 | 0.013923 | 38.1564 | 0.0087827 | 27.6094 | 0.008771 | 23.6236 | 75.1579 | 62.1229 | 23.242 | 50960.7033 | 49488.5953 | 8537 | 0.57175 | 46662.2038 | 45190.0958 | 4.6077 | 0.16635 | -4.4531 | -18.0185 | 53.5439 | 50960.7033 | 45613.2728 | 4366.9689 | 980.4616 | 50960.7033 | 100%
3 | C8-CB60-95-CE | 75N0136 | C8-CB60-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 60 | 0 | CUST 3 | 6/27/2015 | 16:47:16 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1 | 31.7 | 0 | 45125 | 64 | 44529 | 179 | 1452 | 129 | 46578 | 153 | 4.478 | 900 | [38 empty] | 60% condenser coil block(~60 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 47.5` | 75.005 | 0.007 | 61.998 | 0.022 | 94.99 | 0.015 | 74.997 | 0.021 | 74.61 | 0.06 | 58.53 | 0.03 | 62.24 | 0.01 | 0.111 | 0.004 | 0.8721 | 0.0026 | 45125 | 64 | 1452 | 129 | 4.478 | 0.017 | [6 empty] | 229.8 | 0.9 | 229.5 | 0.9 | 230.2 | 0.9 | 31.7 | 0.1 | 29.3 | 0 | 33.2 | 0 | 7277.7 | 34.2 | 3878.4 | 46.9 | 3123.8 | 27.3 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 12 |  | 12 |  | 11.3 |  | 4020 |  | 0.86 | 230 | 230 | 230 | 12.6 | 12.5 | 11.2 | 4120 | 0.75 | 228.1 |  | 2.4 |  | 540.7 |  | 115 |  | 10385.7 | [22 empty] | 317.01 | 0.2 | 210.4 | 0.05 | 135.01 | 0.05 | 75.39 | 0.05 | [16 empty] | 72.88 | 0.04 | 76.72 | 0.04 | 42.71 | 0.02 | 34.01 | 0.05 | [8 empty] | 304.25 | 0.23 | 118.16 | 0.06 | 131.81 | 0.06 | 13.65 | 0.04 | 301.14 | 0.21 | 131.01 | 0.05 | 12.95 | 0.04 | [24 empty] | 339.27 | 0.28 | 214.35 | 0.05 | 140.37 | 0.07 | 73.97 | 0.05 | [20 empty] | 81.63 | 0.04 | 69.67 | 0.08 | 48.31 | 0.03 | 21.35 | 0.09 | [12 empty] | 328.13 | 0.27 | 118.95 | 0.07 | 137.72 | 0.07 | 18.76 | 0.03 | 324.59 | 0.27 | 136.86 | 0.07 | 17.47 | 0.04 | [12 empty] | 59.08 | 0.03 | 57.85 | 0.03 | 58.13 | 0.03 | 57.84 | 0.03 | 58.27 | 0.03 |  |  | 117.66 | 0.06 |  |  | 73.97 | 0.04 | 76.25 | 0.03 | 207.53 | 0.05 |  |  | 119.73 | 0.07 | 72.46 | 0.08 | 78.03 | 0.1 |  |  | 119.23 | 0.05 | [28 empty] | 58.86 | 0.02 | [8 empty] | 119.39 | 0.06 | 118.06 | 0.04 | [8 empty] | 75.75 | 0.03 | 119.3 | 0.06 | 71.51 | 0.07 | 119.92 | 0.07 | [10 empty] | 210.23 | 0.06 | 95.73 | 0.11 | 95.6 | 0.09 | 75.05 | 0.06 | 75.04 | 0.06 | 75.27 | 0.06 | 75.22 | 0.06 | 75.14 | 0.06 | 75.14 | 0.06 |  |  | 80.98 | 0.1 | 80.64 | 0.1 | 75.46 | 0.08 | 86.91 | 0.12 | 75.51 | 0.05 | 82.3 | 0.08 | 77.12 | 0.13 | 79.39 | 0.14 | 85.74 | 0.19 | 82.33 | 0.07 | 81.23 | 0.09 | 83.77 | 0.07 | 74.92 | 0.06 | 82.65 | 0.07 | 77.82 | 0.11 | 82.44 | 0.1 | [78 empty] | 94.16 | 0.11 | [8 empty] | 58.49 | 0.03 | 58.68 | 0.03 | C8-55-CE3 | 75.005 | 0.007 | 61.998 | 0.022 | 58.702 | 0.008 | 55.851 | 0.013 | 94.99 | 0.015 | 74.997 | 0.021 | 2502.9 | 3.7 | 2445.1 | 3.7 | 1.149 | 0.001 | -0.383 | 0.002 | 0.111 | 0.004 | 0.8721 | 0.0026 | 29.258 | 0.001 | 10401 | 15 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.567 | 11430.9002 | 330.0515 | 21.8168 | 92.8399 | 11338.0603 | 0.0088199 | 27.6928 | 57.135 | 14.0997 | 13.1375 | 0.013921 | 38.1544 | 0.0087781 | 27.6071 | 0.0088136 | 23.6694 | 75.1688 | 62.1199 | 23.2872 | 50359.5194 | 49474.288 | 8811 | 0.59715 | 46059.3153 | 45174.0839 | 4.4284 | 0.15992 | -4.4056 | -18.0338 | 53.7021 | 50359.5194 | 45011.2715 | 4369.0392 | 979.2086 | 50359.5194 | 100%
3 | C8-CB70-95-CE | 75N0137 | C8-CB70-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 70 | 0 | CUST 3 | 6/27/2015 | 17:53:06 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.4 | 32.2 | 0 | 44832 | 67 | 44307 | 170 | 1041 | 131 | 45875 | 132 | 4.315 | 900 | [38 empty] | 70% condenser coil block(~70 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 50` | 74.998 | 0.008 | 61.995 | 0.028 | 95.012 | 0.021 | 75 | 0.02 | 74.58 | 0.07 | 58.5 | 0.04 | 62.27 | 0.02 | 0.099 | 0.004 | 0.864 | 0.0027 | 44832 | 67 | 1041 | 131 | 4.315 | 0.012 | [6 empty] | 229.9 | 1.2 | 229.5 | 1.2 | 230.3 | 1.2 | 32.2 | 0.1 | 29.8 | 0.1 | 33.8 | 0.1 | 7396.1 | 44.3 | 3910 | 60.3 | 3234.9 | 34 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.1 |  | 0.63 | 230 |  | 230 |  | 230 |  | 12.3 |  | 12.3 |  | 11.6 |  | 4130 |  | 0.86 | 230 | 230 | 230 | 12.9 | 12.8 | 11.5 | 4230 | 0.75 | 228 |  | 2.4 |  | 540.8 |  | 115 |  | 10605.8 | [22 empty] | 326.19 | 0.3 | 212.5 | 0.05 | 137.25 | 0.07 | 75.25 | 0.07 | [16 empty] | 73.78 | 0.05 | 76.17 | 0.05 | 43.3 | 0.03 | 32.87 | 0.05 | [8 empty] | 313.41 | 0.3 | 120.88 | 0.08 | 134.12 | 0.07 | 13.24 | 0.03 | 310.25 | 0.31 | 133.32 | 0.08 | 12.52 | 0.04 | [24 empty] | 348.2 | 0.37 | 215.72 | 0.07 | 142.45 | 0.09 | 73.27 | 0.09 | [20 empty] | 82.33 | 0.06 | 66.81 | 0.17 | 48.74 | 0.03 | 18.07 | 0.18 | [12 empty] | 337.12 | 0.38 | 121.21 | 0.08 | 139.87 | 0.09 | 18.65 | 0.03 | 333.41 | 0.37 | 138.99 | 0.09 | 17.31 | 0.05 | [12 empty] | 59.13 | 0.03 | 57.89 | 0.03 | 58.18 | 0.03 | 57.85 | 0.04 | 58.3 | 0.03 |  |  | 120.52 | 0.08 |  |  | 73.83 | 0.05 | 75.66 | 0.04 | 209.39 | 0.07 |  |  | 121.85 | 0.09 | 69.49 | 0.18 | 74.71 | 0.13 |  |  | 121.04 | 0.08 | [28 empty] | 58.91 | 0.03 | [8 empty] | 121.67 | 0.08 | 120.81 | 0.07 | [8 empty] | 75.62 | 0.05 | 122 | 0.09 | 68.69 | 0.26 | 122.13 | 0.09 | [10 empty] | 211.68 | 0.09 | 95.83 | 0.1 | 95.8 | 0.08 | 75.05 | 0.06 | 75.05 | 0.06 | 75.32 | 0.06 | 75.26 | 0.06 | 75.14 | 0.06 | 75.14 | 0.06 |  |  | 81.03 | 0.09 | 80.7 | 0.1 | 75.5 | 0.08 | 86.86 | 0.12 | 75.52 | 0.06 | 82.24 | 0.08 | 77.19 | 0.1 | 79.41 | 0.14 | 85.74 | 0.2 | 82.26 | 0.08 | 81.22 | 0.09 | 83.73 | 0.07 | 74.9 | 0.06 | 82.58 | 0.08 | 77.77 | 0.1 | 82.37 | 0.08 | [78 empty] | 94.07 | 0.13 | [8 empty] | 58.58 | 0.02 | 58.76 | 0.02 | C8-55-CE3 | 74.998 | 0.008 | 61.995 | 0.028 | 58.72 | 0.01 | 55.919 | 0.016 | 95.012 | 0.021 | 75 | 0.02 | 2491.6 | 3.9 | 2433.3 | 3.8 | 1.149 | 0.002 | -0.381 | 0.002 | 0.099 | 0.004 | 0.864 | 0.0027 | 29.254 | 0.001 | 10631 | 19 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5762 | 11378.6569 | 328.4587 | 21.7602 | 92.5954 | 11286.0615 | 0.0088196 | 27.6909 | 57.1438 | 14.1002 | 13.1383 | 0.013918 | 38.1569 | 0.0087778 | 27.6051 | 0.0088492 | 23.7125 | 75.1624 | 62.1172 | 23.328 | 49644.133 | 49206.5023 | 9041 | 0.62156 | 45338.4926 | 44900.8619 | 4.2647 | 0.15535 | -4.3629 | -18.0186 | 53.8297 | 49644.133 | 44292.2343 | 4374.8458 | 977.0529 | 49644.133 | 100%
3 | C8-CB80-95-CE | 75N0138 | C8-CB80-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 80 | 0 | CUST 3 | 6/27/2015 | 18:46:34 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.6 | 32.9 | 0 | 44343 | 69 | 43848 | 184 | 496 | 164 | 44840 | 169 | 4.104 | 900 | [38 empty] | 80% condenser coil block(~80 psig DP CK1 above C8-CB0-95-CE), economizer closed (2.8V),--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 51.5` | 74.998 | 0.006 | 61.999 | 0.029 | 94.977 | 0.031 | 74.994 | 0.017 | 74.6 | 0.06 | 58.62 | 0.03 | 62.37 | 0.01 | 0.093 | 0.004 | 0.859 | 0.0025 | 44343 | 69 | 496 | 164 | 4.104 | 0.019 | [6 empty] | 229.8 | 1 | 229.4 | 1 | 230.2 | 1 | 32.9 | 0.1 | 30.5 | 0.1 | 34.5 | 0.1 | 7560.4 | 37.7 | 3936.6 | 50.8 | 3365.4 | 31.2 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 12.6 |  | 12.6 |  | 11.9 |  | 4270 |  | 0.87 | 230 | 230 | 230 | 13.3 | 13.2 | 11.8 | 4390 | 0.76 | 228 |  | 2.4 |  | 537.6 |  | 115 |  | 10902.6 | [22 empty] | 336.09 | 0.47 | 215.69 | 0.1 | 139.62 | 0.11 | 76.07 | 0.1 | [16 empty] | 74.81 | 0.08 | 76.14 | 0.05 | 43.97 | 0.05 | 32.17 | 0.09 | [8 empty] | 323.28 | 0.47 | 123.69 | 0.1 | 136.55 | 0.12 | 12.85 | 0.05 | 320.05 | 0.47 | 135.76 | 0.12 | 12.17 | 0.08 | [24 empty] | 361.17 | 0.5 | 216.88 | 0.1 | 145.41 | 0.11 | 71.47 | 0.14 | [20 empty] | 83.3 | 0.06 | 63.37 | 0.34 | 49.34 | 0.04 | 14.03 | 0.36 | [12 empty] | 349.99 | 0.5 | 124.23 | 0.1 | 142.87 | 0.11 | 18.63 | 0.05 | 346.2 | 0.48 | 141.99 | 0.11 | 17.29 | 0.08 | [12 empty] | 59.29 | 0.03 | 57.95 | 0.04 | 58.27 | 0.03 | 57.95 | 0.04 | 58.36 | 0.04 |  |  | 123.32 | 0.09 |  |  | 73.53 | 0.07 | 75.66 | 0.05 | 210.92 | 0.1 |  |  | 124.84 | 0.1 | 62.63 | 1.04 | 72.35 | 0.29 |  |  | 123.86 | 0.08 | [28 empty] | 59.07 | 0.04 | [8 empty] | 124.7 | 0.1 | 123.58 | 0.09 | [8 empty] | 75.38 | 0.06 | 124.86 | 0.11 | 58.89 | 0.81 | 125.09 | 0.1 | [10 empty] | 214.85 | 0.08 | 95.6 | 0.09 | 94.85 | 0.08 | 75.06 | 0.07 | 75.06 | 0.07 | 75.34 | 0.07 | 75.28 | 0.07 | 75.15 | 0.07 | 75.15 | 0.06 |  |  | 81.11 | 0.07 | 80.71 | 0.09 | 75.49 | 0.08 | 87.08 | 0.11 | 75.54 | 0.06 | 82.33 | 0.07 | 77.22 | 0.11 | 79.34 | 0.13 | 85.6 | 0.22 | 82.33 | 0.06 | 81.34 | 0.07 | 83.99 | 0.07 | 74.91 | 0.07 | 82.66 | 0.07 | 77.8 | 0.1 | 82.49 | 0.08 | [78 empty] | 94.85 | 0.1 | [8 empty] | 58.73 | 0.03 | 58.93 | 0.03 | C8-55-CE3 | 74.998 | 0.006 | 61.999 | 0.029 | 58.843 | 0.014 | 56.051 | 0.014 | 94.977 | 0.031 | 74.994 | 0.017 | 2484.8 | 3.6 | 2425.5 | 3.5 | 1.149 | 0.002 | -0.38 | 0.002 | 0.093 | 0.004 | 0.859 | 0.0025 | 29.247 | 0.001 | 10926 | 21 | 1590 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5822 | 11344.585 | 327.4058 | 21.731 | 92.4767 | 11252.1083 | 0.0088223 | 27.6939 | 57.2608 | 14.0993 | 13.1418 | 0.013921 | 38.1517 | 0.0087804 | 27.6079 | 0.0088975 | 23.7951 | 75.1624 | 62.1213 | 23.4091 | 48609.5 | 48740.7335 | 9336 | 0.6555 | 44300.2661 | 44431.4996 | 4.0546 | 0.15408 | -4.2848 | -17.9016 | 54.0002 | 48609.5 | 43255.5631 | 4378.8824 | 975.0545 | 48609.5 | 100%
3 | C8-95-1FE | 75N0156 | C8-95-1FE | 1 finger | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/26/2015 | 7:16:07 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.8 | 1.5 | 28 | 0 | 41093 | 68 | 40681 | 148 | 1164 | 151 | 42258 | 173 | 4.79 | 899 | [38 empty] | Econo 1-Finger open, unsealed cabinet, Inlet static location inside Cabinet, 95F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions, 2700 cfm--(370 cfm/ton) 7" pulley, 870 rpm (4.5 turns), 75% inlet 75% outlet Meriam, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.03 | 0.011 | 62.003 | 0.026 | 94.992 | 0.007 | 74.995 | 0.016 | 74.58 | 0.05 | 60.05 | 0.03 | 63.46 | 0.02 | 0.104 | 0.005 | 0.8955 | 0.0028 | 41093 | 68 | 1164 | 151 | 4.79 | 0.022 | [6 empty] | 229.8 | 1.1 | 229.6 | 1.1 | 230.3 | 1.1 | 28 | 0.1 | 25.8 | 0.1 | 29.7 | 0.1 | 6419.5 | 41 | 3757.3 | 57.2 | 2402.2 | 30.6 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.5 |  | 9.7 |  | 3310 |  | 0.81 | 230 | 230 | 230 | 10.5 | 10.5 | 9.3 | 3250 | 0.72 | 228.3 |  | 2.4 |  | 528.5 |  | 115 |  | 8668.5 | [22 empty] | 259.63 | 0.11 | 196.3 | 0.02 | 119.82 | 0.03 | 76.48 | 0.04 | [16 empty] | 64.94 | 0.03 | 80.42 | 0.03 | 37.24 | 0.02 | 43.18 | 0.04 | [8 empty] | 247.74 | 0.13 | 100.9 | 0.04 | 116.38 | 0.04 | 15.48 | 0.03 | 245.15 | 0.12 | 115.62 | 0.04 | 13.74 | 0.04 | [24 empty] | 267.69 | 0.17 | 201.8 | 0.04 | 122.09 | 0.05 | 79.71 | 0.04 | [20 empty] | 71.7 | 0.04 | 78.26 | 0.03 | 41.92 | 0.02 | 36.34 | 0.05 | [12 empty] | 257.21 | 0.16 | 102.64 | 0.04 | 119.13 | 0.05 | 16.49 | 0.03 | 254.45 | 0.19 | 118.34 | 0.05 | 15.21 | 0.05 | [12 empty] | 60.82 | 0.04 | 60.26 | 0.04 | 59.86 | 0.04 | 59.36 | 0.05 | 60.32 | 0.04 |  |  | 100.92 | 0.04 |  |  | 75.8 | 0.03 | 79.74 | 0.02 | 195.5 | 0.04 |  |  | 103.12 | 0.04 | 79.53 | 0.03 | 83.93 | 0.03 |  |  | 104.97 | 0.04 | [28 empty] | 60.68 | 0.04 | [8 empty] | 103.13 | 0.04 | 101.88 | 0.03 | [8 empty] | 77.48 | 0.03 | 101.88 | 0.04 | 77.16 | 0.03 | 103.16 | 0.04 | [10 empty] | 196.98 | 0.03 | 95.42 | 0.08 | 95.22 | 0.08 | 74.86 | 0.07 | 74.93 | 0.06 | 74.85 | 0.06 | 74.92 | 0.06 | 74.92 | 0.06 | 74.98 | 0.06 |  |  | 83.66 | 0.07 | 84.02 | 0.08 | 74.99 | 0.06 | 81.68 | 0.28 | 75.64 | 0.07 | 84.89 | 0.08 | 79.65 | 0.1 | 82.21 | 0.15 | 76.33 | 0.08 | 84.53 | 0.07 | 84 | 0.06 | 81.8 | 0.06 | 75.13 | 0.07 | 84.67 | 0.08 | 81.07 | 0.13 | 85.2 | 0.11 | [78 empty] | 94.91 | 0.1 | [8 empty] | 60.57 | 0.04 | 60.65 | 0.03 | C8-55-1FE3 | 75.03 | 0.011 | 62.003 | 0.026 | 60.359 | 0.008 | 56.532 | 0.011 | 94.992 | 0.007 | 74.995 | 0.016 | 2538.9 | 4 | 2475.4 | 3.9 | 1.131 | 0.002 | -0.358 | 0.002 | 0.104 | 0.005 | 0.8955 | 0.0028 | 29.27 | 0 | 8822 | 16 | 1580 |  | 0.091282 | 224.4628 | 13.029 | 0.353 | 1.5388 | 11558.3046 | 328.907 | 235.1515 | 1000.6668 | 10557.6377 | 0.0092208 | 28.523 | 58.8202 | 14.0997 | 13.1796 | 0.013918 | 38.1524 | 0.0087755 | 27.6104 | 0.0088228 | 24.0836 | 76.773 | 63.2856 | 23.7082 | 55650.9728 | 49801.0208 | 7242 | 0.44414 | 51380.9923 | 45531.0403 | 5.8242 | 0.23315 | -4.8148 | -17.9528 | 53.362 | 55650.9728 | 40763.4687 | 4338.4043 | 10549.0997 | 55650.9728 | 100%
3 | C8-95-2FE | 75N0157 | C8-95-2FE | 2 finger | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/26/2015 | 5:49:18 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.6 | 28.1 | 0 | 38951 | 108 | 38861 | 158 | -1601 | 121 | 37348 | 141 | 4.227 | 899 | [38 empty] | Econo 2-Finger open, unsealed cabinet, Inlet static location inside Cabinet, 95F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--2700 cfm (370 cfm/ton) 7" pulley, 870 rpm (4.5 turns), 75% inlet 75% outlet Meriam,--adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.053 | 0.033 | 61.999 | 0.026 | 95.005 | 0.008 | 74.989 | 0.026 | 74.75 | 0.06 | 60.91 | 0.03 | 64.01 | 0.02 | 0.034 | 0.004 | 0.9056 | 0.003 | 38951 | 108 | -1601 | 121 | 4.227 | 0.019 | [6 empty] | 229.9 | 1.1 | 229.7 | 1.1 | 230.2 | 1.1 | 28.1 | 0.1 | 25.8 | 0.1 | 29.6 | 0.1 | 6449.6 | 41.5 | 3737 | 56.9 | 2385.3 | 31.3 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.5 |  | 9.8 |  | 3320 |  | 0.81 | 230 | 230 | 230 | 10.6 | 10.5 | 9.3 | 3260 | 0.71 | 228.4 |  | 2.4 |  | 528.1 |  | 115 |  | 8793.1 | [22 empty] | 260.34 | 0.15 | 197.21 | 0.03 | 120.02 | 0.04 | 77.19 | 0.04 | [16 empty] | 65.4 | 0.03 | 81.63 | 0.03 | 37.56 | 0.02 | 44.07 | 0.04 | [8 empty] | 248.42 | 0.15 | 100.94 | 0.05 | 116.58 | 0.04 | 15.63 | 0.03 | 245.84 | 0.15 | 115.82 | 0.05 | 13.94 | 0.04 | [24 empty] | 268.09 | 0.28 | 202.23 | 0.04 | 122.2 | 0.08 | 80.03 | 0.05 | [20 empty] | 71.94 | 0.06 | 78.85 | 0.03 | 42.07 | 0.04 | 36.78 | 0.06 | [12 empty] | 257.61 | 0.28 | 102.62 | 0.07 | 119.24 | 0.08 | 16.62 | 0.03 | 254.82 | 0.26 | 118.44 | 0.07 | 15.38 | 0.05 | [12 empty] | 61.74 | 0.03 | 61.3 | 0.04 | 60.73 | 0.04 | 60.1 | 0.04 | 60.98 | 0.04 |  |  | 100.94 | 0.05 |  |  | 77.21 | 0.03 | 81.01 | 0.02 | 195.92 | 0.04 |  |  | 103.18 | 0.05 | 80.14 | 0.03 | 84.45 | 0.03 |  |  | 105.01 | 0.04 | [28 empty] | 61.56 | 0.04 | [8 empty] | 103.06 | 0.07 | 101.88 | 0.05 | [8 empty] | 78.79 | 0.02 | 101.92 | 0.05 | 77.81 | 0.03 | 103.22 | 0.06 | [10 empty] | 197.91 | 0.03 | 95.44 | 0.08 | 95.23 | 0.11 | 75.01 | 0.07 | 75.1 | 0.07 | 75 | 0.07 | 75.07 | 0.07 | 75.08 | 0.08 | 75.14 | 0.07 |  |  | 85.23 | 0.07 | 84.96 | 0.08 | 75.11 | 0.07 | 79.87 | 0.19 | 75.75 | 0.08 | 86.89 | 0.09 | 81.04 | 0.12 | 83.57 | 0.12 | 76.6 | 0.1 | 86.09 | 0.08 | 85.27 | 0.06 | 83.41 | 0.07 | 75.25 | 0.08 | 86.32 | 0.08 | 83.84 | 0.14 | 85.41 | 0.09 | [78 empty] | 94.77 | 0.1 | [8 empty] | 61.54 | 0.04 | 61.46 | 0.03 | C8-55-2FE3 | 75.053 | 0.033 | 61.999 | 0.026 | 61.181 | 0.013 | 57.227 | 0.017 | 95.005 | 0.008 | 74.989 | 0.026 | 2556.1 | 4.2 | 2486.1 | 4.1 | 1.129 | 0.001 | -0.336 | 0.002 | 0.034 | 0.004 | 0.9056 | 0.003 | 29.246 | 0 | 8835 | 16 | 1570 |  | 0.1172 | 290.407 | 13.03 | 0.325 | 1.5178 | 11616.7218 | 329.7446 | 307.165 | 1307.0896 | 10309.6322 | 0.0093461 | 28.793 | 59.6632 | 14.1 | 13.2022 | 0.01391 | 38.1464 | 0.0087674 | 27.6071 | 0.0090432 | 24.524 | 77.3166 | 63.6589 | 24.1536 | 53894.7543 | 49217.9908 | 7265 | 0.46007 | 49661.7625 | 44984.999 | 5.621 | 0.23939 | -4.6394 | -17.6534 | 54.1069 | 53894.7543 | 35816.449 | 4302.5487 | 13775.7566 | 53894.7543 | 100%
3 | C8-95-3FE | 75N0158 | C8-95-3FE | 3 finger | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/26/2015 | 4:50:58 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.1 | 28.2 | 0 | 35887 | 53 | 35669 | 149 | -5495 | 74 | 30388 | 82 | 3.434 | 900 | [38 empty] | Econo 3-Finger open, unsealed cabinet, Inlet static location inside Cabinet, 95F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--2700 cfm (370 cfm/ton) 7" pulley, 870 rpm (4.5 turns), 75% inlet 75% outlet Meriam.,--ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.025 | 0.01 | 61.954 | 0.009 | 95.003 | 0.013 | 74.998 | 0.017 | 74.64 | 0.05 | 62.01 | 0.03 | 64.9 | 0.02 | 0.028 | 0.004 | 0.9236 | 0.0028 | 35887 | 53 | -5495 | 74 | 3.434 | 0.012 | [6 empty] | 229.9 | 1 | 229.7 | 1 | 230.1 | 1 | 28.2 | 0.1 | 25.8 | 0.1 | 29.6 | 0.1 | 6472.7 | 37.3 | 3719.3 | 52.9 | 2376.5 | 28.5 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.3 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.4 |  | 9.8 |  | 3330 |  | 0.82 | 230 | 230 | 230 | 10.6 | 10.4 | 9.3 | 3270 | 0.72 | 228.4 |  | 2.4 |  | 527.8 |  | 115 |  | 8822.8 | [22 empty] | 260.98 | 0.19 | 198.32 | 0.05 | 120.2 | 0.05 | 78.12 | 0.06 | [16 empty] | 65.96 | 0.05 | 83.15 | 0.03 | 37.96 | 0.03 | 45.19 | 0.04 | [8 empty] | 249 | 0.19 | 100.9 | 0.05 | 116.75 | 0.06 | 15.85 | 0.03 | 246.37 | 0.18 | 115.98 | 0.05 | 14.1 | 0.04 | [24 empty] | 268.29 | 0.26 | 202.66 | 0.06 | 122.25 | 0.07 | 80.41 | 0.04 | [20 empty] | 72.14 | 0.05 | 79.43 | 0.03 | 42.21 | 0.03 | 37.22 | 0.04 | [12 empty] | 257.79 | 0.24 | 102.65 | 0.06 | 119.29 | 0.07 | 16.64 | 0.03 | 254.99 | 0.25 | 118.49 | 0.07 | 15.4 | 0.04 | [12 empty] | 62.83 | 0.03 | 62.59 | 0.06 | 62.03 | 0.05 | 61.24 | 0.05 | 62.16 | 0.05 |  |  | 100.93 | 0.05 |  |  | 78.94 | 0.02 | 82.56 | 0.03 | 196.31 | 0.05 |  |  | 103.19 | 0.06 | 80.64 | 0.03 | 84.94 | 0.03 |  |  | 105.05 | 0.05 | [28 empty] | 62.76 | 0.04 | [8 empty] | 103.09 | 0.06 | 101.88 | 0.05 | [8 empty] | 80.47 | 0.03 | 101.88 | 0.05 | 78.35 | 0.04 | 103.23 | 0.06 | [10 empty] | 198.99 | 0.04 | 95.44 | 0.1 | 95.19 | 0.1 | 74.94 | 0.07 | 74.99 | 0.06 | 74.93 | 0.07 | 74.99 | 0.07 | 75.01 | 0.06 | 75.07 | 0.06 |  |  | 87.62 | 0.09 | 87.14 | 0.09 | 75.09 | 0.06 | 78.41 | 0.14 | 75.69 | 0.06 | 89.62 | 0.11 | 85.27 | 0.14 | 87.74 | 0.13 | 76.67 | 0.09 | 88.27 | 0.09 | 87.49 | 0.08 | 85.1 | 0.07 | 75.17 | 0.06 | 88.64 | 0.1 | 86.88 | 0.18 | 86.95 | 0.09 | [78 empty] | 94.71 | 0.13 | [8 empty] | 62.71 | 0.04 | 62.72 | 0.04 | C8-55-3FE3 | 75.025 | 0.01 | 61.954 | 0.009 | 62.311 | 0.005 | 58.147 | 0.007 | 95.003 | 0.013 | 74.998 | 0.017 | 2584.2 | 4 | 2507.4 | 3.9 | 1.113 | 0.001 | -0.28 | 0.002 | 0.028 | 0.004 | 0.9236 | 0.0028 | 29.24 | 0.001 | 8849 | 17 | 1580 |  | 0.17753 | 447.8183 | 13.029 | 0.274 | 1.5193 | 11716.9816 | 327.8566 | 470.933 | 2003.9745 | 9713.0071 | 0.0096293 | 29.3846 | 60.7917 | 14.1 | 13.2331 | 0.013918 | 38.1551 | 0.0087444 | 27.5751 | 0.009334 | 25.1162 | 78.4685 | 64.4661 | 24.7453 | 54359.0895 | 49708.4444 | 7269 | 0.45639 | 50085.524 | 45434.8789 | 5.66 | 0.24813 | -4.6393 | -17.6768 | 54.9581 | 54359.0895 | 28810.8738 | 4346.0869 | 21202.1288 | 54359.0895 | 100%
3 | C8-95-CE | 75N0159 | C8-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/26/2015 | 8:43:13 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.6 | 1.7 | 27.9 | 0 | 44846 | 66 | 44238 | 153 | 5178 | 116 | 50029 | 127 | 5.681 | 900 | [38 empty] | Econo closed (2.0V), unsealed cabinet, Inlet static location inside Cabinet, 95F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,2700 cfm (370 cfm/ton)--7" pulley, 870 rpm (4.5 turns), 75% inlet 75% outlet Meriam, adjus | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.006 | 0.019 | 62.005 | 0.024 | 94.99 | 0.008 | 75.007 | 0.024 | 74.53 | 0.05 | 58.7 | 0.03 | 62.47 | 0.02 | 0.134 | 0.003 | 0.8849 | 0.0022 | 44846 | 66 | 5178 | 116 | 5.681 | 0.017 | [6 empty] | 229.6 | 1.4 | 229.5 | 1.4 | 230.3 | 1.4 | 27.9 | 0.1 | 25.7 | 0.1 | 29.8 | 0.1 | 6390.5 | 53.1 | 3769.8 | 75.2 | 2415.7 | 39.2 | 230 |  | 230 |  | 230 |  | 6.5 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.4 |  | 9.7 |  | 3310 |  | 0.82 | 230 | 230 | 230 | 10.5 | 10.5 | 9.2 | 3270 | 0.72 | 228.3 |  | 2.4 |  | 528.4 |  | 115 |  | 8803.4 | [22 empty] | 258.65 | 0.1 | 194.75 | 0.03 | 119.54 | 0.03 | 75.21 | 0.04 | [16 empty] | 64.16 | 0.03 | 78.22 | 0.04 | 36.69 | 0.02 | 41.54 | 0.04 | [8 empty] | 246.86 | 0.09 | 100.93 | 0.04 | 116.12 | 0.03 | 15.19 | 0.04 | 244.31 | 0.1 | 115.37 | 0.03 | 13.44 | 0.04 | [24 empty] | 267.51 | 0.14 | 201.38 | 0.03 | 122.04 | 0.04 | 79.34 | 0.04 | [20 empty] | 71.54 | 0.04 | 77.7 | 0.03 | 41.81 | 0.03 | 35.88 | 0.03 | [12 empty] | 257.07 | 0.15 | 102.66 | 0.03 | 119.09 | 0.04 | 16.43 | 0.03 | 254.29 | 0.16 | 118.29 | 0.05 | 15.14 | 0.04 | [12 empty] | 59.38 | 0.03 | 58.66 | 0.04 | 58.56 | 0.04 | 57.9 | 0.04 | 58.79 | 0.04 |  |  | 100.94 | 0.04 |  |  | 73.33 | 0.04 | 77.49 | 0.03 | 195.13 | 0.04 |  |  | 103.1 | 0.03 | 78.98 | 0.03 | 83.44 | 0.03 |  |  | 104.92 | 0.02 | [28 empty] | 59.18 | 0.04 | [8 empty] | 103.15 | 0.03 | 101.94 | 0.03 | [8 empty] | 75.11 | 0.03 | 101.89 | 0.03 | 76.59 | 0.03 | 103.14 | 0.03 | [10 empty] | 195.42 | 0.03 | 95.42 | 0.06 | 95.25 | 0.09 | 74.81 | 0.06 | 74.88 | 0.06 | 74.8 | 0.06 | 74.88 | 0.06 | 74.88 | 0.06 | 74.93 | 0.06 |  |  | 78.3 | 0.07 | 79.07 | 0.08 | 74.91 | 0.05 | 87.7 | 0.21 | 75.61 | 0.06 | 77.01 | 0.08 | 75.4 | 0.06 | 75.82 | 0.08 | 76.21 | 0.09 | 78.31 | 0.09 | 79.33 | 0.07 | 80.54 | 0.07 | 75.06 | 0.06 | 78.1 | 0.09 | 75.25 | 0.06 | 84.09 | 0.09 | [78 empty] | 94.16 | 0.06 | [8 empty] | 59.09 | 0.04 | 59.13 | 0.03 | C8-55-CE3 | 75.006 | 0.019 | 62.005 | 0.024 | 58.958 | 0.013 | 55.416 | 0.017 | 94.99 | 0.008 | 75.007 | 0.024 | 2521.1 | 3.2 | 2464.1 | 3.2 | 1.136 | 0.002 | -0.394 | 0.002 | 0.134 | 0.003 | 0.8849 | 0.0022 | 29.27 | 0 | 8807 | 19 | 1580 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5453 | 11510.4843 | 328.853 | 22.128 | 94.1634 | 11416.3209 | 0.0088246 | 27.6985 | 57.4127 | 14.0997 | 13.1416 | 0.013929 | 38.1641 | 0.0087825 | 27.6122 | 0.0084997 | 23.3906 | 75.171 | 62.1278 | 23.0139 | 53921.5852 | 49057.5937 | 7227 | 0.45744 | 49651.4204 | 44787.4289 | 5.6377 | 0.21828 | -4.6846 | -17.7583 | 52.4539 | 53921.5852 | 48591.9406 | 4336.0401 | 993.6045 | 53921.5852 | 100%
3 | C8-95-OE | 75N0162 | C8-95-OE | open | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/26/2015 | 3:36:47 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.3 | 28.2 | 0 | 21029 | 69 | 20669 | 116 | -17374 | 111 | 3639 | 132 | 0.412 | 900 | [38 empty] | Econo 100% open, unsealed cabinet, Inlet static location inside Cabinet, 95F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions, 2700 cfm (370 cfm/ton)--7" pulley, 870 rpm (4.5 turns), 75% inlet 75% outlet Meriam,--adjust | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.008 | 0.005 | 62.907 | 0.016 | 94.993 | 0.008 | 75.025 | 0.018 | 74.54 | 0.03 | 66.8 | 0.04 | 68.94 | 0.01 | -0.026 | 0.004 | 0.8657 | 0.003 | 21029 | 69 | -17374 | 111 | 0.412 | 0.015 | [6 empty] | 229.9 | 1.1 | 229.7 | 1.1 | 230.1 | 1.1 | 28.2 | 0.1 | 25.7 | 0.1 | 29.5 | 0.1 | 6466.3 | 42.1 | 3707.5 | 57 | 2356.2 | 32.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.6 |  | 9.7 |  | 3330 |  | 0.82 | 230 | 230 | 230 | 10.7 | 10.5 | 9.2 | 3260 | 0.72 | 228.5 |  | 2.4 |  | 527.7 |  | 115 |  | 8772.7 | [22 empty] | 262.11 | 0.15 | 202.83 | 0.04 | 120.52 | 0.04 | 82.31 | 0.04 | [16 empty] | 67.61 | 0.04 | 89.26 | 0.03 | 39.11 | 0.03 | 50.15 | 0.04 | [8 empty] | 249.96 | 0.15 | 100.74 | 0.04 | 117.03 | 0.04 | 16.28 | 0.02 | 247.31 | 0.15 | 116.25 | 0.04 | 14.52 | 0.03 | [24 empty] | 268.04 | 0.26 | 204.29 | 0.04 | 122.18 | 0.07 | 82.11 | 0.05 | [20 empty] | 72.55 | 0.05 | 81.67 | 0.03 | 42.47 | 0.04 | 39.2 | 0.04 | [12 empty] | 257.5 | 0.26 | 102.54 | 0.05 | 119.21 | 0.08 | 16.67 | 0.04 | 254.76 | 0.25 | 118.42 | 0.07 | 15.4 | 0.05 | [12 empty] | 67.57 | 0.05 | 67.45 | 0.07 | 67.04 | 0.07 | 66.71 | 0.07 | 66.71 | 0.07 |  |  | 100.77 | 0.04 |  |  | 85.85 | 0.03 | 88.9 | 0.03 | 197.77 | 0.04 |  |  | 103.11 | 0.05 | 82.79 | 0.03 | 86.84 | 0.03 |  |  | 105.01 | 0.03 | [28 empty] | 67.51 | 0.06 | [8 empty] | 103.02 | 0.05 | 101.74 | 0.04 | [8 empty] | 87.06 | 0.03 | 101.83 | 0.04 | 80.61 | 0.03 | 103.12 | 0.05 | [10 empty] | 203.53 | 0.04 | 95.3 | 0.1 | 95.12 | 0.11 | 74.88 | 0.04 | 74.91 | 0.04 | 74.92 | 0.04 | 74.99 | 0.04 | 75.01 | 0.04 | 75.02 | 0.03 |  |  | 89.06 | 0.11 | 88.86 | 0.1 | 77.27 | 0.04 | 85.41 | 0.18 | 79.42 | 0.06 | 94.67 | 0.14 | 94.37 | 0.14 | 92.79 | 0.14 | 76.28 | 0.04 | 92.21 | 0.13 | 89.36 | 0.1 | 89.3 | 0.08 | 83 | 0.19 | 93.27 | 0.15 | 94.36 | 0.15 | 88.61 | 0.08 | [78 empty] | 93.63 | 0.15 | [8 empty] | 67.42 | 0.06 | 67.52 | 0.06 | C8-55-OE3 | 75.008 | 0.005 | 62.907 | 0.016 | 67.132 | 0.021 | 62.511 | 0.023 | 94.993 | 0.008 | 75.025 | 0.018 | 2512.4 | 4.4 | 2411.7 | 4.2 | 1.151 | 0.002 | -0.269 | 0.002 | -0.026 | 0.004 | 0.8657 | 0.003 | 29.233 | 0.001 | 8822 | 17 | 1540 |  | 0.40678 | 1006.8652 | 13.03 | 0.11 | 1.5304 | 11276.1474 | 326.1097 | 1637.9001 | 6969.8221 | 4306.3252 | 0.012202 | 34.3961 | 65.6016 | 14.0999 | 13.3684 | 0.013944 | 38.1814 | 0.0093828 | 28.2696 | 0.010987 | 28.0962 | 87.3997 | 70.7727 | 27.7214 | 75265.1378 | 58991.8322 | 7282 | 0.33021 | 71122.1302 | 54848.8246 | 8.0619 | 0.24011 | -6.6747 | -21.7982 | 58.7138 | 75265.1378 | 1955.4064 | 4225.9783 | 69083.7531 | 75265.1378 | 100%
3 | C8-R100-95-CE-1 | 75N0170 | C8-R100-95-CE-1 | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/30/2015 | 12:13:13 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1.9 | 27.7 | 0 | 44673 | 101 | 44188 | 124 | 5663 | 174 | 50340 | 210 | 5.819 | 900 | [38 empty] | 100% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run--C8-R100-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.996 | 0.002 | 62.003 | 0.035 | 95.012 | 0.012 | 75.004 | 0.022 | 74.59 | 0.05 | 58.86 | 0.04 | 62.59 | 0.01 | 0.171 | 0.006 | 0.8932 | 0.0031 | 44673 | 101 | 5663 | 174 | 5.819 | 0.027 | [6 empty] | 229.7 | 1.4 | 229.7 | 1.4 | 230.2 | 1.4 | 27.7 | 0.1 | 25.3 | 0.1 | 29.3 | 0.1 | 6349.7 | 53.8 | 3716.2 | 75.4 | 2302 | 39.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.1 |  | 10.1 |  | 9.3 |  | 3170 |  | 0.82 | 230 | 230 | 230 | 10.6 | 10.5 | 9.2 | 3270 | 0.72 | 228.5 |  | 2.4 |  | 525.6 |  | 115 |  | 8640.6 | [22 empty] | 246.54 | 0.26 | 200.07 | 0.05 | 116.03 | 0.08 | 84.03 | 0.07 | [16 empty] | 57.96 | 0.05 | 79.1 | 0.03 | 32.09 | 0.04 | 47.01 | 0.06 | [8 empty] | 236.22 | 0.23 | 101 | 0.07 | 112.95 | 0.07 | 11.94 | 0.04 | 233.96 | 0.24 | 112.26 | 0.07 | 10.69 | 0.05 | [24 empty] | 268.36 | 0.27 | 198.01 | 0.06 | 122.28 | 0.08 | 75.74 | 0.05 | [20 empty] | 73.01 | 0.05 | 74.92 | 0.03 | 42.8 | 0.04 | 32.12 | 0.05 | [12 empty] | 257.53 | 0.27 | 102.82 | 0.07 | 119.22 | 0.08 | 16.4 | 0.04 | 254.51 | 0.25 | 118.36 | 0.07 | 14.96 | 0 | [12 empty] | 59.42 | 0.04 | 58.45 | 0.04 | 58.55 | 0.04 | 58.14 | 0.05 | 58.66 | 0.04 |  |  | 100.98 | 0.07 |  |  | 74.77 | 0.05 | 78.47 | 0.03 | 192.68 | 0.05 |  |  | 103.33 | 0.07 | 75.85 | 0.05 | 79.21 | 0.05 |  |  | 104.67 | 0.05 | [28 empty] | 59.24 | 0.04 | [8 empty] | 103.4 | 0.25 | 101.57 | 0.06 | [8 empty] | 76.35 | 0.05 | 101.9 | 0.06 | 73.8 | 0.06 | 103.56 | 0.07 | [10 empty] | 199.44 | 0.05 | 95.16 | 0.15 | 95.77 | 0.11 | 74.84 | 0.06 | 74.89 | 0.06 | 74.77 | 0.07 | 74.85 | 0.07 | 74.87 | 0.06 | 74.92 | 0.06 |  |  | 77.42 | 0.08 | 77.02 | 0.07 | 74.81 | 0.06 | 84.89 | 0.15 | 75.85 | 0.05 | 77.09 | 0.12 | 75.43 | 0.06 | 75.58 | 0.07 | 76.64 | 0.09 | 78.66 | 0.08 | 78.45 | 0.06 | 80.97 | 0.1 | 75.11 | 0.05 | 77.27 | 0.11 | 75.29 | 0.05 | 83.82 | 0.09 | [78 empty] | 94.19 | 0.09 | [8 empty] | 59 | 0.04 | 59.15 | 0.04 | C8-55-CE3 | 74.996 | 0.002 | 62.003 | 0.035 | 59.091 | 0.019 | 55.402 | 0.022 | 95.012 | 0.012 | 75.004 | 0.022 | 2532.5 | 4.4 | 2476.3 | 4.3 | 1.154 | 0.002 | -0.426 | 0.002 | 0.171 | 0.006 | 0.8932 | 0.0031 | 29.284 | 0.001 | 8652 | 21 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5057 | 11559.8402 | 335.7176 | 23.0094 | 97.911 | 11461.9292 | 0.0088271 | 27.7002 | 57.5853 | 14.1002 | 13.1446 | 0.013921 | 38.1608 | 0.0087835 | 27.6109 | 0.0084602 | 23.3801 | 75.1671 | 62.1301 | 23.013 | 54183.007 | 48778.1836 | 7092 | 0.44673 | 50004.5313 | 44599.7079 | 5.7795 | 0.23234 | -4.6872 | -17.5818 | 52.2642 | 54183.007 | 48907.4235 | 4242.631 | 1032.9525 | 54183.007 | 100%
3 | C8-R100-95-CE | 75N0171 | C8-R100-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/29/2015 | 10:59:36 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.7 | 27.8 | 0 | 43874 | 118 | 43058 | 153 | 5582 | 185 | 49461 | 197 | 5.704 | 900 |  |  | 5.0593 | [35 empty] | 100% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run--C8-R100-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 51.5` | 75.011 | 0.017 | 62.002 | 0.035 | 95.013 | 0.013 | 75.005 | 0.032 | 74.5 | 0.05 | 59.09 | 0.03 | 62.87 | 0.02 | 0.158 | 0.007 | 0.8848 | 0.0047 | 43874 | 118 | 5582 | 185 | 5.704 | 0.025 | [6 empty] | 229.8 | 1.2 | 229.9 | 1.3 | 230.3 | 1.3 | 27.8 | 0.1 | 25.3 | 0.1 | 29.4 | 0.1 | 6372.1 | 48.5 | 3713.4 | 65.8 | 2299.4 | 36.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.1 |  | 10.2 |  | 9.4 |  | 3170 |  | 0.72 | 230 | 230 | 230 | 10.6 | 10.5 | 9.3 | 3290 | 0.72 | 228.6 |  | 2.4 |  | 528 |  | 115 |  | 8663 | [22 empty] | 246.92 | 0.31 | 200.68 | 0.05 | 116.14 | 0.09 | 84.54 | 0.06 | [16 empty] | 57.4 | 0.06 | 80.1 | 0.04 | 31.65 | 0.04 | 48.45 | 0.05 | [8 empty] | 236.7 | 0.3 | 101.26 | 0.09 | 113.08 | 0.09 | 11.82 | 0.03 | 234.52 | 0.28 | 112.42 | 0.09 | 10.27 | 0.06 | [24 empty] | 268.64 | 0.29 | 199.23 | 0.05 | 122.35 | 0.08 | 76.88 | 0.05 | [20 empty] | 72.38 | 0.06 | 75.88 | 0.03 | 42.37 | 0.04 | 33.5 | 0.05 | [12 empty] | 257.89 | 0.29 | 103.04 | 0.07 | 119.32 | 0.08 | 16.28 | 0.04 | 254.99 | 0.27 | 118.49 | 0.08 | 14.84 | 0.05 | [12 empty] | 59.65 | 0.04 | 59.14 | 0.04 | 58.59 | 0.04 | 58.3 | 0.04 | 58.94 | 0.04 |  |  | 101.19 | 0.08 |  |  | 75.08 | 0.04 | 79.01 | 0.04 | 193.4 | 0.06 |  |  | 103.4 | 0.07 | 78.64 | 0.03 | 81.45 | 0.03 |  |  | 104.71 | 0.06 | [28 empty] | 59.49 | 0.04 | [8 empty] | 103.65 | 0.07 | 102.15 | 0.06 | [8 empty] | 76.58 | 0.04 | 102.22 | 0.08 | 74.82 | 0.03 | 103.56 | 0.07 | [10 empty] | 201.18 | 0.07 | 95.41 | 0.15 | 95.78 | 0.13 | 74.77 | 0.07 | 74.83 | 0.06 | 74.74 | 0.07 | 74.82 | 0.07 | 74.81 | 0.07 | 74.85 | 0.06 |  |  | 75.6 | 0.08 | 77.2 | 0.09 | 74.87 | 0.06 | 87.17 | 0.19 | 75.61 | 0.06 | 75.72 | 0.07 | 75.21 | 0.07 | 76.21 | 0.12 | 78.09 | 0.13 | 76.22 | 0.07 | 76.39 | 0.08 | 81.53 | 0.09 | 74.91 | 0.06 | 75.78 | 0.07 | 75.2 | 0.07 | 82.97 | 0.16 | [78 empty] | 94.08 | 0.15 | [8 empty] | 59.39 | 0.03 | 59.25 | 0.04 | C8-55-CE3 | 75.011 | 0.017 | 62.002 | 0.035 | 59.305 | 0.01 | 55.492 | 0.015 | 95.013 | 0.013 | 75.005 | 0.032 | 2522.7 | 6.8 | 2462.4 | 6.7 | 1.154 | 0.003 | -0.429 | 0.003 | 0.158 | 0.007 | 0.8848 | 0.0047 | 29.25 | 0.001 | 8672 | 21 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5145 | 11510.3476 | 333.8332 | 23.0903 | 98.255 | 11412.0926 | 0.0088232 | 27.7 | 57.7905 | 14.1003 | 13.1501 | 0.013922 | 38.1617 | 0.0087793 | 27.6099 | 0.0084618 | 23.434 | 75.1833 | 62.1302 | 23.0649 | 53352.0884 | 48047.2948 | 7112 | 0.45496 | 49167.1811 | 43862.3874 | 5.6696 | 0.24137 | -4.6351 | -17.3928 | 52.2567 | 53352.0884 | 48066.1464 | 4249.1741 | 1036.7679 | 53352.0884 | 100%
3 | C8-R100-E20C30-95CE | 75N0172 | C8-R100-E20C30-95CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 0 | CUST 3 | 6/29/2015 | 12:09:48 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1.9 | 29.2 | 0 | 43218 | 101 | 42634 | 164 | 6334 | 120 | 49559 | 134 | 5.336 | 901 | [38 empty] | Baseline 100% factory charge, 20% evaporator blockage, 30% condenser blockage,--economizer closed (2.0V), factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB,--62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 29" | 74.895 | 0.038 | 61.984 | 0.027 | 95.003 | 0.013 | 74.998 | 0.021 | 74.46 | 0.07 | 58.52 | 0.03 | 62.65 | 0.03 | 0.132 | 0.003 | 0.8077 | 0.0025 | 43218 | 101 | 6334 | 120 | 5.336 | 0.018 | [6 empty] | 229.7 | 1.5 | 229.8 | 1.4 | 230.2 | 1.5 | 29.2 | 0.1 | 26.6 | 0.1 | 30.8 | 0.1 | 6708.7 | 52.8 | 3756.5 | 75.7 | 2579.3 | 40.2 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.1 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.8 |  | 10.9 |  | 9.4 |  | 3480 |  | 0.83 | 230 | 230 | 230 | 11.6 | 11.4 | 10.1 | 3650 | 0.74 | 228.5 |  | 2.4 |  | 536.7 |  | 115 |  | 9291.7 | [22 empty] | 271.17 | 0.25 | 207.35 | 0.04 | 123.05 | 0.07 | 84.3 | 0.06 | [16 empty] | 59.69 | 0.07 | 75.96 | 0.04 | 33.39 | 0.05 | 42.57 | 0.06 | [8 empty] | 260.78 | 0.26 | 109.11 | 0.05 | 120.14 | 0.07 | 11.03 | 0.05 | 258.48 | 0.25 | 119.49 | 0.07 | 10.01 | 0.07 | [24 empty] | 298.55 | 0.19 | 201.72 | 0.04 | 130.35 | 0.05 | 71.37 | 0.05 | [20 empty] | 75.77 | 0.05 | 67.51 | 0.04 | 44.6 | 0.03 | 22.91 | 0.05 | [12 empty] | 287.42 | 0.2 | 110.63 | 0.05 | 127.44 | 0.05 | 16.81 | 0.03 | 284.24 | 0.19 | 126.6 | 0.05 | 15.77 | 0.04 | [12 empty] | 59.34 | 0.03 | 58.73 | 0.03 | 57.9 | 0.03 | 57.47 | 0.03 | 58.28 | 0.03 |  |  | 109.33 | 0.06 |  |  | 70.68 | 0.04 | 74.16 | 0.03 | 195.97 | 0.04 |  |  | 110.64 | 0.04 | 71.05 | 0.04 | 75.47 | 0.05 |  |  | 111.04 | 0.04 | [28 empty] | 59.2 | 0.03 | [8 empty] | 110.83 | 0.04 | 109.48 | 0.05 | [8 empty] | 72.88 | 0.04 | 109.43 | 0.05 | 66.85 | 0.06 | 110.97 | 0.05 | [10 empty] | 206.86 | 0.04 | 94.92 | 0.1 | 94.81 | 0.09 | 74.74 | 0.07 | 74.8 | 0.07 | 74.7 | 0.07 | 74.77 | 0.07 | 74.79 | 0.07 | 74.83 | 0.07 |  |  | 78.13 | 0.08 | 78.41 | 0.08 | 74.91 | 0.07 | 85.64 | 0.12 | 75.56 | 0.07 | 77.75 | 0.09 | 75.83 | 0.08 | 76.89 | 0.1 | 78.73 | 0.12 | 78.51 | 0.08 | 78.5 | 0.08 | 79.07 | 0.09 | 74.86 | 0.07 | 78.21 | 0.07 | 75.42 | 0.08 | 81.18 | 0.1 | [78 empty] | 94.19 | 0.08 | [8 empty] | 59.06 | 0.02 | 58.97 | 0.03 | C8-EB20-55-CE | 74.895 | 0.038 | 61.984 | 0.027 | 58.729 | 0.015 | 55.133 | 0.017 | 95.003 | 0.013 | 74.998 | 0.021 | 2408.9 | 3.8 | 2352.4 | 3.7 | 1.054 | 0.002 | -0.384 | 0.002 | 0.132 | 0.003 | 0.8077 | 0.0025 | 29.248 | 0 | 9288 | 19 | 1510 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.5746 | 11003.7922 | 291.2842 | 26.4694 | 112.6359 | 10891.1564 | 0.0088473 | 27.7067 | 57.1544 | 14.1 | 13.1349 | 0.013918 | 38.1551 | 0.0087949 | 27.5986 | 0.0083902 | 23.2158 | 75.1027 | 62.1378 | 22.832 | 53640.1553 | 47399.8006 | 7778 | 0.4949 | 49480.6782 | 43240.3234 | 5.3274 | 0.22398 | -4.8747 | -17.9483 | 51.974 | 53640.1553 | 48228.312 | 4222.8024 | 1189.0409 | 53640.1553 | 100%
3 | C8-R105-95-CE | 75N0173 | C8-R105-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/30/2015 | 0:37:36 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 1.7 | 28.1 | 0 | 45361 | 101 | 45088 | 163 | 5822 | 123 | 51188 | 121 | 5.85 | 900 | [38 empty] | 105% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of--run C8-R105-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.025 | 0.042 | 62.006 | 0.02 | 94.979 | 0.033 | 75.002 | 0.013 | 74.68 | 0.07 | 58.54 | 0.03 | 62.59 | 0.03 | 0.151 | 0.005 | 0.8838 | 0.0027 | 45361 | 101 | 5822 | 123 | 5.85 | 0.018 | [6 empty] | 230.1 | 1.3 | 229.8 | 1.3 | 230 | 1.4 | 28.1 | 0.1 | 25.6 | 0.1 | 29.2 | 0.1 | 6463.2 | 50.8 | 3669.3 | 71.2 | 2286.2 | 39.2 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.3 |  | 10.1 |  | 9.5 |  | 3190 |  | 0.82 | 230 | 230 | 230 | 10.8 | 10.5 | 9.4 | 3320 | 0.72 | 228.6 |  | 2.4 |  | 525.9 |  | 115 |  | 8710.9 | [22 empty] | 250.04 | 0.36 | 199.61 | 0.09 | 117.05 | 0.11 | 82.56 | 0.08 | [16 empty] | 59.25 | 0.06 | 78.81 | 0.06 | 33.06 | 0.05 | 45.75 | 0.09 | [8 empty] | 239.14 | 0.36 | 100.75 | 0.12 | 113.82 | 0.11 | 13.07 | 0.04 | 236.93 | 0.35 | 113.15 | 0.11 | 11.78 | 0.06 | [24 empty] | 272.85 | 0.42 | 197.54 | 0.09 | 123.51 | 0.12 | 74.03 | 0.06 | [20 empty] | 74.55 | 0.07 | 74.67 | 0.04 | 43.81 | 0.05 | 30.87 | 0.08 | [12 empty] | 261.77 | 0.44 | 102.67 | 0.12 | 120.42 | 0.13 | 17.76 | 0.04 | 258.67 | 0.43 | 119.54 | 0.12 | 16.17 | 0.06 | [12 empty] | 59.38 | 0.04 | 58.82 | 0.05 | 57.98 | 0.05 | 57.66 | 0.05 | 58.39 | 0.05 |  |  | 100.79 | 0.12 |  |  | 74.36 | 0.05 | 78.03 | 0.03 | 192.17 | 0.09 |  |  | 103.35 | 0.1 | 77.83 | 0.05 | 79.44 | 0.05 |  |  | 104.79 | 0.09 | [28 empty] | 59.22 | 0.04 | [8 empty] | 103.38 | 0.12 | 101.38 | 0.09 | [8 empty] | 75.93 | 0.04 | 101.8 | 0.1 | 73.87 | 0.05 | 103.53 | 0.1 | [10 empty] | 198.96 | 0.09 | 95.18 | 0.21 | 95.76 | 0.16 | 74.97 | 0.07 | 75.03 | 0.07 | 74.88 | 0.08 | 74.97 | 0.08 | 74.98 | 0.07 | 75.04 | 0.07 |  |  | 77.66 | 0.09 | 77.05 | 0.1 | 75.13 | 0.08 | 88.64 | 0.15 | 75.83 | 0.07 | 76.24 | 0.12 | 75.47 | 0.08 | 75.74 | 0.1 | 78.87 | 0.14 | 77.43 | 0.16 | 78.34 | 0.1 | 80.37 | 0.1 | 75.2 | 0.09 | 76.66 | 0.12 | 75.43 | 0.07 | 83.1 | 0.12 | [78 empty] | 94.12 | 0.16 | [8 empty] | 59.18 | 0.04 | 58.95 | 0.04 | C8-55-CE3 | 75.025 | 0.042 | 62.006 | 0.02 | 58.784 | 0.017 | 55.249 | 0.007 | 94.979 | 0.033 | 75.002 | 0.013 | 2520.2 | 3.9 | 2461.9 | 3.8 | 1.159 | 0.002 | -0.427 | 0.003 | 0.151 | 0.005 | 0.8838 | 0.0027 | 29.257 | 0.001 | 8750 | 20 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5127 | 11510.6171 | 335.2115 | 23.0358 | 98.0286 | 11412.5885 | 0.0088225 | 27.7024 | 57.2713 | 14.0994 | 13.1367 | 0.013928 | 38.1594 | 0.0087787 | 27.6126 | 0.0084442 | 23.2878 | 75.1965 | 62.1338 | 22.9191 | 55059.129 | 49519.3394 | 7190 | 0.44569 | 50878.9259 | 45339.1364 | 5.8147 | 0.21957 | -4.7833 | -17.9252 | 52.228 | 55059.129 | 49780.9769 | 4244.261 | 1033.891 | 55059.129 | 100%
3 | C8-R110-110C2-95-CE | 75N0174 | C8-R110-110C2-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/30/2015 | 1:55:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 1.7 | 28.4 | 0 | 46352 | 103 | 46315 | 213 | 6185 | 160 | 52542 | 140 | 5.934 | 900 | [38 empty] | 110% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--4.5 turns, 7" AK59 pulley (865 rpm), duct removed from supply sampling box--(without code tester), record total static, 5 minute snapshot | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.99 | 0.048 | 61.998 | 0.03 | 95.007 | 0.017 | 75.007 | 0.024 | 74.69 | 0.07 | 58.15 | 0.04 | 62.3 | 0.03 | 0.088 | 0.004 | 0.8858 | 0.0027 | 46352 | 103 | 6185 | 160 | 5.934 | 0.02 | [6 empty] | 230.1 | 1.3 | 229.9 | 1.3 | 230 | 1.3 | 28.4 | 0.1 | 25.8 | 0.1 | 29.5 | 0.1 | 6524 | 49.5 | 3676.1 | 65.4 | 2331.3 | 37.1 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.3 |  | 0.64 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.2 |  | 9.5 |  | 3220 |  | 0.8 | 230 | 230 | 230 | 11 | 10.7 | 9.5 | 3370 | 0.72 | 228.6 |  | 2.4 |  | 526.2 |  | 115 |  | 8791.2 | [22 empty] | 253.31 | 0.25 | 199.14 | 0.05 | 118.01 | 0.07 | 81.13 | 0.06 | [16 empty] | 60.48 | 0.05 | 78.42 | 0.05 | 34 | 0.04 | 44.42 | 0.05 | [8 empty] | 242.29 | 0.24 | 100.58 | 0.06 | 114.77 | 0.07 | 14.2 | 0.04 | 239.91 | 0.24 | 114.06 | 0.07 | 12.82 | 0.04 | [24 empty] | 278.31 | 0.23 | 196.09 | 0.06 | 125.01 | 0.06 | 71.08 | 0.03 | [20 empty] | 76.45 | 0.04 | 73 | 0.04 | 45.06 | 0.03 | 27.95 | 0.04 | [12 empty] | 266.89 | 0.26 | 102.49 | 0.05 | 121.87 | 0.07 | 19.37 | 0.04 | 263.68 | 0.26 | 120.97 | 0.07 | 17.78 | 0.05 | [12 empty] | 59.03 | 0.04 | 58.52 | 0.05 | 57.74 | 0.05 | 57.34 | 0.05 | 58.11 | 0.05 |  |  | 100.64 | 0.07 |  |  | 74.09 | 0.04 | 77.83 | 0.05 | 190.86 | 0.05 |  |  | 103.3 | 0.07 | 76.5 | 0.04 | 78.36 | 0.14 |  |  | 104.83 | 0.06 | [28 empty] | 58.87 | 0.04 | [8 empty] | 103.18 | 0.06 | 101.24 | 0.07 | [8 empty] | 75.67 | 0.04 | 101.67 | 0.07 | 72.25 | 0.04 | 103.47 | 0.06 | [10 empty] | 198.57 | 0.06 | 95.28 | 0.14 | 95.76 | 0.13 | 75.06 | 0.09 | 75.11 | 0.09 | 74.97 | 0.09 | 75.06 | 0.09 | 75.07 | 0.09 | 75.13 | 0.08 |  |  | 77.74 | 0.08 | 77.12 | 0.11 | 75.23 | 0.1 | 88.58 | 0.15 | 75.87 | 0.08 | 76.26 | 0.11 | 75.52 | 0.1 | 75.8 | 0.1 | 78.89 | 0.14 | 77.45 | 0.12 | 78.39 | 0.08 | 80.42 | 0.1 | 75.23 | 0.09 | 76.72 | 0.1 | 75.49 | 0.09 | 83.24 | 0.11 | [78 empty] | 94.25 | 0.1 | [8 empty] | 58.89 | 0.04 | 58.64 | 0.04 | C8-55-CE3 | 74.99 | 0.048 | 61.998 | 0.03 | 58.43 | 0.02 | 55.055 | 0.016 | 95.007 | 0.017 | 75.007 | 0.024 | 2520.9 | 3.9 | 2467.2 | 3.7 | 1.156 | 0.002 | -0.431 | 0.003 | 0.088 | 0.004 | 0.8858 | 0.0027 | 29.297 | 0.005 | 8855 | 19 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5114 | 11521.8749 | 335.0636 | 23.144 | 98.4842 | 11423.3907 | 0.0088256 | 27.6976 | 56.9186 | 14.1001 | 13.1276 | 0.013925 | 38.1638 | 0.0087817 | 27.6073 | 0.0084159 | 23.1708 | 75.1627 | 62.1264 | 22.8024 | 56401.4694 | 50449.5406 | 7295 | 0.44144 | 52220.7616 | 46268.8328 | 5.8973 | 0.20773 | -4.8952 | -18.2441 | 52.135 | 56401.4694 | 51117.273 | 4244.555 | 1039.6415 | 56401.4694 | 100%
3 | C8-R120-95-CE | 75N0175 | C8-R120-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/30/2015 | 2:57:39 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 1 | 28.8 | 0 | 47532 | 124 | 47544 | 262 | 7360 | 193 | 54899 | 195 | 6.069 | 900 | [38 empty] | 120% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of--run C8-R120-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.881 | 0.049 | 62.006 | 0.038 | 95.013 | 0.019 | 75.006 | 0.018 | 74.56 | 0.1 | 57.36 | 0.04 | 61.83 | 0.04 | 0.061 | 0.004 | 0.8618 | 0.0026 | 47532 | 124 | 7360 | 193 | 6.069 | 0.021 | [6 empty] | 230.1 | 0.5 | 229.7 | 0.5 | 230 | 0.5 | 28.8 | 0.1 | 26.3 | 0 | 29.9 | 0.1 | 6615.3 | 20.9 | 3713.6 | 23.9 | 2430.1 | 17.1 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.2 |  | 6.3 |  | 0.61 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.3 |  | 9.8 |  | 3320 |  | 0.82 | 230 | 230 | 230 | 11.2 | 11 | 9.9 | 3520 | 0.23 | 228.4 |  | 2.4 |  | 524.8 |  | 115 |  | 9039.8 | [22 empty] | 260.52 | 0.31 | 198.24 | 0.06 | 120.08 | 0.09 | 78.16 | 0.07 | [16 empty] | 63.13 | 0.06 | 77.67 | 0.05 | 35.95 | 0.04 | 41.72 | 0.05 | [8 empty] | 249.17 | 0.31 | 100.4 | 0.07 | 116.81 | 0.09 | 16.4 | 0.06 | 246.59 | 0.3 | 116.05 | 0.09 | 14.93 | 0.07 | [24 empty] | 288.57 | 0.34 | 189 | 0.1 | 127.75 | 0.09 | 61.25 | 0.09 | [20 empty] | 78.84 | 0.07 | 64.21 | 0.15 | 46.59 | 0.04 | 17.62 | 0.15 | [12 empty] | 276.67 | 0.34 | 102.25 | 0.08 | 124.56 | 0.09 | 22.31 | 0.05 | 273.13 | 0.35 | 123.6 | 0.09 | 20.47 | 0 | [12 empty] | 58.1 | 0.05 | 57.26 | 0.05 | 57.35 | 0.05 | 56.99 | 0.06 | 57.48 | 0.05 |  |  | 100.52 | 0.07 |  |  | 73.39 | 0.07 | 77.15 | 0.05 | 184.24 | 0.08 |  |  | 103.14 | 0.08 | 67.43 | 0.18 | 71.16 | 0.16 |  |  | 104.81 | 0.06 | [28 empty] | 58.01 | 0.04 | [10 empty] | 101.13 | 0.08 | [8 empty] | 74.95 | 0.07 | 101.61 | 0.07 | 62.48 | 0.29 | 103.34 | 0.09 | [10 empty] | 197.73 | 0.06 | 95.29 | 0.19 | 95.83 | 0.13 | 74.99 | 0.11 | 75.06 | 0.1 | 74.93 | 0.11 | 75.01 | 0.11 | 75.02 | 0.11 | 75.06 | 0.1 |  |  | 77.78 | 0.12 | 77.13 | 0.12 | 75.23 | 0.11 | 88.64 | 0.19 | 75.84 | 0.1 | 76.25 | 0.14 | 75.51 | 0.12 | 75.81 | 0.12 | 78.94 | 0.16 | 77.46 | 0.17 | 78.41 | 0.11 | 80.54 | 0.11 | 75.21 | 0.12 | 76.67 | 0.16 | 75.43 | 0.12 | 83.37 | 0.15 | [78 empty] | 94.14 | 0.13 | [8 empty] | 57.87 | 0.05 | 57.99 | 0.05 | C8-55-CE3 | 74.881 | 0.049 | 62.006 | 0.038 | 57.691 | 0.024 | 54.622 | 0.025 | 95.013 | 0.019 | 75.006 | 0.018 | 2484.4 | 3.7 | 2435.2 | 3.6 | 1.154 | 0.002 | -0.421 | 0.002 | 0.061 | 0.004 | 0.8618 | 0.0026 | 29.313 | 0.002 | 9046 | 16 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5375 | 11371.7681 | 330.1456 | 22.874 | 97.3346 | 11274.4335 | 0.0088564 | 27.705 | 56.1535 | 14.1003 | 13.1083 | 0.013923 | 38.1627 | 0.0088127 | 27.6147 | 0.0083422 | 22.9106 | 75.0549 | 62.1345 | 22.5359 | 58781.6238 | 51586.256 | 7486 | 0.43465 | 54584.1309 | 47388.763 | 6.0341 | 0.18475 | -5.1691 | -18.9014 | 51.87 | 58781.6238 | 53493.9163 | 4261.0245 | 1026.6831 | 58781.6238 | 100%
3 | C8-R120-E0C30-95CE | 75N0176 | C8-R120-E0C30-95CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 0 | CUST 3 | 6/30/2015 | 6:12:16 | 10 Ton | 0:15:00 | 75/62 - 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 30.6 | 0 | 48264 | 83 | 48059 | 159 | 6150 | 156 | 54420 | 149 | 5.522 | 900 | [38 empty] | Baseline 120% factory charge, 0% evaporator and 30% condenser blockage,--economizer closed (2.0V), 120% factory charge (CK1 9.12 lbs, CK2 9.72 lbs),--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflo | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.024 | 0.021 | 62.003 | 0.029 | 95.003 | 0.032 | 75.009 | 0.023 | 74.59 | 0.06 | 57.21 | 0.03 | 61.31 | 0.02 | 0.08 | 0.005 | 0.8636 | 0.0026 | 48264 | 83 | 6150 | 156 | 5.522 | 0.019 | [6 empty] | 229.9 | 1.5 | 229.6 | 1.5 | 230.1 | 1.5 | 30.6 | 0.1 | 28 | 0.1 | 31.8 | 0.1 | 7027.5 | 54.5 | 3800.7 | 72.4 | 2826.9 | 42.3 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 11.4 |  | 11.1 |  | 10.7 |  | 3710 |  | 0.84 | 230 | 230 | 230 | 12.2 | 11.9 | 10.7 | 3870 | 0.74 | 228.3 |  | 2.4 |  | 533.6 |  | 115 |  | 9778.6 | [22 empty] | 293.39 | 0.37 | 206.05 | 0.07 | 129.01 | 0.1 | 77.03 | 0.07 | [16 empty] | 68.62 | 0.07 | 75.76 | 0.04 | 39.82 | 0.05 | 35.94 | 0.07 | [8 empty] | 281.53 | 0.37 | 108.12 | 0.08 | 125.87 | 0.1 | 17.75 | 0.04 | 278.71 | 0.37 | 125.11 | 0.1 | 16.38 | 0.07 | [24 empty] | 320.78 | 0.35 | 182.64 | 0.07 | 135.93 | 0.09 | 46.71 | 0.1 | [20 empty] | 80.67 | 0.05 | 50.33 | 0.05 | 47.71 | 0.03 | 2.61 | 0.05 | [12 empty] | 308.49 | 0.34 | 109.49 | 0.08 | 132.88 | 0.09 | 23.4 | 0.03 | 304.54 | 0.34 | 131.88 | 0.09 | 22.24 | 0.04 | [12 empty] | 58.02 | 0.03 | 57.15 | 0.03 | 57.1 | 0.03 | 56.56 | 0.04 | 57.32 | 0.03 |  |  | 108.51 | 0.1 |  |  | 71.61 | 0.04 | 74.67 | 0.04 | 178.28 | 0.07 |  |  | 109.72 | 0.08 | 54.36 | 0.06 | 56.56 | 0.06 |  |  | 110.6 | 0.08 | [28 empty] | 57.94 | 0.03 | [8 empty] | 109.64 | 0.08 | 108.73 | 0.09 | [8 empty] | 73.85 | 0.03 | 108.41 | 0.09 | 52.45 | 0.06 | 110.19 | 0.09 | [10 empty] | 204.53 | 0.08 | 94.7 | 0.13 | 94.73 | 0.07 | 74.95 | 0.07 | 75.08 | 0.06 | 74.8 | 0.07 | 74.89 | 0.07 | 74.92 | 0.06 | 75.03 | 0.06 |  |  | 75.82 | 0.1 | 76.74 | 0.1 | 75.08 | 0.06 | 84.59 | 0.2 | 76.04 | 0.06 | 75.93 | 0.06 | 75.58 | 0.06 | 76.18 | 0.09 | 76.83 | 0.11 | 76.62 | 0.06 | 76.91 | 0.12 | 81.92 | 0.08 | 75.3 | 0.06 | 75.89 | 0.06 | 75.54 | 0.06 | 83.47 | 0.14 | [78 empty] | 94.54 | 0.11 | [8 empty] | 57.77 | 0.03 | 57.89 | 0.03 | C8-55-CE3 | 75.024 | 0.021 | 62.003 | 0.029 | 57.568 | 0.01 | 54.704 | 0.017 | 95.003 | 0.032 | 75.009 | 0.023 | 2488.2 | 3.8 | 2436.5 | 3.8 | 1.136 | 0.002 | -0.423 | 0.003 | 0.08 | 0.005 | 0.8636 | 0.0026 | 29.259 | 0.001 | 9855 | 21 | 1550 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5286 | 11391.3559 | 325.1695 | 22.9281 | 97.5662 | 11293.7896 | 0.0088211 | 27.7009 | 56.0394 | 14.1 | 13.1057 | 0.013928 | 38.1658 | 0.0087769 | 27.6105 | 0.0084181 | 22.9631 | 75.1967 | 62.1316 | 22.5905 | 58213.5692 | 52374.6985 | 8305 | 0.48691 | 54033.2228 | 48194.3521 | 5.4828 | 0.16588 | -5.1103 | -19.1573 | 52.2297 | 58213.5692 | 52939.5212 | 4244.2052 | 1029.8428 | 58213.5692 | 100%
3 | C8-R120-E20C0-95CE | 75N0177 | C8-R120-E20C0-95CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/30/2015 | 4:17:59 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 1.7 | 28.6 | 0 | 45779 | 68 | 45413 | 137 | 8306 | 152 | 54093 | 190 | 6.046 | 901 | [38 empty] | Baseline 120% factory charge, 20% evaporator blockage, 0% condenser blockage,--economizer closed (2.0V), 120% factory charge (CK1 9.12 lbs, CK2 9.72 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.999 | 0.009 | 62.003 | 0.029 | 95.007 | 0.013 | 74.996 | 0.027 | 74.55 | 0.06 | 57.43 | 0.04 | 61.76 | 0.01 | 0.068 | 0.003 | 0.7917 | 0.0023 | 45779 | 68 | 8306 | 152 | 6.046 | 0.024 | [6 empty] | 230.1 | 1.3 | 229.8 | 1.3 | 230 | 1.3 | 28.6 | 0.1 | 26 | 0.1 | 29.7 | 0.1 | 6570.2 | 50.3 | 3705.4 | 64.3 | 2376.5 | 37.6 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.2 |  | 6.2 |  | 0.61 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.3 |  | 9.7 |  | 3300 |  | 0.81 | 230 | 230 | 230 | 11.2 | 10.9 | 9.8 | 3470 | 0.73 | 228.5 |  | 2.4 |  | 525.3 |  | 115 |  | 8900.3 | [22 empty] | 259.42 | 0.28 | 195.54 | 0.06 | 119.76 | 0.08 | 75.78 | 0.07 | [16 empty] | 62.14 | 0.06 | 74.14 | 0.05 | 35.21 | 0.05 | 38.93 | 0.06 | [8 empty] | 248.12 | 0.27 | 100.38 | 0.07 | 116.5 | 0.08 | 16.12 | 0.05 | 245.59 | 0.26 | 115.75 | 0.08 | 14.83 | 0.07 | [24 empty] | 285.4 | 0.3 | 180.63 | 0.1 | 126.91 | 0.08 | 53.72 | 0.1 | [20 empty] | 75.5 | 0.05 | 48.78 | 0.27 | 44.42 | 0.03 | 4.36 | 0.28 | [12 empty] | 273.71 | 0.3 | 102.09 | 0.07 | 123.75 | 0.08 | 21.66 | 0.03 | 270.26 | 0.3 | 122.8 | 0.08 | 20.47 | 0 | [12 empty] | 58.08 | 0.04 | 57.37 | 0.04 | 57.3 | 0.04 | 56.76 | 0.04 | 57.45 | 0.04 |  |  | 100.43 | 0.06 |  |  | 69.39 | 0.04 | 73.42 | 0.03 | 176.35 | 0.09 |  |  | 102.83 | 0.06 | 52.08 | 0.04 | 54.58 | 0.13 |  |  | 104.53 | 0.05 | [28 empty] | 58.02 | 0.04 | [10 empty] | 100.92 | 0.07 | [8 empty] | 71.12 | 0.03 | 101.4 | 0.06 | 50 | 0.06 | 103.05 | 0.06 | [10 empty] | 194.97 | 0.06 | 95.18 | 0.17 | 95.68 | 0.14 | 74.87 | 0.07 | 74.97 | 0.06 | 74.75 | 0.07 | 74.85 | 0.07 | 74.86 | 0.07 | 74.95 | 0.06 |  |  | 78.28 | 0.07 | 78.51 | 0.06 | 75.11 | 0.07 | 86.31 | 0.11 | 75.98 | 0.05 | 77.77 | 0.09 | 75.94 | 0.07 | 76.51 | 0.1 | 79.14 | 0.12 | 78.86 | 0.06 | 78.79 | 0.06 | 79.52 | 0.1 | 75.23 | 0.07 | 78.19 | 0.08 | 75.64 | 0.07 | 81.28 | 0.08 | [78 empty] | 94.13 | 0.09 | [8 empty] | 57.83 | 0.04 | 57.94 | 0.04 | C8-EB20-55-CE | 74.999 | 0.009 | 62.003 | 0.029 | 57.74 | 0.011 | 54.4 | 0.017 | 95.007 | 0.013 | 74.996 | 0.027 | 2382.8 | 3.5 | 2331.4 | 3.4 | 1.041 | 0.001 | -0.382 | 0.002 | 0.068 | 0.003 | 0.7917 | 0.0023 | 29.25 | 0.001 | 8946 | 21 | 1490 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.5706 | 10906.58 | 285.1232 | 26.4004 | 112.3418 | 10794.2381 | 0.0088357 | 27.7194 | 56.1694 | 14.1 | 13.1084 | 0.013916 | 38.1531 | 0.0087828 | 27.6108 | 0.0082042 | 22.7726 | 75.207 | 62.1575 | 22.3899 | 58126.2449 | 49832.2834 | 7456 | 0.43779 | 54014.0006 | 45720.039 | 6.0378 | 0.20463 | -5.3295 | -19.0375 | 51.2716 | 58126.2449 | 52768.466 | 4173.436 | 1184.3429 | 58126.2449 | 100%
3 | C8-R120-E20C30-95CE | 75N0178 | C8-R120-E20C30-95CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 0 | CUST 3 | 6/30/2015 | 5:20:09 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.5 | 30.3 | 0 | 46024 | 108 | 45734 | 159 | 7019 | 171 | 53049 | 133 | 5.467 | 901 | [38 empty] | Baseline 120% factory charge, 20% evaporator blockage, 30% condenser blockage,--economizer closed (2.0V), 120% factory charge (CK1 9.12 lbs, CK2 9.72 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.04 | 0.023 | 61.991 | 0.031 | 95.01 | 0.013 | 74.995 | 0.02 | 74.91 | 0.08 | 57.54 | 0.06 | 61.78 | 0.05 | 0.058 | 0.004 | 0.7817 | 0.0019 | 46024 | 108 | 7019 | 171 | 5.467 | 0.018 | [6 empty] | 230 | 1.4 | 229.6 | 1.4 | 230 | 1.4 | 30.3 | 0.1 | 27.7 | 0.1 | 31.4 | 0.1 | 6976.4 | 51.8 | 3771.7 | 69 | 2727.6 | 39.7 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.1 |  | 0.61 | 230 |  | 230 |  | 230 |  | 11.4 |  | 11.2 |  | 10.5 |  | 3680 |  | 0.84 | 230 | 230 | 230 | 12 | 11.7 | 10.5 | 3810 | 0.73 | 228.3 |  | 2.4 |  | 533.9 |  | 115 |  | 9638.9 | [22 empty] | 291.02 | 0.18 | 202.74 | 0.05 | 128.39 | 0.05 | 74.35 | 0.04 | [16 empty] | 67.21 | 0.04 | 71.62 | 0.06 | 38.84 | 0.03 | 32.78 | 0.07 | [8 empty] | 279.26 | 0.18 | 108.19 | 0.07 | 125.26 | 0.05 | 17.07 | 0.07 | 276.51 | 0.18 | 124.51 | 0.05 | 16.01 | 0.04 | [24 empty] | 315.54 | 0.15 | 175.34 | 0.09 | 134.64 | 0.04 | 40.7 | 0.09 | [20 empty] | 77.79 | 0.03 | 48.54 | 0.04 | 45.9 | 0.02 | 2.64 | 0.03 | [12 empty] | 303.64 | 0.16 | 109.36 | 0.07 | 131.65 | 0.04 | 22.3 | 0.05 | 299.8 | 0.16 | 130.67 | 0.04 | 21.14 | 0.35 | [12 empty] | 58.05 | 0.03 | 56.99 | 0.04 | 57.09 | 0.04 | 56.3 | 0.05 | 57.15 | 0.04 |  |  | 108.47 | 0.07 |  |  | 67.07 | 0.06 | 70.51 | 0.06 | 171.63 | 0.08 |  |  | 109.39 | 0.04 | 53.02 | 0.05 | 54.74 | 0.06 |  |  | 110.37 | 0.05 | [28 empty] | 57.82 | 0.03 | [8 empty] | 109.53 | 0.36 | 108.5 | 0.05 | [8 empty] | 69.41 | 0.06 | 108.51 | 0.05 | 51.36 | 0.07 | 109.8 | 0.04 | [10 empty] | 201.4 | 0.06 | 95.2 | 0.11 | 95.14 | 0.08 | 75.19 | 0.08 | 75.19 | 0.07 | 75.3 | 0.08 | 75.33 | 0.08 | 75.29 | 0.08 | 75.3 | 0.07 |  |  | 78.29 | 0.06 | 78.58 | 0.06 | 75.16 | 0.08 | 86.16 | 0.11 | 75.85 | 0.06 | 77.73 | 0.08 | 75.87 | 0.08 | 76.45 | 0.1 | 79.05 | 0.15 | 78.78 | 0.06 | 78.75 | 0.05 | 79.47 | 0.09 | 75.12 | 0.07 | 78.14 | 0.07 | 75.62 | 0.08 | 81.34 | 0.09 | [78 empty] | 94.21 | 0.1 | [8 empty] | 57.55 | 0.03 | 57.71 | 0.03 | C8-EB20-55-CE | 75.04 | 0.023 | 61.991 | 0.031 | 57.565 | 0.012 | 54.493 | 0.021 | 95.01 | 0.013 | 74.995 | 0.02 | 2367.6 | 2.9 | 2316.1 | 2.8 | 1.035 | 0.002 | -0.377 | 0.002 | 0.058 | 0.004 | 0.7817 | 0.0019 | 29.252 | 0.001 | 9704 | 19 | 1500 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.5979 | 10840.0653 | 281.6195 | 26.2271 | 111.604 | 10728.4614 | 0.0088183 | 27.7102 | 55.9671 | 14.1001 | 13.1047 | 0.013914 | 38.1521 | 0.0087652 | 27.6016 | 0.0082984 | 22.8323 | 75.2475 | 62.1455 | 22.4429 | 57097.2482 | 50160.2052 | 8204 | 0.4904 | 52938.9156 | 46001.8727 | 5.4554 | 0.17992 | -5.2672 | -19.2804 | 51.737 | 57097.2482 | 51698.8304 | 4220.9345 | 1177.4832 | 57097.2482 | 100%
3 | C8-R130-95-CE | 75N0179 | C8-R130-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/30/2015 | 8:09:15 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.6 | 29.2 | 0 | 48789 | 87 | 48255 | 175 | 7495 | 120 | 56291 | 178 | 6.074 | 900 | [38 empty] | 130% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns, 7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run C8-R130-95-CE-SPWCT-SS--7" AK49 pulley (865 rpm), adjust code tester speed to match total static o | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. Added CK1=12.2oz CK2= 13 oz | 74.982 | 0.013 | 62.002 | 0.017 | 94.956 | 0.03 | 75.003 | 0.015 | 74.52 | 0.06 | 57.11 | 0.02 | 61.33 | 0.02 | 0.139 | 0.004 | 0.8658 | 0.003 | 48789 | 87 | 7495 | 120 | 6.074 | 0.024 | [6 empty] | 229.8 | 1.2 | 229.7 | 1.2 | 230.2 | 1.2 | 29.2 | 0.1 | 26.7 | 0.1 | 30.6 | 0.1 | 6702.7 | 45.3 | 3765.1 | 61.2 | 2565.2 | 35.4 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.8 |  | 10.7 |  | 9.8 |  | 3410 |  | 0.83 | 230 | 230 | 230 | 11.5 | 11.3 | 10.1 | 3640 | 0.74 | 228.5 |  | 2.4 |  | 524.9 |  | 115 |  | 9259.9 | [22 empty] | 268.15 | 0.3 | 197.48 | 0.07 | 122.22 | 0.08 | 75.26 | 0.05 | [16 empty] | 65.65 | 0.05 | 76.92 | 0.04 | 37.75 | 0.04 | 39.16 | 0.05 | [8 empty] | 256.51 | 0.27 | 100.45 | 0.07 | 118.93 | 0.08 | 18.49 | 0.04 | 253.85 | 0.28 | 118.17 | 0.08 | 17.14 | 0.05 | [24 empty] | 299.83 | 0.31 | 174.33 | 0.08 | 130.68 | 0.08 | 43.65 | 0.11 | [20 empty] | 79.37 | 0.03 | 49.31 | 0.04 | 46.91 | 0.02 | 2.4 | 0.04 | [12 empty] | 287.4 | 0.3 | 101.88 | 0.08 | 127.44 | 0.08 | 25.56 | 0.03 | 283.51 | 0.3 | 126.4 | 0.08 | 23.93 | 0.04 | [12 empty] | 57.76 | 0.03 | 56.82 | 0.03 | 56.71 | 0.03 | 56.36 | 0.03 | 57.05 | 0.03 |  |  | 100.49 | 0.07 |  |  | 72.45 | 0.03 | 76.15 | 0.03 | 170.42 | 0.07 |  |  | 102.5 | 0.07 | 53.88 | 0.05 | 56.14 | 0.06 |  |  | 104.42 | 0.06 | [28 empty] | 57.59 | 0.03 | [8 empty] | 102.48 | 0.08 | 101.03 | 0.08 | [8 empty] | 74.09 | 0.03 | 101.34 | 0.07 | 50.93 | 0.05 | 102.77 | 0.07 | [10 empty] | 196.83 | 0.07 | 94.92 | 0.16 | 95.81 | 0.14 | 74.74 | 0.07 | 74.87 | 0.06 | 74.58 | 0.06 | 74.68 | 0.06 | 74.7 | 0.07 | 74.82 | 0.06 |  |  | 75.42 | 0.09 | 76.47 | 0.09 | 74.8 | 0.06 | 84.4 | 0.19 | 75.85 | 0.06 | 75.78 | 0.07 | 75.38 | 0.07 | 75.97 | 0.09 | 76.68 | 0.1 | 76.46 | 0.07 | 76.63 | 0.11 | 81.75 | 0.11 | 75.11 | 0.06 | 75.68 | 0.06 | 75.34 | 0.07 | 83.36 | 0.14 | [78 empty] | 94.03 | 0.12 | [8 empty] | 57.35 | 0.03 | 57.52 | 0.02 | C8-55-CE3 | 74.982 | 0.013 | 62.002 | 0.017 | 57.381 | 0.008 | 54.439 | 0.009 | 94.956 | 0.03 | 75.003 | 0.015 | 2489.8 | 4.4 | 2441.5 | 4.3 | 1.139 | 0.002 | -0.412 | 0.003 | 0.139 | 0.004 | 0.8658 | 0.003 | 29.29 | 0.001 | 9268 | 19 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.55 | 11403.5289 | 326.6973 | 22.6271 | 96.2932 | 11307.2358 | 0.0088297 | 27.6994 | 55.831 | 14.0989 | 13.1002 | 0.013934 | 38.1608 | 0.0087862 | 27.6103 | 0.0083111 | 22.8013 | 75.1522 | 62.1288 | 22.4236 | 60163.4166 | 52879.2872 | 7698 | 0.4367 | 55920.0245 | 48635.8951 | 6.0337 | 0.17273 | -5.2759 | -19.3212 | 51.7968 | 60163.4166 | 54840.1039 | 4307.3744 | 1015.9383 | 60163.4166 | 100%
3 | C8-R140-95-CE | 75N0180 | C8-R140-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/30/2015 | 9:52:30 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1.8 | 29.6 | 0 | 49643 | 85 | 49063 | 172 | 7177 | 121 | 56826 | 132 | 6.016 | 900 | [38 empty] | 140% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run--C8-R140-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.Added CK1= 12.2 oz and CK2= 13 o | 75.04 | 0.019 | 62.002 | 0.018 | 94.998 | 0.019 | 75.001 | 0.019 | 74.58 | 0.07 | 56.83 | 0.02 | 61.22 | 0.03 | 0.139 | 0.004 | 0.8611 | 0.0025 | 49643 | 85 | 7177 | 121 | 6.016 | 0.02 | [6 empty] | 229.7 | 1.5 | 229.7 | 1.5 | 230.2 | 1.5 | 29.6 | 0.1 | 27 | 0.1 | 31.1 | 0.1 | 6792.6 | 55.3 | 3791.4 | 75.5 | 2653.6 | 42.3 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.1 |  | 0.62 | 230 |  | 230 |  | 230 |  | 11 |  | 10.9 |  | 10.1 |  | 3510 |  | 0.83 | 230 | 230 | 230 | 11.8 | 11.7 | 10.2 | 3735 | 0.74 | 228.4 |  | 2.4 |  | 524.8 |  | 115 |  | 9454.8 | [22 empty] | 276.58 | 0.25 | 195.77 | 0.04 | 124.54 | 0.07 | 71.23 | 0.05 | [16 empty] | 68.26 | 0.04 | 74.85 | 0.05 | 39.59 | 0.03 | 35.27 | 0.06 | [8 empty] | 264.54 | 0.23 | 100.37 | 0.06 | 121.21 | 0.07 | 20.84 | 0.04 | 261.7 | 0.24 | 120.41 | 0.07 | 19.6 | 0.06 | [24 empty] | 306.98 | 0.25 | 161.83 | 0.08 | 132.51 | 0.06 | 29.33 | 0.09 | [20 empty] | 80.13 | 0.03 | 49.37 | 0.05 | 47.39 | 0.02 | 1.98 | 0.05 | [12 empty] | 294.33 | 0.24 | 101.31 | 0.06 | 129.26 | 0.06 | 27.96 | 0.04 | 290.2 | 0.23 | 128.18 | 0.06 | 26.28 | 0.05 | [12 empty] | 57.48 | 0.03 | 56.44 | 0.04 | 56.48 | 0.04 | 55.92 | 0.04 | 56.68 | 0.04 |  |  | 100.44 | 0.05 |  |  | 70.14 | 0.05 | 74.02 | 0.04 | 158.73 | 0.06 |  |  | 102 | 0.06 | 54.27 | 0.03 | 56.31 | 0.05 |  |  | 104.25 | 0.05 | [28 empty] | 57.3 | 0.03 | [8 empty] | 101.9 | 0.05 | 100.81 | 0.05 | [8 empty] | 71.91 | 0.04 | 101.27 | 0.06 | 50.86 | 0.04 | 102.2 | 0.06 | [10 empty] | 195.2 | 0.04 | 95.12 | 0.14 | 95.73 | 0.13 | 74.82 | 0.07 | 74.9 | 0.07 | 74.67 | 0.07 | 74.77 | 0.07 | 74.8 | 0.07 | 74.9 | 0.07 |  |  | 75.46 | 0.08 | 76.53 | 0.11 | 74.82 | 0.07 | 84.47 | 0.15 | 75.87 | 0.07 | 75.8 | 0.08 | 75.41 | 0.08 | 75.95 | 0.1 | 76.66 | 0.11 | 76.46 | 0.07 | 76.59 | 0.09 | 81.76 | 0.1 | 75.15 | 0.07 | 75.69 | 0.07 | 75.37 | 0.07 | 83.4 | 0.14 | [78 empty] | 94.08 | 0.1 | [8 empty] | 57.07 | 0.03 | 57.23 | 0.03 | C8-55-CE3 | 75.04 | 0.019 | 62.002 | 0.018 | 57.081 | 0.01 | 54.339 | 0.008 | 94.998 | 0.019 | 75.001 | 0.019 | 2482.5 | 3.7 | 2435.1 | 3.6 | 1.138 | 0.002 | -0.423 | 0.002 | 0.139 | 0.004 | 0.8611 | 0.0025 | 29.296 | 0.001 | 9447 | 21 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5551 | 11376.6004 | 325.5548 | 22.928 | 97.5668 | 11279.0335 | 0.0088167 | 27.7 | 55.5259 | 14.0999 | 13.0927 | 0.013922 | 38.1581 | 0.0087725 | 27.6095 | 0.0083251 | 22.7434 | 75.2128 | 62.1307 | 22.3644 | 60700.1646 | 53752.6952 | 7877 | 0.4429 | 56452.8733 | 49505.4038 | 5.9757 | 0.15555 | -5.3355 | -19.6869 | 51.8994 | 60700.1646 | 55359.5257 | 4311.4424 | 1029.1965 | 60700.1646 | 100%
3 | C8-R60-95-CE | 75N0181 | C8-R60-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/29/2015 | 23:05:34 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.8 | 25.7 | 0 | 21026 | 29 | 20675 | 62 | -5560 | 89 | 15461 | 87 | 1.997 | 899 | [38 empty] | 60% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run--C8-R60-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.993 | 0.011 | 62.009 | 0.013 | 94.99 | 0.011 | 75.003 | 0.024 | 74.46 | 0.02 | 66.9 | 0.02 | 69.12 | 0.01 | 0.084 | 0.004 | 0.8781 | 0.0026 | 21026 | 29 | -5560 | 89 | 1.997 | 0.013 | [6 empty] | 230 | 1.4 | 229.8 | 1.4 | 230 | 1.4 | 25.7 | 0.1 | 23.5 | 0.1 | 27.1 | 0.1 | 5886.4 | 55.5 | 3615.8 | 77.4 | 1855.3 | 39.8 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.3 |  | 6.2 |  | 0.61 | 230 |  | 230 |  | 230 |  | 9.1 |  | 9.1 |  | 8.4 |  | 2700 |  | 0.76 | 230 | 230 | 230 | 9.6 | 9.4 | 9.4 | 2830 | 0.69 | 228.6 |  | 2.4 |  | 528.3 |  | 115 |  | 7703.3 | [22 empty] | 202 | 0.13 | 259.69 | 0.06 | 101.97 | 0.04 | 157.72 | 0.05 | [16 empty] | 23.31 | 0.03 | 83.61 | 0.02 | -1.31 | 0.04 | 84.92 | 0.04 | [8 empty] | 195.11 | 0.12 | 99.6 | 0.04 | 99.61 | 0.04 | 0.01 | 0.02 | 193.8 | 0.14 | 99.15 | 0.05 | 0.63 | 0.03 | [24 empty] | 228.4 | 0.17 | 219.7 | 0.04 | 110.53 | 0.05 | 109.16 | 0.04 | [20 empty] | 48.71 | 0.04 | 82.13 | 0.03 | 24.62 | 0.04 | 57.5 | 0.04 | [12 empty] | 220.16 | 0.16 | 104.86 | 0.05 | 107.93 | 0.05 | 3.07 | 0.02 | 217.76 | 0.18 | 107.17 | 0.06 | 1.43 | 0.03 | [12 empty] | 67.9 | 0.03 | 67.49 | 0.03 | 66.79 | 0.04 | 66.46 | 0.04 | 67.19 | 0.03 |  |  | 99.52 | 0.04 |  |  | 77.97 | 0.02 | 82.5 | 0.02 | 212.67 | 0.05 |  |  | 104.81 | 0.05 | 82.3 | 0.02 | 86.54 | 0.04 |  |  | 103.95 | 0.04 | [28 empty] | 67.85 | 0.03 | [8 empty] | 105.74 | 0.04 | 99.79 | 0.03 | [8 empty] | 79.13 | 0.03 | 99.64 | 0.04 | 79.89 | 0.03 | 105.4 | 0.05 | [10 empty] | 258.54 | 0.07 | 95.08 | 0.08 | 95.25 | 0.06 | 74.88 | 0.05 | 74.93 | 0.04 | 74.82 | 0.06 | 74.9 | 0.06 | 74.92 | 0.06 | 74.97 | 0.05 |  |  | 77.68 | 0.07 | 77.12 | 0.08 | 75.12 | 0.04 | 89.14 | 0.16 | 75.7 | 0.04 | 76.05 | 0.07 | 75.34 | 0.04 | 75.67 | 0.07 | 78.89 | 0.14 | 77.25 | 0.12 | 78.27 | 0.06 | 80.34 | 0.06 | 75.07 | 0.03 | 76.52 | 0.09 | 75.31 | 0.03 | 82.94 | 0.13 | [78 empty] | 94.54 | 0.09 | [8 empty] | 67.69 | 0.03 | 67.63 | 0.03 | C8-55-CE3 | 74.993 | 0.011 | 62.009 | 0.013 | 67.3 | 0.007 | 60.088 | 0.008 | 94.99 | 0.011 | 75.003 | 0.024 | 2529.3 | 3.7 | 2434.2 | 3.6 | 1.142 | 0.001 | -0.419 | 0.003 | 0.084 | 0.004 | 0.8781 | 0.0026 | 29.234 | 0 | 7742 | 21 | 1530 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5061 | 11359.2872 | 326.5784 | 22.8192 | 97.105 | 11262.1822 | 0.0088321 | 27.7054 | 65.7939 | 14.0997 | 13.3598 | 0.013926 | 38.1602 | 0.0087882 | 27.6152 | 0.0093638 | 26.3668 | 75.1655 | 62.1372 | 25.9991 | 19382.5075 | 25549.3088 | 6212 | 1.0939 | 15275.2296 | 21442.0309 | 1.973 | 0.49023 | -1.7063 | -9.3717 | 56.7816 | 19382.5075 | 14181.3339 | 4177.2042 | 1023.9694 | 19382.5075 | 100%
3 | C8-R70-95-CE | 75N0182 | C8-R70-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/29/2015 | 21:39:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 1.8 | 26.3 | 0 | 29440 | 64 | 29158 | 134 | -1806 | 141 | 27633 | 116 | 3.459 | 900 | [38 empty] | 70% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--4.5 turns, 7" AK49 pulley (865 rpm), adjust code tester speed to match total--static of run C8-R70-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.034 | 0.021 | 62 | 0.034 | 95.011 | 0.012 | 75.002 | 0.021 | 74.73 | 0.04 | 64.16 | 0.06 | 66.84 | 0.02 | 0.078 | 0.004 | 0.8804 | 0.002 | 29440 | 64 | -1806 | 141 | 3.459 | 0.017 | [6 empty] | 230.1 | 1.4 | 229.9 | 1.4 | 230.1 | 1.4 | 26.3 | 0.1 | 24 | 0.1 | 27.6 | 0.1 | 6033.1 | 56.2 | 3630.6 | 74.6 | 1954.9 | 41.7 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 9.4 |  | 9.2 |  | 8.7 |  | 2830 |  | 0.79 | 230 | 230 | 230 | 9.9 | 9.7 | 8.7 | 2960 | 0.69 | 228.7 |  | 2.4 |  | 527.7 |  | 115 |  | 7972.7 | [22 empty] | 214.52 | 0.19 | 232.45 | 0.07 | 106.12 | 0.06 | 126.33 | 0.08 | [16 empty] | 33.15 | 0.04 | 82.18 | 0.04 | 9.96 | 0.04 | 72.21 | 0.05 | [8 empty] | 206.33 | 0.18 | 102.46 | 0.09 | 103.42 | 0.06 | 0.97 | 0.06 | 205.38 | 0.25 | 103.11 | 0.08 | 0.75 | 0.06 | [24 empty] | 240.5 | 0.23 | 208.96 | 0.04 | 114.23 | 0.07 | 94.73 | 0.06 | [20 empty] | 58.43 | 0.05 | 80.79 | 0.02 | 32.43 | 0.04 | 48.36 | 0.05 | [12 empty] | 230.76 | 0.21 | 105.68 | 0.09 | 111.26 | 0.07 | 5.59 | 0.05 | 228.53 | 0.21 | 110.57 | 0.06 | 3.4 | 0.06 | [12 empty] | 65.12 | 0.03 | 64.6 | 0.06 | 63.8 | 0.05 | 63.39 | 0.05 | 64.06 | 0.05 |  |  | 102.28 | 0.08 |  |  | 76.99 | 0.05 | 81.32 | 0.03 | 202.74 | 0.07 |  |  | 107.24 | 0.06 | 82.14 | 0.06 | 85.58 | 0.05 |  |  | 106.51 | 0.06 | [28 empty] | 65.08 | 0.04 | [8 empty] | 107.18 | 0.08 | 102.36 | 0.05 | [8 empty] | 78.27 | 0.05 | 102.81 | 0.06 | 79.44 | 0.07 | 107.56 | 0.06 | [10 empty] | 232.67 | 0.08 | 95.45 | 0.13 | 95.69 | 0.09 | 75.15 | 0.05 | 75.12 | 0.06 | 75.19 | 0.06 | 75.23 | 0.05 | 75.22 | 0.05 | 75.24 | 0.05 |  |  | 77.28 | 0.45 | 76.95 | 0.22 | 75.23 | 0.07 | 88.96 | 0.25 | 75.84 | 0.05 | 76.07 | 0.13 | 75.48 | 0.05 | 75.79 | 0.11 | 78.87 | 0.15 | 77.12 | 0.22 | 77.95 | 0.42 | 80.59 | 0.26 | 75.15 | 0.05 | 76.37 | 0.24 | 75.41 | 0.06 | 83.06 | 0.18 | [78 empty] | 94.43 | 0.1 | [8 empty] | 64.89 | 0.05 | 64.82 | 0.04 | C8-55-CE3 | 75.034 | 0.021 | 62 | 0.034 | 64.363 | 0.013 | 58.467 | 0.026 | 95.011 | 0.012 | 75.002 | 0.021 | 2527.6 | 2.9 | 2443.2 | 2.9 | 1.148 | 0.001 | -0.422 | 0.003 | 0.078 | 0.004 | 0.8804 | 0.002 | 29.221 | 0.001 | 7988 | 20 | 1540 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5073 | 11417.4366 | 329.508 | 22.9011 | 97.4504 | 11319.9862 | 0.0088165 | 27.6982 | 62.8557 | 14.1002 | 13.2828 | 0.01392 | 38.1589 | 0.0087726 | 27.6081 | 0.0090446 | 25.3019 | 75.2061 | 62.1281 | 24.9341 | 31558.7096 | 33842.2744 | 6448 | 0.69734 | 27427.3006 | 29710.8654 | 3.4336 | 0.39368 | -2.7641 | -12.3504 | 54.8367 | 31558.7096 | 26331.2311 | 4199.3072 | 1028.1714 | 31558.7096 | 100%
3 | C8-R80-95-CE | 75N0183 | C8-R80-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/29/2015 | 16:42:34 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.7 | 26.9 | 0 | 35718 | 76 | 35340 | 144 | 1319 | 131 | 37038 | 116 | 4.505 | 900 | [38 empty] | 80% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run--C8-R80-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Removed: CK1:12.2 oz CK2: 13 o | 75.038 | 0.026 | 62 | 0.027 | 95.004 | 0.007 | 75.001 | 0.01 | 74.61 | 0.06 | 61.85 | 0.05 | 65.17 | 0.02 | 0.162 | 0.006 | 0.8792 | 0.0031 | 35718 | 76 | 1319 | 131 | 4.505 | 0.017 | [6 empty] | 229.9 | 1.4 | 230 | 1.4 | 230.1 | 1.4 | 26.9 | 0.1 | 24.3 | 0.1 | 28.3 | 0.1 | 6161 | 53.8 | 3645.4 | 70.9 | 2061 | 39.9 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.1 |  | 6.3 |  | 0.63 | 230 |  | 230 |  | 230 |  | 9.7 |  | 9.6 |  | 8.8 |  | 2950 |  | 0.78 | 230 | 230 | 230 | 10.2 | 10 | 8.8 | 3060 | 0.7 | 228.7 |  | 2.4 |  | 527 |  | 115 |  | 8212 | [22 empty] | 226.3 | 0.18 | 216.62 | 0.04 | 109.87 | 0.06 | 106.75 | 0.08 | [16 empty] | 42.83 | 0.06 | 81.99 | 0.03 | 19.43 | 0.05 | 62.56 | 0.06 | [8 empty] | 218.39 | 0.18 | 103.53 | 0.07 | 107.36 | 0.06 | 3.84 | 0.04 | 216.15 | 0.21 | 106.64 | 0.07 | 2.65 | 0.05 | [24 empty] | 249.56 | 0.23 | 204 | 0.04 | 116.9 | 0.07 | 87.1 | 0.05 | [20 empty] | 63.84 | 0.05 | 78.79 | 0.03 | 36.42 | 0.04 | 42.37 | 0.05 | [12 empty] | 239.65 | 0.22 | 104.2 | 0.06 | 113.97 | 0.07 | 9.77 | 0.03 | 237.17 | 0.22 | 113.22 | 0.07 | 8.44 | 0.05 | [12 empty] | 62.56 | 0.04 | 62.04 | 0.05 | 61.52 | 0.05 | 61.46 | 0.05 | 62.08 | 0.04 |  |  | 103.39 | 0.06 |  |  | 76.98 | 0.03 | 81.02 | 0.03 | 197.91 | 0.05 |  |  | 104.62 | 0.06 | 80.52 | 0.05 | 83.89 | 0.04 |  |  | 104.85 | 0.05 | [28 empty] | 62.51 | 0.04 | [8 empty] | 104.78 | 0.06 | 103.99 | 0.04 | [8 empty] | 78.36 | 0.04 | 104.68 | 0.06 | 77.36 | 0.05 | 104.9 | 0.06 | [10 empty] | 217.05 | 0.06 | 95.38 | 0.11 | 95.7 | 0.1 | 75 | 0.06 | 75.03 | 0.06 | 75.03 | 0.06 | 75.1 | 0.06 | 75.06 | 0.06 | 75.08 | 0.06 |  |  | 75.49 | 0.07 | 76.17 | 0.08 | 75.09 | 0.05 | 87.65 | 0.14 | 75.59 | 0.05 | 75.53 | 0.06 | 75.25 | 0.06 | 76.19 | 0.11 | 78.36 | 0.16 | 76.24 | 0.07 | 76.04 | 0.07 | 81.55 | 0.1 | 74.99 | 0.06 | 75.59 | 0.05 | 75.31 | 0.06 | 82.69 | 0.14 | [78 empty] | 94.22 | 0.09 | [8 empty] | 62.27 | 0.04 | 62.44 | 0.04 | C8-55-CE3 | 75.038 | 0.026 | 62 | 0.027 | 62.137 | 0.019 | 57.194 | 0.019 | 95.004 | 0.007 | 75.001 | 0.01 | 2523 | 4.4 | 2445.3 | 4.3 | 1.152 | 0.002 | -0.423 | 0.003 | 0.162 | 0.006 | 0.8792 | 0.0031 | 29.189 | 0.001 | 8222 | 20 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5264 | 11446.9569 | 330.9404 | 22.9281 | 97.5663 | 11349.3906 | 0.0088155 | 27.698 | 60.6106 | 14.1 | 13.2245 | 0.013921 | 38.158 | 0.0087716 | 27.6081 | 0.0087972 | 24.4894 | 75.2098 | 62.1279 | 24.1171 | 40990.0455 | 40107.9444 | 6662 | 0.55471 | 36795.265 | 35913.1638 | 4.4752 | 0.3235 | -3.5809 | -14.5992 | 53.6293 | 40990.0455 | 35698.9257 | 4261.801 | 1029.3188 | 40990.0455 | 100%
3 | C8-R80-E0C30-95CE | 75N0184 | C8-R80-E0C30-95CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 0 | CUST 3 | 6/29/2015 | 20:28:15 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 28.1 | 0 | 35707 | 81 | 35670 | 172 | 1040 | 158 | 36749 | 155 | 4.185 | 900 | [38 empty] | Baseline 80% factory charge, 0% evaporator and 30% condenser blockage,--economizer closed (2.0V), 80% factory charge (CK1 6.08 lbs, CK2 6.48 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Removed: CK1:6.1 oz CK2 | 74.928 | 0.039 | 61.999 | 0.031 | 95.004 | 0.011 | 74.997 | 0.025 | 74.66 | 0.09 | 61.83 | 0.08 | 65.05 | 0.01 | 0.091 | 0.006 | 0.8875 | 0.0034 | 35707 | 81 | 1040 | 158 | 4.185 | 0.019 | [6 empty] | 229.9 | 1.5 | 229.7 | 1.5 | 230 | 1.5 | 28.1 | 0.1 | 25.6 | 0.1 | 29.4 | 0.1 | 6442.2 | 55.6 | 3686.7 | 75.9 | 2339.4 | 42.2 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.1 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.2 |  | 10 |  | 9.4 |  | 3160 |  | 0.8 | 230 | 230 | 230 | 10.9 | 10.7 | 9.5 | 3380 | 0.72 | 228.4 |  | 2.4 |  | 535.3 |  | 115 |  | 8740.3 | [22 empty] | 244.47 | 0.2 | 227.78 | 0.05 | 115.41 | 0.06 | 112.37 | 0.08 | [16 empty] | 44.52 | 0.07 | 82.05 | 0.04 | 20.96 | 0.06 | 61.1 | 0.06 | [8 empty] | 236.42 | 0.22 | 110.52 | 0.08 | 112.99 | 0.07 | 2.46 | 0.1 | 234.13 | 0.2 | 112.29 | 0.06 | 1.76 | 0.05 | [24 empty] | 276.56 | 0.19 | 211.63 | 0.05 | 124.52 | 0.05 | 87.11 | 0.05 | [20 empty] | 68.64 | 0.04 | 77.62 | 0.03 | 39.81 | 0.03 | 37.81 | 0.05 | [12 empty] | 266.11 | 0.16 | 111.43 | 0.05 | 121.64 | 0.04 | 10.2 | 0.06 | 263.47 | 0.17 | 120.89 | 0.05 | 9.79 | 0.06 | [12 empty] | 62.7 | 0.03 | 62.15 | 0.04 | 61.52 | 0.04 | 61.38 | 0.03 | 61.79 | 0.03 |  |  | 110.69 | 0.07 |  |  | 77.54 | 0.06 | 80.96 | 0.06 | 205.38 | 0.08 |  |  | 111.35 | 0.06 | 80.39 | 0.09 | 83.49 | 0.05 |  |  | 110.87 | 0.05 | [28 empty] | 62.61 | 0.03 | [8 empty] | 111.11 | 0.05 | 110.54 | 0.04 | [8 empty] | 79.21 | 0.07 | 110.49 | 0.06 | 77.61 | 0.11 | 111.51 | 0.07 | [10 empty] | 226.99 | 0.08 | 95.23 | 0.08 | 95.16 | 0.07 | 75.17 | 0.08 | 75.15 | 0.07 | 75.26 | 0.07 | 75.27 | 0.07 | 75.24 | 0.08 | 75.24 | 0.07 |  |  | 77.67 | 0.08 | 77.11 | 0.09 | 75.29 | 0.08 | 89.01 | 0.14 | 75.79 | 0.08 | 76.15 | 0.1 | 75.44 | 0.08 | 75.79 | 0.11 | 78.91 | 0.15 | 77.29 | 0.14 | 78.26 | 0.08 | 80.46 | 0.12 | 75.13 | 0.08 | 76.55 | 0.12 | 75.4 | 0.07 | 83.18 | 0.13 | [78 empty] | 94.46 | 0.08 |  |  |  |  | closed | 0 blockage |  |  | 62.5 | 0.03 | 62.41 | 0.03 | C8-55-CE3 | 74.928 | 0.039 | 61.999 | 0.031 | 62.084 | 0.024 | 57.256 | 0.021 | 95.004 | 0.011 | 74.997 | 0.025 | 2535.6 | 4.9 | 2456.1 | 4.7 | 1.153 | 0.002 | -0.427 | 0.003 | 0.091 | 0.006 | 0.8875 | 0.0034 | 29.172 | 0.001 | 8782 | 19 | 1550 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5042 | 11504.952 | 332.6905 | 23.0362 | 98.0267 | 11406.9254 | 0.0088406 | 27.6988 | 60.5798 | 14.1 | 13.2235 | 0.013917 | 38.1542 | 0.008797 | 27.609 | 0.008847 | 24.5307 | 75.1006 | 62.1269 | 24.1638 | 40670.459 | 40094.8453 | 7232 | 0.6069 | 36515.7818 | 35940.1681 | 4.158 | 0.31779 | -3.535 | -14.5209 | 53.8157 | 40670.459 | 35415.3108 | 4221.4394 | 1033.7088 | 40670.459 | 100%
3 | C8-R80-E20C0-95CE | 75N0185 | C8-R80-E20C0-95CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 20 | CUST 3 | 6/29/2015 | 18:32:36 | 10 Ton | 0:15:00 | 75/62 95 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 |  | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.8 | 26.7 | 0 | 34196 | 67 | 33892 | 114 | 2229 | 102 | 36426 | 128 | 4.469 | 900 | [38 empty] | Baseline 80% factory charge, 20% evaporator blockage, 0% condenser blockage,--economizer closed (2.0V), 80% factory charge (CK1 6.08 lbs, CK2 6.48 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz ai | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Removed: CK1:6.1 oz CK2 | 75.022 | 0.015 | 62.012 | 0.033 | 94.998 | 0.011 | 75.001 | 0.025 | 74.73 | 0.08 | 62.08 | 0.06 | 65.3 | 0.02 | 0.079 | 0.006 | 0.8217 | 0.0036 | 34196 | 67 | 2229 | 102 | 4.469 | 0.019 | [6 empty] | 230 | 1.4 | 229.9 | 1.4 | 230.1 | 1.4 | 26.7 | 0.1 | 24.3 | 0.1 | 28.1 | 0.1 | 6118.4 | 53.5 | 3654.8 | 71.8 | 2031.2 | 39.8 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.2 |  | 0.61 | 230 |  | 230 |  | 230 |  | 9.6 |  | 9.6 |  | 8.9 |  | 2930 |  | 0.79 | 230 | 230 | 230 | 10.1 | 10 | 8.8 | 3050 | 0.7 | 228.7 |  | 2.4 |  | 526.5 |  | 115 |  | 8111.5 | [22 empty] | 225.52 | 0.18 | 214.99 | 0.04 | 109.62 | 0.06 | 105.37 | 0.06 | [16 empty] | 41.86 | 0.05 | 78.72 | 0.03 | 18.52 | 0.05 | 60.2 | 0.06 | [8 empty] | 217.71 | 0.18 | 103.51 | 0.09 | 107.14 | 0.06 | 3.63 | 0.07 | 215.45 | 0.19 | 106.41 | 0.06 | 2.57 | 0.04 | [24 empty] | 248.53 | 0.17 | 200.15 | 0.04 | 116.6 | 0.05 | 83.55 | 0.05 | [20 empty] | 62.53 | 0.04 | 73.52 | 0.03 | 35.47 | 0.03 | 38.06 | 0.06 | [12 empty] | 238.64 | 0.17 | 104.21 | 0.06 | 113.66 | 0.05 | 9.45 | 0.05 | 236.21 | 0.16 | 112.92 | 0.05 | 8.19 | 0.05 | [12 empty] | 63.11 | 0.04 | 62.4 | 0.06 | 61.36 | 0.04 | 61.24 | 0.04 | 61.77 | 0.06 |  |  | 103.36 | 0.08 |  |  | 73.26 | 0.05 | 77.83 | 0.05 | 194.52 | 0.05 |  |  | 104.82 | 0.05 | 75.98 | 0.06 | 79.46 | 0.06 |  |  | 105.04 | 0.05 | [28 empty] | 62.86 | 0.04 | [8 empty] | 104.74 | 0.05 | 103.84 | 0.05 | [8 empty] | 74.72 | 0.05 | 104.74 | 0.06 | 72.18 | 0.08 | 105.01 | 0.05 | [10 empty] | 215.65 | 0.06 | 95.65 | 0.11 | 95.94 | 0.1 | 75.21 | 0.05 | 75.17 | 0.05 | 75.34 | 0.05 | 75.36 | 0.05 | 75.31 | 0.05 | 75.31 | 0.05 |  |  | 78.43 | 0.05 | 78.66 | 0.06 | 75.2 | 0.05 | 85.73 | 0.11 | 75.79 | 0.04 | 77.77 | 0.07 | 75.94 | 0.06 | 76.6 | 0.09 | 78.77 | 0.13 | 78.68 | 0.06 | 78.8 | 0.06 | 79.28 | 0.08 | 75.04 | 0.05 | 78.12 | 0.08 | 75.54 | 0.05 | 81.22 | 0.08 | [78 empty] | 94.23 | 0.11 |  |  |  |  | closed | 20% blockage |  |  | 62.75 | 0.05 | 62.63 | 0.04 | C8-EB20-55-CE | 75.022 | 0.015 | 62.012 | 0.033 | 62.258 | 0.015 | 57.118 | 0.027 | 94.998 | 0.011 | 75.001 | 0.025 | 2440.1 | 5.4 | 2361.9 | 5.2 | 1.06 | 0.003 | -0.39 | 0.003 | 0.079 | 0.006 | 0.8217 | 0.0036 | 29.161 | 0.001 | 8150 | 19 | 1490 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.536 | 11068.7575 | 294.1254 | 26.6753 | 113.5128 | 10955.2447 | 0.008836 | 27.7251 | 60.722 | 14.0999 | 13.227 | 0.013922 | 38.1581 | 0.0087833 | 27.617 | 0.008723 | 24.4382 | 75.2288 | 62.1657 | 24.0636 | 40528.0266 | 38537.1591 | 6660 | 0.56086 | 36446.5065 | 34455.6389 | 4.472 | 0.33995 | -3.6615 | -14.5067 | 53.2506 | 40528.0266 | 35185.3001 | 4146.1709 | 1196.5556 | 40528.0266 | 100%
3 | C8-R80-E20C30-95CE | 75N0186 | C8-R80-E20C30-95CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 30 | 20 | CUST 3 | 6/29/2015 | 19:36:49 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.7 | 27.9 | 0 | 34637 | 56 | 34436 | 96 | 2023 | 95 | 36663 | 93 | 4.215 | 900 | [38 empty] | Baseline 80% factory charge, 20% evaporator blockage, 30% condenser blockage,--economizer closed (2.0V), 80% factory charge (CK1 6.08 lbs, CK2 6.48 lbs), 95F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz a | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Removed: CK1:6.1 oz CK2 | 74.997 | 0.011 | 61.998 | 0.02 | 94.988 | 0.011 | 74.998 | 0.024 | 74.73 | 0.09 | 61.85 | 0.09 | 65.17 | 0.02 | 0.071 | 0.002 | 0.8188 | 0.0017 | 34637 | 56 | 2023 | 95 | 4.215 | 0.015 | [6 empty] | 229.9 | 1.4 | 229.8 | 1.4 | 230.1 | 1.4 | 27.9 | 0.1 | 25.4 | 0.1 | 29.3 | 0.1 | 6395.9 | 51.8 | 3698.8 | 71.1 | 2301.4 | 38.7 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.1 |  | 0.61 | 230 |  | 230 |  | 230 |  | 10.1 |  | 10.1 |  | 9.3 |  | 3150 |  | 0.81 | 230 | 230 | 230 | 10.8 | 10.7 | 9.5 | 3350 | 0.72 | 228.5 |  | 2.4 |  | 535.5 |  | 115 |  | 8640.5 | [22 empty] | 243.82 | 0.19 | 225.28 | 0.06 | 115.21 | 0.06 | 110.07 | 0.07 | [16 empty] | 43.91 | 0.06 | 78.8 | 0.04 | 20.4 | 0.05 | 58.4 | 0.07 | [8 empty] | 235.8 | 0.19 | 110.42 | 0.11 | 112.8 | 0.06 | 2.38 | 0.09 | 233.46 | 0.21 | 112.08 | 0.06 | 1.75 | 0.04 | [24 empty] | 274.49 | 0.14 | 207.71 | 0.04 | 123.95 | 0.04 | 83.76 | 0.05 | [20 empty] | 66.96 | 0.04 | 72.39 | 0.03 | 38.63 | 0.03 | 33.76 | 0.04 | [12 empty] | 264.15 | 0.15 | 111.5 | 0.07 | 121.08 | 0.04 | 9.58 | 0.06 | 261.55 | 0.16 | 120.35 | 0.04 | 9.21 | 0.06 | [12 empty] | 62.63 | 0.03 | 62.08 | 0.05 | 61.42 | 0.05 | 61.19 | 0.04 | 61.83 | 0.03 |  |  | 110.55 | 0.09 |  |  | 73.81 | 0.05 | 77.65 | 0.07 | 201.78 | 0.1 |  |  | 111.42 | 0.04 | 75.63 | 0.11 | 79.07 | 0.06 |  |  | 110.92 | 0.06 | [28 empty] | 62.43 | 0.04 | [8 empty] | 111.14 | 0.06 | 110.33 | 0.05 | [8 empty] | 75.66 | 0.06 | 110.41 | 0.08 | 72.25 | 0.13 | 111.56 | 0.04 | [10 empty] | 224.66 | 0.11 | 95.3 | 0.11 | 95.2 | 0.09 | 75.2 | 0.05 | 75.15 | 0.05 | 75.31 | 0.07 | 75.33 | 0.06 | 75.3 | 0.06 | 75.3 | 0.05 |  |  | 78.56 | 0.05 | 78.8 | 0.07 | 75.25 | 0.05 | 85.97 | 0.1 | 75.85 | 0.05 | 77.9 | 0.07 | 75.99 | 0.06 | 76.65 | 0.09 | 78.93 | 0.15 | 78.78 | 0.06 | 78.87 | 0.06 | 79.38 | 0.09 | 75.09 | 0.05 | 78.28 | 0.06 | 75.63 | 0.05 | 81.34 | 0.09 | [78 empty] | 94.43 | 0.07 |  |  |  |  | closed | 20% blockage |  |  | 62.34 | 0.04 | 62.26 | 0.04 | C8-EB20-55-CE | 74.997 | 0.011 | 61.998 | 0.02 | 62.046 | 0.007 | 57.061 | 0.015 | 94.988 | 0.011 | 74.998 | 0.024 | 2435.2 | 2.5 | 2358.3 | 2.5 | 1.06 | 0.001 | -0.388 | 0.002 | 0.071 | 0.002 | 0.8188 | 0.0017 | 29.168 | 0.001 | 8698 | 19 | 1490 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.539 | 11050.914 | 293.6771 | 26.6065 | 113.2224 | 10937.6916 | 0.0088327 | 27.7153 | 60.507 | 14.0996 | 13.2217 | 0.013922 | 38.1554 | 0.00878 | 27.6072 | 0.008739 | 24.4039 | 75.2037 | 62.1517 | 24.0285 | 40742.2245 | 38979.002 | 7208 | 0.60382 | 36659.1743 | 34895.9518 | 4.2147 | 0.32785 | -3.6868 | -14.6967 | 53.3383 | 40742.2245 | 35400.0899 | 4147.8459 | 1194.2888 | 40742.2245 | 100%
3 | C8-R90-95-CE | 75N0187 | C8-R90-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/29/2015 | 15:05:11 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.6 | 27.3 | 0 | 40386 | 94 | 40185 | 179 | 3991 | 176 | 44381 | 161 | 5.252 | 900 | [38 empty] | 90% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run--C8-R90-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Removed: CK1:6.1 oz CK2: 6.5 o | 74.947 | 0.034 | 61.976 | 0.033 | 95.003 | 0.007 | 75 | 0.018 | 74.65 | 0.08 | 60.21 | 0.04 | 63.95 | 0.02 | 0.147 | 0.004 | 0.8821 | 0.0029 | 40386 | 94 | 3991 | 176 | 5.252 | 0.022 | [6 empty] | 229.8 | 1.2 | 229.9 | 1.2 | 230.2 | 1.2 | 27.3 | 0.1 | 24.8 | 0.1 | 28.8 | 0.1 | 6265.7 | 46 | 3682.3 | 61.2 | 2184.9 | 34.5 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 9.9 |  | 9.9 |  | 9.1 |  | 3070 |  | 0.8 | 230 | 230 | 230 | 10.3 | 10.3 | 9 | 3170 | 0.71 | 228.7 |  | 2.4 |  | 526.5 |  | 115 |  | 8441.5 | [22 empty] | 237.68 | 0.2 | 205.36 | 0.03 | 113.38 | 0.06 | 91.99 | 0.06 | [16 empty] | 52.04 | 0.05 | 81.16 | 0.03 | 27.39 | 0.04 | 53.77 | 0.06 | [8 empty] | 228.14 | 0.2 | 103.16 | 0.06 | 110.45 | 0.06 | 7.29 | 0.05 | 226.2 | 0.18 | 109.84 | 0.06 | 5.83 | 0.06 | [24 empty] | 258.57 | 0.22 | 201.39 | 0.04 | 119.51 | 0.06 | 81.88 | 0.04 | [20 empty] | 68.16 | 0.04 | 77.52 | 0.03 | 39.49 | 0.03 | 38.03 | 0.04 | [12 empty] | 248.4 | 0.19 | 103.21 | 0.06 | 116.57 | 0.06 | 13.36 | 0.03 | 245.67 | 0.22 | 115.77 | 0.07 | 11.89 | 0.05 | [12 empty] | 60.91 | 0.03 | 60.17 | 0.05 | 59.89 | 0.05 | 59.64 | 0.05 | 60.33 | 0.04 |  |  | 103.07 | 0.06 |  |  | 76.25 | 0.04 | 80.16 | 0.04 | 195.62 | 0.04 |  |  | 103.81 | 0.06 | 79.85 | 0.05 | 83.04 | 0.03 |  |  | 104.69 | 0.04 | [28 empty] | 60.72 | 0.04 | [8 empty] | 103.88 | 0.06 | 104.01 | 0.05 | [8 empty] | 77.68 | 0.04 | 105.13 | 0.06 | 76.38 | 0.05 | 104.01 | 0.06 | [10 empty] | 205.89 | 0.04 | 95.46 | 0.12 | 95.84 | 0.11 | 75.03 | 0.08 | 75.06 | 0.08 | 75.05 | 0.08 | 75.11 | 0.08 | 75.08 | 0.08 | 75.09 | 0.08 |  |  | 75.46 | 0.09 | 76.17 | 0.09 | 75.08 | 0.08 | 87.7 | 0.14 | 75.62 | 0.08 | 75.58 | 0.08 | 75.29 | 0.09 | 76.15 | 0.12 | 78.37 | 0.14 | 76.23 | 0.09 | 76.06 | 0.1 | 81.62 | 0.11 | 75 | 0.08 | 75.57 | 0.07 | 75.29 | 0.08 | 82.77 | 0.14 | [78 empty] | 94.12 | 0.09 | [8 empty] | 60.56 | 0.04 | 60.65 | 0.04 | C8-55-CE3 | 74.947 | 0.034 | 61.976 | 0.033 | 60.433 | 0.014 | 56.162 | 0.016 | 95.003 | 0.007 | 75 | 0.018 | 2523.2 | 4.2 | 2454 | 4.1 | 1.154 | 0.002 | -0.426 | 0.002 | 0.147 | 0.004 | 0.8821 | 0.0029 | 29.212 | 0.001 | 8451 | 19 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.519 | 11486.8068 | 332.6944 | 23.0092 | 97.9118 | 11388.895 | 0.0088212 | 27.6822 | 58.914 | 14.1 | 13.1796 | 0.01392 | 38.1571 | 0.0087773 | 27.5921 | 0.0085868 | 23.8449 | 75.1195 | 62.1042 | 23.4746 | 48331.5131 | 44675.9171 | 6891 | 0.48662 | 44142.719 | 40487.123 | 5.2234 | 0.27616 | -4.2076 | -16.2055 | 52.7313 | 48331.5131 | 43042.989 | 4254.0888 | 1034.4353 | 48331.5131 | 100%
3 | C8-R95-95-CE | 75N0188 | C8-R95-95-CE | closed | on | on | 4.5 turns | unsealed | sealed | 865 | 7 | horizontal | 0 | 0 | CUST 3 | 6/29/2015 | 13:56:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.6 | 27.5 | 0 | 42325 | 83 | 41675 | 121 | 4902 | 135 | 47231 | 150 | 5.521 | 900 | [38 empty] | 95% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper, 4.5 turns,--7" AK49 pulley (865 rpm), adjust code tester speed to match total static of run--C8-R95-95-CE-SPWCT-SS | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Removed: CK1=6.1 oz CK2=6.5 oz | 75.032 | 0.019 | 61.994 | 0.03 | 95.005 | 0.013 | 75.002 | 0.025 | 74.56 | 0.05 | 59.58 | 0.03 | 63.46 | 0.03 | 0.143 | 0.005 | 0.8795 | 0.0027 | 42325 | 83 | 4902 | 135 | 5.521 | 0.021 | [6 empty] | 229.8 | 1.2 | 229.8 | 1.2 | 230.1 | 1.2 | 27.5 | 0.1 | 25.1 | 0.1 | 29.1 | 0.1 | 6316.5 | 46.1 | 3689.6 | 61.8 | 2238.2 | 34.8 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10 |  | 10 |  | 9.3 |  | 3120 |  | 0.8 | 230 | 230 | 230 | 10.5 | 10.4 | 9.1 | 3220 | 0.71 | 228.6 |  | 2.4 |  | 526.1 |  | 115 |  | 8551.1 | [22 empty] | 242.13 | 0.19 | 203 | 0.04 | 114.72 | 0.06 | 88.29 | 0.05 | [16 empty] | 54.79 | 0.05 | 80.78 | 0.03 | 29.6 | 0.04 | 51.18 | 0.05 | [8 empty] | 232.34 | 0.2 | 102.14 | 0.05 | 111.75 | 0.06 | 9.61 | 0.04 | 230.27 | 0.21 | 111.11 | 0.06 | 8.52 | 0.05 | [24 empty] | 263.41 | 0.2 | 200.24 | 0.04 | 120.88 | 0.06 | 79.35 | 0.04 | [20 empty] | 70.24 | 0.05 | 76.74 | 0.03 | 40.92 | 0.03 | 35.82 | 0.04 | [12 empty] | 253.07 | 0.2 | 102.99 | 0.04 | 117.93 | 0.06 | 14.94 | 0.03 | 250.25 | 0.19 | 117.11 | 0.05 | 13.42 | 0.04 | [12 empty] | 60.28 | 0.03 | 59.5 | 0.05 | 59.21 | 0.04 | 58.83 | 0.04 | 59.64 | 0.04 |  |  | 102.09 | 0.05 |  |  | 75.8 | 0.03 | 79.7 | 0.03 | 194.49 | 0.04 |  |  | 103.58 | 0.05 | 79.18 | 0.03 | 82.37 | 0.03 |  |  | 104.66 | 0.04 | [28 empty] | 60.08 | 0.03 | [8 empty] | 103.7 | 0.05 | 102.59 | 0.05 | [8 empty] | 77.27 | 0.03 | 103.26 | 0.05 | 75.51 | 0.04 | 103.78 | 0.05 | [10 empty] | 203.47 | 0.04 | 95.44 | 0.12 | 95.88 | 0.12 | 74.95 | 0.06 | 74.95 | 0.05 | 74.96 | 0.06 | 75.01 | 0.06 | 75.01 | 0.06 | 75.03 | 0.05 |  |  | 75.38 | 0.07 | 76.15 | 0.1 | 75 | 0.06 | 87.66 | 0.15 | 75.57 | 0.06 | 75.51 | 0.06 | 75.23 | 0.06 | 76.12 | 0.1 | 78.36 | 0.12 | 76.21 | 0.07 | 75.96 | 0.07 | 81.58 | 0.09 | 74.94 | 0.05 | 75.53 | 0.06 | 75.25 | 0.05 | 82.75 | 0.17 | [78 empty] | 94.03 | 0.08 | [8 empty] | 59.93 | 0.03 | 60.01 | 0.03 | C8-55-CE3 | 75.032 | 0.019 | 61.994 | 0.03 | 59.817 | 0.005 | 55.776 | 0.018 | 95.005 | 0.013 | 75.002 | 0.025 | 2517.4 | 3.8 | 2452.4 | 3.8 | 1.158 | 0.002 | -0.425 | 0.002 | 0.143 | 0.005 | 0.8795 | 0.0027 | 29.228 | 0.001 | 8555 | 18 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5318 | 11474.5419 | 333.6299 | 22.9823 | 97.7966 | 11376.7453 | 0.008813 | 27.6938 | 58.2852 | 14.1 | 13.1634 | 0.013921 | 38.159 | 0.0087691 | 27.6038 | 0.0085062 | 23.6071 | 75.2038 | 62.122 | 23.2336 | 51178.3107 | 46592.0813 | 6985 | 0.46582 | 46958.5795 | 42372.3502 | 5.489 | 0.25727 | -4.4602 | -16.9186 | 52.4248 | 51178.3107 | 45861.176 | 4284.8789 | 1032.2557 | 51178.3107 | 100%
3 | C8-EB10-55-CE | 75N0195 | C8-EB10-55-CE | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 10 | CUST 3 | 6/27/2015 | 2:55:49 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.3 | 6.4 | 0 | 4867 | 20 | 4608 | 126 | 3761 | 72 | 8631 | 82 | 5.705 | 899 | [38 empty] | 10% evaporator coil block, economizer closed (2V), no compressor, factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, Inlet Meriam @ 75%: Outlet @ 75% Horiz airflow.--7` blower pulley A49 belt, 4.5 turns open from closed, 870- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: 10.5" evap coil block | 74.981 | 0.013 | 61.99 | 0.041 | 54.992 | 0.018 | 51.024 | 0.019 | 74.54 | 0.04 | 72.87 | 0.06 | 73.74 | 0.01 | 0.045 | 0.003 | 0.8388 | 0.0021 | 4867 | 20 | 3761 | 72 | 5.705 | 0.066 | [6 empty] | 230 | 0.9 | 230.4 | 0.9 | 230.1 | 0.9 | 6.4 | 0 | 6.1 | 0 | 6.4 | 0 | 1369.5 | 12.6 | 1128.1 | 16.5 | 143.6 | 9.5 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.2 |  | 0.61 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1490 | [22 empty] | 95.33 | 0.04 | 56.92 | 0.02 | 56.37 | 0.02 | -0.56 | 0.02 | [16 empty] | 95.15 | 0.03 | 58.72 | 0.04 | 56.26 | 0.02 | 2.45 | 0.05 | [8 empty] | 96.77 | 0.03 | 55.37 | 0.04 | 57.16 | 0.02 | 1.79 | 0.04 | 96.1 | 0.03 | 56.79 | 0.02 | -0.84 | 0.01 | [24 empty] | 95.8 | 0.03 | 55.89 | 0.01 | 56.62 | 0.02 | -0.73 | 0.01 | [20 empty] | 95.68 | 0.03 | 57.6 | 0.03 | 56.56 | 0.02 | 1.05 | 0.03 | [12 empty] | 97.14 | 0.03 | 55.73 | 0.04 | 57.37 | 0.02 | 1.63 | 0.05 | 96.99 | 0.02 | 57.29 | 0.02 | -1.5 | 0.02 | [12 empty] | 74.41 | 0.03 | 72.97 | 0.03 | 71.67 | 0.03 | 72.35 | 0.04 | 72.89 | 0.04 |  |  | 55.39 | 0.04 |  |  | 56.27 | 0.03 | 58.91 | 0.05 | 56.62 | 0.03 |  |  | 55.97 | 0.09 | 56.73 | 0.02 | 57.59 | 0.02 |  |  | 56.1 | 0.05 | [28 empty] | 74.16 | 0.03 | [8 empty] | 55.79 | 0.02 | 55.95 | 0.02 | [8 empty] | 56.25 | 0.03 | 56.49 | 0.02 | 56.79 | 0.04 | 55.95 | 0.02 | [10 empty] | 57.64 | 0.02 | 55.46 | 0.09 | 55.18 | 0.1 | 75.11 | 0.03 | 75.03 | 0.03 | 75.24 | 0.03 | 75.21 | 0.02 | 75.16 | 0.03 | 75.16 | 0.03 |  |  | 68.58 | 0.07 | 68.16 | 0.08 | 74.74 | 0.04 | 63.77 | 0.1 | 75.2 | 0.04 | 68.79 | 0.08 | 70.78 | 0.1 | 66.57 | 0.09 | 64.47 | 0.16 | 68.95 | 0.1 | 70.02 | 0.14 | 67.98 | 0.08 | 74.63 | 0.04 | 68.38 | 0.09 | 74.06 | 0.06 | 69.44 | 0.06 | [78 empty] | 54.86 | 0.1 | [8 empty] | 73.52 | 0.03 | 73.9 | 0.03 | Economizer test | 74.981 | 0.013 | 61.99 | 0.041 | 73.211 | 0.014 | 60.916 | 0.033 | 54.992 | 0.018 | 51.024 | 0.019 | 2482 | 3.1 | 2370.2 | 2.9 | 1.092 | 0.001 | -0.373 | 0.002 | 0.045 | 0.003 | 0.8388 | 0.0021 | 29.227 | 0.001 | 1513 | 10 | 1490 |  | 0.012007 | 28.4581 | 13.029 | 0.373 | 1.5287 | 11028.8925 | 304.0694 | 28.4585 | 131.0504 | 10897.842 | 0.0087573 | 27.5208 | 71.6823 | 13.0294 | 13.5027 | 0.006996 | 20.7916 | 0.0087785 | 27.6017 | 0.0084963 | 26.8614 | 74.7442 | 61.8729 | 26.4888
3 | C8-EB20-55-CE | 75N0196 | C8-EB20-55-CE | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 20 | CUST 3 | 6/27/2015 | 2:05:29 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 6.4 | 0 | 4781 | 31 | 4443 | 145 | 3788 | 59 | 8572 | 72 | 5.728 | 899 | [38 empty] | 20% evaporator coil block, economizer closed (2V), no compressor, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--95F OD, 75F DB, 62F WB ID conditions, Inlet Meriam @ 75%: Outlet @ 75% Horiz airflow.--7` blower pulley A49 belt, 4.5 turns open from closed, 870- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: 10.5" evap coil block | 74.974 | 0.015 | 61.991 | 0.028 | 55.012 | 0.018 | 50.998 | 0.016 | 74.43 | 0.03 | 72.81 | 0.04 | 73.72 | 0.01 | 0.064 | 0.004 | 0.8271 | 0.0028 | 4781 | 31 | 3788 | 59 | 5.728 | 0.064 | [6 empty] | 229.9 | 1.4 | 230.3 | 1.4 | 230.1 | 1.4 | 6.4 | 0.1 | 6.1 | 0.1 | 6.4 | 0.1 | 1359.2 | 17.1 | 1129 | 24.3 | 137.6 | 12.2 | 230 |  | 230 |  | 230 |  | 6.3 |  | 5.9 |  | 6.2 |  | 0.62 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1480 | [22 empty] | 95.89 | 0.03 | 57.58 | 0.02 | 56.67 | 0.02 | -0.91 | 0.03 | [16 empty] | 95.71 | 0.04 | 60.38 | 0.05 | 56.57 | 0.02 | 3.81 | 0.07 | [8 empty] | 97.34 | 0.04 | 56.06 | 0.01 | 57.48 | 0.02 | 1.42 | 0.03 | 96.76 | 0.02 | 57.16 | 0.01 | -0.77 | 0.02 | [24 empty] | 96.35 | 0.02 | 56.19 | 0.02 | 56.93 | 0.01 | -0.74 | 0.03 | [20 empty] | 96.26 | 0.02 | 58.78 | 0.04 | 56.88 | 0.01 | 1.9 | 0.04 | [12 empty] | 97.5 | 0.09 | 56.18 | 0.01 | 57.56 | 0.05 | 1.38 | 0.06 | 97.43 | 0.03 | 57.53 | 0.01 | -1.53 | 0.01 | [12 empty] | 74.69 | 0.07 | 73.45 | 0.1 | 71.81 | 0.06 | 72.09 | 0.05 | 72.18 | 0.18 |  |  | 55.99 | 0.01 |  |  | 56.79 | 0.01 | 60.39 | 0.04 | 56.92 | 0.02 |  |  | 56.57 | 0.01 | 56.89 | 0.02 | 58.37 | 0.02 |  |  | 56.53 | 0.03 | [28 empty] | 74.43 | 0.05 | [8 empty] | 56 | 0.02 | 56.4 | 0.02 | [8 empty] | 56.76 | 0.02 | 56.89 | 0.01 | 56.89 | 0.03 | 56.18 | 0.02 | [10 empty] | 58.26 | 0.02 | 55.39 | 0.09 | 55.32 | 0.09 | 75.04 | 0.03 | 74.94 | 0.03 | 75.08 | 0.03 | 75.1 | 0.02 | 75.08 | 0.03 | 75.07 | 0.02 |  |  | 69.77 | 0.11 | 69.27 | 0.12 | 74.03 | 0.33 | 64.99 | 0.21 | 75.12 | 0.04 | 73.86 | 14.91 | 71.56 | 0.29 | 69.85 | 0.39 | 67.16 | 1.28 | 70.94 | 0.24 | 70.3 | 0.16 | 69.23 | 0.09 | 74.58 | 0.03 | 70.72 | 0.35 | 74.26 | 0.08 | 68.68 | 0.28 | [78 empty] | 54.82 | 0.08 | [8 empty] | 73.95 | 0.07 | 73.98 | 0.03 | Economizer test | 74.974 | 0.015 | 61.991 | 0.028 | 73.223 | 0.014 | 60.916 | 0.023 | 55.012 | 0.018 | 50.998 | 0.016 | 2464.5 | 4.2 | 2353.4 | 4 | 1.052 | 0.001 | -0.367 | 0.002 | 0.064 | 0.004 | 0.8271 | 0.0028 | 29.224 | 0.001 | 1497 | 11 | 1480 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.5438 | 10950.9022 | 290.855 | 24.8754 | 114.5473 | 10836.3549 | 0.008762 | 27.5311 | 71.6792 | 13.0298 | 13.503 | 0.0069775 | 20.7764 | 0.0087808 | 27.6025 | 0.0084935 | 26.8612 | 74.7659 | 61.8877 | 26.4849
3 | C8-EB35-55-CE | 75N0197 | C8-EB35-55-CE | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 35 | CUST 3 | 6/27/2015 | 1:03:14 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.8 | 6.3 | 0 | 4646 | 21 | 4402 | 122 | 3427 | 58 | 8075 | 60 | 5.576 | 901 | [38 empty] | 35% evaporator coil block, economizer closed (2V), no compressor, factory charge (CK1 7.6 lbs,--CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, Inlet Meriam @ 75%: Outlet @ 75% Horiz airflow.--7` blower pulley A49 belt, 4.5 turns open from closed, 870- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: 16 1/4` evap coil block | 74.991 | 0.012 | 61.984 | 0.024 | 54.969 | 0.023 | 50.991 | 0.029 | 74.46 | 0.02 | 72.78 | 0.05 | 73.77 | 0.01 | 0.053 | 0.003 | 0.755 | 0.0022 | 4646 | 21 | 3427 | 58 | 5.576 | 0.057 | [6 empty] | 230 | 1.3 | 230.4 | 1.3 | 230.1 | 1.3 | 6.3 | 0.1 | 6 | 0.1 | 6.3 | 0.1 | 1337.7 | 16.1 | 1126.8 | 22.4 | 110.5 | 11.8 | 230 |  | 230 |  | 230 |  | 6.2 |  | 5.9 |  | 6.1 |  | 0.58 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1430 | [22 empty] | 96.27 | 0.04 | 58.54 | 0.05 | 56.88 | 0.02 | -1.66 | 0.04 | [16 empty] | 96.04 | 0.04 | 63.14 | 0.1 | 56.75 | 0.02 | 6.38 | 0.09 | [8 empty] | 97.67 | 0.04 | 56.14 | 0.15 | 57.66 | 0.02 | 1.51 | 0.14 | 97.22 | 0.03 | 57.41 | 0.02 | -0.49 | 0.02 | [24 empty] | 96.58 | 0.04 | 56.65 | 0.03 | 57.05 | 0.02 | -0.41 | 0.06 | [20 empty] | 96.45 | 0.04 | 60.77 | 0.07 | 56.99 | 0.02 | 3.78 | 0.06 | [12 empty] | 97.74 | 0.04 | 56.2 | 0.03 | 57.69 | 0.02 | 1.5 | 0.03 | 97.54 | 0.04 | 57.59 | 0.02 | -1.45 | 0.02 | [12 empty] | 74.64 | 0.03 | 73.87 | 0.03 | 72.12 | 0.03 | 72.14 | 0.03 | 72.44 | 0.04 |  |  | 56.21 | 0.14 |  |  | 57.11 | 0.03 | 62.8 | 0.09 | 57.34 | 0.03 |  |  | 56.54 | 0.02 | 56.99 | 0.04 | 59.55 | 0.05 |  |  | 56.52 | 0.02 | [28 empty] | 74.36 | 0.02 | [8 empty] | 56.14 | 0.02 | 56.92 | 0.02 | [8 empty] | 57.19 | 0.03 | 57.23 | 0.03 | 56.95 | 0.04 | 56.36 | 0.02 | [10 empty] | 59.16 | 0.05 | 55.33 | 0.11 | 55.32 | 0.09 | 75.18 | 0.02 | 75.05 | 0.03 | 75.23 | 0.04 | 75.27 | 0.03 | 75.28 | 0.03 | 75.26 | 0.03 |  |  | 69.25 | 0.07 | 68.65 | 0.07 | 74.11 | 0.09 | 62.32 | 0.15 | 75.23 | 0.03 | 71.25 | 0.08 | 72.74 | 0.11 | 68.37 | 0.16 | 68.66 | 0.21 | 70.61 | 0.06 | 70.12 | 0.07 | 68.28 | 0.08 | 74.68 | 0.03 | 69.91 | 0.07 | 73.92 | 0.07 | 66.31 | 0.14 | [78 empty] | 54.69 | 0.1 | [8 empty] | 74.01 | 0.02 | 74.05 | 0.02 | Economizer test | 74.991 | 0.012 | 61.984 | 0.024 | 73.209 | 0.011 | 60.921 | 0.021 | 54.969 | 0.023 | 50.991 | 0.029 | 2354.2 | 3.4 | 2247.2 | 3.3 | 0.967 | 0.002 | -0.333 | 0.002 | 0.053 | 0.003 | 0.755 | 0.0022 | 29.217 | 0.001 | 1449 | 11 | 1430 |  | 0.00909 | 20.4271 | 13.029 | 0.333 | 1.5964 | 10461.023 | 255.2897 | 20.4268 | 94.0698 | 10366.9532 | 0.0087561 | 27.5359 | 71.6126 | 13.0287 | 13.5027 | 0.0069838 | 20.7729 | 0.0087722 | 27.5972 | 0.0085 | 26.865 | 74.8115 | 61.8952 | 26.4758
3 | C8-EB5-55-CE-2 | 75N0198 | C8-EB5-55-CE-2 | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 5 | CUST 3 | 6/29/2015 | 8:21:35 | 10 Ton | 0:15:00 | 75/62 - 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 229.7 | 1.2 | 6.4 | 0 | 4493 | 18 | 3931 | 43 | 3321 | 66 | 7817 | 64 | 5.13 | 899 | [38 empty] | 5% evaporator coil block, economizer closed (2V), no compressor, factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, Inlet Meriam--75%: Outlet @ 75% Horiz airflow. 7` blower pulley A49 belt, 4.5 turns open from closed,--870 RP | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: Cond coil block 51.5` | 75.003 | 0.01 | 61.988 | 0.029 | 54.981 | 0.011 | 50.978 | 0.019 | 74.44 | 0.03 | 73.04 | 0.02 | 73.93 | 0 | 0.139 | 0.004 | 0.8637 | 0.0024 | 4493 | 18 | 3321 | 66 | 5.13 | 0.054 | [6 empty] | 229.7 | 0.9 | 230.5 | 0.9 | 230.3 | 0.9 | 6.4 | 0 | 6.1 | 0 | 6.5 | 0 | 1368.2 | 11.2 | 1131.6 | 15.9 | 155.4 | 8.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.3 |  | 0.61 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1530 | [22 empty] | 97.18 | 0.03 | 57.73 | 0.03 | 57.4 | 0.02 | -0.34 | 0.03 | [16 empty] | 96.87 | 0.01 | 60.44 | 0.05 | 57.23 | 0.01 | 3.21 | 0.05 | [8 empty] | 97.29 | 0.03 | 56.82 | 0.04 | 57.46 | 0.02 | 0.64 | 0.04 | 97.68 | 0.02 | 57.68 | 0.01 | -0.23 | 0.03 | [24 empty] | 95.91 | 0.01 | 57.75 | 0.04 | 56.69 | 0 | 1.06 | 0.04 | [20 empty] | 96.3 | 0.01 | 59.8 | 0.06 | 56.91 | 0.01 | 2.9 | 0.06 | [12 empty] | 97.41 | 0.01 | 55.62 | 0.09 | 57.53 | 0 | 1.91 | 0.11 | 96.82 | 0.02 | 57.2 | 0.01 | -0.63 | 0.05 | [12 empty] | 74.17 | 0.02 | 72.75 | 0.02 | 71.31 | 0.02 | 72.16 | 0.03 | 72.58 | 0.03 |  |  | 56.83 | 0.04 |  |  | 57.36 | 0.01 | 60.23 | 0.04 | 58.21 | 0.05 |  |  | 56.77 | 0.02 | 57.01 | 0.02 | 59.03 | 0.05 |  |  | 56.73 | 0.02 | [28 empty] | 73.94 | 0.02 | [8 empty] | 56.57 | 0.05 | 57.44 | 0.04 | [8 empty] | 57.4 | 0.01 | 57.23 | 0.02 | 57.06 | 0.02 | 56.23 | 0.05 | [10 empty] | 58.24 | 0.02 | 54.78 | 0.09 | 54.48 | 0.06 | 74.93 | 0.03 | 74.91 | 0.02 | 74.87 | 0.04 | 74.96 | 0.04 | 74.97 | 0.03 | 75.01 | 0.03 |  |  | 69.4 | 0.07 | 71.97 | 0.08 | 74.36 | 0.06 | 71.4 | 0.2 | 75.26 | 0.02 | 67.49 | 0.09 | 73.66 | 0.07 | 70.88 | 0.1 | 64.22 | 0.21 | 66.69 | 0.09 | 70.98 | 0.06 | 70.87 | 0.06 | 74.71 | 0.02 | 67.07 | 0.08 | 73.52 | 0.05 | 70.29 | 0.08 | [78 empty] | 54.92 | 0.11 | [8 empty] | 73.26 | 0.02 | 73.67 | 0.02 | Economizer test | 75.003 | 0.01 | 61.988 | 0.029 | 73.391 | 0.01 | 61.037 | 0.024 | 54.981 | 0.011 | 50.978 | 0.019 | 2517.7 | 3.6 | 2406.4 | 3.4 | 1.115 | 0.002 | -0.399 | 0.002 | 0.139 | 0.004 | 0.8637 | 0.0024 | 29.258 | 0.001 | 1524 | 9 | 1515 |  | 0.0040955 | 9.8554 | 13.029 | 0.399 | 1.5252 | 11183.5127 | 315.2157 | 9.8554 | 45.3853 | 11138.1274 | 0.0087647 | 27.5722 | 71.8658 | 13.029 | 13.5076 | 0.0069741 | 20.7652 | 0.008772 | 27.5999 | 0.0085319 | 26.9443 | 74.922 | 61.9479 | 26.5724
3 | C8-EB50-55-CE | 75N0200 | C8-EB50-55-CE | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 50 | CUST 3 | 6/26/2015 | 23:55:37 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.5 | 6.3 | 0 | 4834 | 36 | 4557 | 96 | 3068 | 72 | 7905 | 68 | 5.555 | 902 | [38 empty] | 50% evaporator coil block, economizer closed (2V), no compressor, factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions,--Inlet Meriam @ 75%: Outlet @ 75% Horiz airflow. 7` blower pulley A49 belt, 4.5 turns open from closed,--870 | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: 16 1/4` evap coil block | 75.008 | 0.009 | 61.999 | 0.032 | 54.972 | 0.05 | 50.988 | 0.029 | 74.52 | 0.04 | 72.72 | 0.04 | 73.71 | 0 | 0.067 | 0.003 | 0.7102 | 0.002 | 4834 | 36 | 3068 | 72 | 5.555 | 0.065 | [6 empty] | 230 | 1.1 | 230.2 | 1.2 | 230 | 1.1 | 6.3 | 0.1 | 6 | 0.1 | 6.3 | 0.1 | 1323.3 | 14.7 | 1127.4 | 20.7 | 99.5 | 10.7 | 230 |  | 230 |  | 230 |  | 6.2 |  | 5.9 |  | 6.1 | [25 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1410 | [22 empty] | 97.69 | 0.09 | 60.31 | 0.07 | 57.67 | 0.05 | -2.63 | 0.08 | [16 empty] | 97.43 | 0.1 | 68.28 | 0.13 | 57.53 | 0.05 | 10.75 | 0.14 | [8 empty] | 99.13 | 0.11 | 56.6 | 0.21 | 58.46 | 0.06 | 1.84 | 0.27 | 98.44 | 0.1 | 58.08 | 0.05 | 0.19 | 0.06 | [24 empty] | 96.38 | 0.08 | 59.23 | 0.06 | 56.95 | 0.05 | 2.3 | 0.08 | [20 empty] | 96.32 | 0.11 | 64.87 | 0.13 | 56.91 | 0.06 | 7.95 | 0.14 | [12 empty] | 97.89 | 0.1 | 56.77 | 0.03 | 57.78 | 0.05 | 1.01 | 0.05 | 98.19 | 0.08 | 57.94 | 0.04 | -0.84 | 0.05 | [12 empty] | 74.31 | 0.02 | 73.59 | 0.03 | 72.04 | 0.03 | 72.15 | 0.03 | 72.48 | 0.04 |  |  | 56.7 | 0.21 |  |  | 57.82 | 0.05 | 67.34 | 0.14 | 60.04 | 0.08 |  |  | 56.47 | 0.04 | 57.16 | 0.06 | 62.18 | 0.08 |  |  | 56.52 | 0.04 | [28 empty] | 74.15 | 0.03 | [8 empty] | 57.1 | 0.04 | 58.28 | 0.04 | [8 empty] | 57.91 | 0.06 | 58.22 | 0.05 | 57.11 | 0.07 | 57.13 | 0.04 | [10 empty] | 60.97 | 0.09 | 55.25 | 0.17 | 55.29 | 0.16 | 75.1 | 0.03 | 75.06 | 0.03 | 75.15 | 0.03 | 75.19 | 0.03 | 75.15 | 0.03 | 75.16 | 0.03 |  |  | 68.88 | 0.07 | 68.4 | 0.07 | 74.88 | 0.04 | 62.57 | 0.13 | 75.29 | 0.04 | 70.66 | 0.08 | 71.58 | 0.13 | 68.24 | 0.13 | 71.99 | 0.2 | 69.95 | 0.06 | 69.56 | 0.08 | 64.89 | 0.14 | 74.83 | 0.05 | 69.48 | 0.07 | 73.22 | 0.11 | 65.74 | 0.09 | [78 empty] | 54.75 | 0.16 | [8 empty] | 73.68 | 0.02 | 73.84 | 0.03 | Economizer test | 75.008 | 0.009 | 61.999 | 0.032 | 73.092 | 0.015 | 60.922 | 0.027 | 54.972 | 0.05 | 50.988 | 0.029 | 2282.2 | 3.3 | 2179.7 | 3.2 | 0.878 | 0.001 | -0.304 | 0.002 | 0.067 | 0.003 | 0.7102 | 0.002 | 29.231 | 0.001 | 1423 | 10 | 1410 |  | 0.012777 | 27.85 | 13.029 | 0.304 | 1.6611 | 10143.1435 | 224.8311 | 27.8498 | 128.2535 | 10014.89 | 0.0087554 | 27.5214 | 71.4309 | 13.0288 | 13.5 | 0.0069815 | 20.7711 | 0.0087781 | 27.6078 | 0.0085283 | 26.8674 | 74.7555 | 61.8739 | 26.4624
3 | C8-EB0-115-CE | 75N0189 | C8-EB0-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 7/2/2015 | 5:31:33 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.8 | 32.1 | 0 | 40779 | 78 | 40641 | 235 | 300 | 165 | 41080 | 143 | 3.909 | 900 | [38 empty] | Baseline no evaporator coil blockage, economizer closed damper, factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 115F OD, 75F DB, 62F WB ID conditions,--unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley--4.5 turns open from full | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:No Evaporator coil blockage. | 74.96 | 0.022 | 62 | 0.024 | 114.995 | 0.014 | 80.008 | 0.025 | 74.79 | 0.06 | 60.12 | 0.07 | 63.55 | 0.03 | 0.088 | 0.003 | 0.8786 | 0.0025 | 40779 | 78 | 300 | 165 | 3.909 | 0.017 | [6 empty] | 230 | 1.5 | 229.5 | 1.5 | 230.1 | 1.5 | 32.1 | 0.1 | 29.5 | 0.1 | 33.2 | 0.1 | 7379.5 | 51.2 | 3835.4 | 71.7 | 3128.2 | 39.6 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.3 |  | 0.63 | 230 |  | 230 |  | 230 |  | 12.1 |  | 12 |  | 11.3 |  | 4040 |  | 0.86 | 230 | 230 | 230 | 12.9 | 12.7 | 11.4 | 4240 | 0.75 | 228.3 |  | 2.3 |  | 517.4 |  | 115 |  | 10472.4 | [22 empty] | 320.8 | 0.39 | 221.7 | 0.07 | 135.93 | 0.1 | 85.76 | 0.07 | [16 empty] | 70.02 | 0.07 | 83.42 | 0.04 | 40.76 | 0.05 | 42.66 | 0.06 | [8 empty] | 308.79 | 0.4 | 125.63 | 0.12 | 132.95 | 0.1 | 7.32 | 0.06 | 305.9 | 0.42 | 132.22 | 0.11 | 6.67 | 0.08 | [24 empty] | 347.12 | 0.43 | 227.22 | 0.08 | 142.2 | 0.1 | 85.02 | 0.04 | [20 empty] | 82.11 | 0.05 | 79.87 | 0.04 | 48.59 | 0.03 | 31.28 | 0.06 | [12 empty] | 336.5 | 0.43 | 124.83 | 0.1 | 139.71 | 0.1 | 14.88 | 0.04 | 333.07 | 0.44 | 138.9 | 0.1 | 13.42 | 0.05 | [12 empty] | 60.66 | 0.06 | 60.07 | 0.09 | 59.78 | 0.09 | 59.08 | 0.09 | 60.18 | 0.08 |  |  | 125.42 | 0.12 |  |  | 76.48 | 0.04 | 81.49 | 0.03 | 221.83 | 0.07 |  |  | 125.47 | 0.1 | 81.35 | 0.08 | 85.59 | 0.07 |  |  | 126.53 | 0.07 | [28 empty] | 60.38 | 0.07 | [8 empty] | 125.48 | 0.09 | 125.56 | 0.1 | [8 empty] | 78.64 | 0.04 | 126.92 | 0.11 | 77.95 | 0.05 | 125.66 | 0.11 | [10 empty] | 221.47 | 0.07 | 115.77 | 0.19 | 116.58 | 0.21 | 75.1 | 0.1 | 75.07 | 0.1 | 75.23 | 0.09 | 75.25 | 0.09 | 75.2 | 0.09 | 75.21 | 0.09 |  |  | 76.99 | 0.12 | 79.72 | 0.2 | 75.01 | 0.09 | 96.64 | 0.39 | 75.79 | 0.09 | 77.46 | 0.12 | 75.53 | 0.09 | 76.57 | 0.14 | 79.35 | 0.22 | 78.3 | 0.1 | 78.46 | 0.17 | 88.86 | 0.21 | 75.11 | 0.09 | 76.93 | 0.11 | 75.61 | 0.1 | 90.76 | 0.34 | [78 empty] | 113.96 | 0.17 |  |  |  |  | closed |  |  |  | 60.35 | 0.08 | 60.15 | 0.07 | C8-55-CE3 | 74.96 | 0.022 | 62 | 0.024 | 60.24 | 0.006 | 56.641 | 0.013 | 114.995 | 0.014 | 80.008 | 0.025 | 2517.5 | 3.5 | 2448.8 | 3.5 | 1.154 | 0.002 | -0.431 | 0.002 | 0.088 | 0.003 | 0.8786 | 0.0025 | 29.213 | 0.001 | 10508 | 22 | 1560 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.523 | 11462.8725 | 331.9894 | 23.5563 | 96.7606 | 11366.1119 | 0.0088322 | 27.7385 | 58.717 | 14.607 | 13.1773 | 0.013776 | 42.9186 | 0.0087901 | 27.6092 | 0.0089156 | 24.1556 | 75.301 | 62.1857 | 23.784 | 45329.3057 | 45624.0889 | 8948 | 0.67373 | 41138.1055 | 41432.8887 | 3.9149 | 0.21838 | -3.9544 | -16.584 | 54.0835 | 45329.3057 | 39588.8822 | 4259.0813 | 1481.3422 | 45329.3057 | 100%
3 | C8-EB10-115-CE | 75N0190 | C8-EB10-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 10 | CUST 3 | 7/2/2015 | 3:51:22 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 32 | 0 | 39826 | 71 | 39640 | 194 | 1080 | 133 | 40908 | 113 | 3.914 | 901 | [38 empty] | 10% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs,--CK2 8.1 lbs) 115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--a | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 7.5" | 74.942 | 0.019 | 62.011 | 0.028 | 115.002 | 0.017 | 79.99 | 0.018 | 74.56 | 0.07 | 59.9 | 0.07 | 63.58 | 0.04 | 0.08 | 0.003 | 0.8351 | 0.0019 | 39826 | 71 | 1080 | 133 | 3.914 | 0.013 | [6 empty] | 229.9 | 1.5 | 229.6 | 1.5 | 230 | 1.5 | 32 | 0.1 | 29.3 | 0.1 | 33.2 | 0.1 | 7360.6 | 51.9 | 3826 | 71.6 | 3090.5 | 41.4 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.1 |  | 0.6 | 230 |  | 230 |  | 230 |  | 12.2 |  | 12 |  | 11.3 |  | 4040 |  | 0.85 | 230 | 230 | 230 | 12.9 | 12.7 | 11.4 | 4220 | 0.75 | 228.3 |  | 2.3 |  | 517.7 |  | 115 |  | 10412.7 | [22 empty] | 320.57 | 0.37 | 220.51 | 0.04 | 135.88 | 0.09 | 84.63 | 0.08 | [16 empty] | 69.52 | 0.08 | 81.68 | 0.03 | 40.43 | 0.05 | 41.25 | 0.06 | [8 empty] | 308.58 | 0.35 | 125.61 | 0.09 | 132.9 | 0.09 | 7.29 | 0.05 | 305.68 | 0.37 | 132.17 | 0.09 | 6.63 | 0.08 | [24 empty] | 345.75 | 0.38 | 224.67 | 0.08 | 141.88 | 0.09 | 82.79 | 0.04 | [20 empty] | 80.96 | 0.05 | 76.33 | 0.05 | 47.88 | 0.03 | 28.44 | 0.06 | [12 empty] | 335.2 | 0.37 | 124.71 | 0.08 | 139.41 | 0.09 | 14.7 | 0.04 | 331.78 | 0.36 | 138.59 | 0.09 | 13.19 | 0.05 | [12 empty] | 60.46 | 0.07 | 60.14 | 0.1 | 59.89 | 0.09 | 59.21 | 0.09 | 60.18 | 0.09 |  |  | 125.43 | 0.1 |  |  | 74.45 | 0.05 | 79.45 | 0.04 | 219.18 | 0.07 |  |  | 125.38 | 0.08 | 77.31 | 0.07 | 82.37 | 0.06 |  |  | 126.33 | 0.07 | [28 empty] | 60.36 | 0.08 | [8 empty] | 125.4 | 0.07 | 125.54 | 0.08 | [8 empty] | 76.63 | 0.05 | 126.86 | 0.09 | 73.58 | 0.1 | 125.64 | 0.08 | [10 empty] | 220.1 | 0.05 | 115.46 | 0.23 | 116.24 | 0.21 | 74.85 | 0.11 | 74.89 | 0.1 | 74.84 | 0.1 | 74.91 | 0.1 | 74.9 | 0.1 | 74.95 | 0.1 |  |  | 79.71 | 0.15 | 83.26 | 0.13 | 75.02 | 0.08 | 96.35 | 0.25 | 75.87 | 0.09 | 81.97 | 0.15 | 76.94 | 0.12 | 77.54 | 0.14 | 79.33 | 0.24 | 83.31 | 0.11 | 83.16 | 0.1 | 85.09 | 0.15 | 75.19 | 0.09 | 82.6 | 0.15 | 76.71 | 0.13 | 88.45 | 0.18 | [78 empty] | 114.01 | 0.18 |  |  |  |  | closed |  |  |  | 60.4 | 0.08 | 60.21 | 0.06 | C8-EB10-55-CE | 74.942 | 0.019 | 62.011 | 0.028 | 60.215 | 0.011 | 56.53 | 0.019 | 115.002 | 0.017 | 79.99 | 0.018 | 2453.5 | 2.8 | 2387.4 | 2.9 | 1.087 | 0.002 | -0.403 | 0.002 | 0.08 | 0.003 | 0.8351 | 0.0019 | 29.224 | 0.001 | 10452 | 20 | 1520 |  | 0.012007 | 28.4581 | 13.029 | 0.373 | 1.5462 | 11172.3979 | 304.8736 | 31.3204 | 128.6527 | 11043.7452 | 0.0088586 | 27.7934 | 58.6688 | 14.607 | 13.1762 | 0.013757 | 42.8989 | 0.0088016 | 27.6174 | 0.0088557 | 24.0842 | 75.4074 | 62.2636 | 23.7071 | 45654.2105 | 44882.5748 | 8932 | 0.66774 | 41506.9841 | 40735.3484 | 3.9712 | 0.22425 | -4.0863 | -16.7386 | 53.8302 | 45654.2105 | 39474.2702 | 4213.9353 | 1966.0049 | 45654.2105 | 100%
3 | C8-EB20-115-CE | 75N0191 | C8-EB20-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 20 | CUST 3 | 7/2/2015 | 2:55:54 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.8 | 32 | 0 | 39333 | 62 | 39243 | 203 | 1554 | 99 | 40888 | 134 | 3.924 | 901 | [38 empty] | .--.--.--. | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 10.5" | 75.003 | 0.013 | 62.001 | 0.018 | 115.002 | 0.016 | 80.003 | 0.022 | 74.63 | 0.05 | 59.83 | 0.08 | 63.42 | 0.01 | 0.064 | 0.004 | 0.8015 | 0.0025 | 39333 | 62 | 1554 | 99 | 3.924 | 0.016 | [6 empty] | 230 | 1.5 | 229.7 | 1.5 | 230.1 | 1.5 | 32 | 0.1 | 29.2 | 0.1 | 33.1 | 0.1 | 7356.4 | 51.8 | 3818.1 | 70.8 | 3064.1 | 41 | 230 |  | 230 |  | 230 |  | 6.1 |  | 6.1 |  | 6.1 |  | 0.61 | 230 |  | 230 |  | 230 |  | 12.2 |  | 12 |  | 11.3 |  | 4040 |  | 0.86 | 230 | 230 | 230 | 12.9 | 12.7 | 11.3 | 4200 | 0.76 | 228.4 |  | 2.3 |  | 518.2 |  | 115 |  | 10363.2 | [22 empty] | 320.24 | 0.33 | 219.46 | 0.05 | 135.8 | 0.08 | 83.67 | 0.08 | [16 empty] | 69.09 | 0.06 | 80.1 | 0.04 | 40.13 | 0.04 | 39.97 | 0.06 | [8 empty] | 308.28 | 0.31 | 125.65 | 0.1 | 132.83 | 0.08 | 7.18 | 0.06 | 305.4 | 0.32 | 132.1 | 0.08 | 6.56 | 0.06 | [24 empty] | 344.93 | 0.4 | 221.62 | 0.07 | 141.69 | 0.09 | 79.93 | 0.09 | [20 empty] | 79.9 | 0.05 | 72.21 | 0.16 | 47.22 | 0.03 | 24.98 | 0.18 | [12 empty] | 334.43 | 0.39 | 124.64 | 0.08 | 139.22 | 0.09 | 14.59 | 0.05 | 331.03 | 0.39 | 138.41 | 0.09 | 13.09 | 0.07 | [12 empty] | 60.55 | 0.07 | 60.18 | 0.11 | 59.74 | 0.1 | 59.07 | 0.11 | 60.12 | 0.1 |  |  | 125.48 | 0.1 |  |  | 72.73 | 0.04 | 77.86 | 0.03 | 216.35 | 0.06 |  |  | 125.29 | 0.08 | 72.85 | 0.16 | 78.69 | 0.11 |  |  | 126.22 | 0.07 | [28 empty] | 60.43 | 0.09 | [8 empty] | 125.32 | 0.07 | 125.54 | 0.08 | [8 empty] | 74.95 | 0.04 | 126.9 | 0.1 | 68.84 | 0.22 | 125.56 | 0.08 | [10 empty] | 219.06 | 0.06 | 115.52 | 0.17 | 116.26 | 0.21 | 74.96 | 0.1 | 74.99 | 0.09 | 74.93 | 0.09 | 75 | 0.09 | 75 | 0.09 | 75.06 | 0.08 |  |  | 80.27 | 0.13 | 83.14 | 0.12 | 75.12 | 0.08 | 95.32 | 0.23 | 75.95 | 0.1 | 82.24 | 0.12 | 77.77 | 0.15 | 79.3 | 0.2 | 79.45 | 0.24 | 82.94 | 0.11 | 82.77 | 0.11 | 84.62 | 0.14 | 75.3 | 0.09 | 82.66 | 0.13 | 77.42 | 0.14 | 88.27 | 0.16 | [78 empty] | 114 | 0.17 |  |  |  |  | closed |  |  |  | 60.46 | 0.09 | 60.23 | 0.08 | C8-EB20-55-CE | 75.003 | 0.013 | 62.001 | 0.018 | 60.171 | 0.009 | 56.403 | 0.01 | 115.002 | 0.016 | 80.003 | 0.022 | 2403 | 3.8 | 2339 | 3.7 | 1.046 | 0.002 | -0.383 | 0.002 | 0.064 | 0.004 | 0.8015 | 0.0025 | 29.222 | 0.001 | 10421 | 21 | 1490 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.5622 | 10943.7856 | 287.4266 | 26.906 | 110.5192 | 10833.2664 | 0.008831 | 27.7639 | 58.6088 | 14.6071 | 13.1746 | 0.01377 | 42.913 | 0.0087806 | 27.6093 | 0.0087909 | 24.003 | 75.4106 | 62.223 | 23.622 | 45327.7354 | 44130.0508 | 8931 | 0.67247 | 41223.3525 | 40025.6679 | 3.9558 | 0.22964 | -4.1419 | -16.8018 | 53.6003 | 45327.7354 | 39466.4705 | 4169.9109 | 1691.354 | 45327.7354 | 100%
3 | C8-EB35-115-CE | 75N0192 | C8-EB35-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 35 | CUST 3 | 7/2/2015 | 1:53:07 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230.1 | 1.9 | 31.9 | 0 | 38039 | 68 | 38014 | 213 | 2446 | 176 | 40488 | 170 | 3.91 | 902 | [38 empty] | 35% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%:--Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--a | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 16.25" | 75.008 | 0.019 | 61.988 | 0.033 | 114.995 | 0.026 | 79.946 | 0.019 | 74.62 | 0.06 | 59.67 | 0.08 | 63.73 | 0.04 | 0.056 | 0.003 | 0.7343 | 0.0019 | 38039 | 68 | 2446 | 176 | 3.91 | 0.019 | [6 empty] | 230.1 | 1.7 | 229.8 | 1.7 | 230.2 | 1.7 | 31.9 | 0.1 | 29.1 | 0.1 | 32.9 | 0.1 | 7327.9 | 59.3 | 3822.9 | 80.4 | 3027 | 45.9 | 230 |  | 230 |  | 230 |  | 6.1 |  | 6.1 |  | 6 |  | 0.61 | 230 |  | 230 |  | 230 |  | 12.1 |  | 11.9 |  | 11.3 |  | 4040 |  | 0.86 | 230 | 230 | 230 | 12.9 | 12.6 | 11.3 | 4180 | 0.75 | 228.5 |  | 2.3 |  | 518.3 |  | 115 |  | 10303.3 | [22 empty] | 319.6 | 0.34 | 218.16 | 0.07 | 135.64 | 0.08 | 82.52 | 0.07 | [16 empty] | 68.21 | 0.05 | 77.36 | 0.05 | 39.52 | 0.04 | 37.85 | 0.06 | [8 empty] | 307.71 | 0.33 | 125.9 | 0.11 | 132.68 | 0.08 | 6.77 | 0.05 | 304.85 | 0.33 | 131.96 | 0.08 | 6.24 | 0.07 | [24 empty] | 343.66 | 0.37 | 216.19 | 0.1 | 141.39 | 0.09 | 74.8 | 0.08 | [20 empty] | 77.97 | 0.04 | 65.1 | 0.16 | 46 | 0.03 | 19.09 | 0.17 | [12 empty] | 333.28 | 0.35 | 124.58 | 0.08 | 138.95 | 0.08 | 14.37 | 0.03 | 329.89 | 0.36 | 138.14 | 0.09 | 12.86 | 0.05 | [12 empty] | 60.46 | 0.06 | 60.03 | 0.07 | 59.55 | 0.07 | 58.87 | 0.09 | 60.05 | 0.07 |  |  | 125.73 | 0.1 |  |  | 70.04 | 0.04 | 75.5 | 0.04 | 211.17 | 0.08 |  |  | 125.27 | 0.09 | 57.31 | 0.37 | 71.21 | 0.13 |  |  | 126.12 | 0.07 | [28 empty] | 60.35 | 0.06 | [8 empty] | 125.28 | 0.08 | 125.72 | 0.08 | [8 empty] | 72.08 | 0.03 | 127.18 | 0.11 | 51.24 | 0.12 | 125.55 | 0.08 | [10 empty] | 217.74 | 0.08 | 115.44 | 0.19 | 116.22 | 0.16 | 74.92 | 0.07 | 74.96 | 0.07 | 74.86 | 0.08 | 74.93 | 0.08 | 74.95 | 0.07 | 75.01 | 0.06 |  |  | 80.05 | 0.12 | 82.53 | 0.1 | 75.48 | 0.09 | 95 | 0.26 | 75.93 | 0.08 | 82.03 | 0.12 | 79.74 | 0.15 | 82.07 | 0.19 | 83.32 | 0.31 | 82.48 | 0.1 | 82.09 | 0.11 | 84.44 | 0.15 | 75.28 | 0.08 | 82.22 | 0.13 | 78.46 | 0.16 | 87.65 | 0.29 | [78 empty] | 113.89 | 0.19 |  |  |  |  | closed |  |  |  | 60.4 | 0.06 | 60.17 | 0.05 | C8-EB35-55-CE | 75.008 | 0.019 | 61.988 | 0.033 | 60.04 | 0.013 | 56.182 | 0.015 | 114.995 | 0.026 | 79.946 | 0.019 | 2300.7 | 3 | 2236.9 | 2.9 | 0.947 | 0.001 | -0.345 | 0.002 | 0.056 | 0.003 | 0.7343 | 0.0019 | 29.202 | 0.001 | 10355 | 20 | 1450 |  | 0.00909 | 20.4271 | 13.029 | 0.333 | 1.6292 | 10481.1492 | 248.8638 | 22.0145 | 90.4309 | 10390.7184 | 0.0088135 | 27.7315 | 58.4108 | 14.6064 | 13.1705 | 0.013716 | 42.8513 | 0.0087708 | 27.5999 | 0.0086915 | 23.863 | 75.3561 | 62.1771 | 23.4657 | 44710.497 | 42625.5173 | 8905 | 0.67977 | 40611.019 | 38526.0393 | 3.9219 | 0.23456 | -4.2658 | -16.9453 | 53.2182 | 44710.497 | 39167.1194 | 4164.174 | 1379.2036 | 44710.497 | 100%
3 | C8-EB5-115-CE | 75N0193 | C8-EB5-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 5 | CUST 3 | 7/2/2015 | 4:49:53 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.8 | 32.1 | 0 | 40195 | 73 | 40174 | 193 | 621 | 132 | 40816 | 131 | 3.896 | 901 | [38 empty] | 5% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs,--CK2 8.1 lbs) 115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open--from fully closed, ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 5.5" | 74.983 | 0.016 | 62.001 | 0.019 | 114.999 | 0.027 | 80.005 | 0.035 | 74.72 | 0.06 | 60.01 | 0.06 | 63.5 | 0.01 | 0.079 | 0.003 | 0.8523 | 0.0024 | 40195 | 73 | 621 | 132 | 3.896 | 0.017 | [6 empty] | 230 | 1.5 | 229.6 | 1.5 | 230.1 | 1.5 | 32.1 | 0.1 | 29.4 | 0.1 | 33.2 | 0.1 | 7366.3 | 52.5 | 3835.8 | 73 | 3110.4 | 41.5 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.1 |  | 0.62 | 230 |  | 230 |  | 230 |  | 12.1 |  | 11.9 |  | 11.3 |  | 4040 |  | 0.86 | 230 | 230 | 230 | 12.9 | 12.6 | 12.3 | 4220 | 0.75 | 228.3 |  | 2.3 |  | 517.5 |  | 115 |  | 10432.5 | [22 empty] | 320.5 | 0.44 | 220.79 | 0.07 | 135.86 | 0.11 | 84.93 | 0.08 | [16 empty] | 69.58 | 0.07 | 82.03 | 0.03 | 40.47 | 0.05 | 41.56 | 0.05 | [8 empty] | 308.49 | 0.45 | 125.66 | 0.12 | 132.88 | 0.11 | 7.22 | 0.06 | 305.65 | 0.44 | 132.16 | 0.11 | 6.59 | 0.08 | [24 empty] | 346.4 | 0.47 | 225.62 | 0.08 | 142.04 | 0.11 | 83.59 | 0.05 | [20 empty] | 81.44 | 0.07 | 77.63 | 0.03 | 48.19 | 0.04 | 29.44 | 0.06 | [12 empty] | 335.86 | 0.48 | 124.76 | 0.1 | 139.56 | 0.11 | 14.8 | 0.04 | 332.4 | 0.46 | 138.74 | 0.11 | 13.3 | 0.05 | [12 empty] | 60.5 | 0.08 | 60.12 | 0.12 | 59.96 | 0.11 | 59.31 | 0.11 | 60.27 | 0.11 |  |  | 125.47 | 0.12 |  |  | 74.88 | 0.04 | 79.87 | 0.04 | 220.17 | 0.09 |  |  | 125.38 | 0.1 | 78.58 | 0.06 | 83.28 | 0.06 |  |  | 126.37 | 0.08 | [28 empty] | 60.36 | 0.09 | [8 empty] | 125.44 | 0.09 | 125.57 | 0.09 | [8 empty] | 77.08 | 0.04 | 126.88 | 0.12 | 75.3 | 0.06 | 125.62 | 0.1 | [10 empty] | 220.4 | 0.09 | 115.5 | 0.2 | 116.29 | 0.21 | 74.99 | 0.09 | 75.01 | 0.09 | 74.99 | 0.08 | 75.06 | 0.08 | 75.05 | 0.08 | 75.1 | 0.08 |  |  | 78.45 | 0.19 | 83.05 | 0.15 | 75.12 | 0.09 | 97.7 | 0.36 | 75.96 | 0.1 | 80.52 | 0.29 | 76.37 | 0.12 | 76.89 | 0.15 | 79.86 | 0.24 | 82.6 | 0.19 | 82.89 | 0.13 | 85.37 | 0.17 | 75.27 | 0.1 | 81.49 | 0.25 | 76.01 | 0.12 | 88.83 | 0.25 | [78 empty] | 114.04 | 0.23 |  |  |  |  | closed |  |  |  | 60.39 | 0.1 | 60.19 | 0.08 | C8-EB5-55-CE-2 | 74.983 | 0.016 | 62.001 | 0.019 | 60.264 | 0.007 | 56.592 | 0.006 | 114.999 | 0.027 | 80.005 | 0.035 | 2478.6 | 3.5 | 2412.3 | 3.4 | 1.118 | 0.001 | -0.413 | 0.002 | 0.079 | 0.003 | 0.8523 | 0.0024 | 29.226 | 0.001 | 10477 | 23 | 1540 |  | 0.0040955 | 9.8554 | 13.029 | 0.399 | 1.5409 | 11285.4622 | 316.8387 | 10.6167 | 43.6092 | 11241.853 | 0.0088046 | 27.6688 | 58.7231 | 14.607 | 13.1777 | 0.013772 | 42.9152 | 0.0087853 | 27.6096 | 0.0088809 | 24.1236 | 75.139 | 62.0861 | 23.7477 | 44250.8614 | 44462.6013 | 8937 | 0.6893 | 40076.2119 | 40287.9517 | 3.8252 | 0.22433 | -3.921 | -16.4159 | 53.9755 | 44250.8614 | 39341.4013 | 4241.9941 | 667.466 | 44250.8614 | 100%
3 | C8-EB50-115-CE | 75N0194 | C8-EB50-115-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 50 | CUST 3 | 7/2/2015 | 1:10:13 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 115 | 80 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.7 | 31.7 | 0 | 36473 | 61 | 36373 | 197 | 3423 | 84 | 39899 | 104 | 3.881 | 902 | [38 empty] | 50% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--115F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--a | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 21" | 75.02 | 0.012 | 62.015 | 0.025 | 115 | 0.023 | 80.117 | 0.044 | 74.6 | 0.05 | 59.61 | 0.07 | 63.61 | 0.03 | 0.051 | 0.003 | 0.6671 | 0.0022 | 36473 | 61 | 3423 | 84 | 3.881 | 0.011 | [6 empty] | 230 | 1.3 | 229.6 | 1.3 | 230 | 1.3 | 31.7 | 0.1 | 28.9 | 0.1 | 32.7 | 0.1 | 7295.1 | 45.1 | 3806.4 | 61.4 | 2984.5 | 35.4 | 230 |  | 230 |  | 230 |  | 6 |  | 5.9 |  | 6 |  | 0.57 | 230 |  | 230 |  | 230 |  | 12.1 |  | 11.9 |  | 11.3 |  | 4010 |  | 0.86 | 230 | 230 | 230 | 12.9 | 12.5 | 11.2 | 4160 | 0.75 | 228.4 |  | 2.3 |  | 518.1 |  | 115 |  | 10223.1 | [22 empty] | 318.55 | 0.37 | 216.88 | 0.07 | 135.38 | 0.09 | 81.5 | 0.07 | [16 empty] | 67.2 | 0.06 | 74.83 | 0.04 | 38.82 | 0.04 | 36.01 | 0.05 | [8 empty] | 306.72 | 0.37 | 126.22 | 0.11 | 132.43 | 0.09 | 6.21 | 0.05 | 303.89 | 0.4 | 131.71 | 0.1 | 5.84 | 0.07 | [24 empty] | 341.57 | 0.44 | 210.92 | 0.1 | 140.91 | 0.1 | 70.01 | 0.1 | [20 empty] | 75.85 | 0.06 | 51.6 | 0.44 | 44.64 | 0.04 | 6.97 | 0.46 | [12 empty] | 331.32 | 0.43 | 124.52 | 0.09 | 138.48 | 0.1 | 13.95 | 0.03 | 327.95 | 0.42 | 137.67 | 0.1 | 12.45 | 0.05 | [12 empty] | 60.47 | 0.06 | 60.13 | 0.09 | 59.4 | 0.08 | 58.72 | 0.09 | 59.95 | 0.08 |  |  | 126 | 0.11 |  |  | 67.58 | 0.03 | 73.21 | 0.04 | 206.17 | 0.09 |  |  | 125.2 | 0.08 | 55 | 0.36 | 59.29 | 0.1 |  |  | 126.03 | 0.07 | [28 empty] | 60.4 | 0.08 | [8 empty] | 125.22 | 0.09 | 125.87 | 0.09 | [8 empty] | 69.5 | 0.05 | 127.45 | 0.1 | 49.11 | 0.07 | 125.47 | 0.08 | [10 empty] | 216.48 | 0.08 | 115.46 | 0.19 | 116.19 | 0.18 | 74.89 | 0.09 | 74.92 | 0.08 | 74.83 | 0.09 | 74.89 | 0.09 | 74.92 | 0.08 | 74.99 | 0.08 |  |  | 80.41 | 0.2 | 80.73 | 0.12 | 79.07 | 0.23 | 88.52 | 0.27 | 76.21 | 0.08 | 81.44 | 0.18 | 78.32 | 0.18 | 83.76 | 0.11 | 93.78 | 0.24 | 80.88 | 0.23 | 77.21 | 0.13 | 81.02 | 0.13 | 75.29 | 0.08 | 81.73 | 0.15 | 79.19 | 0.14 | 81.42 | 0.13 | [78 empty] | 113.94 | 0.2 |  |  |  |  | closed |  |  |  | 60.46 | 0.07 | 60.23 | 0.06 | C8-EB50-55-CE | 75.02 | 0.012 | 62.015 | 0.025 | 59.995 | 0.016 | 56.003 | 0.027 | 115 | 0.023 | 80.117 | 0.044 | 2191.5 | 3.5 | 2132 | 3.5 | 0.842 | 0.002 | -0.307 | 0.002 | 0.051 | 0.003 | 0.6671 | 0.0022 | 29.208 | 0.001 | 10280 | 18 | 1420 |  | 0.012777 | 27.85 | 13.029 | 0.304 | 1.7215 | 9985.0994 | 210.8941 | 29.6345 | 121.7191 | 9863.3803 | 0.0088479 | 27.8071 | 58.2735 | 14.608 | 13.1686 | 0.013881 | 43.037 | 0.0087858 | 27.6192 | 0.0085969 | 23.7492 | 75.5118 | 62.2846 | 23.3294 | 44710.134 | 41310.3571 | 8860 | 0.67634 | 40583.4555 | 37183.6786 | 3.9478 | 0.24123 | -4.4777 | -17.2383 | 52.7932 | 44710.134 | 38642.4123 | 4191.0823 | 1876.6394 | 44710.134 | 100%
3 | C8-EB0-82-CE | 75N0201 | C8-EB0-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 7/1/2015 | 17:05:18 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.6 | 25.4 | 0 | 49317 | 80 | 49116 | 294 | 11596 | 145 | 60923 | 177 | 7.993 | 900 | [38 empty] | Baseline no evaporator coil blockage, economizer closed damper, factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: Condenser coil blockage. | 74.989 | 0.012 | 62.001 | 0.031 | 81.982 | 0.012 | 68.004 | 0.018 | 74.64 | 0.08 | 57.28 | 0.11 | 61.41 | 0.02 | 0.183 | 0.004 | 0.9016 | 0.0024 | 49317 | 80 | 11596 | 145 | 7.993 | 0.031 | [6 empty] | 229.8 | 1.1 | 229.6 | 1.1 | 230.1 | 1.1 | 25.4 | 0.1 | 23.3 | 0.1 | 27 | 0.1 | 5806.3 | 44.1 | 3639.9 | 61.5 | 1815.4 | 33.4 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.2 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 9.2 |  | 9 |  | 8.4 |  | 2680 |  | 0.76 | 230 | 230 | 230 | 9.3 | 9.4 | 8.2 | 2730 | 0.68 | 228.3 |  | 2.4 |  | 530.6 |  | 115 |  | 7625.6 | [22 empty] | 206.53 | 0.16 | 179.35 | 0.04 | 103.49 | 0.05 | 75.86 | 0.06 | [16 empty] | 56.26 | 0.05 | 76.06 | 0.04 | 30.75 | 0.04 | 45.31 | 0.06 | [8 empty] | 194.88 | 0.14 | 88.04 | 0.06 | 99.53 | 0.05 | 11.49 | 0.06 | 192.59 | 0.15 | 98.72 | 0.05 | 10.05 | 0.06 | [24 empty] | 221.53 | 0.22 | 182.77 | 0.04 | 108.37 | 0.07 | 74.4 | 0.06 | [20 empty] | 63.85 | 0.05 | 71.96 | 0.04 | 36.44 | 0.04 | 35.53 | 0.06 | [12 empty] | 211.53 | 0.23 | 88.96 | 0.05 | 105.14 | 0.08 | 16.18 | 0.05 | 208.97 | 0.19 | 104.3 | 0.06 | 14.7 | 0.05 | [12 empty] | 58.22 | 0.04 | 57.61 | 0.04 | 56.87 | 0.04 | 56.57 | 0.05 | 57.18 | 0.04 |  |  | 88.01 | 0.06 |  |  | 72.7 | 0.05 | 75.43 | 0.04 | 177.84 | 0.05 |  |  | 89.59 | 0.06 | 72.63 | 0.06 | 75.93 | 0.05 |  |  | 91.05 | 0.05 | [28 empty] | 58.04 | 0.03 | [8 empty] | 89.6 | 0.05 | 88.68 | 0.05 | [8 empty] | 73.79 | 0.06 | 89.11 | 0.06 | 71.02 | 0.07 | 89.72 | 0.06 | [10 empty] | 178.87 | 0.04 | 82.47 | 0.15 | 83.15 | 0.11 | 75.05 | 0.07 | 75.04 | 0.07 | 75.12 | 0.08 | 75.17 | 0.08 | 75.14 | 0.07 | 75.14 | 0.06 |  |  | 75.69 | 0.05 | 75.81 | 0.05 | 74.94 | 0.06 | 78.52 | 0.07 | 75.55 | 0.06 | 75.83 | 0.06 | 75.2 | 0.07 | 75.09 | 0.07 | 75.85 | 0.07 | 76.4 | 0.05 | 76.18 | 0.06 | 76.63 | 0.06 | 74.94 | 0.07 | 75.87 | 0.05 | 75.21 | 0.06 | 77.73 | 0.06 | [78 empty] | 81.2 | 0.08 | [8 empty] | 57.86 | 0.03 | 57.79 | 0.04 | C8-55-CE3 | 74.989 | 0.012 | 62.001 | 0.031 | 57.562 | 0.016 | 53.938 | 0.022 | 81.982 | 0.012 | 68.004 | 0.018 | 2544.7 | 3.5 | 2488.9 | 3.4 | 1.158 | 0.002 | -0.427 | 0.002 | 0.183 | 0.004 | 0.9016 | 0.0024 | 29.203 | 0.001 | 7622 | 18 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.5023 | 11653.1596 | 338.5954 | 22.747 | 99.2729 | 11553.8867 | 0.0088057 | 27.648 | 56.0597 | 13.7482 | 13.1022 | 0.011351 | 32.1319 | 0.0087839 | 27.6095 | 0.0079849 | 22.491 | 75.0488 | 62.0556 | 22.1251 | 64359.9277 | 53108.0429 | 6052 | 0.32094 | 60157.144 | 48905.2592 | 7.8926 | 0.2346 | -5.523 | -18.9891 | 50.2394 | 64359.9277 | 59647.3634 | 4263.6182 | 448.9461 | 64359.9277 | 100%
3 | C8-EB10-82-CE | 75N0202 | C8-EB10-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 10 | CUST 3 | 7/1/2015 | 19:29:54 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.7 | 25.4 | 0 | 48148 | 79 | 48044 | 195 | 12052 | 130 | 60212 | 143 | 7.954 | 900 | [38 empty] | 10% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs,--CK2 8.1 lbs) 82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam--set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 7.5" | 75.008 | 0.012 | 62.005 | 0.025 | 81.991 | 0.013 | 67.999 | 0.027 | 74.62 | 0.06 | 57.15 | 0.06 | 61.39 | 0.02 | 0.074 | 0.003 | 0.8498 | 0.0023 | 48148 | 79 | 12052 | 130 | 7.954 | 0.027 | [6 empty] | 229.9 | 1.3 | 229.7 | 1.3 | 230.2 | 1.3 | 25.4 | 0.1 | 23.2 | 0.1 | 26.9 | 0.1 | 5794.1 | 50.8 | 3637.1 | 68.8 | 1776.7 | 36.8 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.1 |  | 0.63 | 230 |  | 230 |  | 230 |  | 9.1 |  | 9.1 |  | 8.4 |  | 2670 |  | 0.77 | 230 | 230 | 230 | 9.4 | 9.3 | 9.2 | 2720 | 0.67 | 228.4 |  | 2.4 |  | 530.7 |  | 115 |  | 7565.7 | [22 empty] | 205.93 | 0.18 | 177.62 | 0.04 | 103.29 | 0.06 | 74.33 | 0.06 | [16 empty] | 55.58 | 0.05 | 73.66 | 0.03 | 30.22 | 0.04 | 43.44 | 0.05 | [8 empty] | 194.33 | 0.17 | 88.07 | 0.06 | 99.33 | 0.06 | 11.26 | 0.04 | 192.08 | 0.18 | 98.55 | 0.06 | 9.95 | 0.06 | [24 empty] | 220.62 | 0.19 | 180.45 | 0.05 | 108.08 | 0.06 | 72.37 | 0.04 | [20 empty] | 62.96 | 0.04 | 68.82 | 0.03 | 35.79 | 0.03 | 33.03 | 0.04 | [12 empty] | 210.68 | 0.19 | 88.82 | 0.06 | 104.86 | 0.06 | 16.04 | 0.04 | 208.14 | 0.2 | 104.02 | 0.07 | 14.59 | 0.05 | [12 empty] | 58.5 | 0.04 | 57.77 | 0.04 | 56.51 | 0.04 | 56.2 | 0.03 | 56.9 | 0.04 |  |  | 88.05 | 0.05 |  |  | 70.05 | 0.03 | 72.93 | 0.02 | 175.67 | 0.04 |  |  | 89.56 | 0.05 | 69.52 | 0.04 | 73.73 | 0.02 |  |  | 90.96 | 0.05 | [28 empty] | 58.27 | 0.03 | [8 empty] | 89.43 | 0.05 | 88.6 | 0.05 | [8 empty] | 71.25 | 0.03 | 89.07 | 0.06 | 67.72 | 0.03 | 89.72 | 0.05 | [10 empty] | 177.16 | 0.03 | 82.41 | 0.13 | 83.15 | 0.13 | 75.09 | 0.07 | 75.09 | 0.06 | 75.13 | 0.06 | 75.19 | 0.06 | 75.16 | 0.06 | 75.18 | 0.06 |  |  | 75.32 | 0.05 | 76.03 | 0.05 | 75.01 | 0.06 | 77.46 | 0.09 | 75.49 | 0.04 | 75.89 | 0.06 | 75.28 | 0.07 | 75.12 | 0.06 | 75.63 | 0.06 | 76.38 | 0.05 | 76.16 | 0.05 | 76.44 | 0.06 | 75.01 | 0.06 | 75.87 | 0.06 | 75.19 | 0.07 | 77.91 | 0.06 | [78 empty] | 81.09 | 0.09 | [8 empty] | 58.19 | 0.04 | 58 | 0.03 | C8-EB10-55-CE | 75.008 | 0.012 | 62.005 | 0.025 | 57.499 | 0.013 | 53.785 | 0.017 | 81.991 | 0.013 | 67.999 | 0.027 | 2470.5 | 3.4 | 2415.5 | 3.3 | 1.104 | 0.002 | -0.401 | 0.002 | 0.074 | 0.003 | 0.8498 | 0.0023 | 29.197 | 0.001 | 7570 | 20 | 1530 |  | 0.012007 | 28.4581 | 13.029 | 0.373 | 1.5287 | 11315.2266 | 313.2862 | 30.3105 | 132.2796 | 11182.947 | 0.008812 | 27.6649 | 55.9703 | 13.7484 | 13.1 | 0.011345 | 32.1276 | 0.008782 | 27.6121 | 0.0079138 | 22.3983 | 75.09 | 62.0798 | 22.0261 | 63804.7828 | 51922.5325 | 6040 | 0.32309 | 59652.1384 | 47769.8882 | 7.8801 | 0.2417 | -5.6388 | -19.1197 | 49.8762 | 63804.7828 | 58995.2715 | 4212.2067 | 597.3046 | 63804.7828 | 100%
3 | C8-EB20-82-CE | 75N0203 | C8-EB20-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 20 | CUST 3 | 7/1/2015 | 20:29:06 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.3 | 25.3 | 0 | 47509 | 80 | 47368 | 191 | 12206 | 175 | 59728 | 223 | 7.916 | 901 | [38 empty] | 20% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs,--CK2 8.1 lbs) 82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns--open from fully closed, ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 10.5 | 75.022 | 0.01 | 62 | 0.034 | 81.992 | 0.012 | 67.99 | 0.023 | 74.76 | 0.09 | 57.23 | 0.1 | 61.41 | 0.02 | 0.078 | 0.004 | 0.8198 | 0.0026 | 47509 | 80 | 12206 | 175 | 7.916 | 0.035 | [6 empty] | 229.8 | 1.1 | 229.5 | 1.1 | 230.1 | 1.1 | 25.3 | 0.1 | 23.2 | 0.1 | 26.8 | 0.1 | 5775.4 | 46.4 | 3633.7 | 60.4 | 1770 | 35.2 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.1 |  | 0.63 | 230 |  | 230 |  | 230 |  | 9.2 |  | 9 |  | 8.4 |  | 2660 |  | 0.77 | 230 | 230 | 230 | 9.4 | 9.3 | 9.2 | 2720 | 0.67 | 228.3 |  | 2.4 |  | 530.2 |  | 115 |  | 7545.2 | [22 empty] | 205.55 | 0.2 | 176.33 | 0.04 | 103.16 | 0.07 | 73.17 | 0.06 | [16 empty] | 55.13 | 0.05 | 71.93 | 0.04 | 29.86 | 0.04 | 42.06 | 0.05 | [8 empty] | 194.01 | 0.2 | 88.14 | 0.06 | 99.22 | 0.07 | 11.08 | 0.07 | 191.77 | 0.21 | 98.44 | 0.07 | 9.85 | 0.07 | [24 empty] | 219.91 | 0.21 | 178.33 | 0.04 | 107.85 | 0.07 | 70.48 | 0.05 | [20 empty] | 62.22 | 0.04 | 65.99 | 0.04 | 35.25 | 0.03 | 30.73 | 0.05 | [12 empty] | 210.03 | 0.23 | 88.85 | 0.05 | 104.65 | 0.08 | 15.8 | 0.05 | 207.51 | 0.19 | 103.81 | 0.06 | 14.37 | 0.06 | [12 empty] | 58.44 | 0.03 | 57.09 | 0.04 | 56.16 | 0.03 | 56.07 | 0.05 | 57.14 | 0.04 |  |  | 88.11 | 0.06 |  |  | 68.11 | 0.04 | 71.19 | 0.04 | 173.78 | 0.05 |  |  | 89.61 | 0.05 | 66.89 | 0.06 | 71.31 | 0.03 |  |  | 91.01 | 0.05 | [28 empty] | 58.3 | 0.03 | [8 empty] | 89.44 | 0.05 | 88.59 | 0.05 | [8 empty] | 69.36 | 0.04 | 89.18 | 0.06 | 64.97 | 0.07 | 89.71 | 0.06 | [10 empty] | 176 | 0.04 | 82.58 | 0.14 | 83.23 | 0.13 | 75.23 | 0.06 | 75.2 | 0.06 | 75.32 | 0.07 | 75.35 | 0.07 | 75.3 | 0.06 | 75.31 | 0.06 |  |  | 75.48 | 0.05 | 76.08 | 0.05 | 75.12 | 0.05 | 77.96 | 0.08 | 75.55 | 0.04 | 76.04 | 0.06 | 75.38 | 0.07 | 75.27 | 0.06 | 75.76 | 0.06 | 76.41 | 0.05 | 76.11 | 0.04 | 76.1 | 0.06 | 75.06 | 0.06 | 76.06 | 0.05 | 75.35 | 0.06 | 77.97 | 0.06 | [78 empty] | 81.19 | 0.08 | [8 empty] | 57.93 | 0.03 | 58.17 | 0.03 | C8-EB20-55-CE | 75.022 | 0.01 | 62 | 0.034 | 57.444 | 0.014 | 53.691 | 0.019 | 81.992 | 0.012 | 67.99 | 0.023 | 2426 | 3.8 | 2372.6 | 3.7 | 1.062 | 0.002 | -0.385 | 0.003 | 0.078 | 0.004 | 0.8198 | 0.0026 | 29.203 | 0 | 7546 | 19 | 1520 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.5658 | 11112.8553 | 296.0153 | 26.1712 | 114.2156 | 10998.6397 | 0.0088018 | 27.6547 | 55.8782 | 13.7483 | 13.0983 | 0.011338 | 32.1202 | 0.0087754 | 27.6083 | 0.0078741 | 22.3418 | 75.094 | 62.0657 | 21.9605 | 63278.7118 | 51250.2025 | 6026 | 0.32502 | 59101.252 | 47072.7427 | 7.8321 | 0.2434 | -5.6942 | -19.2158 | 49.6965 | 63278.7118 | 58526.3169 | 4237.0712 | 515.3238 | 63278.7118 | 100%
3 | C8-EB35-82-CE | 75N0204 | C8-EB35-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 35 | CUST 3 | 7/1/2015 | 21:46:15 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.5 | 25.3 | 0 | 46580 | 99 | 46425 | 213 | 12952 | 91 | 59542 | 108 | 7.954 | 902 | [38 empty] | 35% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @--75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed,--ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 16.25" | 74.941 | 0.023 | 61.997 | 0.016 | 81.993 | 0.016 | 67.998 | 0.017 | 74.4 | 0.06 | 56.53 | 0.06 | 61.09 | 0.02 | 0.063 | 0.003 | 0.7546 | 0.0024 | 46580 | 99 | 12952 | 91 | 7.954 | 0.023 | [6 empty] | 230 | 1.1 | 229.7 | 1.1 | 230.1 | 1.1 | 25.3 | 0.1 | 23.1 | 0.1 | 26.6 | 0.1 | 5782.9 | 45.8 | 3612.2 | 61.6 | 1703.3 | 33.8 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.1 |  | 6.2 |  | 0.6 | 230 |  | 230 |  | 230 |  | 9.1 |  | 9 |  | 8.3 |  | 2660 |  | 0.76 | 230 | 230 | 230 | 9.4 | 9.2 | 8.1 | 2710 | 0.67 | 228.5 |  | 2.4 |  | 530.8 |  | 115 |  | 7465.8 | [22 empty] | 204.94 | 0.15 | 174.72 | 0.04 | 102.96 | 0.05 | 71.77 | 0.06 | [16 empty] | 54.51 | 0.04 | 69.75 | 0.03 | 29.37 | 0.03 | 40.37 | 0.05 | [8 empty] | 193.44 | 0.14 | 87.95 | 0.05 | 99.02 | 0.05 | 11.07 | 0.03 | 191.21 | 0.14 | 98.24 | 0.05 | 9.72 | 0.06 | [24 empty] | 218.93 | 0.18 | 176.29 | 0.05 | 107.54 | 0.06 | 68.75 | 0.06 | [20 empty] | 61.43 | 0.05 | 63.22 | 0.03 | 34.67 | 0.04 | 28.55 | 0.06 | [12 empty] | 209.12 | 0.16 | 88.64 | 0.05 | 104.35 | 0.05 | 15.71 | 0.05 | 206.62 | 0.17 | 103.52 | 0.06 | 14.25 | 0.06 | [12 empty] | 57.8 | 0.03 | 56.62 | 0.04 | 56.04 | 0.04 | 55.83 | 0.04 | 56.66 | 0.03 |  |  | 87.97 | 0.04 |  |  | 65.53 | 0.03 | 68.77 | 0.03 | 171.65 | 0.05 |  |  | 89.51 | 0.05 | 64.02 | 0.04 | 68.9 | 0.06 |  |  | 90.8 | 0.04 | [28 empty] | 57.83 | 0.03 | [8 empty] | 89.27 | 0.05 | 88.53 | 0.04 | [8 empty] | 66.84 | 0.03 | 89.07 | 0.05 | 61.87 | 0.04 | 89.69 | 0.04 | [10 empty] | 174.24 | 0.05 | 82.12 | 0.13 | 82.85 | 0.13 | 74.88 | 0.07 | 74.96 | 0.06 | 74.79 | 0.07 | 74.87 | 0.07 | 74.88 | 0.07 | 74.94 | 0.06 |  |  | 75.02 | 0.06 | 75.96 | 0.05 | 75.04 | 0.06 | 78.5 | 0.09 | 75.69 | 0.07 | 76.08 | 0.07 | 75.63 | 0.07 | 75.73 | 0.07 | 76.03 | 0.09 | 76.31 | 0.07 | 76.16 | 0.06 | 76.68 | 0.07 | 75.08 | 0.08 | 76.03 | 0.05 | 75.29 | 0.07 | 76.82 | 0.05 | [78 empty] | 81.25 | 0.07 | [8 empty] | 57.54 | 0.03 | 57.75 | 0.03 | C8-EB35-55-CE | 74.941 | 0.023 | 61.997 | 0.016 | 57.013 | 0.012 | 53.336 | 0.013 | 81.993 | 0.016 | 67.998 | 0.017 | 2325.7 | 3.8 | 2276.8 | 3.7 | 0.97 | 0.001 | -0.35 | 0.002 | 0.063 | 0.003 | 0.7546 | 0.0024 | 29.212 | 0.001 | 7486 | 18 | 1450 |  | 0.00909 | 20.4271 | 13.029 | 0.333 | 1.5873 | 10662.9077 | 259.4548 | 21.5124 | 93.883 | 10569.0247 | 0.008815 | 27.6471 | 55.4257 | 13.7484 | 13.0867 | 0.011344 | 32.1267 | 0.0087926 | 27.6073 | 0.0077775 | 22.1319 | 75.0034 | 62.0534 | 21.7455 | 62928.4504 | 50101.2728 | 6036 | 0.32737 | 58865.1197 | 46037.942 | 7.8634 | 0.23953 | -5.9016 | -19.5777 | 49.2592 | 62928.4504 | 58383.5672 | 4120.588 | 424.2952 | 62928.4504 | 100%
3 | C8-EB5-82-CE | 75N0205 | C8-EB5-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 5 | CUST 3 | 7/1/2015 | 18:13:35 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.5 | 25.4 | 0 | 48856 | 88 | 48583 | 264 | 11831 | 98 | 60697 | 109 | 7.991 | 900 | [38 empty] | 5% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%:--Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch: evaporator coil block 5" | 75.039 | 0.01 | 62.003 | 0.018 | 81.991 | 0.011 | 68.001 | 0.023 | 74.62 | 0.07 | 57.18 | 0.08 | 61.36 | 0.03 | 0.161 | 0.005 | 0.8728 | 0.0028 | 48856 | 88 | 11831 | 98 | 7.991 | 0.023 | [6 empty] | 229.9 | 1 | 229.7 | 1 | 230.2 | 1 | 25.4 | 0.1 | 23.2 | 0.1 | 27 | 0.1 | 5806.2 | 39.5 | 3636.8 | 54.3 | 1788.9 | 29.4 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 9.1 |  | 9.1 |  | 8.4 |  | 2670 |  | 0.75 | 230 | 230 | 230 | 9.4 | 9.4 | 8.2 | 2740 | 0.68 | 228.5 |  | 2.4 |  | 530.9 |  | 115 |  | 7595.9 | [22 empty] | 206.15 | 0.14 | 178.04 | 0.04 | 103.36 | 0.05 | 74.68 | 0.05 | [16 empty] | 55.79 | 0.04 | 74.24 | 0.04 | 30.38 | 0.03 | 43.86 | 0.05 | [8 empty] | 194.54 | 0.14 | 88.05 | 0.05 | 99.41 | 0.05 | 11.35 | 0.03 | 192.27 | 0.16 | 98.61 | 0.06 | 9.95 | 0.05 | [24 empty] | 220.97 | 0.17 | 181.26 | 0.04 | 108.19 | 0.05 | 73.07 | 0.05 | [20 empty] | 63.3 | 0.04 | 70.01 | 0.03 | 36.04 | 0.03 | 33.98 | 0.05 | [12 empty] | 211.01 | 0.16 | 88.92 | 0.05 | 104.97 | 0.05 | 16.05 | 0.04 | 208.44 | 0.16 | 104.12 | 0.05 | 14.57 | 0.05 | [12 empty] | 58.33 | 0.03 | 57.61 | 0.03 | 56.64 | 0.03 | 56.3 | 0.04 | 56.96 | 0.03 |  |  | 88.02 | 0.05 |  |  | 70.59 | 0.05 | 73.44 | 0.05 | 176.36 | 0.04 |  |  | 89.46 | 0.04 | 70.53 | 0.04 | 74.45 | 0.09 |  |  | 90.9 | 0.04 | [28 empty] | 58.1 | 0.03 | [8 empty] | 89.55 | 0.04 | 88.67 | 0.04 | [8 empty] | 71.78 | 0.04 | 88.98 | 0.05 | 68.81 | 0.04 | 89.65 | 0.05 | [10 empty] | 177.48 | 0.04 | 82.27 | 0.14 | 83.01 | 0.13 | 74.97 | 0.07 | 75 | 0.07 | 74.97 | 0.07 | 75.05 | 0.07 | 75.03 | 0.07 | 75.06 | 0.06 |  |  | 74.18 | 0.57 | 75.74 | 0.08 | 74.94 | 0.07 | 79.11 | 0.08 | 75.63 | 0.08 | 75.7 | 0.1 | 75.34 | 0.09 | 75.22 | 0.09 | 76.59 | 0.07 | 75.82 | 0.3 | 75.89 | 0.2 | 76.52 | 0.19 | 75.01 | 0.08 | 75.65 | 0.11 | 75.15 | 0.08 | 77.31 | 0.16 | [78 empty] | 81.1 | 0.07 | [8 empty] | 57.95 | 0.03 | 57.83 | 0.03 | C8-EB5-55-CE-2 | 75.039 | 0.01 | 62.003 | 0.018 | 57.502 | 0.012 | 53.831 | 0.013 | 81.991 | 0.011 | 68.001 | 0.023 | 2503.6 | 4 | 2448.5 | 4 | 1.135 | 0.002 | -0.416 | 0.003 | 0.161 | 0.005 | 0.8728 | 0.0028 | 29.198 | 0.001 | 7595 | 17 | 1540 |  | 0.0040955 | 9.8554 | 13.029 | 0.399 | 1.5046 | 11466.5911 | 326.4834 | 10.3372 | 45.1133 | 11421.4779 | 0.0087835 | 27.628 | 55.9974 | 13.7484 | 13.1003 | 0.011346 | 32.1292 | 0.0087734 | 27.6102 | 0.0079389 | 22.4264 | 75.0665 | 62.0282 | 22.06 | 63846.5873 | 52477.6466 | 6055 | 0.32368 | 59704.855 | 48335.9144 | 7.8611 | 0.23804 | -5.5681 | -19.069 | 50.0402 | 63846.5873 | 59441.3893 | 4201.3305 | 203.8675 | 63846.5873 | 100%
3 | C8-EB50-82-CE | 75N0206 | C8-EB50-82-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 50 | CUST 3 | 7/1/2015 | 22:39:19 | 10 Ton | 0:15:00 | 75/62 82/68 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 82 | 68 | 7.6 | 8.1 | 7.6 | 8.1 | 230 | 1.8 | 25.2 | 0 | 45923 | 77 | 45616 | 203 | 13600 | 115 | 59535 | 118 | 8.014 | 902 | [38 empty] | 50% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs,--CK2 8.1 lbs) 82F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet--Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from--fully closed, ad | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch:Evaporator coil blockage 21" | 75.039 | 0.017 | 62 | 0.023 | 82 | 0.007 | 68 | 0.024 | 74.5 | 0.05 | 56.1 | 0.07 | 60.78 | 0.03 | 0.08 | 0.003 | 0.684 | 0.0015 | 45923 | 77 | 13600 | 115 | 8.014 | 0.026 | [6 empty] | 230 | 1.2 | 229.7 | 1.2 | 230 | 1.2 | 25.2 | 0.1 | 23 | 0.1 | 26.5 | 0.1 | 5752.4 | 48.4 | 3608.7 | 63.7 | 1676.9 | 34.9 | 230 |  | 230 |  | 230 |  | 6.1 |  | 5.9 |  | 6 |  | 0.6 | 230 |  | 230 |  | 230 |  | 9.1 |  | 9 |  | 8.3 |  | 2660 |  | 0.76 | 230 | 230 | 230 | 9.4 | 9.2 | 8.2 | 2700 | 0.68 | 228.5 |  | 2.4 |  | 531.3 |  | 115 |  | 7426.3 | [22 empty] | 204.27 | 0.14 | 173.5 | 0.05 | 102.74 | 0.05 | 70.76 | 0.06 | [16 empty] | 53.89 | 0.05 | 67.93 | 0.05 | 28.89 | 0.04 | 39.04 | 0.06 | [8 empty] | 192.82 | 0.17 | 88.08 | 0.04 | 98.81 | 0.06 | 10.73 | 0.04 | 190.62 | 0.15 | 98.04 | 0.05 | 9.46 | 0.07 | [24 empty] | 217.79 | 0.16 | 174.72 | 0.04 | 107.18 | 0.05 | 67.54 | 0.05 | [20 empty] | 60.6 | 0.04 | 61.15 | 0.04 | 34.06 | 0.03 | 27.08 | 0.06 | [12 empty] | 208.06 | 0.16 | 88.68 | 0.05 | 104 | 0.05 | 15.31 | 0.05 | 205.54 | 0.16 | 103.16 | 0.05 | 13.85 | 0.06 | [12 empty] | 56.84 | 0.03 | 55.81 | 0.04 | 56.06 | 0.03 | 55.61 | 0.04 | 56.03 | 0.03 |  |  | 88.07 | 0.04 |  |  | 63.43 | 0.04 | 66.88 | 0.03 | 170.14 | 0.04 |  |  | 89.4 | 0.05 | 61.71 | 0.04 | 67.22 | 0.03 |  |  | 90.7 | 0.05 | [28 empty] | 56.82 | 0.03 | [8 empty] | 89.31 | 0.05 | 88.58 | 0.06 | [8 empty] | 64.84 | 0.04 | 89.12 | 0.05 | 59.52 | 0.03 | 89.59 | 0.05 | [10 empty] | 173.02 | 0.04 | 82.09 | 0.13 | 82.83 | 0.12 | 74.89 | 0.07 | 74.95 | 0.06 | 74.81 | 0.06 | 74.9 | 0.06 | 74.92 | 0.07 | 74.97 | 0.06 |  |  | 75.45 | 0.05 | 75.84 | 0.05 | 75.01 | 0.06 | 79.42 | 0.06 | 75.67 | 0.06 | 76.02 | 0.06 | 75.77 | 0.07 | 75.9 | 0.06 | 76.53 | 0.09 | 76.14 | 0.06 | 76.06 | 0.06 | 76.92 | 0.07 | 75.08 | 0.07 | 76.01 | 0.05 | 75.37 | 0.06 | 76.63 | 0.06 | [78 empty] | 81.24 | 0.08 | [8 empty] | 56.54 | 0.04 | 56.76 | 0.03 | C8-EB50-55-CE | 75.039 | 0.017 | 62 | 0.023 | 56.518 | 0.009 | 52.867 | 0.015 | 82 | 0.007 | 68 | 0.024 | 2212 | 2.5 | 2168.6 | 2.5 | 0.876 | 0.002 | -0.314 | 0.002 | 0.08 | 0.003 | 0.684 | 0.0015 | 29.228 | 0.001 | 7429 | 19 | 1420 |  | 0.012777 | 27.85 | 13.029 | 0.304 | 1.676 | 10152.2044 | 223.1766 | 29.0755 | 126.8879 | 10025.3165 | 0.0088036 | 27.6646 | 54.842 | 13.7486 | 13.073 | 0.011343 | 32.1283 | 0.0087714 | 27.6081 | 0.0076345 | 21.8561 | 75.1264 | 62.08 | 21.4482 | 63110.0271 | 49423.4803 | 6009 | 0.32497 | 59025.2689 | 45338.722 | 7.9453 | 0.23418 | -6.2164 | -20.2844 | 48.6391 | 63110.0271 | 58395.2303 | 4141.2368 | 573.56 | 63110.0271 | 100%
3 | C8-EB0-95-CE | 75N0207 | C8-EB0-95-CE-CAB | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/26/2015 | 10:15:51 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.7 | 1.6 | 27.8 | 0 | 44855 | 81 | 44505 | 157 | 5185 | 121 | 50044 | 159 | 5.686 | 900 | [38 empty] | Baseline no evaporator coil blockage, economizer closed damper, factory charge--(CK1 7.6 lbs, CK2 8.1 lbs) 95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet,--Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow. 7" ID pulley 4.5 turns open from fully- | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.005 | 0.029 | 61.996 | 0.028 | 95.008 | 0.007 | 75.013 | 0.034 | 74.78 | 0.06 | 58.83 | 0.04 | 62.47 | 0.01 | 0.162 | 0.005 | 0.8833 | 0.003 | 44855 | 81 | 5185 | 121 | 5.686 | 0.02 | [6 empty] | 229.7 | 1.1 | 229.6 | 1.1 | 230.4 | 1.1 | 27.8 | 0.1 | 25.7 | 0.1 | 29.8 | 0.1 | 6382 | 43.1 | 3783.4 | 59.9 | 2420.3 | 31.9 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.5 |  | 9.7 |  | 3310 |  | 0.82 | 230 | 230 | 230 | 10.5 | 10.5 | 9.3 | 3270 | 0.72 | 228.3 |  | 2.4 |  | 528.3 |  | 115 |  | 8793.3 | [22 empty] | 258.4 | 0.13 | 194.87 | 0.03 | 119.47 | 0.04 | 75.4 | 0.04 | [16 empty] | 64.05 | 0.03 | 78.34 | 0.03 | 36.61 | 0.02 | 41.73 | 0.04 | [8 empty] | 246.63 | 0.12 | 101 | 0.05 | 116.05 | 0.04 | 15.06 | 0.03 | 244.07 | 0.13 | 115.3 | 0.04 | 13.26 | 0.04 | [24 empty] | 267.52 | 0.22 | 201.39 | 0.03 | 122.04 | 0.06 | 79.35 | 0.04 | [20 empty] | 71.49 | 0.05 | 77.62 | 0.02 | 41.78 | 0.03 | 35.84 | 0.04 | [12 empty] | 257.09 | 0.22 | 102.58 | 0.05 | 119.09 | 0.06 | 16.52 | 0.04 | 254.31 | 0.19 | 118.29 | 0.05 | 15.24 | 0.05 | [12 empty] | 59.9 | 0.04 | 59.21 | 0.05 | 59.01 | 0.04 | 58.32 | 0.05 | 59.21 | 0.05 |  |  | 100.99 | 0.05 |  |  | 73.72 | 0.04 | 78.09 | 0.04 | 195.54 | 0.04 |  |  | 103.54 | 0.04 | 79.54 | 0.04 | 83.69 | 0.03 |  |  | 105.35 | 0.04 | [28 empty] | 59.63 | 0.04 | [8 empty] | 103.05 | 0.06 | 102.03 | 0.04 | [8 empty] | 75.29 | 0.04 | 102.34 | 0.04 | 77.25 | 0.04 | 103.38 | 0.04 | [10 empty] | 195.99 | 0.03 | 96.2 | 0.09 | 95.99 | 0.1 | 75.53 | 0.07 | 75.41 | 0.07 | 75.79 | 0.07 | 75.84 | 0.07 | 75.83 | 0.07 | 75.78 | 0.07 |  |  | 78.97 | 0.08 | 79.84 | 0.08 | 75.34 | 0.06 | 87.91 | 0.24 | 75.78 | 0.07 | 77.21 | 0.08 | 75.63 | 0.07 | 76.14 | 0.1 | 76.43 | 0.09 | 78.55 | 0.09 | 79.8 | 0.07 | 81.02 | 0.08 | 75.3 | 0.07 | 78.12 | 0.08 | 75.27 | 0.07 | 84.1 | 0.14 | [78 empty] | 95.05 | 0.18 | [8 empty] | 59.55 | 0.04 | 59.53 | 0.04 | C8-55-CE3 | 75.005 | 0.029 | 61.996 | 0.028 | 58.939 | 0.016 | 55.398 | 0.02 | 95.008 | 0.007 | 75.013 | 0.034 | 2518.8 | 4.3 | 2461.7 | 4.2 | 1.138 | 0.002 | -0.396 | 0.002 | 0.162 | 0.005 | 0.8833 | 0.003 | 29.265 | 0.001 | 8802 | 17 | 1570 |  | 0.0087943 | 21.3789 | 13.029 | 0.398 | 1.534 | 11500.4453 | 329.1111 | 22.1844 | 94.4006 | 11406.0447 | 0.0088191 | 27.6924 | 57.405 | 14.1002 | 13.1411 | 0.01393 | 38.1696 | 0.0087768 | 27.6057 | 0.0084938 | 23.3795 | 75.1707 | 62.1194 | 23.0056 | 53900.3151 | 49035.1971 | 7232 | 0.45793 | 49665.1611 | 44800.0432 | 5.6425 | 0.21863 | -4.6868 | -17.7657 | 52.4342 | 53900.3151 | 48602.6369 | 4300.4425 | 997.2356 | 53900.3151 | 100%
3 | C8-EB10-95-CE | 75N0208 | C8-EB10-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 10 | CUST 3 | 6/26/2015 | 16:30:01 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs CK2 8.1 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.8 | 1.7 | 27.9 | 0 | 43773 | 73 | 43329 | 139 | 5492 | 122 | 49270 | 127 | 5.637 | 900 | [38 empty] | 10% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @--75% Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. 7.5" evap coil blockage | 75.036 | 0.017 | 61.996 | 0.025 | 95.007 | 0.012 | 75.008 | 0.025 | 74.55 | 0.06 | 58.7 | 0.05 | 62.78 | 0.03 | 0.126 | 0.004 | 0.8481 | 0.0024 | 43773 | 73 | 5492 | 122 | 5.637 | 0.018 | [6 empty] | 229.8 | 1.2 | 229.5 | 1.2 | 230.1 | 1.2 | 27.9 | 0.1 | 25.7 | 0.1 | 29.4 | 0.1 | 6397.8 | 46.9 | 3731.5 | 64.7 | 2343.1 | 34.4 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.2 |  | 6.1 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.2 |  | 10.3 |  | 9.6 |  | 3280 |  | 0.82 | 230 | 230 | 230 | 10.5 | 10.4 | 9.3 | 3260 | 0.71 | 228.3 |  | 2.4 |  | 527.9 |  | 115 |  | 8742.9 | [22 empty] | 256.84 | 0.1 | 193.62 | 0.05 | 119.01 | 0.03 | 74.61 | 0.04 | [16 empty] | 63.05 | 0.03 | 76.36 | 0.04 | 35.84 | 0.02 | 40.52 | 0.04 | [8 empty] | 245.21 | 0.1 | 100.92 | 0.05 | 115.62 | 0.03 | 14.7 | 0.04 | 242.7 | 0.09 | 114.88 | 0.03 | 12.81 | 0.04 | [24 empty] | 266.65 | 0.13 | 199.24 | 0.04 | 121.78 | 0.04 | 77.46 | 0.03 | [20 empty] | 70.57 | 0.03 | 74.56 | 0.04 | 41.12 | 0.02 | 33.44 | 0.04 | [12 empty] | 256.3 | 0.14 | 102.57 | 0.04 | 118.85 | 0.04 | 16.29 | 0.03 | 253.57 | 0.13 | 118.07 | 0.04 | 15 | 0.03 | [12 empty] | 59.32 | 0.04 | 58.76 | 0.05 | 58.7 | 0.04 | 58.34 | 0.04 | 58.97 | 0.03 |  |  | 100.92 | 0.04 |  |  | 71.36 | 0.04 | 75.84 | 0.04 | 193.39 | 0.05 |  |  | 103.36 | 0.04 | 76.12 | 0.05 | 80.95 | 0.03 |  |  | 105.04 | 0.04 | [28 empty] | 59.19 | 0.03 | [8 empty] | 103.07 | 0.04 | 102.07 | 0.05 | [8 empty] | 73.1 | 0.04 | 102.19 | 0.05 | 73.5 | 0.05 | 103.27 | 0.03 | [10 empty] | 194.48 | 0.05 | 95.78 | 0.1 | 95.6 | 0.09 | 75.12 | 0.06 | 75.1 | 0.06 | 75.26 | 0.07 | 75.26 | 0.07 | 75.21 | 0.07 | 75.19 | 0.06 |  |  | 80.3 | 0.06 | 80.52 | 0.07 | 75.21 | 0.05 | 87.1 | 0.11 | 75.61 | 0.06 | 79.04 | 0.09 | 76.15 | 0.09 | 76.85 | 0.11 | 77.74 | 0.15 | 81.19 | 0.1 | 80.76 | 0.07 | 80.83 | 0.07 | 75 | 0.06 | 80.25 | 0.08 | 75.38 | 0.07 | 83.45 | 0.12 | [78 empty] | 94.98 | 0.06 | [8 empty] | 59.06 | 0.04 | 59.09 | 0.03 | C8-EB10-55-CE | 75.036 | 0.017 | 61.996 | 0.025 | 59.016 | 0.014 | 55.367 | 0.016 | 95.007 | 0.012 | 75.008 | 0.025 | 2473 | 3.6 | 2406.8 | 3.5 | 1.093 | 0.002 | -0.381 | 0.002 | 0.126 | 0.004 | 0.8481 | 0.0024 | 29.163 | 0.001 | 8741 | 18 | 1560 |  | 0.012007 | 28.4581 | 13.029 | 0.373 | 1.5752 | 11289.8961 | 309.0475 | 29.9205 | 127.3202 | 11162.5759 | 0.0088276 | 27.7243 | 57.4408 | 14.1001 | 13.1427 | 0.013926 | 38.1647 | 0.0087695 | 27.6052 | 0.0084576 | 23.359 | 75.2633 | 62.1654 | 22.975 | 53618.9871 | 48291.5567 | 7181 | 0.45709 | 49349.4863 | 44022.0559 | 5.6457 | 0.22496 | -4.7493 | -17.8226 | 52.2677 | 53618.9871 | 47939.5148 | 4335.0335 | 1344.4388 | 53618.9871 | 100%
3 | C8-EB20-95-CE | 75N0209 | C8-EB20-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 20 | CUST 3 | 6/26/2015 | 17:38:04 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.6 | 27.8 | 0 | 43381 | 70 | 42778 | 159 | 5932 | 142 | 49318 | 175 | 5.665 | 900 | [38 empty] | 20% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75%--Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: 10.5` evap coil blockag | 75.035 | 0.02 | 62.001 | 0.032 | 95.008 | 0.008 | 74.994 | 0.015 | 74.56 | 0.07 | 58.68 | 0.06 | 62.65 | 0.02 | 0.141 | 0.003 | 0.823 | 0.002 | 43381 | 70 | 5932 | 142 | 5.665 | 0.023 | [6 empty] | 229.9 | 1.1 | 229.5 | 1.1 | 230.1 | 1.1 | 27.8 | 0.1 | 25.7 | 0.1 | 29.3 | 0.1 | 6378.6 | 44.2 | 3733.4 | 59.7 | 2327.1 | 32.5 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.2 |  | 6.2 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.3 |  | 10.3 |  | 9.7 |  | 3270 |  | 0.82 | 230 | 230 | 230 | 10.4 | 10.5 | 9.3 | 3250 | 0.72 | 228.3 |  | 2.4 |  | 527.5 |  | 115 |  | 8702.5 | [22 empty] | 256.24 | 0.15 | 192.77 | 0.04 | 118.84 | 0.04 | 73.93 | 0.04 | [16 empty] | 62.62 | 0.03 | 75.22 | 0.04 | 35.53 | 0.02 | 39.68 | 0.05 | [8 empty] | 244.66 | 0.15 | 100.98 | 0.06 | 115.46 | 0.05 | 14.49 | 0.05 | 242.14 | 0.15 | 114.71 | 0.04 | 12.64 | 0.04 | [24 empty] | 265.96 | 0.14 | 197.74 | 0.05 | 121.59 | 0.04 | 76.15 | 0.04 | [20 empty] | 69.96 | 0.04 | 72.66 | 0.04 | 40.71 | 0.02 | 31.95 | 0.05 | [12 empty] | 255.65 | 0.15 | 102.58 | 0.05 | 118.67 | 0.04 | 16.08 | 0.04 | 252.91 | 0.16 | 117.87 | 0.05 | 14.81 | 0.04 | [12 empty] | 59.23 | 0.04 | 58.46 | 0.05 | 58.64 | 0.04 | 58.17 | 0.04 | 58.69 | 0.03 |  |  | 100.97 | 0.06 |  |  | 70.05 | 0.05 | 74.66 | 0.04 | 192.04 | 0.07 |  |  | 103.28 | 0.03 | 74.26 | 0.07 | 79.34 | 0.04 |  |  | 104.97 | 0.04 | [28 empty] | 59.08 | 0.04 | [8 empty] | 103.06 | 0.05 | 102.07 | 0.04 | [8 empty] | 71.87 | 0.06 | 102.17 | 0.04 | 71.46 | 0.08 | 103.21 | 0.04 | [10 empty] | 193.62 | 0.06 | 95.73 | 0.09 | 95.56 | 0.09 | 75.05 | 0.07 | 75.04 | 0.06 | 75.18 | 0.08 | 75.18 | 0.07 | 75.14 | 0.07 | 75.15 | 0.06 |  |  | 79.6 | 0.06 | 79.96 | 0.06 | 75.16 | 0.07 | 86.56 | 0.16 | 75.69 | 0.06 | 79.1 | 0.09 | 76.96 | 0.1 | 77.71 | 0.12 | 78.29 | 0.22 | 80.13 | 0.08 | 80.02 | 0.07 | 80.14 | 0.08 | 74.99 | 0.07 | 79.8 | 0.09 | 75.47 | 0.07 | 80.9 | 0.1 | [78 empty] | 95.11 | 0.12 | [8 empty] | 58.9 | 0.04 | 59 | 0.04 | C8-EB20-55-CE | 75.035 | 0.02 | 62.001 | 0.032 | 58.932 | 0.013 | 55.259 | 0.015 | 95.008 | 0.008 | 74.994 | 0.015 | 2435.4 | 3 | 2371.4 | 2.9 | 1.057 | 0.001 | -0.368 | 0.002 | 0.141 | 0.003 | 0.823 | 0.002 | 29.166 | 0.001 | 8706 | 17 | 1540 |  | 0.01057 | 24.8756 | 13.03 | 0.367 | 1.5923 | 11120.325 | 294.4726 | 25.9121 | 110.264 | 11010.061 | 0.008824 | 27.7134 | 57.3397 | 14.1001 | 13.1403 | 0.013914 | 38.1512 | 0.008773 | 27.6088 | 0.008415 | 23.2922 | 75.2349 | 62.1497 | 22.9041 | 53481.2542 | 47760.1313 | 7166 | 0.45731 | 49230.2692 | 43509.1463 | 5.6548 | 0.22676 | -4.8093 | -17.8952 | 52.0919 | 53481.2542 | 48002.9165 | 4315.8982 | 1162.4394 | 53481.2542 | 100%
3 | C8-EB35-95-CE | 75N0210 | C8-EB35-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 35 | CUST 3 | 6/26/2015 | 19:45:00 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.8 | 27.6 | 0 | 42740 | 67 | 41948 | 117 | 7237 | 152 | 49984 | 159 | 5.795 | 901 | [38 empty] | 35% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow.--7" ID pulley 4.5 turns open from fully closed, adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.: 16 1/4` evap coil block | 75.023 | 0.012 | 62.009 | 0.034 | 94.994 | 0.011 | 75.005 | 0.022 | 74.45 | 0.07 | 58.22 | 0.07 | 62.35 | 0.02 | 0.106 | 0.003 | 0.7536 | 0.0019 | 42740 | 67 | 7237 | 152 | 5.795 | 0.022 | [6 empty] | 229.9 | 1.4 | 229.5 | 1.4 | 230.1 | 1.4 | 27.6 | 0.1 | 25.5 | 0.1 | 29.1 | 0.1 | 6340.1 | 54.8 | 3730 | 74.8 | 2285.1 | 41.1 | 230 |  | 230 |  | 230 |  | 6.1 |  | 6.1 |  | 6.2 |  | 0.61 | 230 |  | 230 |  | 230 |  | 10.3 |  | 10.3 |  | 9.2 |  | 3250 |  | 0.82 | 230 | 230 | 230 | 10.5 | 10.3 | 9.2 | 3220 | 0.71 | 228.3 |  | 2.4 |  | 528.6 |  | 115 |  | 8583.6 | [22 empty] | 255.03 | 0.17 | 191.55 | 0.04 | 118.5 | 0.05 | 73.06 | 0.05 | [16 empty] | 61.95 | 0.04 | 73.59 | 0.03 | 35.06 | 0.03 | 38.54 | 0.04 | [8 empty] | 243.54 | 0.16 | 100.89 | 0.06 | 115.13 | 0.05 | 14.25 | 0.04 | 241.06 | 0.16 | 114.39 | 0.05 | 12.4 | 0.05 | [24 empty] | 264.31 | 0.23 | 195.69 | 0.05 | 121.14 | 0.06 | 74.55 | 0.04 | [20 empty] | 68.94 | 0.05 | 69.98 | 0.04 | 40.02 | 0.03 | 29.96 | 0.04 | [12 empty] | 254.09 | 0.23 | 102.46 | 0.06 | 118.22 | 0.07 | 15.76 | 0.03 | 251.37 | 0.22 | 117.44 | 0.06 | 14.5 | 0.03 | [12 empty] | 59.11 | 0.05 | 58.58 | 0.06 | 57.75 | 0.05 | 57.42 | 0.06 | 58.48 | 0.04 |  |  | 100.88 | 0.06 |  |  | 68.3 | 0.05 | 73.02 | 0.05 | 190.1 | 0.06 |  |  | 103.14 | 0.05 | 71.42 | 0.06 | 77.09 | 0.04 |  |  | 104.78 | 0.05 | [28 empty] | 58.96 | 0.04 | [8 empty] | 102.94 | 0.06 | 101.99 | 0.05 | [8 empty] | 70.06 | 0.04 | 102.08 | 0.05 | 68.62 | 0.08 | 103.1 | 0.05 | [10 empty] | 192.38 | 0.04 | 95.64 | 0.1 | 95.44 | 0.1 | 74.94 | 0.08 | 74.94 | 0.07 | 75.06 | 0.09 | 75.07 | 0.09 | 75.02 | 0.08 | 75.03 | 0.07 |  |  | 80.09 | 0.11 | 79.4 | 0.09 | 77.69 | 0.14 | 82.47 | 0.07 | 75.54 | 0.06 | 78.91 | 0.11 | 78.83 | 0.09 | 80.63 | 0.09 | 86.91 | 0.1 | 79.3 | 0.15 | 78.9 | 0.13 | 78.1 | 0.08 | 74.94 | 0.07 | 80.04 | 0.1 | 75.68 | 0.07 | 78.6 | 0.07 | [78 empty] | 95.12 | 0.09 | [8 empty] | 58.87 | 0.04 | 58.77 | 0.04 | C8-EB35-55-CE | 75.023 | 0.012 | 62.009 | 0.034 | 58.491 | 0.014 | 54.837 | 0.022 | 94.994 | 0.011 | 75.005 | 0.022 | 2326.9 | 3 | 2271.1 | 2.9 | 0.957 | 0.002 | -0.332 | 0.002 | 0.106 | 0.003 | 0.7536 | 0.0019 | 29.214 | 0.005 | 8626 | 19 | 1470 |  | 0.00909 | 20.4271 | 13.029 | 0.333 | 1.6238 | 10634.8211 | 255.3367 | 21.218 | 90.2904 | 10544.5307 | 0.0088248 | 27.7043 | 56.8672 | 14.0998 | 13.128 | 0.013927 | 38.1621 | 0.0087811 | 27.6148 | 0.0082763 | 23.0339 | 75.1941 | 62.1364 | 22.6382 | 53877.0626 | 46776.7827 | 7156 | 0.45332 | 49731.4169 | 42631.137 | 5.7653 | 0.22605 | -5.0661 | -18.3269 | 51.5144 | 53877.0626 | 48716.8582 | 4207.887 | 952.3175 | 53877.0626 | 100%
3 | C8-EB5-95-CE | 75N0211 | C8-EB5-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 5 | CUST 3 | 6/26/2015 | 12:43:50 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.6 | 1.8 | 27.8 | 0 | 44313 | 74 | 43709 | 172 | 5249 | 136 | 49566 | 148 | 5.647 | 900 | [38 empty] | 5% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75%--Horiz airflow. 7" ID pulley 4.5 turns open from fully closed, adju | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.014 | 0.014 | 61.999 | 0.03 | 94.986 | 0.011 | 74.998 | 0.025 | 74.58 | 0.05 | 58.8 | 0.03 | 62.68 | 0.02 | 0.138 | 0.004 | 0.8701 | 0.0026 | 44313 | 74 | 5249 | 136 | 5.647 | 0.021 | [6 empty] | 229.6 | 1.2 | 229.5 | 1.2 | 230.3 | 1.2 | 27.8 | 0.1 | 25.7 | 0.1 | 29.7 | 0.1 | 6368.4 | 47.3 | 3776.3 | 64.2 | 2408.7 | 35.9 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.3 |  | 10.5 |  | 9.7 |  | 3290 |  | 0.81 | 230 | 230 | 230 | 10.5 | 10.5 | 9.3 | 3260 | 0.72 | 228.2 |  | 2.4 |  | 527.8 |  | 115 |  | 8762.8 | [22 empty] | 257.72 | 0.11 | 193.91 | 0.03 | 119.27 | 0.03 | 74.64 | 0.04 | [16 empty] | 63.47 | 0.02 | 76.82 | 0.04 | 36.17 | 0.02 | 40.65 | 0.04 | [8 empty] | 246.03 | 0.12 | 101.03 | 0.05 | 115.87 | 0.03 | 14.84 | 0.03 | 243.48 | 0.11 | 115.12 | 0.03 | 12.99 | 0.03 | [24 empty] | 267.15 | 0.18 | 200.02 | 0.03 | 121.93 | 0.05 | 78.09 | 0.03 | [20 empty] | 70.98 | 0.04 | 75.82 | 0.03 | 41.43 | 0.03 | 34.39 | 0.04 | [12 empty] | 256.77 | 0.2 | 102.66 | 0.04 | 119 | 0.06 | 16.34 | 0.04 | 254.02 | 0.17 | 118.21 | 0.05 | 15.05 | 0.04 | [12 empty] | 59.38 | 0.04 | 58.73 | 0.06 | 58.64 | 0.06 | 58.16 | 0.05 | 58.87 | 0.04 |  |  | 101.04 | 0.04 |  |  | 71.8 | 0.03 | 76.25 | 0.03 | 194.1 | 0.03 |  |  | 103.31 | 0.04 | 77.23 | 0.02 | 81.88 | 0.02 |  |  | 105.06 | 0.03 | [28 empty] | 59.13 | 0.04 | [8 empty] | 103.16 | 0.04 | 102.13 | 0.03 | [8 empty] | 73.6 | 0.03 | 102.18 | 0.04 | 74.76 | 0.02 | 103.23 | 0.04 | [10 empty] | 194.73 | 0.03 | 95.9 | 0.08 | 95.7 | 0.09 | 75.12 | 0.06 | 75.07 | 0.06 | 75.29 | 0.06 | 75.28 | 0.06 | 75.24 | 0.06 | 75.24 | 0.05 |  |  | 79.06 | 0.07 | 79.82 | 0.08 | 74.96 | 0.05 | 87.39 | 0.16 | 75.43 | 0.06 | 77.58 | 0.09 | 75.53 | 0.07 | 76.49 | 0.09 | 76.08 | 0.08 | 79.06 | 0.08 | 79.31 | 0.07 | 80.71 | 0.08 | 74.84 | 0.05 | 78.76 | 0.08 | 75.28 | 0.06 | 82.81 | 0.14 | [78 empty] | 94.94 | 0.12 | [8 empty] | 58.98 | 0.05 | 59.02 | 0.03 | C8-EB5-55-CE-2 | 75.014 | 0.014 | 61.999 | 0.03 | 59.015 | 0.013 | 55.416 | 0.022 | 94.986 | 0.011 | 74.998 | 0.025 | 2501.6 | 3.7 | 2441.4 | 3.6 | 1.12 | 0.002 | -0.39 | 0.002 | 0.138 | 0.004 | 0.8701 | 0.0026 | 29.237 | 0.001 | 8777 | 18 | 1570 |  | 0.0040955 | 9.8554 | 13.029 | 0.399 | 1.5545 | 11420.2903 | 321.2344 | 10.136 | 43.1333 | 11377.1569 | 0.0087961 | 27.6475 | 57.4605 | 14.0996 | 13.1429 | 0.013922 | 38.1554 | 0.0087767 | 27.6077 | 0.0084863 | 23.3899 | 75.0901 | 62.0557 | 23.0109 | 52951.5614 | 48320.6413 | 7207 | 0.46453 | 48689.5245 | 44058.6044 | 5.5474 | 0.2224 | -4.6366 | -17.6297 | 52.4182 | 52951.5614 | 48168.9222 | 4327.6807 | 454.9586 | 52951.5614 | 100%
3 | C8-EB50-95-CE | 75N0212 | C8-EB50-95-CE | closed | on | on | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 50 | CUST 3 | 6/26/2015 | 21:03:07 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. CK1 7.6 lbs/CK2 8.1 lb | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 7.6 | 8.1 | 7.6 | 8.1 | 229.9 | 1.7 | 27.5 | 0 | 41701 | 58 | 41180 | 143 | 8178 | 129 | 49887 | 129 | 5.834 | 903 | [38 empty] | 50% evaporator coil block, economizer closed damper, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--95F OD, 75F DB, 62F WB ID conditions, unsealed cabinet, Inlet Meriam set @ 75%: Outlet @ 75% Horiz airflow.--7" ID pulley 4.5 turns open from fully closed, adj | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch.:21" evap coil block | 75.04 | 0.017 | 61.982 | 0.026 | 94.989 | 0.008 | 75.005 | 0.015 | 74.55 | 0.08 | 57.86 | 0.06 | 62.36 | 0.03 | 0.051 | 0.003 | 0.6838 | 0.0016 | 41701 | 58 | 8178 | 129 | 5.834 | 0.018 | [6 empty] | 229.9 | 1.3 | 229.4 | 1.3 | 230.1 | 1.3 | 27.5 | 0.1 | 25.4 | 0.1 | 28.9 | 0.1 | 6298.6 | 51.5 | 3729.1 | 68.9 | 2253.1 | 38.6 | 230 |  | 230 |  | 230 |  | 6 |  | 6.1 |  | 6.1 |  | 0.61 | 230 |  | 230 |  | 230 |  | 10.3 |  | 10.3 |  | 9.6 |  | 3240 |  | 0.82 | 230 | 230 | 230 | 10.4 | 10.3 | 9.2 | 3200 | 0.7 | 228.2 |  | 2.4 |  | 528.3 |  | 115 |  | 8523.3 | [22 empty] | 253.56 | 0.13 | 190.36 | 0.03 | 118.07 | 0.04 | 72.29 | 0.04 | [16 empty] | 61.07 | 0.04 | 71.95 | 0.03 | 34.4 | 0.03 | 37.55 | 0.04 | [8 empty] | 242.18 | 0.13 | 100.89 | 0.05 | 114.73 | 0.04 | 13.84 | 0.05 | 239.71 | 0.12 | 113.99 | 0.04 | 12.12 | 0.04 | [24 empty] | 262.38 | 0.13 | 192.56 | 0.03 | 120.59 | 0.04 | 71.97 | 0.03 | [20 empty] | 67.47 | 0.03 | 65.19 | 0.03 | 39 | 0.02 | 26.18 | 0.04 | [12 empty] | 252.27 | 0.13 | 102.36 | 0.03 | 117.7 | 0.04 | 15.33 | 0.04 | 249.62 | 0.13 | 116.92 | 0.04 | 14.11 | 0.04 | [12 empty] | 58.78 | 0.03 | 58.21 | 0.04 | 57.25 | 0.04 | 56.86 | 0.04 | 58.05 | 0.03 |  |  | 100.88 | 0.04 |  |  | 66.43 | 0.05 | 71.39 | 0.05 | 187.19 | 0.04 |  |  | 103.08 | 0.03 | 67.05 | 0.06 | 73.04 | 0.06 |  |  | 104.66 | 0.03 | [28 empty] | 58.71 | 0.03 | [8 empty] | 102.81 | 0.03 | 101.87 | 0.04 | [8 empty] | 68.19 | 0.07 | 102.04 | 0.04 | 64.13 | 0.06 | 103.07 | 0.04 | [10 empty] | 191.21 | 0.04 | 95.58 | 0.07 | 95.35 | 0.08 | 75.01 | 0.07 | 75.03 | 0.06 | 75.1 | 0.06 | 75.11 | 0.07 | 75.07 | 0.07 | 75.09 | 0.07 |  |  | 79.39 | 0.07 | 80.41 | 0.08 | 75.89 | 0.11 | 86.97 | 0.11 | 75.73 | 0.07 | 79.19 | 0.07 | 78.73 | 0.12 | 80.79 | 0.11 | 83.44 | 0.19 | 79.47 | 0.07 | 79.57 | 0.07 | 84.9 | 0.15 | 75.08 | 0.07 | 79.57 | 0.07 | 77.24 | 0.09 | 84.89 | 0.09 | [78 empty] | 95.13 | 0.1 | [8 empty] | 58.56 | 0.03 | 58.49 | 0.03 | C8-EB50-55-CE | 75.04 | 0.017 | 61.982 | 0.026 | 58.137 | 0.013 | 54.437 | 0.016 | 94.989 | 0.008 | 75.005 | 0.015 | 2216 | 2.6 | 2162.6 | 2.6 | 0.852 | 0.002 | -0.302 | 0.002 | 0.051 | 0.003 | 0.6838 | 0.0016 | 29.208 | 0.001 | 8552 | 17 | 1440 |  | 0.012777 | 27.85 | 13.029 | 0.304 | 1.7162 | 10135.7626 | 216.4616 | 28.8763 | 122.8806 | 10012.882 | 0.008822 | 27.7232 | 56.4208 | 14.0997 | 13.1179 | 0.013928 | 38.1622 | 0.0087593 | 27.5951 | 0.0081315 | 22.7903 | 75.2841 | 62.1642 | 22.3723 | 54235.4948 | 45886.4546 | 7112 | 0.44755 | 50059.5583 | 41710.518 | 5.8535 | 0.22642 | -5.3509 | -18.8633 | 50.8999 | 54235.4948 | 48699.4901 | 4237.5147 | 1298.49 | 54235.4948 | 100%
3 | C8-55-T1FE3 | 75N0146 | C8-55-T1FE3 | 1 finger | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 1:50:19 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 230 | 1.4 | 6.5 | 0 | 7710 | 27 | 7189 | 66 | 4782 | 82 | 12496 | 96 | 7.994 | 899 | [38 empty] | Econo 1-Finger open with perimeter tape and on damper with hood removed,--Inlet static location inside Cabinet, unsealed cabinet, no compressor 55F OD ambient,--factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--duct removed from sup | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.008 | 0.01 | 61.998 | 0.024 | 54.994 | 0.027 | 51.013 | 0.027 | 74.56 | 0.04 | 72.01 | 0.04 | 72.76 | 0.01 | 0.131 | 0.005 | 0.8879 | 0.0032 | 7710 | 27 | 4782 | 82 | 7.994 | 0.08 | [6 empty] | 230 | 0.9 | 230.5 | 0.9 | 230.3 | 0.9 | 6.5 | 0 | 6.2 | 0 | 6.5 | 0 | 1393.1 | 11.8 | 1127.2 | 16.3 | 169.9 | 8.7 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.2 |  | 0.62 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1550 | [22 empty] | 93.28 | 0.05 | 55.49 | 0.01 | 55.24 | 0.03 | -0.25 | 0.03 | [16 empty] | 93.73 | 0.05 | 55.63 | 0.02 | 55.5 | 0.03 | 0.14 | 0.03 | [8 empty] | 93.66 | 0.06 | 55.18 | 0.03 | 55.46 | 0.03 | 0.27 | 0.05 | 93.13 | 0.05 | 55.16 | 0.03 | -0.08 | 0.02 | [24 empty] | 93.84 | 0.04 | 55.55 | 0.02 | 55.56 | 0.02 | -0.01 | 0.02 | [20 empty] | 93.57 | 0.04 | 55.16 | 0.01 | 55.41 | 0.02 | -0.24 | 0.02 | [12 empty] | 95.59 | 0.04 | 55.11 | 0.04 | 56.55 | 0.03 | 1.43 | 0.04 | 94.36 | 0.04 | 55.85 | 0.02 | -0.79 | 0.03 | [12 empty] | 73.34 | 0.02 | 71.54 | 0.04 | 70.93 | 0.04 | 71.59 | 0.03 | 71.65 | 0.02 |  |  | 55.17 | 0.03 |  |  | 55.85 | 0.04 | 56.38 | 0.02 | 56.24 | 0.04 |  |  | 55.79 | 0.03 | 55.99 | 0.06 | 55.91 | 0.03 |  |  | 55.91 | 0.03 | [28 empty] | 73.11 | 0.02 | [8 empty] | 55.06 | 0.03 | 55.08 | 0.02 | [8 empty] | 55.74 | 0.04 | 55.78 | 0.01 | 56.18 | 0.06 | 55.26 | 0.02 | [10 empty] | 56.37 | 0.03 | 55.51 | 0.12 | 54.92 | 0.22 | 75.15 | 0.02 | 75.04 | 0.02 | 75.29 | 0.03 | 75.27 | 0.02 | 75.22 | 0.02 | 75.22 | 0.02 |  |  | 65.6 | 0.08 | 66 | 0.07 | 74.83 | 0.03 | 70.19 | 0.21 | 75.2 | 0.02 | 64.9 | 0.08 | 71.03 | 0.08 | 68.65 | 0.15 | 74.45 | 0.08 | 65.78 | 0.07 | 66.15 | 0.07 | 67.54 | 0.05 | 74.68 | 0.02 | 65.06 | 0.07 | 68.15 | 0.13 | 65.47 | 0.09 | [78 empty] | 55.01 | 0.13 | [8 empty] | 72.41 | 0.03 | 72.84 | 0.02 | Economizer test | 75.008 | 0.01 | 61.998 | 0.024 | 72.274 | 0.006 | 60.461 | 0.026 | 54.994 | 0.027 | 51.013 | 0.027 | 2546.2 | 4.6 | 2447.4 | 4.5 | 1.136 | 0.002 | -0.374 | 0.002 | 0.131 | 0.005 | 0.8879 | 0.0032 | 29.351 | 0.001 | 1563 | 10 | 1550 |  | 0.060158 | 147.2304 | 13.029 | 0.374 | 1.5344 | 11334.5753 | 326.6242 | 147.2328 | 678.0017 | 10656.5735 | 0.0086705 | 27.199 | 70.7396 | 13.0294 | 13.4784 | 0.0069897 | 20.7853 | 0.0087774 | 27.6071 | 0.0084255 | 26.5556 | 73.8145 | 61.4046 | 26.1816
3 | C8-55-T2FE3 | 75N0147 | C8-55-T2FE3 | 2 finger | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 1:05:53 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 230 | 1.4 | 6.5 | 0 | 10072 | 278 | 9619 | 48 | 5855 | 239 | 15933 | 95 | 10.141 | 899 | [38 empty] | Econo 2-Finger open with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet,--unsealed cabinet, no compressor 55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--75F DB, 62F WB ID conditions, duct removed from supp | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.974 | 0.014 | 61.996 | 0.033 | 54.977 | 0.019 | 50.981 | 0.019 | 74.56 | 0.04 | 71.17 | 0.04 | 72.15 | 0.01 | 0.108 | 0.004 | 0.8988 | 0.0026 | 10072 | 278 | 5855 | 239 | 10.141 | 0.316 | [6 empty] | 230 | 0.9 | 230.4 | 0.9 | 230.1 | 0.9 | 6.5 | 0 | 6.2 | 0 | 6.5 | 0 | 1398.3 | 12.1 | 1123.1 | 16.6 | 173.3 | 9.1 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.4 |  | 0.63 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1550 | [22 empty] | 93.4 | 0.03 | 55.55 | 0.02 | 55.31 | 0.01 | -0.24 | 0.03 | [16 empty] | 93.83 | 0.03 | 55.69 | 0.02 | 55.55 | 0.02 | 0.13 | 0.03 | [8 empty] | 93.79 | 0.03 | 55.27 | 0.03 | 55.53 | 0.02 | 0.26 | 0.04 | 93.25 | 0.02 | 55.23 | 0.01 | -0.09 | 0.02 | [24 empty] | 93.93 | 0.02 | 55.56 | 0.03 | 55.61 | 0.01 | -0.05 | 0.03 | [20 empty] | 93.65 | 0.02 | 55.24 | 0.03 | 55.45 | 0.01 | -0.22 | 0.03 | [12 empty] | 95.66 | 0.02 | 55.2 | 0.03 | 56.58 | 0.01 | 1.38 | 0.04 | 94.4 | 0.02 | 55.87 | 0.01 | -0.74 | 0.04 | [12 empty] | 72.28 | 0.03 | 70.42 | 0.04 | 70.3 | 0.04 | 70.93 | 0.04 | 70.56 | 0.04 |  |  | 55.25 | 0.02 |  |  | 55.75 | 0.02 | 56.33 | 0.02 | 56.2 | 0.03 |  |  | 55.69 | 0.03 | 55.89 | 0.06 | 55.91 | 0.02 |  |  | 55.85 | 0.02 | [28 empty] | 72.11 | 0.04 | [8 empty] | 55.13 | 0.03 | 55.14 | 0.02 | [8 empty] | 55.7 | 0.02 | 55.76 | 0.01 | 56.06 | 0.07 | 55.24 | 0.02 | [10 empty] | 56.33 | 0.04 | 55.47 | 0.11 | 54.91 | 0.21 | 75.12 | 0.03 | 75.01 | 0.03 | 75.27 | 0.04 | 75.24 | 0.03 | 75.18 | 0.03 | 75.18 | 0.03 |  |  | 63.85 | 0.1 | 64.38 | 0.09 | 74.92 | 0.04 | 73.6 | 0.13 | 75.01 | 0.03 | 62.89 | 0.11 | 68.65 | 0.12 | 65.76 | 0.12 | 74.5 | 0.08 | 64.14 | 0.08 | 64.53 | 0.08 | 65.89 | 0.06 | 74.62 | 0.03 | 63.3 | 0.1 | 65.08 | 0.18 | 64.72 | 0.11 | [78 empty] | 54.82 | 0.15 | [8 empty] | 71.39 | 0.03 | 71.83 | 0.03 | Economizer test | 74.974 | 0.014 | 61.996 | 0.033 | 71.416 | 0.016 | 60.018 | 0.027 | 54.977 | 0.019 | 50.981 | 0.019 | 2559.7 | 3.7 | 2464.5 | 3.6 | 1.13 | 0.001 | -0.348 | 0.002 | 0.108 | 0.004 | 0.8988 | 0.0026 | 29.365 | 0 | 1571 | 10 | 1570 |  | 0.10042 | 247.4729 | 13.029 | 0.348 | 1.5481 | 11413.618 | 327.1692 | 247.4718 | 1139.6456 | 10273.9725 | 0.0086037 | 26.9232 | 69.8679 | 13.0289 | 13.456 | 0.0069767 | 20.767 | 0.0087841 | 27.6061 | 0.0083462 | 26.2599 | 72.9832 | 60.999 | 25.8826
3 | C8-55-T3FE3 | 75N0148 | C8-55-T3FE3 | 3 finger | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 0:12:06 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.5 | 6.5 | 0 | 13647 | 36 | 13101 | 73 | 7165 | 162 | 20818 | 174 | 13.116 | 899 | [38 empty] | Econo 3-Finger open with perimeter tape and on damper with hood removed, Inlet Static location inside Cabinet,--unsealed cabinet, no compressor 55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--75F DB, 62F WB ID conditions, duct removed from supp | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.013 | 0.007 | 61.995 | 0.039 | 55.004 | 0.016 | 51.016 | 0.027 | 74.54 | 0.04 | 69.97 | 0.05 | 71.18 | 0.01 | 0.096 | 0.006 | 0.9208 | 0.0032 | 13647 | 36 | 7165 | 162 | 13.116 | 0.141 | [6 empty] | 229.9 | 1.1 | 230.4 | 1.1 | 230.1 | 1.2 | 6.5 | 0.1 | 6.2 | 0 | 6.5 | 0.1 | 1405.5 | 14.4 | 1124.1 | 20.4 | 181.7 | 10.3 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.2 |  | 6.4 |  | 0.62 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1570 | [22 empty] | 93.49 | 0.04 | 55.57 | 0.01 | 55.37 | 0.02 | -0.2 | 0.03 | [16 empty] | 93.84 | 0.04 | 55.67 | 0.02 | 55.56 | 0.02 | 0.11 | 0.03 | [8 empty] | 93.83 | 0.07 | 55.2 | 0.04 | 55.56 | 0.04 | 0.36 | 0.07 | 93.37 | 0.04 | 55.3 | 0.02 | -0.13 | 0.03 | [24 empty] | 93.97 | 0.04 | 55.57 | 0.03 | 55.64 | 0.02 | -0.07 | 0.03 | [20 empty] | 93.73 | 0.04 | 55.28 | 0.02 | 55.5 | 0.02 | -0.22 | 0.03 | [12 empty] | 95.74 | 0.04 | 55.23 | 0.03 | 56.63 | 0.02 | 1.4 | 0.04 | 94.44 | 0.04 | 55.91 | 0.02 | -0.75 | 0.02 | [12 empty] | 71.09 | 0.03 | 68.9 | 0.03 | 69.03 | 0.03 | 69.79 | 0.03 | 69.04 | 0.03 |  |  | 55.22 | 0.04 |  |  | 55.63 | 0.02 | 56.31 | 0.01 | 56.17 | 0.02 |  |  | 55.67 | 0.03 | 55.85 | 0.02 | 55.94 | 0.01 |  |  | 55.81 | 0.02 | [28 empty] | 71 | 0.03 | [8 empty] | 55.16 | 0.02 | 55.17 | 0.02 | [8 empty] | 55.59 | 0.02 | 55.8 | 0.02 | 56 | 0.03 | 55.31 | 0.03 | [10 empty] | 56.33 | 0.02 | 55.5 | 0.14 | 54.95 | 0.29 | 75.1 | 0.03 | 75.01 | 0.03 | 75.26 | 0.03 | 75.23 | 0.03 | 75.17 | 0.02 | 75.17 | 0.03 |  |  | 61.61 | 0.08 | 62.34 | 0.07 | 74.93 | 0.03 | 74.34 | 0.07 | 74.95 | 0.03 | 60.5 | 0.11 | 64 | 0.13 | 62.62 | 0.15 | 74.37 | 0.07 | 62.02 | 0.09 | 62.42 | 0.09 | 63.83 | 0.07 | 74.37 | 0.06 | 61.25 | 0.08 | 62.09 | 0.18 | 62.66 | 0.07 | [78 empty] | 54.87 | 0.11 | [8 empty] | 70.17 | 0.03 | 70.72 | 0.03 | Economizer test | 75.013 | 0.007 | 61.995 | 0.039 | 70.254 | 0.009 | 59.411 | 0.024 | 55.004 | 0.016 | 51.016 | 0.027 | 2588.4 | 4.5 | 2497.8 | 4.4 | 1.122 | 0.002 | -0.298 | 0.004 | 0.096 | 0.006 | 0.9208 | 0.0032 | 29.373 | 0 | 1587 | 10 | 1570 |  | 0.16138 | 403.0884 | 13.03 | 0.298 | 1.5249 | 11567.6401 | 329.2423 | 403.0832 | 1856.1488 | 9711.4913 | 0.0084878 | 26.5108 | 68.7291 | 13.0297 | 13.4257 | 0.0069889 | 20.7869 | 0.0087743 | 27.6048 | 0.0082385 | 25.8589 | 71.8111 | 60.3874 | 25.4874
3 | C8-55-TCE3 | 75N0149 | C8-55-TCE3 | closed | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 3:00:23 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.3 | 6.5 | 0 | 3386 | 22 | 2891 | 67 | 2927 | 68 | 6316 | 65 | 4.077 | 899 | [38 empty] | Econo closed (2.0V) with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet,--unsealed cabinet, no compressor 55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--75F DB, 62F WB ID conditions, duct removed from supp | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.987 | 0.015 | 61.995 | 0.024 | 55.029 | 0.045 | 51.046 | 0.063 | 74.49 | 0.03 | 73.46 | 0.04 | 73.95 | 0.01 | 0.169 | 0.005 | 0.8678 | 0.0031 | 3386 | 22 | 2927 | 68 | 4.077 | 0.051 | [6 empty] | 229.9 | 0.9 | 230.4 | 0.9 | 230.1 | 0.9 | 6.5 | 0 | 6.2 | 0 | 6.5 | 0 | 1386.3 | 11.7 | 1124.2 | 15.5 | 162.5 | 9.3 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.1 |  | 6.3 |  | 0.62 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1530 | [22 empty] | 93.05 | 0.1 | 55.35 | 0.02 | 55.12 | 0.06 | -0.24 | 0.05 | [16 empty] | 93.49 | 0.1 | 55.53 | 0.01 | 55.37 | 0.05 | 0.16 | 0.05 | [8 empty] | 93.41 | 0.1 | 54.98 | 0.05 | 55.31 | 0.06 | 0.33 | 0.06 | 92.92 | 0.1 | 55.04 | 0.06 | -0.09 | 0.05 | [24 empty] | 93.65 | 0.08 | 55.34 | 0.03 | 55.46 | 0.04 | -0.11 | 0.03 | [20 empty] | 93.38 | 0.08 | 55.05 | 0.02 | 55.3 | 0.05 | -0.25 | 0.04 | [12 empty] | 95.4 | 0.1 | 54.91 | 0.03 | 56.43 | 0.05 | 1.52 | 0.06 | 94.16 | 0.07 | 55.74 | 0.04 | -0.8 | 0.02 | [12 empty] | 74.64 | 0.03 | 73.55 | 0.02 | 72.48 | 0.03 | 73.29 | 0.03 | 73.64 | 0.03 |  |  | 54.99 | 0.04 |  |  | 55.91 | 0.03 | 56.22 | 0.03 | 55.99 | 0.05 |  |  | 55.59 | 0.03 | 55.84 | 0.07 | 55.76 | 0.02 |  |  | 55.72 | 0.03 | [28 empty] | 74.49 | 0.02 | [8 empty] | 54.94 | 0.05 | 54.94 | 0.03 | [8 empty] | 55.74 | 0.03 | 55.63 | 0.03 | 56.05 | 0.07 | 55.13 | 0.03 | [10 empty] | 56.18 | 0.03 | 55.46 | 0.18 | 54.73 | 0.24 | 75.13 | 0.03 | 75.02 | 0.03 | 75.29 | 0.04 | 75.25 | 0.03 | 75.19 | 0.03 | 75.19 | 0.03 |  |  | 71.06 | 0.07 | 71.72 | 0.07 | 74.89 | 0.03 | 65.85 | 0.21 | 75.14 | 0.03 | 72.7 | 0.08 | 74.77 | 0.04 | 73.9 | 0.07 | 74.99 | 0.04 | 71.67 | 0.09 | 70.91 | 0.07 | 69.37 | 0.07 | 74.65 | 0.03 | 71.52 | 0.08 | 74.73 | 0.03 | 66.3 | 0.12 | [78 empty] | 55.09 | 0.13 | [8 empty] | 73.83 | 0.02 | 74.21 | 0.02 | Economizer test | 74.987 | 0.015 | 61.995 | 0.024 | 73.781 | 0.017 | 61.241 | 0.022 | 55.029 | 0.045 | 51.046 | 0.063 | 2519.8 | 4.5 | 2415.8 | 4.4 | 1.138 | 0.002 | -0.417 | 0.002 | 0.169 | 0.005 | 0.8678 | 0.0031 | 29.346 | 0 | 1549 | 10 | 1530 |  | 0 | 0 | 13.03 | 0.417 | 1.5343 | 11184.3916 | 322.9746 | 0 | 0 | 11184.3916 | 0.0087804 | 27.6052 | 72.2467 | 13.0304 | 13.5178 | 0.006999 | 20.8039 | 0.0087804 | 27.6052 | 0.008572 | 27.0831 | 74.987 | 61.995 | 26.7091
3 | C8-55-TOE3 | 75N0150 | C8-55-TOE3 | open | off | off | 4.5 turns | unsealed | sealed |  | 7 | horizontal | 0 | 0 | CUST 3 | 6/24/2015 | 22:55:08 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 55 | 51 | 5.5 |  | 7.6 | 8.1 | 229.8 | 1 | 6.5 | 0 | 28809 | 75 | 28278 | 148 | 13776 | 178 | 42599 | 234 | 26.935 | 899 | [38 empty] | Econo 100% open with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet,--unsealed cabinet, no compressor 55F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--75F DB, 62F WB ID conditions, duct removed from supply s | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: No econo: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.038 | 0.029 | 62.006 | 0.018 | 54.758 | 0.021 | 50.807 | 0.024 | 74.61 | 0.06 | 64.58 | 0.05 | 67.05 | 0.02 | -0.08 | 0.005 | 0.8853 | 0.0032 | 28809 | 75 | 13776 | 178 | 26.935 | 0.236 | [6 empty] | 229.8 | 0.7 | 230.3 | 0.7 | 230.2 | 0.7 | 6.5 | 0 | 6.2 | 0 | 6.5 | 0 | 1396.7 | 10.3 | 1130.3 | 12.6 | 184.7 | 8 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.3 |  | 0.63 | [23 empty] | 0 |  | 0 |  | 0 |  | 15 |  | 1560 | [22 empty] | 93.47 | 0.05 | 55.51 | 0.02 | 55.35 | 0.03 | -0.16 | 0.03 | [16 empty] | 93.83 | 0.05 | 55.61 | 0.02 | 55.55 | 0.03 | 0.06 | 0.04 | [8 empty] | 93.81 | 0.05 | 55.27 | 0.04 | 55.54 | 0.03 | 0.27 | 0.05 | 93.37 | 0.05 | 55.3 | 0.03 | -0.04 | 0.03 | [24 empty] | 93.85 | 0.04 | 55.4 | 0.03 | 55.57 | 0.02 | -0.18 | 0.03 | [20 empty] | 93.61 | 0.03 | 55.3 | 0.01 | 55.44 | 0.02 | -0.14 | 0.03 | [12 empty] | 95.52 | 0.03 | 55.37 | 0.02 | 56.5 | 0.02 | 1.13 | 0.02 | 94.34 | 0.03 | 55.85 | 0.02 | -0.73 | 0.03 | [12 empty] | 66.9 | 0.05 | 65.01 | 0.07 | 62.72 | 0.07 | 63.08 | 0.07 | 63.52 | 0.07 |  |  | 55.29 | 0.03 |  |  | 55.21 | 0.03 | 56.16 | 0.02 | 55.95 | 0.02 |  |  | 55.49 | 0.02 | 55.61 | 0.02 | 55.92 | 0.02 |  |  | 55.58 | 0.01 | [28 empty] | 66.62 | 0.07 | [8 empty] | 55.11 | 0.02 | 55.26 | 0.02 | [8 empty] | 55.24 | 0.03 | 55.81 | 0.02 | 55.68 | 0.02 | 55.32 | 0.02 | [10 empty] | 56.2 | 0.02 | 55.36 | 0.15 | 55.04 | 0.27 | 75.18 | 0.05 | 75.13 | 0.05 | 75.41 | 0.05 | 75.35 | 0.05 | 75.31 | 0.05 | 75.29 | 0.05 |  |  | 59.54 | 0.11 | 60.44 | 0.09 | 72.55 | 0.05 | 65.56 | 0.19 | 70.29 | 0.07 | 55.81 | 0.15 | 55.16 | 0.17 | 55.75 | 0.15 | 74.53 | 0.05 | 58.19 | 0.11 | 59.99 | 0.09 | 59.81 | 0.08 | 69.41 | 0.11 | 57.22 | 0.12 | 57.72 | 0.18 | 63.06 | 0.18 | [78 empty] | 55.73 | 0.15 | [8 empty] | 66.24 | 0.05 | 65.72 | 0.07 | Economizer test | 75.038 | 0.029 | 62.006 | 0.018 | 64.815 | 0.031 | 56.429 | 0.025 | 54.758 | 0.021 | 50.807 | 0.024 | 2528.1 | 4.6 | 2459.7 | 4.5 | 1.176 | 0.002 | -0.11 | 0.002 | -0.08 | 0.005 | 0.8853 | 0.0032 | 29.371 | 0 | 1581 | 11 | 1560 |  | 0.42914 | 1055.5606 | 13.023 | 0.11 | 1.5191 | 11418.9126 | 339.8244 | 1055.5615 | 4863.21 | 6555.7026 | 0.0079921 | 24.6555 | 63.2959 | 13.023 | 13.2838 | 0.0069359 | 20.6695 | 0.0087756 | 27.6124 | 0.0077101 | 23.9579 | 66.4176 | 57.5359 | 23.5881
3 | C8-95-T1FE | 75N0163 | C8-95-T1FE | 1 finger | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 21:08:13 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.8 | 1.7 | 28 | 0 | 42721 | 82 | 42537 | 136 | 2989 | 96 | 45712 | 125 | 5.169 | 900 | [38 empty] | Econo 1-Finger open with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet,--unsealed cabinet, 95F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--2700 cfm (370 cfm/ton) 7" pulley, 87 | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.983 | 0.007 | 61.987 | 0.026 | 95.006 | 0.006 | 75.005 | 0.019 | 74.67 | 0.05 | 59.48 | 0.03 | 62.8 | 0.02 | 0.06 | 0.005 | 0.8929 | 0.0028 | 42721 | 82 | 2989 | 96 | 5.169 | 0.017 | [6 empty] | 229.8 | 1.3 | 229.5 | 1.3 | 230.1 | 1.3 | 28 | 0.1 | 25.9 | 0.1 | 29.6 | 0.1 | 6433.6 | 50.3 | 3748 | 67.5 | 2410 | 37.8 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.5 |  | 9.8 |  | 3340 |  | 0.82 | 230 | 230 | 230 | 10.6 | 10.5 | 9.3 | 3250 | 0.72 | 228.2 |  | 2.4 |  | 526.4 |  | 115 |  | 8801.4 | [22 empty] | 261.61 | 0.11 | 196.11 | 0.02 | 120.38 | 0.03 | 75.73 | 0.03 | [16 empty] | 65.7 | 0.03 | 80.28 | 0.03 | 37.78 | 0.02 | 42.5 | 0.04 | [8 empty] | 249.64 | 0.11 | 100.97 | 0.03 | 116.94 | 0.03 | 15.97 | 0.02 | 247.05 | 0.11 | 116.18 | 0.03 | 14.36 | 0.04 | [24 empty] | 267.34 | 0.19 | 200.8 | 0.04 | 121.99 | 0.05 | 78.81 | 0.04 | [20 empty] | 71.35 | 0.04 | 77.02 | 0.04 | 41.68 | 0.03 | 35.34 | 0.06 | [12 empty] | 256.93 | 0.19 | 102.69 | 0.03 | 119.05 | 0.05 | 16.36 | 0.04 | 254.18 | 0.18 | 118.25 | 0.05 | 15.12 | 0.04 | [12 empty] | 60.32 | 0.04 | 59.77 | 0.05 | 59.11 | 0.05 | 58.68 | 0.05 | 59.31 | 0.05 |  |  | 100.98 | 0.03 |  |  | 75.69 | 0.03 | 79.66 | 0.02 | 194.5 | 0.03 |  |  | 103.22 | 0.04 | 78.27 | 0.02 | 82.82 | 0.02 |  |  | 105.08 | 0.04 | [28 empty] | 60.18 | 0.04 | [8 empty] | 103.13 | 0.03 | 101.82 | 0.04 | [8 empty] | 77.27 | 0.02 | 101.92 | 0.03 | 75.62 | 0.03 | 103.26 | 0.04 | [10 empty] | 196.78 | 0.03 | 95.41 | 0.08 | 95.24 | 0.09 | 74.9 | 0.06 | 75.02 | 0.06 | 74.81 | 0.06 | 74.88 | 0.06 | 74.92 | 0.06 | 75.02 | 0.05 |  |  | 83.37 | 0.06 | 83.16 | 0.06 | 75.09 | 0.05 | 79.41 | 0.2 | 75.8 | 0.06 | 85.14 | 0.09 | 79.53 | 0.11 | 81.24 | 0.1 | 76.46 | 0.08 | 84.47 | 0.08 | 83.7 | 0.06 | 81.45 | 0.07 | 75.25 | 0.06 | 84.55 | 0.07 | 82.03 | 0.12 | 82.19 | 0.07 | [78 empty] | 94.37 | 0.09 | [8 empty] | 60.09 | 0.04 | 60.03 | 0.04 | C8-55-T1FE3 | 74.983 | 0.007 | 61.987 | 0.026 | 59.731 | 0.016 | 56.032 | 0.024 | 95.006 | 0.006 | 75.005 | 0.019 | 2534.7 | 3.9 | 2472.9 | 3.9 | 1.152 | 0.002 | -0.395 | 0.003 | 0.06 | 0.005 | 0.8929 | 0.0028 | 29.249 | 0 | 8844 | 17 | 1570 |  | 0.060158 | 147.2304 | 13.029 | 0.374 | 1.52 | 11554.1412 | 334.6757 | 157.404 | 669.7999 | 10884.3413 | 0.0090745 | 28.2118 | 58.211 | 14.1001 | 13.1626 | 0.013924 | 38.1619 | 0.0087761 | 27.5995 | 0.0086764 | 23.7712 | 76.154 | 62.8516 | 23.4005 | 55590.486 | 49755.7649 | 7274 | 0.44659 | 51374.3241 | 45539.6029 | 5.8089 | 0.22766 | -4.8113 | -17.943 | 52.9221 | 55590.486 | 44233.2487 | 4282.5816 | 7074.6557 | 55590.486 | 100%
3 | C8-95-T2FE | 75N0164 | C8-95-T2FE | 2 finger | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 22:23:04 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 230 | 1.7 | 28.2 | 0 | 40300 | 55 | 40114 | 137 | 346 | 165 | 40646 | 171 | 4.592 | 900 | [38 empty] | Econo 2-Finger open with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet, unsealed cabinet,--95F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--2700 cfm (370 cfm/ton) 7" pulley, 87 | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.992 | 0.004 | 62.002 | 0.034 | 95 | 0.006 | 75.014 | 0.022 | 74.69 | 0.04 | 60.38 | 0.03 | 63.73 | 0.01 | 0.05 | 0.003 | 0.9001 | 0.0021 | 40300 | 55 | 346 | 165 | 4.592 | 0.021 | [6 empty] | 230 | 1.3 | 229.8 | 1.3 | 230.2 | 1.3 | 28.2 | 0.1 | 25.8 | 0.1 | 29.7 | 0.1 | 6479.5 | 50.3 | 3724.7 | 67.4 | 2372.2 | 37.9 | 230 |  | 230 |  | 230 |  | 6.4 |  | 6.2 |  | 6.2 |  | 0.64 | 230 |  | 230 |  | 230 |  | 10.6 |  | 10.5 |  | 9.8 |  | 3350 |  | 0.82 | 230 | 230 | 230 | 10.6 | 10.4 | 9.3 | 3250 | 0.71 | 228.6 |  | 2.4 |  | 527.7 |  | 115 |  | 8822.7 | [22 empty] | 261.81 | 0.11 | 197.01 | 0.03 | 120.44 | 0.03 | 76.58 | 0.04 | [16 empty] | 66.01 | 0.04 | 81.5 | 0.03 | 38 | 0.03 | 43.5 | 0.04 | [8 empty] | 249.82 | 0.11 | 101 | 0.03 | 116.99 | 0.03 | 15.99 | 0.02 | 247.21 | 0.11 | 116.23 | 0.03 | 14.39 | 0.04 | [24 empty] | 267.56 | 0.15 | 201.25 | 0.04 | 122.05 | 0.04 | 79.2 | 0.03 | [20 empty] | 71.49 | 0.04 | 77.54 | 0.03 | 41.77 | 0.02 | 35.76 | 0.03 | [12 empty] | 257.1 | 0.15 | 102.71 | 0.04 | 119.1 | 0.04 | 16.39 | 0.03 | 254.38 | 0.14 | 118.31 | 0.04 | 15.16 | 0.03 | [12 empty] | 61.2 | 0.04 | 60.7 | 0.06 | 60.06 | 0.05 | 59.57 | 0.05 | 60.22 | 0.06 |  |  | 100.98 | 0.03 |  |  | 77.05 | 0.03 | 80.87 | 0.03 | 194.94 | 0.03 |  |  | 103.21 | 0.03 | 78.75 | 0.02 | 83.28 | 0.02 |  |  | 105.12 | 0.02 | [28 empty] | 61.06 | 0.05 | [8 empty] | 103.15 | 0.04 | 101.84 | 0.03 | [8 empty] | 78.56 | 0.03 | 101.92 | 0.03 | 76.17 | 0.03 | 103.26 | 0.04 | [10 empty] | 197.69 | 0.03 | 95.42 | 0.08 | 95.24 | 0.09 | 74.9 | 0.06 | 74.97 | 0.05 | 74.8 | 0.05 | 74.87 | 0.05 | 74.92 | 0.05 | 75.02 | 0.05 |  |  | 85.08 | 0.08 | 84.84 | 0.08 | 75.01 | 0.05 | 77.8 | 0.14 | 75.71 | 0.05 | 86.77 | 0.09 | 82.28 | 0.1 | 84.46 | 0.1 | 76.43 | 0.07 | 85.67 | 0.08 | 85.22 | 0.07 | 82.9 | 0.07 | 75.22 | 0.06 | 85.82 | 0.08 | 85.04 | 0.14 | 83.41 | 0.07 | [78 empty] | 94.81 | 0.14 | [8 empty] | 61 | 0.05 | 60.96 | 0.05 | C8-55-T2FE3 | 74.992 | 0.004 | 62.002 | 0.034 | 60.622 | 0.012 | 56.767 | 0.025 | 95 | 0.006 | 75.014 | 0.022 | 2547.3 | 3 | 2479.8 | 2.9 | 1.145 | 0.002 | -0.366 | 0.002 | 0.05 | 0.003 | 0.9001 | 0.0021 | 29.25 | 0.001 | 8852 | 18 | 1580 |  | 0.10042 | 247.4729 | 13.029 | 0.348 | 1.5289 | 11590.1505 | 333.5702 | 264.0176 | 1123.4779 | 10466.6726 | 0.009283 | 28.6339 | 59.0931 | 14.1 | 13.1869 | 0.013933 | 38.1707 | 0.0087838 | 27.6102 | 0.0089002 | 24.232 | 76.9479 | 63.4383 | 23.859 | 55341.2769 | 49665.4069 | 7272 | 0.44848 | 51087.212 | 45411.342 | 5.7713 | 0.23499 | -4.7749 | -17.8547 | 53.6085 | 55341.2769 | 39153.9864 | 4322.843 | 11864.4475 | 55341.2769 | 100%
3 | C8-95-T3FE | 75N0166 | C8-95-T3FE | 3 finger | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 23:36:59 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.4 | 28.2 | 0 | 37188 | 65 | 36888 | 93 | -3323 | 134 | 33862 | 156 | 3.823 | 900 | [38 empty] | Econo 3-Finger open with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet,--unsealed cabinet, 95F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs)--75F DB, 62F WB ID conditions, 2700 cfm (370 cfm/ton) 7" pulley, 87 | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 74.994 | 0.006 | 61.998 | 0.023 | 94.998 | 0.01 | 75 | 0.015 | 74.62 | 0.05 | 61.53 | 0.04 | 64.55 | 0.02 | 0.071 | 0.005 | 0.9158 | 0.003 | 37188 | 65 | -3323 | 134 | 3.823 | 0.019 | [6 empty] | 229.9 | 1 | 229.8 | 1 | 230.1 | 1 | 28.2 | 0.1 | 25.8 | 0.1 | 29.7 | 0.1 | 6483.5 | 38.6 | 3715.7 | 51.8 | 2374.5 | 29.2 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.5 |  | 9.8 |  | 3340 |  | 0.82 | 230 | 230 | 230 | 10.6 | 10.4 | 9.2 | 3240 | 0.71 | 228.6 |  | 2.4 |  | 527.6 |  | 115 |  | 8802.6 | [22 empty] | 261.86 | 0.11 | 198.23 | 0.02 | 120.45 | 0.03 | 77.78 | 0.03 | [16 empty] | 66.31 | 0.03 | 83.1 | 0.02 | 38.21 | 0.02 | 44.89 | 0.02 | [8 empty] | 249.8 | 0.1 | 100.9 | 0.04 | 116.98 | 0.03 | 16.09 | 0.04 | 247.2 | 0.11 | 116.22 | 0.03 | 14.41 | 0.04 | [24 empty] | 267.51 | 0.11 | 201.58 | 0.03 | 122.04 | 0.03 | 79.54 | 0.03 | [20 empty] | 71.58 | 0.03 | 77.94 | 0.02 | 41.83 | 0.02 | 36.11 | 0.04 | [12 empty] | 257.08 | 0.11 | 102.63 | 0.03 | 119.09 | 0.03 | 16.46 | 0.04 | 254.3 | 0.12 | 118.29 | 0.04 | 15.24 | 0.04 | [12 empty] | 62.47 | 0.03 | 62.01 | 0.06 | 61.16 | 0.05 | 60.85 | 0.06 | 62.02 | 0.05 |  |  | 100.93 | 0.05 |  |  | 79.02 | 0.03 | 82.76 | 0.02 | 195.38 | 0.04 |  |  | 103.4 | 0.03 | 79.36 | 0.04 | 83.73 | 0.03 |  |  | 105.26 | 0.03 | [28 empty] | 62.3 | 0.04 | [8 empty] | 103.05 | 0.02 | 101.81 | 0.04 | [8 empty] | 80.43 | 0.04 | 102.12 | 0.03 | 76.95 | 0.04 | 103.29 | 0.03 | [10 empty] | 199.18 | 0.04 | 95.91 | 0.07 | 95.69 | 0.1 | 75.18 | 0.05 | 75.15 | 0.05 | 75.4 | 0.05 | 75.4 | 0.05 | 75.33 | 0.05 | 75.32 | 0.04 |  |  | 87.03 | 0.09 | 86.32 | 0.08 | 75.06 | 0.05 | 76.74 | 0.1 | 75.59 | 0.06 | 88.98 | 0.09 | 86.29 | 0.14 | 87.39 | 0.11 | 76.15 | 0.06 | 87.25 | 0.08 | 86.79 | 0.08 | 84.05 | 0.06 | 75.33 | 0.08 | 87.6 | 0.1 | 88.49 | 0.13 | 85.14 | 0.07 | [78 empty] | 94.65 | 0.12 | [8 empty] | 62.12 | 0.04 | 62.22 | 0.04 | C8-55-T3FE3 | 74.994 | 0.006 | 61.998 | 0.023 | 61.797 | 0.012 | 57.719 | 0.012 | 94.998 | 0.01 | 75 | 0.015 | 2571.9 | 4.2 | 2498.6 | 4.1 | 1.126 | 0.002 | -0.313 | 0.003 | 0.071 | 0.005 | 0.9158 | 0.003 | 29.247 | 0 | 8858 | 15 | 1580 |  | 0.16138 | 403.0884 | 13.03 | 0.298 | 1.5217 | 11673.6713 | 330.5219 | 429.7339 | 1828.6724 | 9844.9989 | 0.009586 | 29.2599 | 60.2753 | 14.0999 | 13.219 | 0.013921 | 38.1572 | 0.0087807 | 27.6073 | 0.0091947 | 24.8391 | 78.1523 | 64.2956 | 24.4677 | 55942.8252 | 50085.5738 | 7278 | 0.44402 | 51678.3564 | 45821.105 | 5.8341 | 0.24542 | -4.7922 | -17.877 | 54.4611 | 55942.8252 | 32314.8196 | 4335.7372 | 19292.2683 | 55942.8252 | 100%
3 | C8-95-TCE | 75N0168 | C8-95-TCE | closed | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/25/2015 | 19:47:00 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.8 | 1.8 | 28 | 0 | 47425 | 77 | 47079 | 187 | 7856 | 179 | 55289 | 175 | 6.266 | 900 | [38 empty] | Econo closed (2.0V), with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet,--unsealed cabinet, 95F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--2700 cfm (370 cfm/ton) 7" pulley, 8 | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75.034 | 0.013 | 61.983 | 0.034 | 95 | 0.013 | 74.999 | 0.009 | 74.76 | 0.08 | 57.87 | 0.05 | 61.64 | 0.02 | 0.079 | 0.003 | 0.8763 | 0.0022 | 47425 | 77 | 7856 | 179 | 6.266 | 0.022 | [6 empty] | 229.8 | 1.3 | 229.5 | 1.3 | 230.1 | 1.3 | 28 | 0.1 | 25.9 | 0.1 | 29.6 | 0.1 | 6427.1 | 48.4 | 3747.3 | 66.5 | 2396.7 | 35.6 | 230 |  | 230 |  | 230 |  | 6.3 |  | 6.3 |  | 6.2 |  | 0.63 | 230 |  | 230 |  | 230 |  | 10.4 |  | 10.4 |  | 9.8 |  | 3320 |  | 0.82 | 230 | 230 | 230 | 10.6 | 10.4 | 9.3 | 3250 | 0.71 | 228.2 |  | 2.4 |  | 526.3 |  | 115 |  | 8771.3 | [22 empty] | 260.96 | 0.13 | 194.27 | 0.04 | 120.19 | 0.04 | 74.08 | 0.04 | [16 empty] | 65.04 | 0.04 | 77.8 | 0.03 | 37.3 | 0.03 | 40.5 | 0.05 | [8 empty] | 249.05 | 0.13 | 101 | 0.06 | 116.76 | 0.04 | 15.76 | 0.04 | 246.46 | 0.13 | 116 | 0.04 | 14.17 | 0.04 | [24 empty] | 266.89 | 0.16 | 199.83 | 0.03 | 121.86 | 0.04 | 77.97 | 0.04 | [20 empty] | 71.03 | 0.04 | 75.82 | 0.03 | 41.46 | 0.03 | 34.37 | 0.05 | [12 empty] | 256.5 | 0.15 | 102.64 | 0.04 | 118.92 | 0.04 | 16.28 | 0.04 | 253.78 | 0.16 | 118.14 | 0.05 | 15.08 | 0.05 | [12 empty] | 58.65 | 0.05 | 57.95 | 0.07 | 57.29 | 0.07 | 56.87 | 0.07 | 57.7 | 0.06 |  |  | 101.02 | 0.06 |  |  | 73.05 | 0.04 | 77.37 | 0.04 | 193.74 | 0.05 |  |  | 103.42 | 0.04 | 77.33 | 0.06 | 81.87 | 0.04 |  |  | 105.26 | 0.04 | [28 empty] | 58.45 | 0.05 | [8 empty] | 103.06 | 0.04 | 101.83 | 0.04 | [8 empty] | 74.66 | 0.05 | 102.15 | 0.04 | 74.65 | 0.07 | 103.3 | 0.03 | [10 empty] | 195.12 | 0.04 | 95.91 | 0.09 | 95.69 | 0.1 | 75.22 | 0.08 | 75.2 | 0.08 | 75.4 | 0.09 | 75.38 | 0.08 | 75.31 | 0.08 | 75.32 | 0.07 |  |  | 77.37 | 0.08 | 77.19 | 0.08 | 75.1 | 0.07 | 84.32 | 0.13 | 75.72 | 0.07 | 76.66 | 0.1 | 75.46 | 0.08 | 75.5 | 0.07 | 75.86 | 0.07 | 77.7 | 0.11 | 78.25 | 0.08 | 79.36 | 0.08 | 75.11 | 0.07 | 77.51 | 0.11 | 75.45 | 0.09 | 82.6 | 0.13 | [78 empty] | 95.16 | 0.13 | [8 empty] | 58.32 | 0.06 | 58.15 | 0.05 | C8-55-TCE3 | 75.034 | 0.013 | 61.983 | 0.034 | 58.012 | 0.012 | 54.61 | 0.02 | 95 | 0.013 | 74.999 | 0.009 | 2507.8 | 3.2 | 2453.6 | 3.1 | 1.161 | 0.001 | -0.44 | 0.002 | 0.079 | 0.003 | 0.8763 | 0.0022 | 29.245 | 0 | 8823 | 18 | 1560 |  | 0 | 0 | 13.03 | 0.417 | 1.5185 | 11472.3224 | 334.6579 | 0 | 0 | 11472.3224 | 0.0087614 | 27.5959 | 56.4935 | 14.0999 | 13.1157 | 0.01392 | 38.1562 | 0.0087614 | 27.5959 | 0.0082596 | 22.899 | 75.034 | 61.983 | 22.529 | 58128.467 | 51048.5165 | 7263 | 0.42645 | 53946.3744 | 46866.4239 | 6.1143 | 0.21063 | -5.0668 | -18.5405 | 51.5464 | 58128.467 | 53883.7153 | 4244.7518 | 0 | 58128.467 | 100%
3 | C8-95-TOE | 75N0169 | C8-95-TOE | open | on | on | 4.5 turns | unsealed | sealed | 870 | 7 | horizontal | 0 | 0 | CUST 3 | 6/26/2015 | 1:57:56 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU3 | RTU3 | 7.5 | R22 | PSC Air Handler | Manuf. 5.5 lbs | 208/230/3 | TU2 | AHRI 340-360 | 75 | 62 | 95 | 75 | 5.5 |  | 7.6 | 8.1 | 229.9 | 1.2 | 28.2 | 0 | 21786 | 37 | 21482 | 85 | -16568 | 91 | 5202 | 104 | 0.589 | 900 | [38 empty] | Econo 100% open with perimeter tape and on damper with hood removed, Inlet static location inside Cabinet,--unsealed cabinet, 95F OD ambient, factory charge (CK1 7.6 lbs, CK2 8.1 lbs) 75F DB, 62F WB ID conditions,--2700 cfm (370 cfm/ton) 7" pulley, 870 rp | New R22 CK 1 : 7.6 lbs / Ck 2 : 8.1lbs: No tape on unit: Sealed ductwork: 7` blower pulley with A49 belt at 2500 scfm : motor pulley 4.5 turns opened from closed: inlet M set to 75%: outlet M set @ 75% Horizontal air disch. | 75 | 0.009 | 62.847 | 0.011 | 95.001 | 0.011 | 75.018 | 0.013 | 74.59 | 0.04 | 66.52 | 0.02 | 68.72 | 0.01 | -0.091 | 0.004 | 0.8558 | 0.0023 | 21786 | 37 | -16568 | 91 | 0.589 | 0.012 | [6 empty] | 229.9 | 0.9 | 229.8 | 0.9 | 230.1 | 0.9 | 28.2 | 0.1 | 25.7 | 0.1 | 29.6 | 0.1 | 6474.2 | 36.5 | 3711.8 | 49.6 | 2361.5 | 28 | 230 |  | 230 |  | 230 |  | 6.2 |  | 6.3 |  | 6.3 |  | 0.62 | 230 |  | 230 |  | 230 |  | 10.5 |  | 10.5 |  | 9.8 |  | 3350 |  | 0.82 | 230 | 230 | 230 | 10.7 | 10.5 | 9.3 | 3270 | 0.71 | 228.6 |  | 2.4 |  | 527.7 |  | 115 |  | 8812.7 | [22 empty] | 262.68 | 0.2 | 202.51 | 0.04 | 120.68 | 0.06 | 81.83 | 0.05 | [16 empty] | 67.7 | 0.04 | 88.82 | 0.03 | 39.18 | 0.03 | 49.64 | 0.04 | [8 empty] | 250.5 | 0.19 | 100.83 | 0.05 | 117.19 | 0.06 | 16.36 | 0.02 | 247.86 | 0.19 | 116.41 | 0.06 | 14.6 | 0.04 | [24 empty] | 268.39 | 0.21 | 204.17 | 0.05 | 122.28 | 0.06 | 81.89 | 0.03 | [20 empty] | 72.56 | 0.04 | 81.51 | 0.03 | 42.49 | 0.03 | 39.03 | 0.04 | [12 empty] | 257.85 | 0.21 | 102.66 | 0.06 | 119.31 | 0.06 | 16.65 | 0.03 | 255.08 | 0.22 | 118.51 | 0.06 | 15.41 | 0.04 | [12 empty] | 67.3 | 0.05 | 67.32 | 0.07 | 66.11 | 0.07 | 66.4 | 0.07 | 67.23 | 0.06 |  |  | 100.86 | 0.05 |  |  | 85.4 | 0.02 | 88.53 | 0.03 | 197.74 | 0.05 |  |  | 103.27 | 0.05 | 82.66 | 0.03 | 86.71 | 0.03 |  |  | 105.17 | 0.03 | [28 empty] | 67.18 | 0.06 | [8 empty] | 103.1 | 0.05 | 101.82 | 0.04 | [8 empty] | 86.63 | 0.02 | 101.97 | 0.05 | 80.51 | 0.03 | 103.22 | 0.05 | [10 empty] | 203.33 | 0.04 | 95.66 | 0.1 | 95.44 | 0.11 | 75.09 | 0.06 | 75.05 | 0.06 | 75.25 | 0.06 | 75.26 | 0.06 | 75.23 | 0.05 | 75.22 | 0.05 |  |  | 89.16 | 0.1 | 89.34 | 0.09 | 77.85 | 0.07 | 85.8 | 0.18 | 79.9 | 0.07 | 94.41 | 0.14 | 94.29 | 0.12 | 92.81 | 0.13 | 75.92 | 0.05 | 92.01 | 0.12 | 89.44 | 0.1 | 89.14 | 0.09 | 80.43 | 0.11 | 93.16 | 0.13 | 94 | 0.15 | 88.56 | 0.09 | [78 empty] | 93.33 | 0.13 | [8 empty] | 67.03 | 0.06 | 67.1 | 0.05 | C8-55-TOE3 | 75 | 0.009 | 62.847 | 0.011 | 66.813 | 0.007 | 62.251 | 0.014 | 95.001 | 0.011 | 75.018 | 0.013 | 2497.2 | 3.5 | 2398.7 | 3.3 | 1.153 | 0.002 | -0.277 | 0.002 | -0.091 | 0.004 | 0.8558 | 0.0023 | 29.241 | 0.001 | 8836 | 16 | 1550 |  | 0.42914 | 1055.5606 | 13.023 | 0.11 | 1.5529 | 11215.3672 | 324.9154 | 1742.9374 | 7416.7196 | 3798.6476 | 0.012381 | 34.8048 | 65.2601 | 14.1001 | 13.3595 | 0.013936 | 38.1745 | 0.0093444 | 28.2256 | 0.010889 | 27.9112 | 88.2639 | 71.2528 | 27.531 | 81578.9235 | 61919.0164 | 7286 | 0.30482 | 77397.7099 | 57737.8027 | 8.7594 | 0.23303 | -7.2739 | -23.0038 | 58.2706 | 81578.9235 | 3526.1816 | 4264.1914 | 73788.5505 | 81578.9235 | 100%
1 | T2-22A-ONE-6T-US | 75T0050 | T2-22A-ONE-6T-US | none | on | on | 6 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 7 | 2/15/2014 | 14:43:36 | 10 Ton | 0:30:00 | 80/67 95/70 | ENG 1 | TECH 4 | RTU1 | RTU1 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU3 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 15.2 | 0 | 68462 | 226 | 67898 | 398 | 21478 | 174 | 89961 | 296 | 10.5638 | 744 | [38 empty] | A test factory chg, unsealed cab, no econo, 6 drive-pulley turns | Out of the box: fixed leak CK1: Removed charge CK2: recharge circuits to Manuf: 2 HP motor: belt AX35 & wheel pulley AK59: 1VL40-7/8 motor pulley:with no tape on unit: 100% Open damper: Motor pulley at 6 Turns open from fully close: No econo | 79.904 | 0.021 | 67.151 | 0.018 | 94.899 | 0.043 | 69.998 | 0.025 | 79.75 | 0.09 | 60.44 | 0.04 | 65.41 | 0.02 | 0.825 | 0.009 | 0.8633 | 0.0052 | 68462 | 226 | 21478 | 174 | 10.564 | 0.038 | [6 empty] | 459.7 | 2 | 461 | 2.1 | 460.4 | 2 | 15.2 | 0.1 | 13 | 0 | 13.2 | 0.1 | 6889.4 | 44.7 | 3329.2 | 52.4 | 1626.8 | 34.2 | 460 |  | 460 |  | 461 |  | 2.7 |  | 2.8 |  | 2.8 |  | 0.49 | 460 |  | 461 |  | 456 |  | 5.2 |  | 5.1 |  | 4.5 |  | 3230 |  | 0.72 | 458 | 458 | 459 | 5.3 | 5.1 | 4.7 | 3360 | 0.83 | 459 |  | 1.7 |  | 734.6 |  | 115 |  | 8539.6 | [22 empty] | 256.38 | 0.26 | 169.64 | 0.11 | 118.87 | 0.07 | -50.77 | 0.12 |  |  | 99.66 | 0.09 | [6 empty] | 52.99 | 0.23 |  |  |  |  | 84.18 | 0.06 | 66.81 | 0.18 | 49.83 | 0.04 | 16.98 | 0.19 | [46 empty] | 263.08 | 0.25 | 174.17 | 0.09 | 120.78 | 0.07 | 53.39 | 0.11 | [8 empty] | 97.81 | 0.07 | [10 empty] | 81.07 | 0.06 | 61.99 | 0.2 | 47.92 | 0.04 | 14.07 | 0.2 | 100.58 | 0.08 | [36 empty] | 60.24 | 0.04 | 61.03 | 0.05 | 60.36 | 0.03 | 60.66 | 0.05 | 60.18 | 0.03 | 60.49 | 0.04 | [18 empty] | 99.66 | 0.09 | [12 empty] | 105.43 | 0.09 | 101.02 | 0.09 | 89.94 | 0.15 | 89.56 | 0.12 | 88.93 | 0.15 | 89.18 | 0.11 | 88.17 | 0.14 | 88.02 | 0.11 | [8 empty] | 105.41 | 0.1 | 100.58 | 0.08 | [16 empty] | 56.34 | 0.26 | [14 empty] | 96.22 | 0.09 | 95.37 | 0.13 | 80.1 | 0.08 | 80.05 | 0.07 | 79.88 | 0.06 | 80.19 | 0.09 | 80.18 | 0.09 | 80.25 | 0.09 | 80.12 | 0.08 | 80.42 | 0.07 | 80.41 | 0.06 | 80.2 | 0.07 | 79.85 | 0.07 | 79.46 | 0.07 | 80.53 | 0.07 | 80.49 | 0.06 | 80.39 | 0.07 | 79.96 | 0.07 | 79.81 | 0.08 | 79.85 | 0.07 | 80.51 | 0.07 | 80.08 | 0.07 |  |  | 80.15 | 0.07 | 79.69 | 0.06 | 79.55 | 0.07 | 80.73 | 0.07 | 79.49 | 0.07 | 79.48 | 0.08 | [84 empty] | No Economizer | 79.904 | 0.021 | 67.151 | 0.018 | 60.428 | 0.024 | 58.477 | 0.022 | 94.899 | 0.043 | 69.998 | 0.025 | 3229.5 | 9.7 | 3119.1 | 9.4 | 0.25 | 0.005 | -0.365 | 0.003 | 0.825 | 0.009 | 0.8633 | 0.0052 | 29.108 | 0.001 | 8516 | 16 | 1100 |  |  | 0 |  |  | 0.97589 | 14690.1825 | 91.6082 | 0 | 0 | 14690.1825 | 0.01121 | 31.469 | 59.4521 | 14.0632 | 13.1904 | 0.0098106 | 33.5982 | 0.01121 | 31.469 | 0.0099836 | 25.3632 | 79.904 | 67.151 | 25.1246 | 93199.8387 | 72106.0712 | 7416 | 0.27158 | 89758.1976 | 68664.43 | 10.5399 | 0.1227 | -6.3444 | -20.4519 | 56.5918 | 93199.8387 | 89695.6587 | 3504.18 | 0 | 93199.8387 | 100%
1 | T2-ONE-3HP | 75T0165 | T2-ONE-3HP | none | on | on | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 7 | 2/12/2014 | 5:06:28 | 10 Ton | 0:30:00 | 80/67 95/70 | ENG 1 | TECH 2 | RTU1 | RTU1 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU3 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 6.4 | 6.2 | 6.4 | 6.2 | 459.6 | 0 | 17.2 | 0 | 80908 | 192 | 81307 | 384 | 7801 | 148 | 88716 | 244 | 8.3908 | 1047 | [38 empty] | . | Out of the box: fixed leak CK1: removed charge CK2: recharge circuits to Manuf.: Original motor belt and pulley: no adjustments: no tape: 100% open damper: Motor pulley at 3 Turns open from fully close | 79.853 | 0.005 | 67.15 | 0.022 | 94.846 | 0.023 | 69.814 | 0.07 | 79.8 | 0.06 | 65.39 | 0.03 | 68.12 | 0.01 | 2.641 | 0.022 | 2.2791 | 0.0104 | 80908 | 192 | 7801 | 148 | 8.391 | 0.028 | [6 empty] | 459.6 | 2.1 | 460.6 | 2.1 | 460.4 | 2.1 | 17.2 | 0 | 15.2 | 0 | 15.1 | 0 | 7887.4 | 42.2 | 3305.1 | 44.3 | 2685.2 | 33.5 | 460 |  | 460 |  | 458 |  | 4.5 |  | 4.5 |  | 4.4 |  | 0.86 | 460 |  | 461 |  | 459 |  | 5.2 |  | 5 |  | 4.6 |  | 3270 |  | 0.73 | 459 | 461 | 459 | 5.4 | 5.1 | 4.7 | 3370 | 0.83 | 458.9 |  | 1.7 |  | 742.5 |  | 115 |  | 10567.5 | [22 empty] | 258.55 | 0.31 | 166.45 | 0.1 | 119.51 | 0.09 | 46.94 | 0.12 |  |  | 100.51 | 0.11 | [6 empty] | 55.52 | 0.12 |  |  |  |  | 88.5 | 0.06 | 67.78 | 0.16 | 52.45 | 0.03 | 15.33 | 0.17 | [46 empty] | 265.13 | 0.3 | 169.43 | 0.11 | 121.37 | 0.08 | 48.06 | 0.12 | [8 empty] | 97.11 | 0.08 | [10 empty] | 87.26 | 0.06 | 64.34 | 0.19 | 51.72 | 0.04 | 12.63 | 0.2 | 99.73 | 0.08 | [36 empty] | 65.08 | 0.03 | 65.91 | 0.05 | 65.22 | 0.05 | 65.64 | 0.05 | 65.15 | 0.04 | 65.41 | 0.04 | [32 empty] | 105.96 | 0.12 | 100.13 | 0.08 | [20 empty] | 105.77 | 0.11 | 99.73 | 0.08 | [16 empty] | 60.25 | 0.23 | [14 empty] | 95.72 | 0.12 | 95.49 | 0.22 | 80.15 | 0.06 | 80.11 | 0.05 | 79.88 | 0.05 | 80.36 | 0.06 | 80.31 | 0.06 | 80.39 | 0.06 | 80.23 | 0.06 | 80.03 | 0.05 | 79.96 | 0.05 | 79.89 | 0.05 | 79.73 | 0.05 | 79.58 | 0.05 | 80.21 | 0.08 | 80.15 | 0.07 | 80.22 | 0.08 | 80.19 | 0.08 | 80.15 | 0.08 | 80.23 | 0.09 | 80.39 | 0.07 | 80.31 | 0.07 | 80.18 | 0.07 | 80.17 | 0.05 | 79.77 | 0.08 | 79.76 | 0.08 | 79.7 | 0.08 | 79.76 | 0.08 | 79.82 | 0.08 | [84 empty] | No Economizer | 79.853 | 0.005 | 67.15 | 0.022 | 65.509 | 0.02 | 62.013 | 0.022 | 94.846 | 0.023 | 69.814 | 0.07 | 5254.7 | 12 | 5087.9 | 11.8 | 0.251 | 0.012 | -0.957 | 0.008 | 2.641 | 0.022 | 2.2791 | 0.0104 | 29.247 | 0.002 | 10573 | 22 | 3070 |  |  | 0 |  |  | 1.7548 | 23656.2599 | 150.0298 | 0 | 0 | 23656.2599 | 0.011222 | 31.469 | 63.7542 | 14.0608 | 13.3276 | 0.0096802 | 33.4413 | 0.011222 | 31.469 | 0.011041 | 27.7577 | 79.853 | 67.15 | 27.3279 | 97963.0188 | 91401.0327 | 7503 | 0.2614 | 87997.1604 | 81435.1743 | 8.3228 | 0.19964 | -4.1411 | -16.0988 | 59.7385 | 97963.0188 | 87796.5813 | 10166.4375 | 0 | 97963.0188 | 100%
1 | T2-ONE | 75T0166 | T2- One | none | on | on | 3 turns | unsealed | unsealed |  |  |  | 0 | 0 | CUST 7 | 2/13/2014 | 7:14:07 | 10 Ton | 0:30:00 | 80/67 95/70 | ENG 1 | TECH 4 | RTU1 | RTU1 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU3 | AHRI 210/240 2008 | 80 | 67 | 95 | 70 | 6.4 | 6.2 | 6.4 | 6.2 | 459.6 | 0 | 16 | 0 | 78414 | 182 | 79099 | 329 | 11189 | 181 | 89614 | 242 | 9.5334 | 915 | [38 empty] | Out-of-box factory chg, unsealed cab, no econo, factory drive-pulley turns | Out of the box: fixed leak CK1: Removed charge CK2: recharge circuits to Manuf: 2 HP motor: belt AX35 & pulley AK59: No tape: 100% Open damper: Motor pulley at 3 Turns open from fully close: with no econo | 80.003 | 0.013 | 66.998 | 0.018 | 94.92 | 0.051 | 69.914 | 0.063 | 80.05 | 0.06 | 63.44 | 0.03 | 66.92 | 0.02 | 1.786 | 0.013 | 1.6154 | 0.0068 | 78414 | 182 | 11189 | 181 | 9.533 | 0.032 | [6 empty] | 459.6 | 2.1 | 460.4 | 2.2 | 460.4 | 2.2 | 16 | 0 | 14 | 0 | 14 | 0 | 7300.9 | 45.9 | 3361.6 | 53.3 | 2099.6 | 36.3 | 460 |  | 458 |  | 460 |  | 3.4 |  | 3.5 |  | 3.4 |  | 0.72 | 462 |  | 458 |  | 456 |  | 5.1 |  | 5 |  | 4.5 |  | 3230 |  | 0.72 | 458 | 462 | 458 | 5.3 | 5.1 | 4.7 | 3340 | 0.84 | 458.9 |  | 1.7 |  | 739.9 |  | 115 |  | 9394.9 | [22 empty] | 257.14 | 0.36 | 168.64 | 0.09 | 119.09 | 0.1 | 49.55 | 0.09 |  |  | 99.54 | 0.11 | [6 empty] | 54.54 | 0.17 |  |  |  |  | 86.71 | 0.05 | 68.17 | 0.14 | 51.36 | 0.03 | 16.82 | 0.14 | [46 empty] | 264.14 | 0.35 | 171.76 | 0.19 | 121.08 | 0.1 | 50.68 | 0.18 | [8 empty] | 96.83 | 0.09 | [10 empty] | 84.95 | 0.09 | 63.24 | 0.32 | 50.3 | 0.05 | 12.94 | 0.35 | 99.62 | 0.09 | [36 empty] | 63.22 | 0.04 | 63.97 | 0.04 | 63.33 | 0.04 | 63.75 | 0.03 | 63.22 | 0.03 | 63.43 | 0.04 | [18 empty] | 99.54 | 0.11 | [12 empty] | 105.22 | 0.13 | 100 | 0.1 | 89.57 | 0.31 | 88.31 | 0.36 | 91.34 | 0.18 | 92.01 | 0.16 | 91.47 | 0.19 | 91.93 | 0.21 | [8 empty] | 105.1 | 0.12 | 99.62 | 0.09 | [16 empty] | 58.86 | 0.39 | [14 empty] | 95.86 | 0.16 | 95.74 | 0.17 | 80.44 | 0.06 | 80.41 | 0.06 | 80.19 | 0.05 | 80.62 | 0.06 | 80.58 | 0.06 | 80.66 | 0.07 | 80.5 | 0.06 | 80.42 | 0.05 | 80.36 | 0.05 | 80.23 | 0.06 | 80 | 0.05 | 79.83 | 0.06 | 80.59 | 0.07 | 80.53 | 0.07 | 80.55 | 0.07 | 80.44 | 0.08 | 80.42 | 0.08 | 80.42 | 0.07 | 80.73 | 0.06 | 80.54 | 0.06 | 80.4 | 0.06 | 80.49 | 0.06 | 79.97 | 0.07 | 79.94 | 0.07 | 80.83 | 0.07 | 80 | 0.06 | 80.04 | 0.07 | [84 empty] | No Economizer | 80.003 | 0.013 | 66.998 | 0.018 | 63.532 | 0.012 | 60.775 | 0.016 | 94.92 | 0.051 | 69.914 | 0.063 | 4427.9 | 9.4 | 4272 | 9.2 | 0.251 | 0.007 | -0.686 | 0.005 | 1.786 | 0.013 | 1.6154 | 0.0068 | 29.124 | 0.001 | 9400 | 20 | 1970 |  |  | 0 |  |  | 1.3099 | 20013.4308 | 125.9709 | 0 | 0 | 20013.4308 | 0.011074 | 31.3439 | 62.2221 | 14.0632 | 13.2748 | 0.0097403 | 33.5258 | 0.011074 | 31.3439 | 0.010699 | 26.9016 | 80.003 | 66.998 | 26.581 | 95322.7824 | 85405.7198 | 7430 | 0.26603 | 89029.111 | 79112.0483 | 9.4712 | 0.1619 | -4.7629 | -17.7809 | 58.7873 | 95322.7824 | 88906.4151 | 6416.3674 | 0 | 95322.7824 | 100%
2 | T2-TRN-100A-55-NE | 75T0001 | T2-TRN-100A-55-NE | none | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/24/2014 | 9:05:36 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 3.6 | 0 | -208 | 17 | -483 | 123 | 1052 | 65 | 845 | 74 | 0.49911 | 946 | 1580 |  | -0.12286 | [35 empty] | No economizer, no compressor, 55/51 ambient, 100% airflow (400 cfm/ton), 2 HP fan motor,--3 turns, 5.75" AK59 pulley (950 rpm), Econo closed unsealed cab, adjust code tester speed--to match total static of run T2-TRN-100A-55-NE-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley:3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.007 | 0.007 | 61.998 | 0.029 | 55.012 | 0.008 | 51.002 | 0.014 | 75.02 | 0.04 | 75.17 | 0.02 | 75.1 | 0 | 0.217 | 0.004 | 1.9568 | 0.0027 | -208 | 17 | 1052 | 65 | 0.499 | 0.043 | [6 empty] | 460 | 2 | 460.9 | 2 | 460 | 2 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1576.7 | 14 | 1097 | 17.9 | 116.2 | 9.9 | 460 |  | 459 |  | 459 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.54 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 1665 | [14 empty] | 94.93 | 0.01 | 55.99 | 0.04 | 56.21 | 0 | 0.22 | 0.03 | 93.99 | 0 | 57.08 | 0.01 | 55.68 | 0 | -1.39 | 0.02 |  |  | 69.35 | 0.02 |  |  |  |  | 94.19 | 0.01 | 71.44 | 0.02 | 55.79 | 0.01 | 15.65 | 0.02 | 92.7 | 0.03 | 57.18 | 0.02 | 54.95 | 0.02 | 2.23 | 0.03 | [46 empty] | 95.27 | 0.02 | 57.87 | 0.02 | 56.41 | 0.01 | 1.47 | 0.01 | 95.96 | 0.01 | 56.79 | 0.01 | 1.21 | 0.03 |  |  | 72.62 | 0.02 |  |  |  |  | 94.94 | 0.01 | 56.22 | 0.01 | 14.94 | 0.03 | 94.74 | 0.01 | 58.92 | 0.01 | 56.1 | 0.01 | 2.81 | 0.02 | 57.6 | 0.02 | [28 empty] | 57.29 | 0.03 | 57.66 | 0.02 | 57.6 | 0.02 | 58.7 | 0.04 | 75.17 | 0.03 | 74.98 | 0.02 | 74.82 | 0.03 | 75.42 | 0.02 | 75.41 | 0.02 |  |  | 55.64 | 0.02 | 69.73 | 0.02 | 71.88 | 0.02 | 57.64 | 0.01 | 58.63 | 0.01 | 55.88 | 0.01 | 73.23 | 0.02 | 72.39 | 0.02 | 60.88 | 0.02 | 69.35 | 0.02 | 72.62 | 0.02 | 55.94 | 0.03 | 56.63 | 0.01 | 58.46 | 0.02 | 56.78 | 0.04 | 57.79 | 0.02 | 57.66 | 0.02 | 58.7 | 0.04 | [16 empty] | 55.99 | 0.04 | 55.57 | 0.03 | 57.29 | 0.03 | 57.6 | 0.02 | [16 empty] | 71.16 | 0.03 | [12 empty] | 57.25 | 0.02 | 56.05 | 0.05 | 55.56 | 0.02 | 75.45 | 0.01 | 75.21 | 0.01 | 75 | 0.02 | 75.84 | 0.02 | 75.82 | 0.03 | 75.76 | 0.02 | 75.55 | 0.02 | 74.52 | 0.05 | 74.42 | 0.06 | 74.57 | 0.03 | 74.85 | 0.03 | 74.77 | 0.02 | 74.82 | 0.02 | 74.88 | 0.02 | 74.41 | 0.06 | 74.77 | 0.02 | 74.76 | 0.03 | 74.81 | 0.02 | 74.94 | 0.02 | 74.44 | 0.08 | 73.2 | 0.08 | 73.41 | 0.06 | 74.94 | 0.03 | 73.32 | 0.1 | 70.04 | 0.09 | 69.8 | 0.07 |  |  | 75.17 | 0.01 | 75.74 | 0.02 | 75.55 | 0.02 | 75.39 | 0.02 | 75.2 |  | 75.06 | 0.02 | 74.99 | 0.02 | 75.59 | 0.04 | 74.95 | 0.02 | 74.88 | 0.02 | 74.94 | 0.02 | [62 empty] | No Economizer | 75.007 | 0.007 | 61.998 | 0.029 | 75.08 | 0.005 | 61.944 | 0.028 | 55.012 | 0.008 | 51.002 | 0.014 | 3116.3 | 2.2 | 2996.7 | 2.1 | 0.674 | 0.003 | -0.315 | 0.002 | 0.217 | 0.004 | 1.9568 | 0.0027 | 29.5 | 0.001 | 1693 | 10 | 1580 |  |  | 0 |  |  | 1.3835 | 13797.1647 | 237.2839 | 0 | 0 | 13797.1647 | 0.0087777 | 27.6071 | 73.6965 | 13.0298 | 13.5519 | 0.0069796 | 20.7787 | 0.0087777 | 27.6071 | 0.0087248 | 27.5671 | 75.007 | 61.998 | 27.2297 | 5207.2911 | 4339.621 | 113 | 0.074063 | 624.601 | -243.069 | 0.36893 | 0.94676 | -0.37742 | -1.3105 | 50.3924 | 5207.2911 | 551.9965 | 4655.2945 | 0 | 5207.2911 | 100%
2 | T2-TRN-100A-55-NE-SC | 75T0004 | T2-TRN-100A-55-NE-SC | none | off | off | 3 turns | sealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/23/2014 | 23:18:51 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 3.6 | 0 | -2192 | 21 | -2510 | 142 | 496 | 60 | -1696 | 57 | -1.0101 | 945 | 1580 |  | -1.3055 | [35 empty] | No economizer, no compressor, 55/51 ambient, 100% airflow (400 cfm/ton), 2 HP fan motor,--3 turns, 5.75" AK59 pulley (950 rpm), Econo closed sealed cab,--adjust code tester speed to match total static of run T2-TRN-100A-55-NE-SPWCT-SS-SC | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley:3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.996 | 0.009 | 62.002 | 0.021 | 55.021 | 0.01 | 51.007 | 0.016 | 74.83 | 0.06 | 75.61 | 0.06 | 75.62 | 0 | 0.192 | 0.004 | 1.8891 | 0.0029 | -2192 | 21 | 496 | 60 | 0 | 0 | [6 empty] | 460 | 2 | 462 | 2 | 460.1 | 2 | 3.6 | 0 | 3.1 | 0 | 3.5 | 0 | 1582.9 | 14.3 | 1083.2 | 17.8 | 96.4 | 10.1 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.55 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 1665 | [14 empty] | 94.58 | 0.01 | 55.6 | 0.05 | 56.01 | 0.01 | 0.4 | 0.05 | 93.87 | 0.02 | 57.01 | 0.02 | 55.6 | 0.01 | 1.4 | 0.01 |  |  | 71.87 | 0.02 |  |  |  |  | 93.86 | 0.01 | 73.39 | 0.02 | 55.6 | 0 | 17.79 | 0.02 | 93.23 | 0.02 | 57.27 | 0.01 | 55.24 | 0.01 | 2.03 | 0.01 | [46 empty] | 94.96 | 0.02 | 58.1 | 0.02 | 56.21 | 0.01 | 1.88 | 0.02 | 95.66 | 0.01 | 56.61 | 0.01 | 0.66 | 0.04 |  |  | 74.18 | 0.02 |  |  |  |  | 94.65 | 0.01 | 56.04 | 0.01 | 17.15 | 0.03 | 94.48 | 0.01 | 59.1 | 0.02 | 55.95 | 0.01 | 3.15 | 0.02 | 58.48 | 0.04 | [28 empty] | 57.16 | 0.05 | 58.45 | 0.05 | 58.48 | 0.04 | 59.63 | 0.05 | 75.64 | 0.05 | 75.53 | 0.04 | 75.41 | 0.05 | 75.76 | 0.03 | 75.78 | 0.02 |  |  | 55.4 | 0.03 | 72.14 | 0.03 | 73.46 | 0.03 | 57.45 | 0.03 | 58.65 | 0.03 | 56.07 | 0.03 | 74.77 | 0.03 | 74.39 | 0.02 | 60.98 | 0.02 | 71.87 | 0.02 | 74.18 | 0.02 | 55.94 | 0.03 | 56.47 | 0.03 | 59.38 | 0.02 | 57.21 | 0.03 | 57.96 | 0.02 | 58.45 | 0.05 | 59.63 | 0.05 | [16 empty] | 55.6 | 0.05 | 55.94 | 0.04 | 57.16 | 0.05 | 58.48 | 0.04 | [16 empty] | 73.19 | 0.04 | [12 empty] | 57.05 | 0.03 | 55.6 | 0.04 | 55.35 | 0.02 | 75.28 | 0.03 | 75.14 | 0.02 | 74.9 | 0.02 | 75.61 | 0.03 | 75.63 | 0.03 | 75.61 | 0.03 | 75.43 | 0.03 | 75.13 | 0.03 | 75 | 0.03 | 74.76 | 0.03 | 75.02 | 0.03 | 74.85 | 0.03 | 74.82 | 0.03 | 74.9 | 0.03 | 74.76 | 0.03 | 74.74 | 0.03 | 74.79 | 0.03 | 74.78 | 0.03 | 74.93 | 0.03 | 74.78 | 0.03 | 74.46 | 0.03 | 74.56 | 0.02 | 75.01 | 0.03 | 74.47 | 0.03 | 74.24 | 0.05 | 74.38 | 0.03 |  |  | 75.03 | 0.02 | 75.79 | 0.02 | 75.59 | 0.03 | 75.42 | 0.03 | 75.22 |  | 75.06 | 0.02 | 75.44 | 0.03 | 76.77 | 0.05 | 75.03 | 0.03 | 74.88 | 0.03 | 74.95 | 0.03 | [62 empty] | No Economizer | 74.996 | 0.009 | 62.002 | 0.021 | 75.674 | 0.005 | 62.217 | 0.019 | 55.021 | 0.01 | 51.007 | 0.016 | 3065.7 | 2.4 | 2939.8 | 2.3 | 0.725 | 0.003 | -0.325 | 0.002 | 0.192 | 0.004 | 1.8891 | 0.0029 | 29.451 | 0.001 | 1679 | 10 | 1580 |  |  | 0 |  |  | 1.3942 | 13557.7551 | 250.3923 | 0 | 0 | 13557.7551 | 0.0087829 | 27.6101 | 74.2798 | 13.03 | 13.5673 | 0.0069801 | 20.7815 | 0.0087829 | 27.6101 | 0.0087648 | 27.7557 | 74.996 | 62.002 | 27.4156 | 2636.9174 | 2330.5037 | 99 | 0.12814 | -1901.0338 | -2207.4475 | -1.1322 | 0.96918 | -0.1945 | -0.71623 | 51.7588 | 2636.9174 | -1973.2648 | 4610.1823 | 0 | 2636.9174 | 100%
2 | T2-TRN-75A-55-NE-DM-SC | 75T0079 | T2-TRN-75A-55-NE-DM-SC | none | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/24/2014 | 4:00:05 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.4 | 0 | 3.2 | 0 | -277 | 27 | -533 | 111 | 286 | 62 | 9 | 70 | 0.0082873 | 754 | 990 |  | -0.25506 | [35 empty] | No economizer, no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-75A-55-NE-DM-SPWCT-SS-SC | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley:3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.015 | 0.012 | 62.002 | 0.034 | 54.989 | 0.007 | 51.007 | 0.015 | 74.95 | 0.05 | 75.16 | 0.03 | 75.3 | 0.01 | 0.102 | 0.002 | 1.1662 | 0.0019 | -277 | 27 | 286 | 62 | 0.066 | 0.031 | [6 empty] | 460.4 | 2 | 461.4 | 2.1 | 459.8 | 2 | 3.2 | 0 | 2.7 | 0 | 3 | 0 | 1261.6 | 15.2 | 1091.5 | 19.4 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.6 |  | 0.37 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 1075 | [14 empty] | 94.43 | 0.01 | 55.54 | 0.04 | 55.92 | 0.01 | 0.38 | 0.04 | 93.8 | 0 | 56.74 | 0.02 | 55.56 | 0 | -1.18 | 0.02 |  |  | 71.53 | 0.03 |  |  |  |  | 93.7 | 0.01 | 73.21 | 0.02 | 55.51 | 0 | 17.7 | 0.02 | 92.58 | 0.07 | 57.24 | 0.02 | 54.88 | 0.04 | 2.36 | 0.04 | [46 empty] | 94.83 | 0.02 | 57.88 | 0.03 | 56.15 | 0.01 | 1.73 | 0.03 | 95.51 | 0.01 | 56.53 | 0.01 | 1.22 | 0.05 |  |  | 74.18 | 0.04 |  |  |  |  | 94.51 | 0.01 | 55.96 | 0.01 | 17.04 | 0.05 | 94.38 | 0.01 | 59.08 | 0.02 | 55.89 | 0 | 3.19 | 0.03 | 58.44 | 0.03 | [28 empty] | 57.34 | 0.02 | 58.46 | 0.03 | 58.44 | 0.03 | 59.5 | 0.03 | 75.17 | 0.04 | 75.01 | 0.02 | 74.94 | 0.04 | 75.46 | 0.02 | 75.46 | 0.02 |  |  | 55.45 | 0.02 | 71.92 | 0.02 | 73.64 | 0.02 | 57.72 | 0.02 | 58.55 | 0.01 | 55.67 | 0.01 | 74.78 | 0.02 | 74.41 | 0.02 | 61.18 | 0.02 | 71.53 | 0.03 | 74.18 | 0.04 | 56.11 | 0.03 | 56.7 | 0.02 | 59.4 | 0.02 | 56.62 | 0.01 | 57.74 | 0.02 | 58.46 | 0.03 | 59.5 | 0.03 | [16 empty] | 55.54 | 0.04 | 55.31 | 0.06 | 57.34 | 0.02 | 58.44 | 0.03 | [16 empty] | 73 | 0.05 | [12 empty] | 56.99 | 0.02 | 55.75 | 0.03 | 55.53 | 0.01 | 75.4 | 0.02 | 75.19 | 0.02 | 74.97 | 0.03 | 75.84 | 0.03 | 75.83 | 0.03 | 75.8 | 0.04 | 75.59 | 0.04 | 75.13 | 0.03 | 74.99 | 0.03 | 74.77 | 0.03 | 74.95 | 0.03 | 74.82 | 0.03 | 74.8 | 0.03 | 74.89 | 0.03 | 74.71 | 0.03 | 74.72 | 0.03 | 74.77 | 0.03 | 74.78 | 0.03 | 74.84 | 0.03 | 74.69 | 0.04 | 74.36 | 0.03 | 74.47 | 0.03 | 74.87 | 0.03 | 74.29 | 0.03 | 74.09 | 0.05 | 74.27 | 0.03 |  |  | 75.15 | 0.03 | 75.84 | 0.03 | 75.64 | 0.04 | 75.45 | 0.03 | 75.21 |  | 75.09 | 0.03 | 75.47 | 0.03 | 77.45 | 0.06 | 74.98 | 0.03 | 74.86 | 0.03 | 74.86 | 0.03 | [62 empty] | No Economizer | 75.015 | 0.012 | 62.002 | 0.034 | 75.127 | 0.007 | 62.021 | 0.031 | 54.989 | 0.007 | 51.007 | 0.015 | 2404.4 | 1.9 | 2306.4 | 1.9 | 0.424 | 0.002 | -0.207 | 0.001 | 0.102 | 0.002 | 1.1662 | 0.0019 | 29.45 | 0 | 1086 | 9 | 990 |  |  | 0 |  |  | 1.1688 | 10644.0991 | 114.8856 | 0 | 0 | 10644.0991 | 0.0087784 | 27.6099 | 73.9582 | 13.0293 | 13.5534 | 0.0069876 | 20.7819 | 0.0087784 | 27.6099 | 0.0087645 | 27.6219 | 75.015 | 62.002 | 27.3369 | 2905.8081 | 2699.777 | 96 | 0.11276 | -80.9573 | -286.9885 | -0.074546 | 0.95267 | -0.273 | -1.0568 | 52.6841 | 2905.8081 | -128.4962 | 3034.3044 | 0 | 2905.8081 | 100%
2 | T2-TRN-75A-55-NE-DM | 75T0080 | T2-TRN-75A-55-NE-DM | none | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/24/2014 | 7:09:24 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 3.2 | 0 | 1245 | 17 | 968 | 87 | 1018 | 49 | 2264 | 50 | 2.1318 | 754 | 960 |  | 1.1723 | [35 empty] | No economizer, no compressor, 55/51 ambient, 75% airflow (300 cfm/ton),--2 HP fan motor, 3 turns, 7.25" AK74 pulley (725 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-75A-55-NE-DM-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley:3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.999 | 0.005 | 62.001 | 0.027 | 54.998 | 0.013 | 51.002 | 0.017 | 74.93 | 0.04 | 74.57 | 0.04 | 74.82 | 0 | 0.115 | 0.003 | 1.2012 | 0.002 | 1245 | 17 | 1018 | 49 | 2.132 | 0.05 | [6 empty] | 460.2 | 2.1 | 461.1 | 2.1 | 459.8 | 2.1 | 3.2 | 0 | 2.7 | 0 | 3.1 | 0 | 1257.8 | 15.2 | 1100.5 | 19.6 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.7 |  | 0.39 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1045 | [14 empty] | 94.84 | 0.02 | 56 | 0.04 | 56.16 | 0.01 | 0.15 | 0.04 | 94.06 | 0.01 | 57.02 | 0.02 | 55.72 | 0 | -1.3 | 0.02 |  |  | 68.89 | 0.02 |  |  |  |  | 94.12 | 0.01 | 71.35 | 0.02 | 55.75 | 0 | 15.59 | 0.02 | 92.3 | 0.03 | 57.3 | 0.02 | 54.71 | 0.02 | 2.59 | 0.03 | [46 empty] | 95.26 | 0 | 58.05 | 0.01 | 56.39 | 0 | 1.66 | 0.01 | 95.95 | 0.01 | 56.78 | 0.01 | 1.19 | 0.04 |  |  | 72.41 | 0.02 |  |  |  |  | 94.93 | 0.01 | 56.2 | 0.01 | 14.9 | 0.04 | 94.73 | 0.01 | 59.01 | 0.02 | 56.09 | 0.01 | 2.91 | 0.02 | 57.57 | 0.02 | [28 empty] | 57.1 | 0.03 | 57.59 | 0.03 | 57.57 | 0.02 | 58.67 | 0.04 | 74.61 | 0.03 | 74.4 | 0.03 | 74.26 | 0.04 | 74.84 | 0.02 | 74.83 | 0.02 |  |  | 55.61 | 0.02 | 69.14 | 0.02 | 71.66 | 0.02 | 57.63 | 0.02 | 58.73 | 0.02 | 55.84 | 0.02 | 72.99 | 0.02 | 72.31 | 0.01 | 60.98 | 0.01 | 68.89 | 0.02 | 72.41 | 0.02 | 55.92 | 0.02 | 56.7 | 0.01 | 58.36 | 0.01 | 56.72 | 0.04 | 57.82 | 0.02 | 57.59 | 0.03 | 58.67 | 0.04 | [16 empty] | 56 | 0.04 | 55.59 | 0.04 | 57.1 | 0.03 | 57.57 | 0.02 | [16 empty] | 71.11 | 0.04 | [12 empty] | 57.12 | 0.02 | 55.84 | 0.06 | 55.48 | 0.03 | 75.29 | 0.02 | 75.06 | 0.03 | 74.85 | 0.03 | 75.66 | 0.03 | 75.64 | 0.03 | 75.64 | 0.03 | 75.44 | 0.03 | 74.47 | 0.06 | 74.4 | 0.05 | 74.52 | 0.03 | 74.79 | 0.03 | 74.74 | 0.02 | 74.78 | 0.02 | 74.82 | 0.03 | 74.34 | 0.05 | 74.73 | 0.02 | 74.69 | 0.03 | 74.74 | 0.02 | 74.88 | 0.02 | 74.25 | 0.1 | 73.01 | 0.09 | 73.31 | 0.07 | 74.85 | 0.02 | 72.97 | 0.08 | 69.84 | 0.08 | 69.79 | 0.09 |  |  | 75.03 | 0.03 | 75.6 | 0.02 | 75.44 | 0.03 | 75.28 | 0.02 | 75.08 |  | 74.99 | 0.02 | 74.88 | 0.03 | 76.77 | 0.08 | 74.91 | 0.02 | 74.87 | 0.02 | 74.87 | 0.02 | [62 empty] | No Economizer | 74.999 | 0.005 | 62.001 | 0.027 | 74.532 | 0.004 | 61.72 | 0.029 | 54.998 | 0.013 | 51.002 | 0.017 | 2438.3 | 2.1 | 2343.4 | 2 | 0.417 | 0.002 | -0.199 | 0.001 | 0.115 | 0.003 | 1.2012 | 0.002 | 29.475 | 0.001 | 1062 | 8 | 960 |  |  | 0 |  |  | 1.1119 | 10806.5629 | 114.8015 | 0 | 0 | 10806.5629 | 0.0087815 | 27.6094 | 73.4201 | 13.0295 | 13.5379 | 0.0069829 | 20.7789 | 0.0087815 | 27.6094 | 0.0087071 | 27.414 | 74.999 | 62.001 | 27.1429 | 5041.133 | 4095.0168 | 102 | 0.069057 | 2156.4706 | 1210.3544 | 2.0306 | 0.93755 | -0.46649 | -1.5789 | 49.7159 | 5041.133 | 2110.8629 | 2930.2701 | 0 | 5041.133 | 100%
2 | T2-TRN-75A-55-RD-DM | 75T0082 | T2-TRN-75A-55-RD-DM | none | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/24/2014 | 23:31:43 | 10 Ton | 0:15:00 | 75/60 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 60 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 3.2 | 0 | 1840 | 17 | 1531 | 71 | 507 | 72 | 2348 | 80 | 2.2555 | 754 | 960 |  | 1.7675 | [35 empty] | Relief damper and no economizer, no compressor, 55/51 ambient, 75% airflow (300 cfm/ton),--2 HP fan motor, 3 turns, 7.25" AK74 pulley (725 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-75A-55-RD-DM-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.997 | 0.007 | 62 | 0.014 | 55 | 0.012 | 50.997 | 0.013 | 75.07 | 0.03 | 74.49 | 0.02 | 74.59 | 0.01 | 0.119 | 0.002 | 1.1973 | 0.002 | 1840 | 17 | 507 | 72 | 2.256 | 0.078 | [6 empty] | 459.7 | 2 | 461.7 | 2.1 | 460.2 | 2.1 | 3.2 | 0 | 2.7 | 0 | 3.1 | 0 | 1257.2 | 14.7 | 1108 | 20.2 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.6 |  | 0.38 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1045 | [14 empty] | 95.93 | 0.02 | 56.42 | 0.03 | 56.76 | 0.01 | 0.34 | 0.02 | 94.93 | 0.02 | 57.03 | 0.02 | 56.2 | 0.01 | -0.83 | 0.01 |  |  | 68.36 | 0.02 |  |  |  |  | 95.12 | 0.01 | 71.02 | 0.01 | 56.3 | 0.01 | 14.73 | 0.02 | 94.7 | 0.03 | 57.69 | 0.01 | 56.07 | 0.02 | 1.63 | 0.02 | [46 empty] | 95.94 | 0.01 | 58.45 | 0.02 | 56.76 | 0.01 | 1.68 | 0.02 | 96.59 | 0.04 | 57.12 | 0.02 | 0.85 | 0.06 |  |  | 72.28 | 0.02 |  |  |  |  | 95.64 | 0.01 | 56.59 | 0.01 | 14.07 | 0.03 | 95.42 | 0.01 | 59.25 | 0.02 | 56.47 | 0.01 | 2.78 | 0.02 | 57.77 | 0.02 | [28 empty] | 56.78 | 0.01 | 58.22 | 0.02 | 57.77 | 0.02 | 59.61 | 0.03 | 74.51 | 0.01 | 74.22 | 0.02 | 73.99 | 0.02 | 74.75 | 0.02 | 74.73 | 0.02 |  |  | 56.13 | 0.01 | 68.77 | 0.03 | 71.39 | 0.02 | 58.14 | 0.01 | 59.2 | 0.02 | 56.53 | 0.03 | 72.86 | 0.02 | 71.89 | 0.02 | 61.26 | 0.01 | 68.36 | 0.02 | 72.28 | 0.02 | 56.11 | 0.03 | 57.13 | 0.01 | 59.03 | 0.01 | 57.44 | 0.02 | 58.3 | 0.03 | 58.22 | 0.02 | 59.61 | 0.03 | [16 empty] | 56.42 | 0.03 | 56.27 | 0.06 | 56.78 | 0.01 | 57.77 | 0.02 | [16 empty] | 70.67 | 0.03 | [12 empty] | 57.26 | 0.02 | 56.18 | 0.06 | 55.87 | 0.04 | 75.47 | 0.01 | 72.84 | 0.05 | 74.8 | 0.03 | 73.87 | 0.05 | 75.89 | 0.03 | 75.88 | 0.02 | 75.53 | 0.02 | 74.01 | 0.04 | 73.94 | 0.04 | 74.22 | 0.03 | 74.36 | 0.04 | 74.3 | 0.03 | 74.56 | 0.03 | 74.69 | 0.03 | 74.19 | 0.05 | 74.68 | 0.02 | 74.67 | 0.03 | 74.62 | 0.03 | 74.95 | 0.02 | 74.44 | 0.08 | 72.69 | 0.08 | 72.96 | 0.05 | 74.63 | 0.03 | 72.94 | 0.07 | 69.31 | 0.1 | 69 | 0.1 |  |  | 73.39 | 0.05 | 75.85 | 0.01 | 75.67 | 0.02 | 75.09 | 0.03 | 72.94 |  | 75.07 | 0.02 | 74.43 | 0.03 | 74.64 | 0.04 | 74.37 | 0.03 | 74.54 | 0.03 | 74.95 | 0.02 | [62 empty] | No Economizer | 74.997 | 0.007 | 62 | 0.014 | 74.293 | 0.004 | 61.706 | 0.014 | 55 | 0.012 | 50.997 | 0.013 | 2435.5 | 2.1 | 2338.4 | 2 | 0.436 | 0.002 | -0.196 | 0.001 | 0.119 | 0.002 | 1.1973 | 0.002 | 29.436 | 0 | 1041 | 8 | 960 |  |  | 0 |  |  | 1.1062 | 10798.6813 | 119.7762 | 0 | 0 | 10798.6813 | 0.0087813 | 27.6087 | 73.1868 | 13.0295 | 13.5322 | 0.0069797 | 20.776 | 0.0087813 | 27.6087 | 0.0087544 | 27.4075 | 74.997 | 62 | 27.1377 | 5085.9186 | 4691.3889 | 81 | 0.054357 | 2218.2347 | 1823.705 | 2.1309 | 0.91929 | -0.47098 | -1.8102 | 52.5683 | 5085.9186 | 2172.6446 | 2913.274 | 0 | 5085.9186 | 100%
2 | T2-TRN-110A-55-RD-DM | 75T0115 | T2-TRN-110A-55-RD-DM | none | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/24/2014 | 20:29:39 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 4.1 | 0 | -1047 | 30 | -1356 | 150 | 719 | 85 | -327 | 86 | -0.14495 | 1054 | 2170 |  | -0.4641 | [35 empty] | Relief damper and no economizer, no compressor, 55/51 ambient, 110% airflow (450 cfm/ton),--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-110A-55-RD-DM-SPWCT-S | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.992 | 0.009 | 62.002 | 0.023 | 54.97 | 0.022 | 50.994 | 0.005 | 74.91 | 0.05 | 75.29 | 0.04 | 75.19 | 0.01 | 0.264 | 0.005 | 2.4115 | 0.0035 | -1047 | 30 | 719 | 85 | 0 | 0 | [6 empty] | 459.7 | 2 | 461.1 | 2 | 460.5 | 2 | 4.1 | 0 | 3.7 | 0 | 3.9 | 0 | 1861.2 | 13.4 | 1112.8 | 17.2 | 395 | 9.7 | 460 |  | 460 |  | 460 |  | 3.6 |  | 3.7 |  | 3.6 |  | 0.65 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 2255 | [14 empty] | 96.23 | 0.03 | 56.62 | 0.04 | 56.92 | 0.01 | 0.3 | 0.05 | 95.18 | 0.03 | 57.59 | 0.02 | 56.33 | 0.01 | -1.27 | 0.02 |  |  | 69.26 | 0.03 |  |  |  |  | 95.45 | 0.03 | 71.62 | 0.01 | 56.48 | 0.01 | 15.14 | 0.02 | 94.98 | 0.03 | 59.64 | 0.02 | 56.23 | 0.02 | 3.42 | 0.02 | [46 empty] | 96.31 | 0.03 | 56.15 | 0.02 | 56.96 | 0.01 | -0.82 | 0.02 | 96.92 | 0.03 | 57.3 | 0.02 | 0.84 | 0.09 |  |  | 72.67 | 0.02 |  |  |  |  | 96.08 | 0.03 | 56.84 | 0.02 | 14.22 | 0.04 | 95.81 | 0.03 | 61.01 | 0.02 | 56.69 | 0.02 | 4.33 | 0.02 | 58.02 | 0.05 | [28 empty] | 56.77 | 0.05 | 59.01 | 0.02 | 58.02 | 0.05 | 59.63 | 0.03 | 75.25 | 0.03 | 75.17 | 0.03 | 75.05 | 0.02 | 75.53 | 0.02 | 75.54 | 0.02 |  |  | 56.3 | 0.02 | 69.58 | 0.03 | 71.92 | 0.02 | 59.76 | 0.01 | 56.62 | 0.01 | 56.72 | 0.04 | 73.24 | 0.02 | 72.28 | 0.02 | 63.23 | 0.02 | 69.26 | 0.03 | 72.67 | 0.02 | 55.9 | 0.09 | 57.36 | 0.02 | 60.09 | 0.03 | 57.62 | 0.04 | 58.83 | 0.09 | 59.01 | 0.02 | 59.63 | 0.03 | [16 empty] | 56.62 | 0.04 | 56.47 | 0.09 | 56.77 | 0.05 | 58.02 | 0.05 | [16 empty] | 71.06 | 0.03 | [12 empty] | 57.63 | 0.01 | 55.97 | 0.07 | 55.53 | 0.05 | 75.37 | 0.02 | 73.04 | 0.04 | 74.74 | 0.03 | 73.9 | 0.04 | 75.75 | 0.03 | 75.71 | 0.03 | 75.4 | 0.03 | 74.05 | 0.05 | 73.92 | 0.05 | 74.16 | 0.03 | 74.42 | 0.04 | 74.28 | 0.04 | 74.49 | 0.03 | 74.62 | 0.03 | 74.19 | 0.04 | 74.61 | 0.03 | 74.63 | 0.03 | 74.56 | 0.03 | 74.82 | 0.02 | 74.41 | 0.05 | 72.75 | 0.06 | 73.02 | 0.04 | 74.56 | 0.04 | 73.01 | 0.06 | 69.53 | 0.1 | 69.05 | 0.08 |  |  | 73.43 | 0.05 | 75.78 | 0.03 | 75.58 | 0.03 | 75.01 | 0.03 | 73.04 |  | 75.05 | 0.02 | 74.43 | 0.03 | 74.75 | 0.04 | 74.39 | 0.04 | 74.51 | 0.04 | 74.84 | 0.02 | [62 empty] | No Economizer | 74.992 | 0.009 | 62.002 | 0.023 | 75.283 | 0.008 | 62.075 | 0.017 | 54.97 | 0.022 | 50.994 | 0.005 | 3466.9 | 2.5 | 3323.8 | 2.4 | 0.882 | 0.004 | -0.381 | 0.002 | 0.264 | 0.005 | 2.4115 | 0.0035 | 29.416 | 0 | 2256 | 10 | 2170 |  |  | 0 |  |  | 1.6916 | 15343.2426 | 344.4043 | 0 | 0 | 15343.2426 | 0.0087838 | 27.6102 | 73.5914 | 13.0288 | 13.5574 | 0.0069852 | 20.7746 | 0.0087838 | 27.6102 | 0.0087633 | 27.6587 | 74.992 | 62.002 | 27.2461 | 5586.5134 | 5157.3605 | 86 | 0.05254 | -644.2447 | -1073.3977 | -0.28557 | 0.93748 | -0.3641 | -1.4006 | 52.5913 | 5586.5134 | -743.4027 | 6329.9161 | 0 | 5586.5134 | 100%
2 | T2-TRN-110A-55-NE-DM-2 | 75T0112 | T2-TRN-110A-55-NE-DM | none | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/24/2014 | 12:48:27 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 4.2 | 0 | -1763 | 15 | -2060 | 133 | 906 | 89 | -856 | 92 | -0.37843 | 1055 | 2150 |  | -0.7794 | [35 empty] | No economizer, no compressor, 55/51 ambient, 110% airflow (450 cfm/ton), 2 HP fan motor,--1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam, adjust code tester speed to--to match total static of run T2-TRN-110A-55-CE-DM-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.002 | 0.009 | 62.009 | 0.021 | 54.997 | 0.01 | 51.003 | 0.014 | 74.96 | 0.06 | 75.53 | 0.05 | 75.37 | 0.01 | 0.27 | 0.004 | 2.4145 | 0.0037 | -1763 | 15 | 906 | 89 | 0 | 0 | [6 empty] | 460.5 | 2 | 461 | 2 | 459.6 | 2 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1883.8 | 13.6 | 1092.2 | 16.7 | 378.1 | 9.3 | 460 |  | 459 |  | 459 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.64 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 2235 | [14 empty] | 95.02 | 0.01 | 56.02 | 0.06 | 56.26 | 0 | 0.24 | 0.06 | 94.08 | 0.01 | 57.22 | 0.01 | 55.73 | 0.01 | -1.49 | 0.01 |  |  | 69.2 | 0.02 |  |  |  |  | 94.3 | 0.01 | 71.65 | 0.03 | 55.85 | 0 | 15.8 | 0.03 | 92.9 | 0.03 | 57.36 | 0.01 | 55.06 | 0.02 | 2.3 | 0.02 | [46 empty] | 95.34 | 0.01 | 58.02 | 0.02 | 56.44 | 0 | 1.59 | 0.02 | 96 | 0.01 | 56.81 | 0.01 | 0.99 | 0.07 |  |  | 72.74 | 0.02 |  |  |  |  | 94.99 | 0.01 | 56.24 | 0.01 | 15 | 0.04 | 94.78 | 0.01 | 59.36 | 0.02 | 56.13 | 0 | 3.24 | 0.02 | 57.76 | 0.03 | [28 empty] | 57.27 | 0.04 | 57.98 | 0.04 | 57.76 | 0.03 | 59.29 | 0.06 | 75.52 | 0.04 | 75.41 | 0.03 | 75.25 | 0.02 | 75.72 | 0.02 | 75.72 | 0.02 |  |  | 55.67 | 0.02 | 69.65 | 0.03 | 71.86 | 0.03 | 57.73 | 0.02 | 58.71 | 0.02 | 56.03 | 0.04 | 73.29 | 0.03 | 72.32 | 0.01 | 61.23 | 0.02 | 69.2 | 0.02 | 72.74 | 0.02 | 55.8 | 0.02 | 56.54 | 0.02 | 58.79 | 0.02 | 57.08 | 0.07 | 57.76 | 0.03 | 57.98 | 0.04 | 59.29 | 0.06 | [16 empty] | 56.02 | 0.06 | 55.82 | 0.07 | 57.27 | 0.04 | 57.76 | 0.03 | [16 empty] | 71.24 | 0.05 | [12 empty] | 57.28 | 0.01 | 56 | 0.05 | 55.49 | 0.03 | 75.37 | 0.02 | 75.19 | 0.02 | 74.94 | 0.02 | 75.72 | 0.02 | 75.71 | 0.04 | 75.67 | 0.03 | 75.48 | 0.03 | 74.44 | 0.04 | 74.31 | 0.05 | 74.47 | 0.03 | 74.76 | 0.03 | 74.7 | 0.02 | 74.75 | 0.03 | 74.77 | 0.03 | 74.34 | 0.04 | 74.72 | 0.02 | 74.72 | 0.03 | 74.72 | 0.02 | 74.81 | 0.02 | 74.35 | 0.07 | 73.19 | 0.08 | 73.28 | 0.06 | 74.76 | 0.04 | 73.3 | 0.08 | 69.96 | 0.1 | 69.59 | 0.07 |  |  | 75.11 | 0.02 | 75.66 | 0.02 | 75.48 | 0.03 | 75.32 | 0.03 | 75.15 |  | 75 | 0.02 | 74.9 | 0.03 | 75.5 | 0.04 | 74.87 | 0.02 | 74.79 | 0.02 | 74.81 | 0.02 | [62 empty] | No Economizer | 75.002 | 0.009 | 62.009 | 0.021 | 75.489 | 0.007 | 62.13 | 0.016 | 54.997 | 0.01 | 51.003 | 0.014 | 3465.8 | 2.7 | 3329 | 2.5 | 0.846 | 0.003 | -0.385 | 0.003 | 0.27 | 0.004 | 2.4145 | 0.0037 | 29.479 | 0.001 | 2262 | 10 | 2150 |  |  | 0 |  |  | 1.6867 | 15332.5825 | 330.8638 | 0 | 0 | 15332.5825 | 0.0087861 | 27.6151 | 73.8023 | 13.0294 | 13.5625 | 0.0069836 | 20.7795 | 0.0087861 | 27.6151 | 0.0087509 | 27.6954 | 75.002 | 62.009 | 27.284 | 5076.253 | 4414.8205 | 112 | 0.075303 | -1132.4589 | -1793.8914 | -0.50064 | 0.9491 | -0.33108 | -1.1997 | 51.4311 | 5076.253 | -1231.1244 | 6307.3774 | 0 | 5076.253 | 100%
2 | T2-TRN-110A-55-NE-DM-SC | 75T0113 | T2-TRN-110A-55-NE-DM-SC | none | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/23/2014 | 17:42:19 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 4.2 | 0 | -3751 | 26 | -4168 | 153 | 1062 | 63 | -2689 | 63 | -1.2021 | 1060 | 2140 |  | -1.6768 | [35 empty] | No economizer, no compressor, 55/51 ambient, 110% airflow (450 cfm/ton), 2 HP fan motor,--1 turn, 5.75" AK59 pulley (1060 rpm), sealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-110A-55-CE-DM-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam, Sealed Cabinet | 74.992 | 0.009 | 62.019 | 0.02 | 55 | 0.013 | 51.007 | 0.016 | 74.89 | 0.08 | 76.04 | 0.06 | 75.85 | 0 | 0.271 | 0.004 | 2.4037 | 0.0038 | -3751 | 26 | 1062 | 63 | 0 | 0 | [6 empty] | 460.6 | 2 | 461.1 | 2 | 459.6 | 2 | 4.2 | 0 | 3.7 | 0 | 3.8 | 0 | 1870.6 | 13.9 | 1089.9 | 16.8 | 366.4 | 10.3 | 460 |  | 459 |  | 460 |  | 3.7 |  | 3.6 |  | 3.6 |  | 0.64 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 2225 | [14 empty] | 94.65 | 0.01 | 55.72 | 0.07 | 56.02 | 0 | 0.33 | 0.07 | 93.97 | 0.01 | 57.39 | 0.02 | 55.64 | 0.01 | -1.74 | 0.02 |  |  | 71.86 | 0.03 |  |  |  |  | 93.91 | 0.02 | 73.55 | 0.02 | 55.61 | 0.01 | 17.94 | 0.02 | 93.39 | 0.08 | 57.57 | 0.02 | 55.31 | 0.04 | 2.25 | 0.04 | [46 empty] | 94.92 | 0.01 | 58.48 | 0.02 | 56.18 | 0.01 | 2.3 | 0.02 | 95.62 | 0.02 | 56.57 | 0.01 | 0.58 | 0.05 |  |  | 74.16 | 0.02 |  |  |  |  | 94.67 | 0.01 | 56.04 | 0.01 | 17.32 | 0.04 | 94.48 | 0.01 | 59.51 | 0.02 | 55.93 | 0 | 3.57 | 0.02 | 58.92 | 0.04 | [28 empty] | 57.24 | 0.06 | 58.46 | 0.05 | 58.92 | 0.04 | 59.79 | 0.07 | 76.04 | 0.06 | 75.94 | 0.05 | 75.83 | 0.04 | 76.26 | 0.02 | 76.27 | 0.02 |  |  | 55.52 | 0.03 | 72.47 | 0.03 | 73.73 | 0.02 | 57.83 | 0.02 | 59.12 | 0.02 | 56.41 | 0.02 | 74.7 | 0.02 | 74.41 | 0.01 | 61.27 | 0.01 | 71.86 | 0.03 | 74.16 | 0.02 | 55.64 | 0.05 | 56.92 | 0.01 | 59.39 | 0.01 | 58.06 | 0.03 | 58.69 | 0.04 | 58.46 | 0.05 | 59.79 | 0.07 | [16 empty] | 55.72 | 0.07 | 55.99 | 0.05 | 57.24 | 0.06 | 58.92 | 0.04 | [16 empty] | 73.36 | 0.04 | [12 empty] | 57.44 | 0.01 | 55.67 | 0.03 | 55.39 | 0.03 | 75.36 | 0.02 | 75.2 | 0.02 | 74.96 | 0.02 | 75.69 | 0.02 | 75.69 | 0.02 | 75.65 | 0.02 | 75.46 | 0.02 | 75.06 | 0.02 | 74.94 | 0.03 | 74.71 | 0.02 | 74.94 | 0.03 | 74.81 | 0.03 | 74.8 | 0.03 | 74.85 | 0.03 | 74.68 | 0.03 | 74.72 | 0.03 | 74.77 | 0.03 | 74.73 | 0.03 | 74.82 | 0.02 | 74.69 | 0.03 | 74.39 | 0.03 | 74.52 | 0.02 | 74.83 | 0.02 | 74.37 | 0.03 | 74.19 | 0.04 | 74.33 | 0.03 |  |  | 75.1 | 0.02 | 75.65 | 0.02 | 75.47 | 0.03 | 75.31 | 0.03 | 75.16 |  | 75 | 0.02 | 75.3 | 0.02 | 76.11 | 0.33 | 74.97 | 0.03 | 74.83 | 0.03 | 74.83 | 0.02 | [62 empty] | No Economizer | 74.992 | 0.009 | 62.019 | 0.02 | 76.025 | 0.005 | 62.317 | 0.018 | 55 | 0.013 | 51.007 | 0.016 | 3464 | 2.8 | 3315.6 | 2.6 | 0.903 | 0.004 | -0.408 | 0.003 | 0.271 | 0.004 | 2.4037 | 0.0038 | 29.403 | 0 | 2237 | 10 | 2140 |  |  | 0 |  |  | 1.6606 | 15309.3112 | 351.7345 | 0 | 0 | 15309.3112 | 0.008795 | 27.6225 | 74.3644 | 13.0295 | 13.5761 | 0.0069851 | 20.7817 | 0.008795 | 27.6225 | 0.0087482 | 27.8231 | 74.992 | 62.019 | 27.4181 | 3129.0339 | 2306.0774 | 97 | 0.1058 | -2974.3162 | -3797.2727 | -1.3296 | 0.97824 | -0.20439 | -0.62763 | 46.1537 | 3129.0339 | -3071.2761 | 6200.31 | 0 | 3129.0339 | 100%
2 | T2-TRN-88A-55-NE-DM-SC | 75T0090 | T2-TRN-88A-55-NE-DM-SC | none | off | off | 4.5 turns | unsealed | unsealed | 864 | 5.75 |  | 0 | 0 | CUST 5 | 10/24/2014 | 2:43:09 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 3.4 | 0 | -1335 | 15 | -1592 | 110 | 273 | 54 | -1062 | 51 | -0.77124 | 860 | 1280 |  | -0.9695 | [35 empty] | No economizer, no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor,--4.5 turns, 5.75" AK59 pulley (864 rpm), 100% inlet/outlet Meriam, adjust code tester speed--to match total static of run T2-TRN-88A-55-NE-DM-SPWCT-SS-SC | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley:4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.995 | 0.006 | 61.999 | 0.027 | 54.994 | 0.008 | 51.001 | 0.01 | 74.95 | 0.06 | 75.5 | 0.05 | 75.49 | 0 | 0.154 | 0.003 | 1.546 | 0.0023 | -1335 | 15 | 273 | 54 | 0 | 0 | [6 empty] | 460.3 | 2.1 | 461.4 | 2.1 | 459.7 | 2.1 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1415.3 | 15.3 | 1083.4 | 19.3 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.8 |  | 0.47 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 1365 | [14 empty] | 94.49 | 0 | 55.75 | 0.06 | 55.95 | 0 | 0.2 | 0.06 | 93.81 | 0.01 | 57.2 | 0.01 | 55.57 | 0 | -1.63 | 0.01 |  |  | 71.78 | 0.02 |  |  |  |  | 93.75 | 0.01 | 73.44 | 0.01 | 55.54 | 0.01 | 17.9 | 0.01 | 92.5 | 0.03 | 57.54 | 0.02 | 54.82 | 0.01 | 2.72 | 0.02 | [46 empty] | 94.92 | 0.01 | 58.45 | 0.02 | 56.19 | 0 | 2.25 | 0.02 | 95.6 | 0.01 | 56.57 | 0.01 | 0.9 | 0.05 |  |  | 74.17 | 0.02 |  |  |  |  | 94.59 | 0.01 | 56.01 | 0.01 | 17.25 | 0.03 | 94.46 | 0.01 | 59.54 | 0.01 | 55.93 | 0.01 | 3.6 | 0.02 | 59.05 | 0.03 | [28 empty] | 57.89 | 0.05 | 58.76 | 0.04 | 59.05 | 0.03 | 59.96 | 0.06 | 75.49 | 0.06 | 75.36 | 0.05 | 75.23 | 0.03 | 75.67 | 0.03 | 75.68 | 0.03 |  |  | 55.52 | 0.02 | 72.24 | 0.03 | 73.68 | 0.03 | 57.86 | 0.02 | 59.06 | 0.02 | 55.97 | 0.04 | 74.71 | 0.02 | 74.36 | 0.02 | 61.42 | 0.02 | 71.78 | 0.02 | 74.17 | 0.02 | 55.88 | 0.03 | 57.18 | 0.02 | 59.59 | 0.03 | 58.51 | 0.01 | 59.36 | 0.02 | 58.76 | 0.04 | 59.96 | 0.06 | [16 empty] | 55.75 | 0.06 | 55.67 | 0.05 | 57.89 | 0.05 | 59.05 | 0.03 | [16 empty] | 73.26 | 0.03 | [12 empty] | 57.27 | 0.02 | 55.63 | 0.03 | 55.4 | 0.02 | 75.3 | 0.02 | 75.09 | 0.02 | 74.88 | 0.02 | 75.64 | 0.02 | 75.63 | 0.03 | 75.59 | 0.03 | 75.39 | 0.03 | 75.06 | 0.02 | 74.93 | 0.02 | 74.68 | 0.02 | 74.91 | 0.02 | 74.76 | 0.03 | 74.78 | 0.02 | 74.83 | 0.02 | 74.67 | 0.03 | 74.7 | 0.03 | 74.75 | 0.03 | 74.7 | 0.02 | 74.84 | 0.02 | 74.72 | 0.03 | 74.4 | 0.03 | 74.5 | 0.02 | 74.89 | 0.02 | 74.41 | 0.02 | 74.19 | 0.04 | 74.32 | 0.03 |  |  | 75.02 | 0.03 | 75.64 | 0.02 | 75.46 | 0.03 | 75.3 | 0.02 | 75.14 |  | 75 | 0.02 | 75.3 | 0.02 | 77.01 | 0.1 | 74.94 | 0.02 | 74.79 | 0.03 | 74.86 | 0.02 | [62 empty] | No Economizer | 74.995 | 0.006 | 61.999 | 0.027 | 75.452 | 0.005 | 62.151 | 0.029 | 54.994 | 0.008 | 51.001 | 0.01 | 2771.6 | 2.1 | 2657.8 | 2 | 0.563 | 0.003 | -0.27 | 0.002 | 0.154 | 0.003 | 1.546 | 0.0023 | 29.448 | 0 | 1377 | 11 | 1280 |  |  | 0 |  |  | 1.2802 | 12262.148 | 175.7907 | 0 | 0 | 12262.148 | 0.0087811 | 27.608 | 74.1718 | 13.0294 | 13.5617 | 0.0069833 | 20.7783 | 0.0087811 | 27.608 | 0.0087736 | 27.7111 | 74.995 | 61.999 | 27.3989 | 2563.8854 | 2422.6499 | 97 | 0.12912 | -1204.7811 | -1346.0166 | -0.87493 | 0.96261 | -0.20909 | -0.82321 | 52.9791 | 2563.8854 | -1264.8285 | 3828.7138 | 0 | 2563.8854 | 100%
2 | T2-TRN-88A-55-NE-DM | 75T0091 | T2-TRN-88A-55-NE-DM | none | off | off | 4.5 turns | unsealed | unsealed | 864 | 5.75 |  | 0 | 0 | CUST 5 | 10/24/2014 | 10:47:42 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 3.4 | 0 | 380 | 14 | 80 | 93 | 905 | 67 | 1286 | 68 | 0.91923 | 854 | 1300 |  | 0.27162 | [35 empty] | No economizer, no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor,--4.5 turns, 5.75" AK59 pulley (864 rpm), 100% inlet/outlet Meriam, adjust code tester speed--to match total static of run T2-TRN-88A-55-NE-DM-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley:4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.005 | 0.009 | 62 | 0.022 | 55.004 | 0.013 | 51.002 | 0.016 | 74.98 | 0.04 | 74.96 | 0.03 | 75.03 | 0.01 | 0.162 | 0.003 | 1.5686 | 0.0027 | 380 | 14 | 905 | 67 | 0.919 | 0.049 | [6 empty] | 460 | 2 | 460.9 | 2 | 460.2 | 2 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1421 | 15 | 1104.2 | 18.7 | -9.2 | 2.5 | 460 |  | 459 |  | 459 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1385 | [14 empty] | 94.87 | 0.01 | 55.99 | 0.03 | 56.18 | 0 | 0.19 | 0.03 | 94.05 | 0 | 56.97 | 0.01 | 55.72 | 0 | -1.26 | 0.01 |  |  | 69.11 | 0.03 |  |  |  |  | 94.14 | 0.02 | 71.19 | 0.02 | 55.77 | 0.01 | 15.42 | 0.02 | 92.5 | 0.03 | 57.22 | 0.01 | 54.84 | 0.02 | 2.38 | 0.02 | [46 empty] | 95.26 | 0.01 | 58.14 | 0.01 | 56.39 | 0.01 | 1.74 | 0.01 | 95.92 | 0.01 | 56.77 | 0.01 | 1.24 | 0.03 |  |  | 72.46 | 0.02 |  |  |  |  | 94.9 | 0.01 | 56.2 | 0 | 14.66 | 0.04 | 94.7 | 0.01 | 58.99 | 0.01 | 56.08 | 0 | 2.9 | 0.02 | 57.79 | 0.02 | [28 empty] | 57.12 | 0.02 | 57.87 | 0.02 | 57.79 | 0.02 | 59.13 | 0.03 | 74.95 | 0.03 | 74.76 | 0.02 | 74.62 | 0.03 | 75.19 | 0.02 | 75.19 | 0.02 |  |  | 55.57 | 0.01 | 69.5 | 0.02 | 71.63 | 0.02 | 57.66 | 0.01 | 58.89 | 0.02 | 55.84 | 0.01 | 73.05 | 0.02 | 72.09 | 0.02 | 61 | 0.02 | 69.11 | 0.03 | 72.46 | 0.02 | 55.93 | 0.05 | 56.53 | 0.02 | 58.7 | 0.03 | 56.74 | 0.05 | 57.87 | 0.02 | 57.87 | 0.02 | 59.13 | 0.03 | [16 empty] | 55.99 | 0.03 | 55.53 | 0.03 | 57.12 | 0.02 | 57.79 | 0.02 | [16 empty] | 70.86 | 0.04 | [12 empty] | 57.13 | 0.01 | 55.99 | 0.05 | 55.56 | 0.03 | 75.38 | 0.02 | 75.14 | 0.01 | 74.94 | 0.02 | 75.75 | 0.02 | 75.76 | 0.03 | 75.71 | 0.02 | 75.52 | 0.02 | 74.49 | 0.06 | 74.39 | 0.05 | 74.5 | 0.03 | 74.78 | 0.03 | 74.72 | 0.03 | 74.77 | 0.03 | 74.82 | 0.03 | 74.34 | 0.05 | 74.72 | 0.02 | 74.7 | 0.03 | 74.74 | 0.03 | 74.88 | 0.02 | 74.35 | 0.08 | 73.13 | 0.08 | 73.32 | 0.07 | 74.87 | 0.02 | 73.23 | 0.08 | 69.92 | 0.08 | 69.64 | 0.08 |  |  | 75.13 | 0.02 | 75.68 | 0.02 | 75.5 | 0.02 | 75.33 | 0.02 | 75.14 |  | 75 | 0.02 | 74.93 | 0.03 | 75.53 | 0.04 | 74.89 | 0.03 | 74.83 | 0.03 | 74.89 | 0.02 | [62 empty] | No Economizer | 75.005 | 0.009 | 62 | 0.022 | 74.887 | 0.01 | 61.877 | 0.016 | 55.004 | 0.013 | 51.002 | 0.016 | 2787.6 | 2.4 | 2681.6 | 2.3 | 0.547 | 0.002 | -0.256 | 0.002 | 0.162 | 0.003 | 1.5686 | 0.0027 | 29.51 | 0.001 | 1399 | 13 | 1300 |  |  | 0 |  |  | 1.2985 | 12346.3171 | 172.3243 | 0 | 0 | 12346.3171 | 0.0087794 | 27.6086 | 73.5885 | 13.0296 | 13.547 | 0.0069815 | 20.7788 | 0.0087794 | 27.6086 | 0.0087263 | 27.5217 | 75.005 | 62 | 27.205 | 4982.7374 | 4197.2773 | 99 | 0.067812 | 1133.9801 | 348.52 | 0.81056 | 0.94179 | -0.40358 | -1.4165 | 50.6692 | 4982.7374 | 1072.9928 | 3909.7446 | 0 | 4982.7374 | 100%
2 | T2-TRN-88A-55-RD-DM | 75T0093 | T2-TRN-88A-55-RD-DM | none | off | off | 4.5 turns | unsealed | unsealed | 864 | 5.75 |  | 0 | 0 | CUST 5 | 10/24/2014 | 22:21:08 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 3.3 | 0 | 1126 | 16 | 801 | 102 | 477 | 78 | 1603 | 79 | 1.1641 | 858 | 1270 |  | 0.81772 | [35 empty] | Relief damper and no economizer, no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton),--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (864 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-88A-55-RD-DM-SPWCT | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.004 | 0.009 | 62.007 | 0.029 | 55 | 0.011 | 50.994 | 0.015 | 74.97 | 0.04 | 74.7 | 0.05 | 74.79 | 0.01 | 0.151 | 0.003 | 1.5679 | 0.0027 | 1126 | 16 | 477 | 78 | 1.165 | 0.058 | [6 empty] | 459.7 | 2 | 461.5 | 2.1 | 460.3 | 2.1 | 3.3 | 0 | 2.9 | 0 | 3.2 | 0 | 1400.8 | 14.8 | 1096.5 | 19.2 | -9.6 | 1.6 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.8 |  | 0.48 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1355 | [14 empty] | 95.89 | 0.01 | 56.43 | 0.07 | 56.73 | 0 | 0.29 | 0.08 | 94.94 | 0.02 | 57.34 | 0.02 | 56.21 | 0.01 | -1.13 | 0.02 |  |  | 68.84 | 0.03 |  |  |  |  | 95.17 | 0.01 | 71.28 | 0.02 | 56.33 | 0 | 14.95 | 0.02 | 94.71 | 0.04 | 58.63 | 0.02 | 56.08 | 0.02 | 2.56 | 0.03 | [46 empty] | 96.03 | 0.01 | 59.03 | 0.04 | 56.81 | 0 | 2.21 | 0.04 | 96.65 | 0.04 | 57.15 | 0.02 | 0.89 | 0.03 |  |  | 72.49 | 0.01 |  |  |  |  | 95.72 | 0.01 | 56.64 | 0.01 | 14.2 | 0.05 | 95.49 | 0.01 | 60.05 | 0.02 | 56.51 | 0.01 | 3.54 | 0.02 | 57.76 | 0.03 | [28 empty] | 57.13 | 0.03 | 58.8 | 0.03 | 57.76 | 0.03 | 59.68 | 0.06 | 74.69 | 0.06 | 74.5 | 0.04 | 74.36 | 0.04 | 74.97 | 0.01 | 74.95 | 0.02 |  |  | 56.09 | 0.02 | 69.15 | 0.02 | 71.67 | 0.02 | 58.93 | 0.03 | 59.74 | 0.04 | 56.58 | 0.03 | 73.07 | 0.01 | 72.12 | 0.01 | 62.1 | 0.02 | 68.84 | 0.03 | 72.49 | 0.01 | 56.1 | 0.03 | 57.23 | 0.02 | 59.81 | 0.03 | 57.46 | 0.02 | 58.47 | 0.04 | 58.8 | 0.03 | 59.68 | 0.06 | [16 empty] | 56.43 | 0.07 | 56.26 | 0.04 | 57.13 | 0.03 | 57.76 | 0.03 | [16 empty] | 70.84 | 0.06 | [12 empty] | 57.45 | 0.02 | 56.06 | 0.05 | 55.73 | 0.03 | 75.38 | 0.02 | 73 | 0.04 | 74.74 | 0.02 | 73.89 | 0.04 | 75.8 | 0.02 | 75.78 | 0.03 | 75.46 | 0.03 | 73.97 | 0.04 | 73.88 | 0.05 | 74.18 | 0.03 | 74.34 | 0.03 | 74.27 | 0.03 | 74.5 | 0.03 | 74.65 | 0.03 | 74.15 | 0.05 | 74.6 | 0.02 | 74.61 | 0.03 | 74.56 | 0.02 | 74.88 | 0.02 | 74.45 | 0.06 | 72.73 | 0.09 | 73.01 | 0.04 | 74.63 | 0.03 | 73.01 | 0.07 | 69.4 | 0.1 | 68.99 | 0.09 |  |  | 73.44 | 0.05 | 75.75 | 0.02 | 75.57 | 0.02 | 75 | 0.03 | 72.93 |  | 75.05 | 0.02 | 74.37 | 0.03 | 74.61 | 0.04 | 74.34 | 0.03 | 74.48 | 0.03 | 74.9 | 0.02 | [62 empty] | No Economizer | 75.004 | 0.009 | 62.007 | 0.029 | 74.629 | 0.005 | 61.847 | 0.025 | 55 | 0.011 | 50.994 | 0.015 | 2790.3 | 2.4 | 2677.7 | 2.3 | 0.583 | 0.003 | -0.253 | 0.002 | 0.151 | 0.003 | 1.5679 | 0.0027 | 29.431 | 0 | 1377 | 10 | 1270 |  |  | 0 |  |  | 1.2494 | 12363.9401 | 183.3984 | 0 | 0 | 12363.9401 | 0.0087843 | 27.6136 | 73.3796 | 13.0295 | 13.5408 | 0.0069782 | 20.7742 | 0.0087843 | 27.6136 | 0.0087675 | 27.5038 | 75.004 | 62.007 | 27.1991 | 5125.0153 | 4820.2392 | 107 | 0.071257 | 1416.4441 | 1111.668 | 1.0286 | 0.92647 | -0.41451 | -1.6244 | 52.912 | 5125.0153 | 1357.3954 | 3767.6199 | 0 | 5125.0153 | 100%
2 | T2-TRN-100A-55-RD | 75T0098 | T2-TRN-100A-55-RD | none | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/24/2014 | 21:31:33 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.5 | 0 | 3.6 | 0 | 373 | 12 | 73 | 119 | 535 | 75 | 909 | 79 | 0.53819 | 945 | 1590 |  | 0.22084 | [35 empty] | Relief damper and no economizer, no compressor, 55/51 ambient, 100% airflow (400 cfm/ton),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), Econo closed unsealed cab,--adjust code tester speed to match total static of run T2-TRN-100A-55-RD-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.982 | 0.004 | 62.004 | 0.03 | 55.014 | 0.01 | 51 | 0.014 | 74.95 | 0.05 | 74.93 | 0.03 | 74.92 | 0.01 | 0.201 | 0.004 | 1.9324 | 0.0025 | 373 | 12 | 535 | 75 | 0.538 | 0.047 | [6 empty] | 459.5 | 2 | 461 | 2 | 460.5 | 2 | 3.6 | 0 | 3.1 | 0 | 3.4 | 0 | 1557.6 | 14 | 1103.5 | 18.1 | 131.5 | 9.6 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.56 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1675 | [14 empty] | 96.05 | 0.02 | 56.58 | 0.04 | 56.81 | 0.01 | 0.24 | 0.04 | 95.08 | 0.02 | 57.38 | 0.02 | 56.28 | 0.01 | -1.1 | 0.02 |  |  | 69.01 | 0.02 |  |  |  |  | 95.3 | 0.02 | 71.37 | 0.02 | 56.4 | 0.01 | 14.96 | 0.02 | 94.83 | 0.03 | 58.76 | 0.02 | 56.13 | 0.01 | 2.63 | 0.03 | [46 empty] | 96.19 | 0.02 | 56.48 | 0.03 | 56.89 | 0.01 | -0.42 | 0.03 | 96.8 | 0.03 | 57.23 | 0.02 | 0.8 | 0.09 |  |  | 72.63 | 0.02 |  |  |  |  | 95.89 | 0.02 | 56.73 | 0.01 | 14.2 | 0.04 | 95.64 | 0.02 | 60.22 | 0.03 | 56.59 | 0.01 | 3.63 | 0.03 | 57.84 | 0.04 | [28 empty] | 56.91 | 0.04 | 58.91 | 0.03 | 57.84 | 0.04 | 59.85 | 0.04 | 74.89 | 0.03 | 74.76 | 0.02 | 74.65 | 0.03 | 75.19 | 0.01 | 75.18 | 0.01 |  |  | 56.2 | 0.02 | 69.35 | 0.02 | 71.74 | 0.02 | 59.05 | 0.01 | 56.92 | 0.02 | 56.72 | 0.05 | 73.2 | 0.03 | 72.22 | 0.02 | 62.39 | 0.01 | 69.01 | 0.02 | 72.63 | 0.02 | 56.1 | 0.06 | 57.28 | 0.02 | 59.98 | 0.02 | 57.54 | 0.02 | 58.68 | 0.06 | 58.91 | 0.03 | 59.85 | 0.04 | [16 empty] | 56.58 | 0.04 | 56.43 | 0.09 | 56.91 | 0.04 | 57.84 | 0.04 | [16 empty] | 70.93 | 0.04 | [12 empty] | 57.49 | 0.02 | 56.1 | 0.06 | 55.7 | 0.04 | 75.36 | 0.02 | 73.02 | 0.04 | 74.74 | 0.02 | 73.9 | 0.04 | 75.77 | 0.02 | 75.76 | 0.03 | 75.44 | 0.03 | 74.03 | 0.04 | 73.9 | 0.04 | 74.15 | 0.03 | 74.4 | 0.04 | 74.29 | 0.03 | 74.49 | 0.02 | 74.62 | 0.03 | 74.17 | 0.05 | 74.59 | 0.02 | 74.61 | 0.03 | 74.56 | 0.02 | 74.87 | 0.02 | 74.45 | 0.07 | 72.8 | 0.08 | 73.04 | 0.06 | 74.62 | 0.02 | 73.06 | 0.07 | 69.43 | 0.09 | 68.96 | 0.08 |  |  | 73.45 | 0.05 | 75.77 | 0.02 | 75.58 | 0.03 | 75.01 | 0.03 | 72.98 |  | 75.04 | 0.02 | 74.4 | 0.03 | 74.74 | 0.03 | 74.39 | 0.03 | 74.52 | 0.03 | 74.9 | 0.02 | [62 empty] | No Economizer | 74.982 | 0.004 | 62.004 | 0.03 | 74.874 | 0.003 | 61.942 | 0.033 | 55.014 | 0.01 | 51 | 0.014 | 3100.3 | 2 | 2974.2 | 1.9 | 0.71 | 0.003 | -0.308 | 0.002 | 0.201 | 0.004 | 1.9324 | 0.0025 | 29.424 | 0 | 1689 | 10 | 1590 |  |  | 0 |  |  | 1.3894 | 13731.2294 | 248.0811 | 0 | 0 | 13731.2294 | 0.0087875 | 27.6118 | 73.4846 | 13.0298 | 13.5471 | 0.0069781 | 20.7775 | 0.0087875 | 27.6118 | 0.0087722 | 27.5687 | 74.982 | 62.004 | 27.2298 | 5245.1671 | 4934.5409 | 99 | 0.064419 | 665.1977 | 354.5715 | 0.39384 | 0.93211 | -0.38199 | -1.4974 | 52.9275 | 5245.1671 | 592.2353 | 4652.9317 | 0 | 5245.1671 | 100%
2 | T2-TRN-63A-55-NE-DM-SC | 75T0064 | T2-TRN-63A-55-NE-DM-SC | none | off | off | 5.5 turns | sealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/24/2014 | 5:11:19 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.1 | 0 | 71 | 20 | -111 | 58 | 135 | 41 | 206 | 44 | 0.26142 | 635 | 710 |  | 0.090102 | [35 empty] | No economizer, no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton), 2 HP fan motor,--5.5 turns, 7.25" AK74 pulley (620 rpm), sealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-NE-DM-SPWCT-SS-SC | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley:5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.006 | 0.01 | 62.007 | 0.018 | 54.999 | 0.013 | 51.001 | 0.017 | 74.92 | 0.04 | 74.98 | 0.04 | 75.26 | 0 | 0.066 | 0.002 | 0.8137 | 0.0014 | 71 | 20 | 135 | 41 | 0.262 | 0.057 | [6 empty] | 460.5 | 2 | 461.3 | 2 | 459.7 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1138.4 | 15.4 | 1112.8 | 19.9 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.29 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 | [16 empty] | 94.49 | 0.01 | 55.64 | 0.05 | 55.96 | 0.01 | 0.31 | 0.06 | 93.86 | 0 | 56.88 | 0.02 | 55.6 | 0 | -1.28 | 0.02 |  |  | 71.34 | 0.02 |  |  |  |  | 93.75 | 0 | 73.04 | 0.01 | 55.53 | 0 | 17.51 | 0.01 | 92.24 | 0.03 | 57.27 | 0.03 | 54.68 | 0.02 | 2.6 | 0.03 | [46 empty] | 94.89 | 0 | 58.06 | 0.02 | 56.18 | 0 | 1.87 | 0.02 | 95.58 | 0.01 | 56.56 | 0.01 | 1.15 | 0.06 |  |  | 73.98 | 0.02 |  |  |  |  | 94.54 | 0.01 | 55.99 | 0.01 | 16.91 | 0.05 | 94.44 | 0 | 59.19 | 0.02 | 55.92 | 0 | 3.27 | 0.02 | 58.38 | 0.03 | [28 empty] | 57.5 | 0.03 | 58.6 | 0.03 | 58.38 | 0.03 | 59.8 | 0.05 | 74.98 | 0.04 | 74.84 | 0.03 | 74.76 | 0.03 | 75.27 | 0.02 | 75.27 | 0.03 |  |  | 55.53 | 0.03 | 71.74 | 0.02 | 73.47 | 0.02 | 57.75 | 0.02 | 58.71 | 0.02 | 55.75 | 0.01 | 74.6 | 0.02 | 74.24 | 0.03 | 61.19 | 0.03 | 71.34 | 0.02 | 73.98 | 0.02 | 56.14 | 0.05 | 56.87 | 0.02 | 59.58 | 0.01 | 56.67 | 0.02 | 57.8 | 0.03 | 58.6 | 0.03 | 59.8 | 0.05 | [16 empty] | 55.64 | 0.05 | 55.41 | 0.06 | 57.5 | 0.03 | 58.38 | 0.03 | [16 empty] | 72.89 | 0.06 | [12 empty] | 57.07 | 0.02 | 55.73 | 0.03 | 55.53 | 0.03 | 75.32 | 0.02 | 75.11 | 0.02 | 74.92 | 0.01 | 75.74 | 0.02 | 75.72 | 0.04 | 75.71 | 0.03 | 75.52 | 0.02 | 75.03 | 0.03 | 74.9 | 0.03 | 74.7 | 0.03 | 74.89 | 0.02 | 74.73 | 0.02 | 74.72 | 0.02 | 74.82 | 0.02 | 74.63 | 0.02 | 74.65 | 0.02 | 74.7 | 0.02 | 74.72 | 0.02 | 74.82 | 0.02 | 74.66 | 0.03 | 74.32 | 0.03 | 74.42 | 0.03 | 74.83 | 0.03 | 74.18 | 0.03 | 73.97 | 0.06 | 74.18 | 0.04 |  |  | 75.11 | 0.01 | 75.74 | 0.02 | 75.56 | 0.02 | 75.39 | 0.02 | 75.14 |  | 75.04 | 0.02 | 75.37 | 0.02 | 77.21 | 0.06 | 74.91 | 0.02 | 74.78 | 0.02 | 74.84 | 0.02 | [62 empty] | No Economizer | 75.006 | 0.01 | 62.007 | 0.018 | 74.975 | 0.001 | 61.987 | 0.016 | 54.999 | 0.013 | 51.001 | 0.017 | 2005.6 | 1.7 | 1924.2 | 1.7 | 0.29 | 0.002 | -0.149 | 0.001 | 0.066 | 0.002 | 0.8137 | 0.0014 | 29.457 | 0 | 788 | 9 | 710 |  |  | 0 |  |  | 1.0316 | 8881.0943 | 65.5561 | 0 | 0 | 8881.0943 | 0.0087838 | 27.6136 | 73.9434 | 13.0295 | 13.5497 | 0.0069821 | 20.7783 | 0.0087838 | 27.6136 | 0.008778 | 27.5996 | 75.006 | 62.007 | 27.348 | 2358.6758 | 2264.9178 | 78 | 0.11287 | 159.1889 | 65.4309 | 0.20202 | 0.95117 | -0.26558 | -1.0626 | 53.2458 | 2358.6758 | 124.1258 | 2234.55 | 0 | 2358.6758 | 100%
2 | T2-TRN-63A-55-NE-DM | 75T0065 | T2-TRN-63A-55-NE-DM | none | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/24/2014 | 6:18:50 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 3 | 0 | 1434 | 15 | 1264 | 61 | 835 | 51 | 2270 | 57 | 2.8662 | 635 | 700 |  | 1.8106 | [35 empty] | No economizer, no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton), 2 HP fan motor,--5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-NE-DM-SPWCT-SS | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley:5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.999 | 0.008 | 62.002 | 0.025 | 55.005 | 0.008 | 51.001 | 0.01 | 74.95 | 0.03 | 74.38 | 0.02 | 74.8 | 0 | 0.075 | 0.002 | 0.8422 | 0.0013 | 1434 | 15 | 835 | 51 | 2.866 | 0.078 | [6 empty] | 460.2 | 2 | 461.3 | 2 | 459.9 | 2 | 3 | 0 | 2.6 | 0 | 3 | 0 | 1134.6 | 14.8 | 1118.2 | 19.5 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.3 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 785 | [14 empty] | 94.8 | 0.01 | 55.75 | 0.02 | 56.13 | 0 | 0.38 | 0.02 | 94.08 | 0.02 | 57.08 | 0.02 | 55.72 | 0.01 | -1.36 | 0.02 |  |  | 69.13 | 0.05 |  |  |  |  | 94.12 | 0.01 | 71.18 | 0.02 | 55.75 | 0.01 | 15.43 | 0.02 | 92.33 | 0.02 | 57.3 | 0.02 | 54.73 | 0.01 | 2.57 | 0.03 | [46 empty] | 95.2 | 0.01 | 58.24 | 0.03 | 56.36 | 0 | 1.88 | 0.03 | 95.89 | 0.01 | 56.74 | 0.01 | 1.23 | 0.03 |  |  | 72.4 | 0.02 |  |  |  |  | 94.86 | 0.01 | 56.17 | 0.01 | 14.85 | 0.02 | 94.67 | 0.01 | 58.91 | 0.02 | 56.06 | 0.01 | 2.85 | 0.02 | 57.76 | 0.03 | [28 empty] | 57.15 | 0.02 | 57.64 | 0.02 | 57.76 | 0.03 | 58.73 | 0.03 | 74.4 | 0.02 | 74.19 | 0.02 | 74.11 | 0.02 | 74.71 | 0.02 | 74.69 | 0.02 |  |  | 55.61 | 0.02 | 69.29 | 0.02 | 71.58 | 0.02 | 57.67 | 0.01 | 58.94 | 0.02 | 55.87 | 0.02 | 73.03 | 0.01 | 72.39 | 0.03 | 61.08 | 0.03 | 69.13 | 0.05 | 72.4 | 0.02 | 56.09 | 0.03 | 56.91 | 0.02 | 58.41 | 0.02 | 56.97 | 0.04 | 58.01 | 0.02 | 57.64 | 0.02 | 58.73 | 0.03 | [16 empty] | 55.75 | 0.02 | 55.51 | 0.03 | 57.15 | 0.02 | 57.76 | 0.03 | [16 empty] | 71.02 | 0.02 | [12 empty] | 57.25 | 0.01 | 55.86 | 0.04 | 55.55 | 0.02 | 75.32 | 0.02 | 75.06 | 0.02 | 74.89 | 0.02 | 75.72 | 0.02 | 75.7 | 0.03 | 75.7 | 0.03 | 75.5 | 0.02 | 74.58 | 0.06 | 74.51 | 0.05 | 74.59 | 0.02 | 74.76 | 0.03 | 74.69 | 0.03 | 74.76 | 0.03 | 74.81 | 0.03 | 74.28 | 0.05 | 74.7 | 0.03 | 74.65 | 0.04 | 74.73 | 0.02 | 74.89 | 0.02 | 74.21 | 0.11 | 72.95 | 0.09 | 73.33 | 0.07 | 74.85 | 0.03 | 72.78 | 0.11 | 69.87 | 0.1 | 69.99 | 0.1 |  |  | 75.08 | 0.02 | 75.71 | 0.03 | 75.53 | 0.02 | 75.37 | 0.02 | 75.15 |  | 75.04 | 0.01 | 75.03 | 0.03 | 76.98 | 0.08 | 74.86 | 0.03 | 74.82 | 0.03 | 74.88 | 0.02 | [62 empty] | No Economizer | 74.999 | 0.008 | 62.002 | 0.025 | 74.352 | 0.003 | 61.654 | 0.019 | 55.005 | 0.008 | 51.001 | 0.01 | 2039.3 | 1.6 | 1959.4 | 1.6 | 0.286 | 0.002 | -0.144 | 0.001 | 0.075 | 0.002 | 0.8422 | 0.0013 | 29.47 | 0.001 | 792 | 9 | 700 |  |  | 0 |  |  | 0.99718 | 9041.2424 | 65.8346 | 0 | 0 | 9041.2424 | 0.0087822 | 27.6101 | 73.3548 | 13.0296 | 13.5333 | 0.0069807 | 20.7782 | 0.0087822 | 27.6101 | 0.0087064 | 27.3694 | 74.999 | 62.002 | 27.1262 | 4375.179 | 3567.6964 | 92 | 0.071768 | 2210.7725 | 1403.29 | 2.7914 | 0.93468 | -0.48391 | -1.6442 | 49.8275 | 4375.179 | 2176.5553 | 2198.6238 | 0 | 4375.179 | 100%
2 | T2-TRN-63A-55-RD-DM | 75T0067 | T2-TRN-63A-55-RD-DM | none | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/25/2014 | 0:36:42 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.9 | 0 | 3 | 0 | 2010 | 15 | 1661 | 52 | 1552 | 54 | 3563 | 48 | 4.5331 | 635 | 700 |  | 2.5573 | [35 empty] | Relief damper and no economizer, no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton),--2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A- | WO/ECO: No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.997 | 0.005 | 61.999 | 0.014 | 54.998 | 0.011 | 51.009 | 0.017 | 75.07 | 0.02 | 74.33 | 0.01 | 74.57 | 0.01 | 0.073 | 0.002 | 0.8346 | 0.0014 | 2010 | 15 | 1552 | 54 | 4.531 | 0.076 | [6 empty] | 459.9 | 2.1 | 462 | 2.1 | 460.3 | 2.1 | 3 | 0 | 2.6 | 0 | 3 | 0 | 1136.5 | 15.7 | 1122 | 20.8 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.29 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 785 | [14 empty] | 95.37 | 0 | 56.28 | 0.01 | 56.44 | 0 | 0.17 | 0.01 | 94.58 | 0.02 | 57.05 | 0.01 | 56 | 0.01 | -1.05 | 0.01 |  |  | 68.78 | 0.02 |  |  |  |  | 94.73 | 0.01 | 71.11 | 0.02 | 56.09 | 0.01 | 15.03 | 0.02 | 94.28 | 0.05 | 57.81 | 0.01 | 55.83 | 0.02 | 1.98 | 0.02 | [46 empty] | 95.52 | 0 | 58.43 | 0.01 | 56.52 | 0 | 1.91 | 0.01 | 96.19 | 0.02 | 56.89 | 0.01 | 0.9 | 0.03 |  |  | 72.49 | 0.01 |  |  |  |  | 95.18 | 0.01 | 56.33 | 0.01 | 14.56 | 0.03 | 94.97 | 0.01 | 59.57 | 0.02 | 56.22 | 0 | 3.35 | 0.01 | 57.68 | 0.02 | [28 empty] | 57.25 | 0.02 | 58.09 | 0.02 | 57.68 | 0.02 | 59.12 | 0.02 | 74.34 | 0.01 | 74.07 | 0.01 | 73.85 | 0.01 | 74.62 | 0.01 | 74.61 | 0.02 |  |  | 56.19 | 0.02 | 69.16 | 0.01 | 71.56 | 0.02 | 58.38 | 0.02 | 59.27 | 0.01 | 56.37 | 0.02 | 73.07 | 0.01 | 72.24 | 0.02 | 61.72 | 0.02 | 68.78 | 0.02 | 72.49 | 0.01 | 56.24 | 0.03 | 57.13 | 0.01 | 59.02 | 0.01 | 57.27 | 0.02 | 58.19 | 0.02 | 58.09 | 0.02 | 59.12 | 0.02 | [16 empty] | 56.28 | 0.01 | 56 | 0.03 | 57.25 | 0.02 | 57.68 | 0.02 | [16 empty] | 70.89 | 0.03 | [12 empty] | 57.37 | 0.02 | 56.06 | 0.03 | 55.76 | 0.02 | 75.47 | 0.01 | 72.75 | 0.05 | 74.8 | 0.02 | 73.75 | 0.05 | 75.9 | 0.01 | 75.92 | 0.02 | 75.54 | 0.02 | 74.01 | 0.04 | 73.95 | 0.04 | 74.26 | 0.03 | 74.28 | 0.04 | 74.25 | 0.03 | 74.54 | 0.03 | 74.67 | 0.03 | 74.14 | 0.06 | 74.63 | 0.02 | 74.64 | 0.03 | 74.59 | 0.02 | 74.95 | 0.02 | 74.47 | 0.08 | 72.67 | 0.1 | 72.91 | 0.06 | 74.64 | 0.02 | 72.92 | 0.09 | 69.27 | 0.1 | 69.13 | 0.1 |  |  | 73.31 | 0.05 | 75.86 | 0.01 | 75.68 | 0.01 | 75.11 | 0.03 | 72.89 |  | 75.1 | 0.02 | 74.37 | 0.03 | 74.6 | 0.04 | 74.3 | 0.03 | 74.5 | 0.03 | 74.98 | 0.02 | [62 empty] | No Economizer | 74.997 | 0.005 | 61.999 | 0.014 | 74.091 | 0.004 | 61.444 | 0.011 | 54.998 | 0.011 | 51.009 | 0.017 | 2030.7 | 1.6 | 1949.9 | 1.6 | 0.3 | 0.002 | -0.141 | 0.001 | 0.073 | 0.002 | 0.8346 | 0.0014 | 29.436 | 0 | 786 | 8 | 700 |  |  | 0 |  |  | 0.99631 | 9007.921 | 68.7225 | 0 | 0 | 9007.921 | 0.0087807 | 27.608 | 73.0947 | 13.0295 | 13.5261 | 0.0069866 | 20.7829 | 0.0087807 | 27.608 | 0.0086308 | 27.2231 | 74.997 | 61.999 | 26.9801 | 5655.2972 | 4112.6013 | 86 | 0.051901 | 3500.7469 | 1958.0511 | 4.4539 | 0.9358 | -0.62781 | -1.9023 | 45.3644 | 5655.2972 | 3466.9865 | 2188.3107 | 0 | 5655.2972 | 100%
2 | 3T-22AA-0 | 75T0159 | 3T-22AA-0 | none | on | on | 6 turns | sealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 8/5/2014 | 16:24:51 | 10 Ton | 0:30:00 | 80/67 95/70 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 80 | 67 | 95 | 70 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.3 | 14.6 | 0 | 64167 | 145 | 63630 | 840 | 24100 | 286 | 88290 | 261 | 10.9135 | 776 | [38 empty] | A test factory chg, sealed cab, no econo, no mass flow meter, 2 HP fan,--760 rpm 5.75" pulley AK59 | Installed:SG:FD:LSV on 2 circuits: sealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 6 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 79.992 | 0.043 | 67.149 | 0.024 | 94.818 | 0.026 | 70.098 | 0.012 | 79.93 | 0.26 | 61.05 | 0.04 | 63.98 | 0.03 | 0.871 | 0.005 | 1.3046 | 0.0035 | 64167 | 145 | 24100 | 286 | 10.914 | 0.048 | [6 empty] | 460.8 | 2.5 | 460 | 2.5 | 459.3 | 2.5 | 14.6 | 0.1 | 12.8 | 0 | 12.4 | 0.1 | 6630.3 | 61.6 | 3260.5 | 69.6 | 1459.2 | 51.3 | 459 |  | 459 |  | 459 |  | 2.9 |  | 2.9 |  | 2.9 |  | 0.45 | 460 |  | 460 |  | 460 |  | 4.5 |  | 4.9 |  | 4.5 |  | 3160 |  | 0.85 | 459 | 459 | 459 | 4.9 | 4.6 | 4.5 | 3000 | 0.81 | 459.9 |  | 1.6 |  | 702 |  | 85 |  | 8097 | [14 empty] | 212.83 | 0.22 | 105.49 | 0.09 | 105.59 | 0.07 | 0.1 | 0.04 | 246.95 | 0.24 | 174.38 | 0.11 | 116.16 | 0.07 | 58.22 | 0.08 | 203 | 0.02 | 98.14 | 0.08 | 102.32 | 0.02 | 4.18 | 0.05 | 82.84 | 0.08 | 62.24 | 0.27 | 49.09 | 0.05 | 13.16 | 0.25 | 82.17 | 0.07 | 64.97 | 0.15 | 48.67 | 0.05 | 16.3 | 0.13 | [46 empty] | 247.21 | 0.26 | 166.43 | 0.27 | 116.24 | 0.08 | 50.19 | 0.29 | 228 | 0.34 | 110.42 | 0.1 | 9.21 | 0.13 | 217.4 | 0.01 | 100.11 | 0.12 | 107.07 | 0.1 | 6.96 | 0.08 | 82 | 0.16 | 48.57 | 0.09 | 4.01 | 1.11 | 81.55 | 0.14 | 59.84 | 0.6 | 48.29 | 0.09 | 11.55 | 0.64 | 103.47 | 0.09 | [28 empty] | 103.95 | 0.09 | 103.47 | 0.09 | 101.03 | 0.12 | 101.35 | 0.12 | 60.78 | 0.06 | 60.35 | 0.06 | 60.04 | 0.06 | 60.89 | 0.06 | 60.64 | 0.06 | 60.91 | 0.06 | 104.25 | 0.08 | 99.33 | 0.09 | 62.69 | 0.28 | 65.25 | 0.19 | 166.54 | 0.3 | 101.65 | 0.11 | 100.39 | 0.11 | 52.13 | 0.29 | 61.52 | 0.77 | 98.14 | 0.08 | 100.11 | 0.12 | 90.97 | 0.06 | 104.71 | 0.09 | 104.91 | 0.08 | 101.44 | 0.08 | 101.55 | 0.09 | 101.03 | 0.12 | 101.35 | 0.12 | [12 empty] | 105.49 | 0.09 | 60.91 | 0.06 |  |  | 101.21 | 0.12 | 103.95 | 0.09 | 103.47 | 0.09 | [16 empty] | 52.64 | 1.09 | [12 empty] | 174.06 | 0.12 | 94.09 | 0.15 | 94.07 | 0.15 | 80.76 | 0.15 | 80.42 | 0.14 | 80.29 | 0.15 | 80.92 | 0.11 | 81 | 0.15 | 80.88 | 0.15 | 80.66 | 0.15 | 80.43 | 0.16 | 80.39 | 0.14 | 80.25 | 0.15 | 80.58 | 0.19 | 80.56 | 0.18 | 80.42 | 0.17 | 80.31 | 0.16 | 80.67 | 0.14 | 80.43 | 0.17 | 80.28 | 0.16 | 80.19 | 0.16 | 80.38 | 0.16 | 79.58 | 0.25 | 80.4 | 0.14 | 80.28 | 0.15 | 80.35 | 0.13 | 80.39 | 0.11 | 80.39 | 0.11 | 80.47 | 0.12 |  |  | 80.24 | 0.14 | 80.92 | 0.12 | 80.7 | 0.14 | 80.42 | 0.15 | 80.28 |  | 80.17 | 0.17 | 80.95 | 0.14 | 81.38 | 0.16 | 80.55 | 0.18 | 80.55 | 0.17 | 80.38 | 0.15 | [62 empty] | No Economizer | 79.992 | 0.043 | 67.149 | 0.024 | 60.954 | 0.014 | 58.183 | 0.034 | 94.818 | 0.026 | 70.098 | 0.012 | 3063.8 | 4.1 | 2993.9 | 4.1 | 0.282 | 0.003 | -0.333 | 0.003 | 0.871 | 0.005 | 1.3046 | 0.0035 | 29.349 | 0.001 | 8090 | 25 | 1150 |  |  | 0 |  |  | 1.0728 | 13924.8978 | 99.1863 | 0 | 0 | 13924.8978 | 0.011188 | 31.466 | 59.8812 | 14.062 | 13.2014 | 0.0099078 | 33.6856 | 0.011188 | 31.466 | 0.0096777 | 25.1589 | 79.992 | 67.149 | 24.8968 | 91474.4154 | 67209.9056 | 6940 | 0.25894 | 87887.9881 | 63623.4783 | 10.8638 | 0.18837 | -6.5691 | -20.1108 | 55.2136 | 91474.4154 | 87824.8471 | 3649.5683 | 0 | 91474.4154 | 100%
2 | 3T-22B | 75T0160 | 3T-22B | none | on | on | 6 turns | unsealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 7/28/2014 | 17:55:41 | 10 Ton | 0:30:00 | 80/67 82 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 80 | 67 | 82 |  | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1 | 14 | 0 | 68698 | 119 | 66161 | 348 | 27271 | 129 | 95994 | 201 | 13.1932 | 762 |  |  |  | 112.8 | 0.01 | -0.85 | [32 empty] | B test factory chg, sealed cab, no econo | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: AK59 5.75 diam BP: ID Blw M: MQC 56T17D5563B: Mtr Pulley 6 T/O: No econo: Meriam @100%: Horiz Air Disch | 79.998 | 0.01 | 67.15 | 0.016 | 81.84 | 0.011 | 67.594 | 0.018 | 79.29 | 0.11 | 59.68 | 0.04 | 62.7 | 0.02 | 0.886 | 0.006 | 1.2974 | 0.004 | 68698 | 119 | 27271 | 129 | 13.193 | 0.047 | 95185 | 94 | 13.082 | 0.038 | -0.85 | 0.21 | 460.8 | 2.3 | 460.4 | 2.3 | 459.2 | 2.3 | 14 | 0.1 | 11.9 | 0.1 | 11.6 | 0.1 | 6256.8 | 63.2 | 3191.6 | 68.7 | 1018.7 | 54.2 | 460 |  | 460 |  | 461 |  | 2.8 |  | 2.8 |  | 2.8 |  | 0.44 | 460 |  | 460 |  | 461 |  | 4.7 |  | 4.4 |  | 4 |  | 2730 |  | 0.78 | 460 | 460 | 460 | 4.5 | 4.2 | 4 | 2620 | 0.78 | 459.8 |  | 1.7 |  | 716.5 |  | 110 |  | 7296.5 | [14 empty] | 183.17 | 0.12 | 94.18 | 0.05 | 95.41 | 0.04 | 1.1885 | 0.05 | 213.35 | 0.14 | 167.98 | 0.05 | 105.77 | 0.05 | 62.21 | 0.05 | 172.5 | 0.05 | 91.78 | 0.14 | 91.4662 | 0.05 | 3.63 | 0.14 | 79.58 | 0.05 | 68.79 | 0.07 | 47.08 | 0.03 | 21.7 | 0.07 | 78.86 | 0.05 | 70.2 | 0.05 | 46.64 | 0.03 | 23.57 | 0.05 | 664.29 | 0.84 | 36.92 | 0.04 | 95185 | 94 | 50409 | 73 | [38 empty] | 213.8 | 0.15 | 153.69 | 0.19 | 105.92 | 0.05 | 47.77 | 0.2 | 193.07 | 0.17 | 98.93 | 0.06 | 8.8381 | 0.05 | 182.3 | 0.02 | 88.53 | 0.06 | 95.0807 | 0.05 | 10.39 | 0.09 | 80.25 | 0.07 | 47.5 | 0.04 | 3.13 | 0.41 | 79.83 | 0.06 | 57.81 | 0.33 | 47.24 | 0.04 | 10.57 | 0.35 | 92.29 | 0.05 | 659.07 | 0.91 | 35.92 | 0.02 | 109.45 | 0.08 | 95185 | 94 | 48464 | 44 | [18 empty] | 92.85 | 0.05 | 92.29 | 0.05 | 89.64 | 0.05 | 89.92 | 0.06 | 59.37 | 0.05 | 59 | 0.04 | 58.74 | 0.04 | 59.57 | 0.04 | 59.63 | 0.04 | 59.58 | 0.03 | 93.89 | 0.08 | 89.21 | 0.05 | 68.81 | 0.06 | 70.28 | 0.05 | 152.48 | 0.17 | 89.49 | 0.05 | 89.77 | 0.06 | 50.63 | 0.15 | 58.24 | 0.44 | [14 empty] | 89.64 | 0.05 | 89.92 | 0.06 | [14 empty] | 59.58 | 0.03 | 94.18 | 0.05 | 90.04 | 0.06 | 92.85 | 0.05 | 92.29 | 0.05 | [16 empty] | 50.66 | 0.4 | [12 empty] | 167.26 | 0.05 | 82.22 | 0.09 | 82.35 | 0.08 | 80.1 | 0.07 | 79.81 | 0.07 | 79.68 | 0.07 | 80.3 | 0.05 | 80.37 | 0.07 | 80.26 | 0.07 | 80.03 | 0.07 | 79.88 | 0.07 | 79.75 | 0.06 | 79.57 | 0.07 | 79.9 | 0.09 | 79.81 | 0.09 | 79.7 | 0.08 | 79.63 | 0.07 | 79.91 | 0.07 | 79.7 | 0.08 | 79.62 | 0.08 | 79.51 | 0.08 | 79.83 | 0.07 | 79.86 | 0.07 | 79.79 | 0.07 | 79.68 | 0.07 | 80 | 0.08 | 79.8 | 0.07 | 79.56 | 0.06 | 79.62 | 0.05 |  |  | 79.63 | 0.06 | 80.35 | 0.07 | 80.14 | 0.07 | 79.87 | 0.07 | 86.74 |  | 79.55 | 0.08 |  |  | 79.97 | 0.07 | 79.84 | 0.08 | 79.82 | 0.08 | 79.83 | 0.08 | [62 empty] | No Economizer | 79.998 | 0.01 | 67.15 | 0.016 | 59.622 | 0.011 | 57.298 | 0.018 | 81.84 | 0.011 | 67.594 | 0.018 | 3047.4 | 4.7 | 2994.1 | 4.7 | 0.255 | 0.003 | -0.011 | 0.001 | 0.886 | 0.006 | 1.2974 | 0.004 | 29.423 | 0.001 | 7276 | 21 | 1120 |  |  | 0 |  |  | 1.0547 | 13887.7184 | 89.6957 | 0 | 0 | 13887.7184 | 0.011187 | 31.4667 | 58.5673 | 13.7424 | 13.1659 | 0.011078 | 31.7979 | 0.011187 | 31.4667 | 0.0094553 | 24.5916 | 79.998 | 67.15 | 24.334 | 99056.0223 | 71429.6745 | 6156 | 0.21211 | 95539.5937 | 67913.2459 | 13.1308 | 0.15388 | -7.1326 | -21.4307 | 54.6698 | 99056.0223 | 95479.1319 | 3576.8904 | 0 | 99056.0223 | 100%
2 | 3T-22C Cyclic #2 | 75T0161 | 3T-22C Cyclic #2 | none | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 6 | 7/28/2014 | 22:43:15 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 |  |  | 80 | 57 | 82 |  | 6.4 | 6.2 | 6.4 | 6.2 | [16 empty] | 11.784 |  |  |  | 2 | 7.033 | 82.027 | 30.017 | 71.881 | 0.68 | 1045.8 | 2994.1 | 13.247 | 85438.32 | 0.242 | 6221.684 | 0.00438 | 16.2858 | 157.05 | 60.05 | 114.538 | 573.7 | 9.817 | 60.06 | 13.19 | 0.01 | 0 | 0.146 | 633.74 | 0.195 | 724 | 723.97 | 11.904 | 723.97 |  |  | C test factory chg, sealed cab, no econo | [514 empty] | No Economizer | 80.084 |  | 55.203 |  | 63.78 |  | 50.475 | [5 empty] | 2906.8 |  | 2851.6 |  | 0.335 |  |  |  | 0.673 |  | 1.1909 |  | 29.45 |  | 5198 |  |  |  |  | 0 |  |  | 1.007 | 13179.4808 | 112.2273 | 0 | 0 | 13179.4808 | 0.0034322 | 22.9837 | 62.773 | 11.5938 | 13.2333 | 0.00078408 | 0.83191 | 0.0034322 | 22.9837 | 0.0046503 | 20.3728 | 80.084 | 55.203 | 20.1291 | 37622.7783 | 54756.1314 | 4152.2 | 0.37667 | 34436.4947 | 51569.8478 | 6.625 | 0.52496 | -2.8546 | -17.311 | 43.6427 | 37622.7783 | 34410.0246 | 3212.7537 | 0 | 37622.7783 | 100%
2 | 3T-22C Cyclic #3 | 75T0162 | 3T-22C Cyclic #3 | none | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 6 | 7/28/2014 | 23:13:15 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 |  |  | 80 | 57 | 82 |  | 6.4 | 6.2 | 6.4 | 6.2 | [16 empty] | 11.784 |  |  |  | 3 | 7.033 | 81.486 | 30.15 | 71.624 | 0.68 | 1046.3 | 2994.1 | 13.247 | 85438.32 | 0.242 | 5994.178 | 0.00438 | 15.6902 | 157.173 | 60.11 | 110.349 | 566.5 | 9.566 | 60.12 | 13.19 | 0.01 | 0 | 0.14 | 626.6 | 0.219 | 724.5 | 724.54 | 11.7457 | 724.54 | 1.16 | [516 empty] | No Economizer | 79.868 |  | 55.019 |  | 64.009 |  | 50.479 | [5 empty] | 2908.5 |  | 2853.1 |  | 0.334 |  |  |  | 0.677 |  | 1.1936 |  | 29.45 |  | 5123 |  |  |  |  | 0 |  |  | 1.0077 | 13181.8278 | 111.9512 | 0 | 0 | 13181.8278 | 0.0033781 | 22.8722 | 63.0013 | 11.5938 | 13.2387 | 0.00078408 | 0.83191 | 0.0033781 | 22.8722 | 0.004599 | 20.3724 | 79.868 | 55.019 | 20.1285 | 36167.3667 | 53360.1441 | 4076.7 | 0.38471 | 32978.4341 | 50171.2115 | 6.4373 | 0.5342 | -2.7437 | -16.8667 | 43.6582 | 36167.3667 | 32952.2444 | 3215.1224 | 0 | 36167.3667 | 100%
2 | 3T-22C Cyclic #4 | 75T0163 | 3T-22C Cyclic #4 | none | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 6 | 7/28/2014 | 23:43:23 | 10 Ton |  | 80/57 82 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 |  |  | 80 | 57 | 82 |  | 6.4 | 6.2 | 6.4 | 6.2 | [16 empty] | 11.784 |  |  |  | 4 | 7.033 | 81.534 | 30.017 | 71.553 | 0.68 | 1045.6 | 2994.1 | 13.247 | 85438.32 | 0.242 | 5929.62 | 0.00438 | 15.5213 | 153.335 | 71.48 | 109.161 | 555.7 | 9.454 | 71.49 | 13.19 | 0.02 | 0 | 0.14 | 627.24 | 0.23 | 706.8 | 706.84 | 11.6731 | 706.84 | 1.13 | [516 empty] | No Economizer | 79.475 |  | 54.842 |  | 63.884 |  | 50.362 | [5 empty] | 2905.5 |  | 2851.4 |  | 0.335 |  |  |  | 0.677 |  | 1.1902 |  | 29.452 |  | 5207 |  |  |  |  | 0 |  |  | 1.0074 | 13171.6273 | 112.2194 | 0 | 0 | 13171.6273 | 0.0033693 | 22.7678 | 62.8766 | 11.5938 | 13.2353 | 0.00078408 | 0.83191 | 0.0033693 | 22.7678 | 0.0045672 | 20.3075 | 79.475 | 54.842 | 20.0636 | 35617.7967 | 52470.8164 | 4161.4 | 0.39876 | 32432.1688 | 49285.1885 | 6.2286 | 0.53854 | -2.7041 | -16.5984 | 43.5054 | 35617.7967 | 32406.1939 | 3211.6028 | 0 | 35617.7967 | 100%
2 | 3T-ONE | 75T0164 | 3T-ONE | none | on | on | 3 turns | unsealed | sealed |  | 5.5 |  | 0 | 0 | CUST 12 | 10/18/2013 | 3:18:39 | 10 Ton | 0:30:00 | 80/67 95/70 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | ck1: 6.4 lbs / ck2: 6.2 lbs | 460/480/3 | TU4 | AHRI 340-360 | 80 | 67 | 95 | 70 | 6.4 | 6.2 | 6.4 | 6.2 | 461.3 | 1.1 | 14.2 | 0 | 78747 | 180 | 79746 | 351 | 14937 | 134 | 93699 | 235 | 10.3045 | 924 | [38 empty] | Out-of-box factory chg, unsealed cab, no econo, factory drive-pulley turns | New R22 CK 1 : 6.4 lbs /Ck 2 : 6.2 lbs: Unsealed cabinet/ Sealed ductwork: 5.5` blower pulley with AX35 (notched) belt : motor pulley 3 turns opened. With econo Meriam set @ 100%: Horiz airflow disch config. set on floor. | 79.999 | 0.013 | 67.002 | 0.026 | 94.975 | 0.056 | 69.978 | 0.064 | 79.94 | 0.08 | 62.57 | 0.05 | 66.21 | 0.02 | -1.69 | 0.012 | 1.472 | 0.0059 | 78747 | 180 | 14937 | 134 | 10.305 | 0.034 | [6 empty] | 461.3 | 2.6 | 461.1 | 2.6 | 458.7 | 2.6 | 14.2 | 0 | 13.5 | 0 | 15.4 | 0.1 | 6503.9 | 41.7 | 3970.2 | 74.7 | 2588.7 | 30 | 460 |  | 460 |  | 460 |  | 3.4 |  | 3.5 |  | 3.5 |  | 0.61 | 460 |  | 460 |  | 460 |  | 5 |  | 5.1 |  | 4.7 |  | 3290 |  | 0.84 | 460 | 460 | 460 | 4.9 | 4.7 | 4.7 | 3080 | 0.82 | [8 empty] | 9756 | [22 empty] | 257.16 | 0.37 | 169.4 | 0.12 | 119.13 | 0.11 | 50.27 | 0.09 |  |  | 103.57 | 0.12 | [12 empty] | 86.48 | 0.06 | 60.63 | 0.17 | 51.29 | 0.03 | 9.34 | 0.17 | [46 empty] | 258.13 | 0.39 | 169.48 | 0.33 | 119.4 | 0.11 | 50.07 | 0.33 | [8 empty] | 101.7 | 0.14 | [10 empty] | 85.83 | 0.12 | 58.69 | 1.22 | 50.9 | 0.07 | 7.79 | 1.27 | 103.19 | 0.13 | [36 empty] | 61.82 | 0.03 | 62.63 | 0.04 | 62.43 | 0.03 | 62.31 | 0.04 | 62.09 | 0.04 | [20 empty] | 103.57 | 0.12 | [12 empty] | 108 | 0.11 | 102.88 | 0.14 | [14 empty] | 62.4 | 0.03 |  |  |  |  | 108.38 | 0.12 | 103.19 | 0.13 | 108 | 0.11 | 102.88 | 0.14 | [28 empty] | 95.32 | 0.19 | 94.68 | 0.16 | 79.87 | 0.06 | 80.03 | 0.05 | 80.14 | 0.06 | 79.78 | 0.06 | 79.75 | 0.06 | 79.82 | 0.05 | 80.01 | 0.05 | 80.78 | 0.12 | 80.72 | 0.1 | 80.73 | 0.08 | 80.75 | 0.07 | 81.04 | 0.08 | 81 | 0.12 | 80.75 | 0.11 | 80.68 | 0.1 | 81.04 | 0.08 | 80.95 | 0.08 | 80.91 | 0.07 | 80.88 | 0.08 | 81.16 | 0.07 | 81.11 | 0.07 | 80.98 | 0.07 | 80.76 | 0.08 | 81.05 | 0.06 | 81.02 | 0.08 | 80.92 | 0.09 | 80.85 | 0.09 | 80.17 | 0.06 | [82 empty] | No Economizer | 79.999 | 0.013 | 67.002 | 0.026 | 62.849 | 0.023 | 60.173 | 0.028 | 94.975 | 0.056 | 69.978 | 0.064 | 4223.5 | 8.6 | 4080.1 | 8.2 | 0.25 | 0.005 | -0.626 | 0.005 | -1.69 | 0.012 | 1.472 | 0.0059 | 29.363 | 0.001 | 9093 | 22 | 1916 |  |  | 0 |  |  | 1.3357 | 19117.0698 | 119.8329 | 0 | 0 | 19117.0698 | 0.011078 | 31.3472 | 61.5133 | 14.0649 | 13.2557 | 0.0097771 | 33.5798 | 0.011078 | 31.3472 | 0.010474 | 26.4894 | 79.999 | 67.002 | 26.1626 | 99113.7709 | 84814.3816 | 7177 | 0.24714 | 92983.4524 | 78684.0631 | 10.2258 | 0.15627 | -5.1846 | -18.4857 | 58.0895 | 99113.7709 | 92866.492 | 6247.2789 | 0 | 99113.7709 | 100%
2 | 3T-75629575-NE3-Retest | 75T0005 | 3T-75629575-NE3-Retest | none | on | on | 3 turns | unsealed | sealed |  | 5.375 |  | 0 | 0 | CUST 8 | 2/21/2014 | 12:19:13 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU4 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.4 | 0 | 15 | 0 | 63494 | 231 | 61849 | 424 | 12095 | 230 | 75601 | 298 | 8.797 | 928 |  | 33.25 | 7.3882 | [35 empty] | Factory charge, 3 turns, no econo unsealed cab, 75% Meriam, adjust code tester--speed to match total static of run 3T-75629575-E3-SPWCT-SS | R22 CK1 : 6.4 lbs /Ck2 : 6.2 lbs: Unsealed cab/ Sealed ductwork: 5.375` blower pulley with AX35 (notched) belt : motor pulley 3 turns opened. no econo: Meriam set @ 75%: Horiz airflow. set on floor. | 75 | 0.024 | 62.004 | 0.03 | 95 | 0.015 | 74.979 | 0.027 | 74.69 | 0.13 | 55.54 | 0.05 | 60.62 | 0.02 | 0.291 | 0.011 | 1.1883 | 0.0077 | 63494 | 231 | 12095 | 230 | 8.797 | 0.039 | [6 empty] | 459.4 | 2.1 | 461 | 2.1 | 460.7 | 2.1 | 15 | 0.1 | 12.9 | 0 | 13.2 | 0.1 | 6812.2 | 46.3 | 3230.1 | 55 | 1782.1 | 39.1 | 460 |  | 461 |  | 459 |  | 2.8 |  | 2.8 |  | 3 |  | 0.65 | 460 |  | 460 |  | 459 |  | 5.1 |  | 5 |  | 4.5 |  | 3200 |  | 0.73 | 460 | 459 | 461 | 5.1 | 4.7 | 4.4 | 3090 | 0.82 | 458.6 |  | 1.7 |  | 714.6 |  | 115 |  | 8589.6 | [22 empty] | 248.89 | 0.34 | 175.07 | 0.19 | 116.75 | 0.1 | 58.33 | 0.17 |  |  | 100.42 | 0.13 | [6 empty] | 48.54 | 0.43 |  |  |  |  | 75.05 | 0.06 | 56.43 | 0.32 | 44.19 | 0.04 | 12.23 | 0.31 | [46 empty] | 255.87 | 0.35 | 175.85 | 0.37 | 118.77 | 0.1 | 57.08 | 0.37 | [8 empty] | 97.77 | 0.11 | [10 empty] | 75.11 | 0.17 | 53.91 | 1.24 | 44.23 | 0.11 | 9.67 | 1.29 | 99.06 | 0.09 | [36 empty] | 55.43 | 0.07 | 55.78 | 0.08 | 55.98 | 0.07 | 55.54 | 0.07 | 55.87 | 0.06 | 55.73 | 0.06 | [32 empty] | 103.48 | 0.12 | 99.23 | 0.12 | 91.76 | 0.17 | 91.49 | 0.14 | 92.96 | 0.18 | 93.27 | 0.17 | 93.22 | 0.2 | 93.35 | 0.18 | [8 empty] | 103.74 | 0.13 | 99.06 | 0.09 | [16 empty] | 46.23 | 0.24 | [14 empty] | 95.37 | 0.27 | 95.45 | 0.13 | 74.78 | 0.14 | 74.79 | 0.13 | 74.69 | 0.11 | 74.81 | 0.15 | 74.79 | 0.15 | 74.79 | 0.15 | 74.7 | 0.14 | 75.81 | 0.11 | 75.87 | 0.11 | 75.58 | 0.11 | 75.39 | 0.1 | 75.73 | 0.08 | 75.66 | 0.11 | 75.44 | 0.11 | 75.37 | 0.11 | 76.3 | 0.11 | 75.94 | 0.11 | 75.02 | 0.11 | 74.87 | 0.11 | 75.86 | 0.1 | 75.37 | 0.11 | 75.17 | 0.1 | 74.89 | 0.11 | 76.31 | 0.11 | 75.14 | 0.11 | 75.15 | 0.1 | 75.08 | 0.1 | [84 empty] | No Economizer | 75 | 0.024 | 62.004 | 0.03 | 55.335 | 0.019 | 53.155 | 0.026 | 95 | 0.015 | 74.979 | 0.027 | 2909.9 | 9.4 | 2874.5 | 9.3 | 0.92 | 0.007 | -0.586 | 0.006 | 0.291 | 0.011 | 1.1883 | 0.0077 | 29.442 | 0.002 | 8594 | 22 | 1470 |  |  | 0 |  |  | 1.2316 | 13382.4748 | 310.6814 | 0 | 0 | 13382.4748 | 0.0087833 | 27.6115 | 54.1034 | 14.0998 | 13.0465 | 0.013902 | 38.1368 | 0.0087833 | 27.6115 | 0.0080727 | 22.0438 | 75 | 62.004 | 21.7438 | 78524.3754 | 67115.523 | 7124 | 0.30964 | 74567.621 | 63158.7686 | 8.6767 | 0.12817 | -5.8677 | -20.8966 | 51.0314 | 78524.3754 | 74509.7058 | 4014.6695 | 0 | 78524.3754 | 100%
2 | 3T-22A-Retest-OB | 75T0048 | 3T-22A-Retest-OB | none | on | on | 6 turns | sealed | sealed |  | 5.375 |  | 0 | 0 | CUST 8 | 2/20/2014 | 11:19:05 | 10 Ton | 0:30:00 | 80/67 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU4 | AHRI 210/240 2008 | 80 | 67 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.3 | 0 | 14.4 | 0 | 65989 | 227 | 64473 | 456 | 23177 | 276 | 89187 | 371 | 11.008 | 749 | [38 empty] | Out of box, AHRI Verification H (IEER 100%), sealed cab, no econo. | R22 CK1 : 6.4 lbs /Ck2 : 6.2 lbs: Sealed cab/ Sealed ductwork: 5.375` blower pulley with AX35 (notched) belt : motor pulley 6 turns opened. No econo Meriam set @ 100%: Horiz airflow. set on floor. | 80.006 | 0.032 | 67.151 | 0.031 | 94.797 | 0.035 | 74.753 | 0.072 | 79.69 | 0.14 | 59.6 | 0.05 | 64.67 | 0.03 | 0.7 | 0.009 | 1.1827 | 0.0069 | 65989 | 227 | 23177 | 276 | 11.008 | 0.052 | [6 empty] | 459.3 | 2 | 461.1 | 2 | 460.8 | 2 | 14.4 | 0 | 12.3 | 0 | 12.7 | 0 | 6541.5 | 41.4 | 3227.9 | 49.4 | 1560.5 | 33.4 | 460 |  | 460 |  | 459 |  | 2.4 |  | 2.5 |  | 5.6 |  | 0.5 | 460 |  | 459 |  | 460 |  | 5.1 |  | 5 |  | 4.4 |  | 3210 |  | 0.73 | 460 | 460 | 459 | 4.9 | 4.7 | 4.4 | 3050 | 0.82 | 458.5 |  | 1.7 |  | 707.9 |  | 115 |  | 8102.9 | [22 empty] | 252 | 0.29 | 174.75 | 0.09 | 117.61 | 0.08 | 57.13 | 0.09 |  |  | 103.77 | 0.08 | [6 empty] | 57.34 | 0.41 |  |  |  |  | 82.16 | 0.06 | 63.14 | 0.17 | 48.61 | 0.04 | 14.52 | 0.15 | [46 empty] | 254.39 | 0.29 | 172.21 | 0.29 | 118.3 | 0.08 | 53.9 | 0.3 | [8 empty] | 100.87 | 0.1 | [10 empty] | 81.84 | 0.15 | 58.89 | 0.98 | 48.41 | 0.09 | 10.47 | 1.02 | 102.68 | 0.08 | [36 empty] | 59.39 | 0.1 | 59.97 | 0.07 | 60.11 | 0.07 | 59.74 | 0.06 | 59.99 | 0.06 | 59.79 | 0.07 | [32 empty] | 107.19 | 0.08 | 102.37 | 0.1 | 94.56 | 0.19 | 94.68 | 0.17 | 94.58 | 0.17 | 94.56 | 0.15 | 94.71 | 0.22 | 94.72 | 0.18 | [8 empty] | 107.62 | 0.08 | 102.68 | 0.08 | [16 empty] | 51.23 | 0.83 | [14 empty] | 94.84 | 0.12 | 94.67 | 0.14 | 79.89 | 0.1 | 79.84 | 0.11 | 79.73 | 0.14 | 79.96 | 0.11 | 79.9 | 0.11 | 79.93 | 0.12 | 79.8 | 0.11 | 80.52 | 0.09 | 80.48 | 0.09 | 80.36 | 0.09 | 80.25 | 0.09 | 80.24 | 0.12 | 79.85 | 0.13 | 79.8 | 0.13 | 79.84 | 0.13 | 80.08 | 0.12 | 80.16 | 0.11 | 79.63 | 0.14 | 79.65 | 0.14 | 79.83 | 0.14 | 79.91 | 0.13 | 80.05 | 0.12 | 79.77 | 0.12 | 80.03 | 0.11 | 79.89 | 0.12 | 79.98 | 0.12 | 79.99 | 0.13 | [84 empty] | No Economizer | 80.006 | 0.032 | 67.151 | 0.031 | 59.433 | 0.026 | 57.625 | 0.039 | 94.797 | 0.035 | 74.753 | 0.072 | 2927.9 | 8.7 | 2837.7 | 8.4 | 0.25 | 0.006 | -0.318 | 0.003 | 0.7 | 0.009 | 1.1827 | 0.0069 | 29.164 | 0.002 | 8102 | 21 | 1020 |  |  | 0 |  |  | 0.99776 | 13346.0667 | 83.3435 | 0 | 0 | 13346.0667 | 0.011186 | 31.4674 | 58.4352 | 14.0934 | 13.163 | 0.013754 | 37.9226 | 0.011186 | 31.4674 | 0.0096979 | 24.8093 | 80.006 | 67.151 | 24.5656 | 92111.8498 | 69092.3433 | 7082 | 0.26241 | 88915.041 | 65895.5346 | 10.9745 | 0.11069 | -6.9018 | -21.5708 | 55.7503 | 92111.8498 | 88858.6401 | 3253.2097 | 0 | 92111.8498 | 100%
2 | 3T-22A-Retest | 75T0049 | 3T-22A-Retest | none | on | on | 6 turns | sealed | sealed |  | 5.375 |  | 0 | 0 | CUST 8 | 2/20/2014 | 20:54:56 | 10 Ton | 0:30:00 | 80/67 - 95/75 | ENG 1 | TECH 1 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU4 | AHRI 210/240 2008 | 80 | 67 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.2 | 0 | 14.5 | 0 | 66480 | 245 | 65012 | 495 | 23152 | 254 | 89655 | 357 | 10.9189 | 746 |  | 36.8 | [36 empty] | . | R22 CK1 : 6.4 lbs /Ck2 : 6.2 lbs: Sealed cab/ Sealed ductwork: 5.375` blower pulley with AX35 (notched) belt : motor pulley 6 turns opened. No econo Meriam set @ 100%: Horiz airflow. set on floor. | 79.991 | 0.049 | 67.149 | 0.02 | 94.801 | 0.022 | 74.88 | 0.04 | 79.52 | 0.16 | 59.41 | 0.06 | 64.84 | 0.02 | 0.7 | 0.01 | 1.1905 | 0.008 | 66480 | 245 | 23152 | 254 | 10.919 | 0.054 | [6 empty] | 459.2 | 2.2 | 460.7 | 2.2 | 460.8 | 2.2 | 14.5 | 0 | 12.5 | 0 | 12.8 | 0.1 | 6587.1 | 42.6 | 3231 | 54.3 | 1623.6 | 36.2 | 460 |  | 461 |  | 459 |  | 2.4 |  | 2.5 |  | 2.7 |  | 0.51 | 459 |  | 460 |  | 460 |  | 5.1 |  | 5.1 |  | 4.5 |  | 3240 |  | 0.74 | 461 | 460 | 460 | 5 | 4.8 | 4.5 | 3130 | 0.82 | 458.4 |  | 1.7 |  | 712.5 |  | 115 |  | 8207.5 | [22 empty] | 254.53 | 0.3 | 173.92 | 0.18 | 118.38 | 0.08 | 55.54 | 0.17 |  |  | 103.04 | 0.13 | [6 empty] | 55.25 | 0.45 |  |  |  |  | 82.32 | 0.08 | 61.49 | 0.26 | 48.79 | 0.05 | 12.7 | 0.26 | [46 empty] | 261.05 | 0.31 | 174.57 | 0.28 | 120.25 | 0.09 | 54.32 | 0.28 | [8 empty] | 99.11 | 0.09 | [10 empty] | 81.62 | 0.16 | 57.76 | 1.14 | 48.35 | 0.1 | 9.41 | 1.17 | 100.17 | 0.11 | [36 empty] | 59.46 | 0.06 | 59.35 | 0.07 | 59.55 | 0.07 | 59.23 | 0.06 | 59.59 | 0.06 | 59.49 | 0.05 | [32 empty] | 106.27 | 0.11 | 100.64 | 0.1 | [20 empty] | 105.95 | 0.13 | 100.17 | 0.11 | [16 empty] | 50.86 | 0.73 | [14 empty] | 95.49 | 0.23 | 95.03 | 0.11 | 79.58 | 0.14 | 79.61 | 0.14 | 79.64 | 0.12 | 79.52 | 0.16 | 79.53 | 0.15 | 79.65 | 0.15 | 79.64 | 0.14 | 79.94 | 0.12 | 79.95 | 0.12 | 79.9 | 0.13 | 79.9 | 0.12 | 80.03 | 0.1 | 80.01 | 0.13 | 79.93 | 0.13 | 79.97 | 0.13 | 80.13 | 0.12 | 80.16 | 0.13 | 79.85 | 0.13 | 79.77 | 0.14 | 79.86 | 0.12 | 79.88 | 0.13 | 80 | 0.12 | 79.58 | 0.14 | 79.86 | 0.12 | 79.6 | 0.14 | 79.83 | 0.13 | 79.96 | 0.12 | [84 empty] | No Economizer | 79.991 | 0.049 | 67.149 | 0.02 | 59.424 | 0.025 | 57.587 | 0.029 | 94.801 | 0.022 | 74.88 | 0.04 | 2925.2 | 9.9 | 2859.7 | 9.7 | 0.25 | 0.006 | -0.32 | 0.003 | 0.7 | 0.01 | 1.1905 | 0.008 | 29.421 | 0.001 | 8211 | 26 | 1010 |  |  | 0 |  |  | 0.9873 | 13334.156 | 83.9896 | 0 | 0 | 13334.156 | 0.011188 | 31.466 | 58.4367 | 14.0944 | 13.1626 | 0.013863 | 38.0448 | 0.011188 | 31.466 | 0.009677 | 24.7844 | 79.991 | 67.149 | 24.5432 | 92309.8512 | 68978.0083 | 7201 | 0.26624 | 89149.3777 | 65817.5349 | 10.8573 | 0.11396 | -6.9228 | -21.5543 | 55.6644 | 92309.8512 | 89093.7402 | 3216.111 | 0 | 92309.8512 | 100%
2 | T2-55-1ER-DMM | 75T0051 | T2-55-1ER-DMM | 1 finger | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/2/2014 | 0:49:30 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0.6 | 3.7 | 0 | [9 empty] | 957 | 1690 | [37 empty] | Econo 1F-open, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-55-1E-DMM-SPWCT-SSR | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.96 | 0.016 | 61.998 | 0.059 | 54.975 | 0.024 | 51.019 | 0.027 | 75.01 | 0.03 | 71.51 | 0.02 | 71.97 | 0.01 | 0.263 | 0.004 | 1.7042 | 0.0034 | 11719 | 45 | 7000 | 106 | 10.51 | 0.087 | 5077 | 135 | 2.85 | 0.078 | -269.09 | 10.21 | 460.5 | 3.2 | 460.5 | 3.2 | 459.9 | 3.2 | 3.7 | 0 | 3.3 | 0 | 3.5 | 0 | 1630.7 | 25.1 | 1108 | 30.3 | 151.2 | 18.4 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 115 | [168 empty] | 51.67 | 0.06 | 52.3 | 0.09 | 58.73 | 0.02 | 53.19 | 0.1 | 71.15 | 0.02 | 71.35 | 0.03 | 71.52 | 0.04 | 71.55 | 0.03 | 72.05 | 0.15 | 71.7 | 0.03 | 51.61 | 0.06 | 72.9 | 0.02 | 72.23 | 0.02 | 54.66 | 0.02 | 57.2 | 0.02 | 51.55 | 0.06 | 72.84 | 0.02 | 72.68 | 0.01 | 56.32 | 0.02 |  |  |  |  | 56.7 | 0.08 | [26 empty] | 71.7 | 0.03 | 53.5 | 0.02 | 54.6 | 0.06 | [34 empty] | 56.03 | 0.03 | 55.4 | 0.24 | 55 | 0.2 | 75.6 | 0.03 | 75.53 | 0.02 | 75.19 | 0.03 | 76 | 0.02 | 75.99 | 0.03 | 75.96 | 0.03 | 75.77 | 0.03 | 65.03 | 0.14 | 62.5 | 0.18 | 65.6 | 0.52 | 65.92 | 0.13 | 66.02 | 0.16 | 64.34 | 0.24 | 68.33 | 0.1 | 68.42 | 0.11 | 73.16 | 0.12 | 67.92 | 0.16 | 74.2 | 0.07 | 74.59 | 0.03 | 74.14 | 0.2 | 73.33 | 0.06 | 74.67 | 0.03 | 74.88 | 0.02 | 74.74 | 0.02 | 74.61 | 0.02 | 73.78 | 0.04 |  |  | 75.33 | 0.03 | 76.01 | 0.02 | 75.77 | 0.03 | 75.58 | 0.03 | 75.38 |  | 75.2 | 0.03 | 61.95 | 0.11 | 63.41 | 0.11 | 66.72 | 0.11 | 74.32 | 0.06 | 74.84 | 0.02 | [62 empty] | Economizer test | 74.96 | 0.016 | 61.998 | 0.059 | 71.456 | 0.015 | 60.024 | 0.059 | 54.975 | 0.024 | 51.019 | 0.027 | 3075.3 | 3.1 | 2966.3 | 3 | 0.636 | 0.003 | -0.218 | 0.001 | 0.263 | 0.004 | 1.7042 | 0.0034 | 29.397 | 0 | 1782 | 12 | 1690 |  | 0.099274 | 294.4778 | 13.029 | 0.218 | 1.5224 | 13711.6747 | 221.6345 | 294.4777 | 1356.1036 | 12355.5711 | 0.0086116 | 26.9334 | 69.9336 | 13.029 | 13.457 | 0.0069973 | 20.7889 | 0.0087888 | 27.6078 | 0.0083406 | 26.2634 | 72.9893 | 61.0134 | 25.8924
2 | T2-55-2ER-DMM | 75T0052 | T2-55-2ER-DMM | 2 finger | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/1/2014 | 23:25:36 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0.8 | 3.7 | 0 | [9 empty] | 957 | 1700 |  |  | 115.87 | 0.05 | [33 empty] | Econo 2F-open, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-55-2E-DMM-SPWCT-SSR | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.003 | 0.012 | 61.99 | 0.07 | 55.063 | 0.042 | 50.983 | 0.031 | 74.99 | 0.04 | 70.71 | 0.05 | 71.28 | 0.04 | 0.272 | 0.004 | 1.7446 | 0.0042 | [12 empty] | 460.2 | 2.5 | 460.4 | 2.5 | 459.8 | 2.5 | 3.7 | 0 | 3.3 | 0 | 3.5 | 0 | 1636.3 | 21.4 | 1105 | 23.6 | 162.8 | 16.5 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.58 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 105 |  | 1805 | [14 empty] | 22.94 | 0.9 | 50.3 | 0.33 |  |  |  |  | 22.5 | 0.9 | 52.68 | 0.43 | -2.33 | 1.17 | -55.01 | 0.75 |  |  | 55.58 | 0.35 | -1.78 | 1.16 | -57.35 | 1.22 | 22.54 | 0.91 | 69.96 | 0.04 | -2.28 | 1.17 | 72.25 | 1.2 | 22.52 | 0.91 | 54.71 | 0.12 | -2.31 | 1.18 | 57.02 | 1.06 | 96.69 | 1.36 | 26.11 | 0.1 | 4994 | 124 | 8679 | 123 | [38 empty] | -11.03 | 0.01 | 56.35 | 0.1 | -90.12 | 0.17 | 146.45 | 0.11 | -10.61 | 0.02 | [6 empty] | 70.82 | 0.04 | -86.56 | 0.13 | -157.42 | 0.19 | -10.95 | 0.02 | -89.34 | 0.13 | 160.32 | 0.16 | -10.93 | 0.02 | 56.28 | 0.03 | -89.2 | 0.12 | 145.49 | 0.16 | 52.86 | 0.26 | -2.4 | 0 | 30.57 | 0.01 | 117.52 | 0.01 | 4994 | 124 | 0 | 0 | [18 empty] | 51.74 | 0.09 | 52.86 | 0.26 | 58.24 | 0.09 | 53.14 | 0.15 | 70.34 | 0.07 | 70.53 | 0.07 | 70.69 | 0.05 | 70.72 | 0.06 | 70.64 | 0.19 | 70.85 | 0.06 | 51.63 | 0.09 | 72.44 | 0.03 | 69.94 | 0.05 | 54.56 | 0.05 | 56.39 | 0.05 | 51.62 | 0.09 | 72.25 | 0.03 | 71.82 | 0.04 | 56.29 | 0.05 |  |  |  |  | 56.11 | 0.12 | [8 empty] | 58.24 | 0.09 | 53.14 | 0.15 | [14 empty] | 70.85 | 0.06 | 50.3 | 0.33 | 54.62 | 0.08 | 51.74 | 0.09 | 52.86 | 0.26 | [16 empty] | 70.96 | 0.04 | [12 empty] | 53.28 | 0.4 | 55.46 | 0.18 | 55.03 | 0.16 | 75.56 | 0.03 | 75.48 | 0.02 | 75.19 | 0.03 | 75.93 | 0.02 | 75.93 | 0.03 | 75.91 | 0.03 | 75.71 | 0.03 | 62.12 | 0.24 | 62.84 | 0.16 | 61.83 | 0.2 | 64.37 | 0.14 | 65.83 | 0.17 | 66.18 | 0.16 | 66.71 | 0.2 | 68.46 | 0.08 | 72.64 | 0.08 | 68.06 | 0.09 | 72.12 | 0.07 | 72.9 | 0.08 | 74.48 | 0.24 | 72.32 | 0.06 | 74.27 | 0.03 | 74.97 | 0.03 | 74.82 | 0.03 | 74.64 | 0.02 | 73.43 | 0.04 |  |  | 75.32 | 0.02 | 75.97 | 0.03 | 75.74 | 0.03 | 75.54 | 0.03 | 75.35 |  | 75.17 | 0.03 | 62.86 | 0.17 | 61.19 | 0.19 | 66.37 | 0.16 | 70.5 | 0.09 | 74.91 | 0.02 | [62 empty] | Economizer test | 75.003 | 0.012 | 61.99 | 0.07 | 70.719 | 0.041 | 59.584 | 0.072 | 55.063 | 0.042 | 50.983 | 0.031 | 3109.5 | 3.8 | 3004.2 | 3.7 | 0.614 | 0.004 | -0.187 | 0.003 | 0.272 | 0.004 | 1.7446 | 0.0042 | 29.401 | 0 | 1799 | 11 | 1700 |  | 0.13862 | 416.4297 | 13.031 | 0.187 | 1.5188 | 13884.2799 | 216.7017 | 416.4283 | 1917.4176 | 11966.8623 | 0.0085226 | 26.6576 | 69.2002 | 13.0309 | 13.4375 | 0.0069575 | 20.7671 | 0.0087733 | 27.6014 | 0.0082371 | 25.9708 | 72.2571 | 60.6065 | 25.6007
2 | T2-55-CE-DMM | 75T0053 | T2-55-CE-DMM | closed | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/2/2014 | 3:09:45 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.1 | 0.8 | 3.7 | 0 | [9 empty] | 958 |  |  |  | 117.31 | 0.02 | [33 empty] | Econo closed, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley,--3 turns (939 rpm), 100% inlet/outlet Meriam, adjust code tester speed to match--total static of run T2-55-CE-DMM-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.069 | 0.04 | 61.998 | 0.046 | 54.998 | 0.032 | 51 | 0.032 | 75.01 | 0.06 | 72.98 | 0.03 | 73.27 | 0.05 | 0.266 | 0.004 | 1.6776 | 0.003 | 7048 | 31 | 5002 | 100 | 6.876 | 0.072 | -3686 | 0 | 0 | 0 | 0 | 0 | 460.1 | 2.6 | 460 | 2.6 | 459.6 | 2.6 | 3.7 | 0 | 3.2 | 0 | 3.5 | 0 | 1612.5 | 22.3 | 1104.7 | 24.1 | 140.8 | 16.8 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.57 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 115 |  | 1745 | [14 empty] | 2.07 | 0.01 | 55.61 | 0.5 |  |  |  |  | -0.41 | 0.16 | 62.94 | 2.98 | -42.97 | 0.57 | -106.16 | 3.18 |  |  | 56.52 | 1.43 | -36.96 | 0.03 | -93.43 | 1.39 | -0.39 | 0.12 | 72.56 | 0.08 | -43.01 | 0.43 | 115.69 | 0.41 | -0.42 | 0.12 | 55.43 | 0.25 | -43.07 | 0.44 | 98.66 | 0.55 | -600 | 0 | 26.38 | 0.42 | -3686 |  | 0 | 0 | [38 empty] | -0.33 | 0.28 | 57.27 | 0.38 | -42.59 | 0.98 | 100.27 | 0.99 | -0.02 | 0.01 | [6 empty] | 72.24 | 0.04 | -42.18 | 0.03 | -114.43 | 0.04 | -0.34 | 0 | -43.04 | 0.01 | 115.24 | 0.04 | -0.34 | 0 | 56.31 | 0.07 | -43.06 | 0 | 99.39 | 0.06 | 54.99 | 0.62 | -600 | 0 | 31 | 0.01 | 117.26 | 0.01 | -3686 | 0 | 0 | 0 | [18 empty] | 54.27 | 0.27 | 54.99 | 0.62 | 54.72 | 0.92 | 56.65 | 1 | 72.68 | 0.05 | 72.77 | 0.05 | 72.82 | 0.05 | 73.07 | 0.05 | 72.69 | 0.21 | 73.15 | 0.05 | 54.04 | 0.31 | 73.73 | 0.04 | 73.16 | 0.08 | 55.06 | 0.13 | 57.14 | 0.18 | 53.92 | 0.27 | 73.67 | 0.04 | 73.47 | 0.04 | 56.37 | 0.05 |  |  |  |  | 56.22 | 0.07 | [8 empty] | 54.72 | 0.92 | 56.65 | 1 | [12 empty] | 56.52 | 1.43 | 73.15 | 0.05 | 55.61 | 0.5 | 53 | 0.27 | 54.27 | 0.27 | 54.99 | 0.62 | [16 empty] | 72.19 | 0.04 | [12 empty] | 58.81 | 1.21 | 56.45 | 0.17 | 56 | 0.18 | 75.58 | 0.05 | 75.54 | 0.05 | 75.17 | 0.05 | 76.02 | 0.05 | 75.95 | 0.05 | 75.92 | 0.06 | 75.74 | 0.06 | 67.7 | 0.18 | 65.06 | 0.13 | 66.23 | 0.2 | 68.92 | 0.12 | 71.3 | 0.12 | 68.26 | 0.13 | 69.31 | 0.15 | 70.29 | 0.09 | 74.38 | 0.08 | 70.37 | 0.11 | 74.76 | 0.06 | 74.76 | 0.06 | 74.8 | 0.23 | 73.73 | 0.09 | 74.72 | 0.06 | 74.85 | 0.07 | 74.7 | 0.06 | 74.62 | 0.06 | 74.14 | 0.06 |  |  | 75.32 | 0.06 | 75.95 | 0.05 | 75.71 | 0.06 | 75.52 | 0.06 | 75.4 |  | 75.18 | 0.06 | 64.43 | 0.16 | 65.16 | 0.15 | 71.29 | 0.1 | 74.89 | 0.05 | 74.81 | 0.06 | [62 empty] | Economizer test | 75.069 | 0.04 | 61.998 | 0.046 | 72.949 | 0.039 | 60.74 | 0.048 | 54.998 | 0.032 | 51 | 0.032 | 3055.4 | 2.8 | 2938.4 | 2.7 | 0.667 | 0.003 | -0.245 | 0.003 | 0.266 | 0.004 | 1.6776 | 0.003 | 29.387 | 0 | 1753 | 12 | 1630 |  | 0.032385 | 95.1602 | 13.029 | 0.245 | 1.465 | 13583.9182 | 230.2512 | 95.1618 | 438.2156 | 13145.7026 | 0.0087055 | 27.3859 | 71.484 | 13.0295 | 13.4957 | 0.0069818 | 20.7777 | 0.008763 | 27.6062 | 0.0084449 | 26.7413 | 74.4235 | 61.6785 | 26.3842
2 | T2-55-OER-DMM | 75T0054 | T2-55-OER-DMM | open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/1/2014 | 22:04:12 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0.9 | 3.7 | 0 | 15414 | 142 | 15182 | 205 | 8262 | 168 | 23685 | 139 | 13.1219 | 959 | 1700 |  |  | 112.13 | 0.01 | 0 | [32 empty] | Econo fully open, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-55-OE-DMM-SPWCT-SSR | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.99 | 0.061 | 61.976 | 0.052 | 55.084 | 0.06 | 51.058 | 0.039 | 74.89 | 0.05 | 70.42 | 0.05 | 71.2 | 0.08 | 0.274 | 0.004 | 1.765 | 0.0037 | 15414 | 142 | 8262 | 168 | 13.121 | 0.11 | -3686 | 0 | 0 | 0 | 0 | 0 | 460.3 | 2.4 | 460.3 | 2.4 | 459.8 | 2.4 | 3.7 | 0 | 3.3 | 0 | 3.5 | 0 | 1639.6 | 19.4 | 1105.9 | 22.8 | 165.7 | 14.5 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.2 |  | 0.57 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 105 |  | 1805 | [14 empty] | 98.02 | 0.06 | 53.81 | 0.07 |  |  |  |  | 96.79 | 0.06 | 56.94 | 0.03 | 57.21 | 0.03 | 0.27 | 0.03 |  |  | 57.25 | 0.32 | 57.89 | 0.03 | 0.64 | 0.32 | 97.56 | 0.05 | 70.62 | 0.04 | 57.64 | 0.03 | 12.98 | 0.04 | 96.73 | 0.05 | 56.88 | 0.04 | 57.18 | 0.03 | -0.31 | 0.02 | 0 | 0 |  | 0.09 | -3686 | 0 | 0 | 0 | [38 empty] | -11.98 | 0 | 55.51 | 0.07 | -99.26 | 0.03 | 154.76 | 0.09 | -11.53 | 0.01 | [6 empty] | 71.05 | 0.04 | -94.68 | 0.08 | -165.73 | 0.09 | -11.82 | 0.01 | -97.62 | 0.07 | 168.8 | 0.07 | -11.86 | 0 | 56.23 | 0.06 | -98.02 | 0.04 | 154.24 | 0.08 | 53.84 | 0.15 | -2.4 | 0 | 30.64 | 0.01 | 117.6 | 0.01 | -3686 | 0 | 0 | 0 | [18 empty] | 51.84 | 0.17 | 53.84 | 0.15 | 59.25 | 0.08 | 52.91 | 0.13 | 70.09 | 0.07 | 70.27 | 0.07 | 70.38 | 0.08 | 70.41 | 0.08 | 70.82 | 0.3 | 70.54 | 0.08 | 51.89 | 0.17 | 72.78 | 0.06 | 70.62 | 0.04 | 57.21 | 0.03 | 55.87 | 0.07 | 53.1 | 0.12 | 72.44 | 0.06 | 72.05 | 0.06 | 56.35 | 0.06 |  |  |  |  | 70.82 | 0.16 | [8 empty] | 59.25 | 0.08 | 52.91 | 0.13 | [14 empty] | 70.54 | 0.08 | 53.81 | 0.07 | 53.5 | 0.12 | 51.84 | 0.17 | 53.84 | 0.15 | [16 empty] | 71.19 | 0.04 | [12 empty] | 56.59 | 0.05 | 55.83 | 0.17 | 55.52 | 0.16 | 75.49 | 0.07 | 75.42 | 0.06 | 75.1 | 0.06 | 75.87 | 0.06 | 75.84 | 0.07 | 75.81 | 0.07 | 75.62 | 0.07 | 61.18 | 0.21 | 62.58 | 0.16 | 61.44 | 0.24 | 63.97 | 0.19 | 65.54 | 0.2 | 65.78 | 0.14 | 65.65 | 0.23 | 68.16 | 0.12 | 71.71 | 0.12 | 67.61 | 0.13 | 71.34 | 0.12 | 72.66 | 0.08 | 75.31 | 0.23 | 71.71 | 0.07 | 73.84 | 0.05 | 74.9 | 0.04 | 74.7 | 0.04 | 74.47 | 0.05 | 73.27 | 0.08 |  |  | 75.2 | 0.07 | 75.86 | 0.06 | 75.62 | 0.06 | 75.42 | 0.06 | 75.29 |  | 75.07 | 0.06 | 61.92 | 0.22 | 59.68 | 0.24 | 65.9 | 0.21 | 69.58 | 0.15 | 74.83 | 0.05 | [62 empty] | Economizer test | 74.99 | 0.061 | 61.976 | 0.052 | 70.456 | 0.06 | 59.497 | 0.052 | 55.084 | 0.06 | 51.058 | 0.039 | 3128.5 | 3.2 | 3020.9 | 3.2 | 0.607 | 0.002 | -0.182 | 0.003 | 0.274 | 0.004 | 1.765 | 0.0037 | 29.381 | 0.001 | 1805 | 11 | 1700 |  | 0.15191 | 458.917 | 13.032 | 0.182 | 1.5101 | 13975.985 | 215.422 | 458.912 | 2112.9006 | 11863.0844 | 0.0084989 | 26.5663 | 68.9459 | 13.0317 | 13.4309 | 0.0069924 | 20.8102 | 0.0087672 | 27.5915 | 0.0082446 | 25.9149 | 71.9889 | 60.4705 | 25.5469
2 | T2-55-T1ER-DMM | 75T0055 | T2-55-T1ER-DMM | 1 finger | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/2/2014 | 1:49:02 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0.9 | 3.7 | 0 | [9 empty] | 957 | 1670 | [37 empty] | Econo 1F-open, tape around damper perimeter frame gaps, no compressor, 55/51 ambient,--2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-55-T1E-DMM-SPWCT-SSR | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.942 | 0.019 | 62 | 0.059 | 54.968 | 0.037 | 51.021 | 0.043 | 74.98 | 0.03 | 71.94 | 0.03 | 72.33 | 0.03 | 0.273 | 0.005 | 1.7195 | 0.003 | [12 empty] | 460.2 | 2.6 | 460.1 | 2.6 | 459.5 | 2.5 | 3.7 | 0 | 3.3 | 0 | 3.5 | 0 | 1624.6 | 21.3 | 1103.3 | 23.7 | 147 | 16.7 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.2 |  | 0.57 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 105 |  | 1775 | [166 empty] | 51.99 | 0.07 | 52.53 | 0.11 | 59.77 | 0.05 | 53.41 | 0.06 | 71.58 | 0.03 | 71.76 | 0.03 | 71.9 | 0.04 | 71.99 | 0.03 | 72.32 | 0.22 | 72.11 | 0.03 | 52.38 | 0.1 | 73.08 | 0.02 | 72.31 | 0.03 | 55.04 | 0.07 | 57.06 | 0.04 | 51.88 | 0.08 | 73.18 | 0.03 | 72.83 | 0.03 | 56.83 | 0.06 |  |  |  |  | 56.87 | 0.06 | [26 empty] | 72.11 | 0.03 | 54.06 | 0.08 | 52.08 | 0.1 | [34 empty] | 55.56 | 0.03 | 55.3 | 0.15 | 54.91 | 0.12 | 75.54 | 0.03 | 75.45 | 0.03 | 75.12 | 0.03 | 75.93 | 0.02 | 75.9 | 0.03 | 75.83 | 0.03 | 75.64 | 0.03 | 65.71 | 0.15 | 63.97 | 0.15 | 64.26 | 0.31 | 66.4 | 0.17 | 66.58 | 0.13 | 65.77 | 0.16 | 69.28 | 0.12 | 69.73 | 0.08 | 73.02 | 0.19 | 68.9 | 0.14 | 74.25 | 0.07 | 74.54 | 0.03 | 74.12 | 0.15 | 73.09 | 0.07 | 74.54 | 0.04 | 74.81 | 0.03 | 74.67 | 0.02 | 74.55 | 0.03 | 73.79 | 0.04 |  |  | 75.25 | 0.03 | 75.89 | 0.03 | 75.66 | 0.03 | 75.47 | 0.03 | 75.3 |  | 75.13 | 0.03 |  |  | 64.52 | 0.13 | 67.29 | 0.13 | 74.55 | 0.04 | 74.76 | 0.03 | [62 empty] | Economizer test | 74.942 | 0.019 | 62 | 0.059 | 71.871 | 0.035 | 60.241 | 0.063 | 54.968 | 0.037 | 51.021 | 0.043 | 3090.2 | 2.7 | 2978.4 | 2.7 | 0.656 | 0.003 | -0.225 | 0.004 | 0.273 | 0.005 | 1.7195 | 0.003 | 29.395 | 0 | 1772 | 11 | 1670 |  | 0.079153 | 235.749 | 13.029 | 0.225 | 1.4875 | 13767.0257 | 229.5366 | 235.7475 | 1085.6572 | 12681.3685 | 0.0086528 | 27.0717 | 70.3835 | 13.0288 | 13.4678 | 0.007 | 20.7902 | 0.0087943 | 27.6095 | 0.0083804 | 26.408 | 73.3716 | 61.2166 | 26.0455
2 | T2-55-TCE-DMM | 75T0056 | T2-55-TCE-DMM | closed | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/2/2014 | 2:37:48 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0.5 | 3.7 | 0 | [9 empty] | 958 | 1620 | [37 empty] | Econo closed, tape around damper perimeter frame gaps, no compressor, 55/51 ambient,--2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-55-TCE-DMM-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.969 | 0.011 | 61.99 | 0.052 | 55.007 | 0.077 | 50.986 | 0.067 | 74.94 | 0.03 | 73.37 | 0.03 | 73.58 | 0.03 | 0.254 | 0.004 | 1.6603 | 0.0032 | 5334 | 106 | 4168 | 150 | 5.444 | 0.112 | -3686 | 0 | 0 | 0 | 0 | 0 | 460.3 | 2.4 | 460.3 | 2.4 | 459.6 | 2.4 | 3.7 | 0 | 3.2 | 0 | 3.5 | 0 | 1613.5 | 20.5 | 1103.6 | 23.3 | 133.4 | 16 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.57 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 115 |  | 1735 | [166 empty] | 53.26 | 0.37 | 53.01 | 0.29 | 57.79 | 0.75 | 54.19 | 0.59 | 73.15 | 0.07 | 73.21 | 0.07 | 73.23 | 0.06 | 73.58 | 0.06 | 73.27 | 0.22 | 73.64 | 0.06 | 53.68 | 0.31 | 73.6 | 0.04 | 73.4 | 0.02 | 55.01 | 0.05 | 56.71 | 0.14 | 53.13 | 0.35 | 73.92 | 0.05 | 73.67 | 0.02 | 57.43 | 0.15 |  |  |  |  | 56.25 | 0.13 | [26 empty] | 73.64 | 0.06 | 54.28 | 0.37 | 52.74 | 0.4 | [34 empty] | 55.18 | 0.09 | 55.69 | 0.19 | 55.27 | 0.18 | 75.52 | 0.02 | 75.47 | 0.02 | 75.15 | 0.02 | 75.93 | 0.02 | 75.89 | 0.02 | 75.86 | 0.02 | 75.68 | 0.02 | 69.14 | 0.14 | 67.81 | 0.12 | 64.45 | 0.18 | 70.39 | 0.1 | 72.16 | 0.09 | 68.91 | 0.1 | 69.69 | 0.13 | 71.25 | 0.07 | 73.63 | 0.06 | 70.1 | 0.09 | 73.97 | 0.07 | 74.76 | 0.03 | 74.76 | 0.22 | 74.25 | 0.04 | 74.73 | 0.03 | 74.84 | 0.03 | 74.69 | 0.02 | 74.6 | 0.02 | 74.12 | 0.02 |  |  | 75.3 | 0.02 | 75.9 | 0.03 | 75.67 | 0.03 | 75.49 | 0.03 | 75.35 |  | 75.19 | 0.03 | 65.13 | 0.23 | 65.49 | 0.2 | 72.69 | 0.07 | 74.33 | 0.06 | 74.79 | 0.02 | [62 empty] | Economizer test | 74.969 | 0.011 | 61.99 | 0.052 | 73.36 | 0.028 | 61.002 | 0.056 | 55.007 | 0.077 | 50.986 | 0.067 | 3040.1 | 2.9 | 2922 | 2.8 | 0.674 | 0.003 | -0.254 | 0.004 | 0.254 | 0.004 | 1.6603 | 0.0032 | 29.391 | 0 | 1747 | 11 | 1620 |  | 0.0074642 | 21.8103 | 13.03 | 0.254 | 1.4618 | 13504.8987 | 231.369 | 21.81 | 100.4329 | 13404.4658 | 0.0087679 | 27.5511 | 71.8982 | 13.0296 | 13.5067 | 0.0069723 | 20.7695 | 0.0087814 | 27.6019 | 0.0085166 | 26.92 | 74.821 | 61.9165 | 26.5636
2 | T2-TRN-63A-55-T1E-DM | 75T0068 | T2-TRN-63A-55-T1E-DM | 10% open | off | off | 3 turns | unsealed | unsealed | 650 | 9.25 |  | 0 | 0 | CUST 5 | 10/20/2014 | 11:04:16 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 3.1 | 0 | 2581 | 13 | 2227 | 47 | 2183 | 47 | 4766 | 44 | 5.7078 | 648 | 750 |  | 3.091 | [35 empty] | Econo 10%-open (2.8V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--62.5% airflow (250 cfm/ton), 2 HP fan motor, 3 turns, 9.25" AK94 pulley (650 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester sp | W/ECO: Eco set at 2.8v: No Compr:55/51 amb:2HP blwr mtr 9.25` AK94 mtr. pulley:3 turns open: AX38 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.987 | 0.008 | 62.004 | 0.032 | 55.001 | 0.013 | 50.867 | 0.02 | 74.88 | 0.06 | 73.89 | 0.06 | 74.54 | 0.01 | 0.07 | 0.002 | 0.8416 | 0.0014 | 2581 | 13 | 2183 | 47 | 5.712 | 0.098 | [6 empty] | 460.6 | 2 | 461.7 | 2 | 459.6 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1169.9 | 15.5 | 1107.2 | 19.8 | -10 | 0 | 460 |  | 460 |  | 459 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.31 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 835 | [14 empty] | 97 | 0.03 | 55.62 | 0.08 | 57.35 | 0.02 | 1.74 | 0.08 | 96.7 | 0.03 | 57.18 | 0.03 | 57.19 | 0.02 | 0.01 | 0.02 |  |  | 68.73 | 0.01 |  |  |  |  | 96.49 | 0.04 | 71.32 | 0.03 | 57.07 | 0.02 | 14.25 | 0.02 | 96.37 | 0.04 | 56.85 | 0.02 | 57 | 0.02 | -0.15 | 0.03 | [46 empty] | 96.99 | 0.02 | 56.69 | 0.02 | 57.34 | 0.01 | -0.65 | 0.02 | 96.99 | 0.05 | 57.34 | 0.03 | 0.86 | 0.07 |  |  | 72.44 | 0.02 |  |  |  |  | 97.35 | 0.03 | 57.55 | 0.02 | 13.39 | 0.05 | 96.89 | 0.03 | 58.17 | 0.02 | 57.29 | 0.02 | 0.88 | 0.02 | 57.59 | 0.03 | [28 empty] | 56.66 | 0.06 | 58.06 | 0.04 | 57.59 | 0.03 | 59.32 | 0.08 | 73.95 | 0.05 | 73.76 | 0.04 | 73.62 | 0.03 | 74.2 | 0.02 | 74.2 | 0.02 |  |  | 55.01 | 0.02 | 69.26 | 0.04 | 71.49 | 0.03 | 57.22 | 0.03 | 57.28 | 0.03 | 56.65 | 0.05 | 73 | 0.02 | 71.92 | 0.01 | 59.91 | 0.02 | 68.73 | 0.01 | 72.44 | 0.02 | 54.85 | 0.06 | 55.82 | 0.01 | 58.82 | 0.03 | 56.68 | 0.02 | 57.35 | 0.01 | 58.06 | 0.04 | 59.32 | 0.08 | [16 empty] | 55.62 | 0.08 | 56.47 | 0.07 | 56.66 | 0.06 | 57.59 | 0.03 | [16 empty] | 70.93 | 0.05 | [12 empty] | 57.18 | 0.03 | 56.85 | 0.13 | 56.82 | 0.15 | 75.22 | 0.02 | 74.85 | 0.02 | 74.77 | 0.02 | 75.53 | 0.02 | 75.54 | 0.02 | 75.52 | 0.02 | 75.34 | 0.02 | 73.07 | 0.05 | 73.75 | 0.02 | 73.46 | 0.03 | 74.33 | 0.04 | 73.21 | 0.04 | 73.14 | 0.04 | 73.82 | 0.03 | 74.28 | 0.02 | 74.45 | 0.03 | 74.12 | 0.04 | 74.58 | 0.02 | 74.62 | 0.02 | 74.62 | 0.02 | 74.25 | 0.05 | 72.48 | 0.09 | 74.62 | 0.03 | 71.35 | 0.18 | 67.73 | 0.14 | 69.04 | 0.22 |  |  | 74.95 | 0.02 | 75.46 | 0.02 | 75.31 | 0.02 | 75.18 | 0.02 | 74.66 |  | 74.86 | 0.02 | 71.37 | 0.05 | 72.24 | 0.05 | 73.17 | 0.05 | 74.65 | 0.02 | 74.66 | 0.02 | [62 empty] | Economizer test | 74.987 | 0.008 | 62.004 | 0.032 | 73.832 | 0.005 | 61.259 | 0.033 | 55.001 | 0.013 | 50.867 | 0.02 | 2039 | 1.7 | 1958.4 | 1.6 | 0.289 | 0.002 | -0.14 | 0.001 | 0.07 | 0.002 | 0.8416 | 0.0014 | 29.438 | 0 | 835 | 12 | 750 |  | 0.004253 | 8.329 | 13.029 | 0.14 | 1.0738 | 9049.448 | 66.4912 | 8.329 | 38.3561 | 9011.0919 | 0.0087784 | 27.5824 | 72.7582 | 13.029 | 13.5191 | 0.0069105 | 20.7011 | 0.0087863 | 27.6117 | 0.0085716 | 27.0952 | 74.9026 | 61.9617 | 26.8334
2 | T2-TRN-63A-55-T2E-DM-2 | 75T0069 | T2-TRN-63A-55-T2E-DM-2 | 20% open | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 10:52:14 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 3 | 0 | 3601 | 8 | 3399 | 49 | 1822 | 35 | 5424 | 34 | 6.8658 | 634 | 700 |  | 4.5582 | [35 empty] | Econo 20%-open (3.6V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 62.5% airflow (250 cfm/ton), 2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.982 | 0.003 | 61.993 | 0.023 | 55.008 | 0.011 | 51.005 | 0.015 | 75 | 0.03 | 73.44 | 0.02 | 73.99 | 0.01 | 0.07 | 0.002 | 0.8123 | 0.0016 | 3601 | 8 | 1822 | 35 | 6.865 | 0.082 | [6 empty] | 460 | 2 | 460.7 | 2 | 459.9 | 2 | 3 | 0 | 2.6 | 0 | 3 | 0 | 1126.6 | 14.6 | 1129.5 | 19.5 | -10 | 0 | 460 |  | 459 |  | 459 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 785 | [14 empty] | 95.9 | 0.01 | 57.77 | 0.02 | 56.76 | 0.01 | -1.01 | 0.02 | 95.3 | 0.01 | 58.63 | 0.01 | 56.43 | 0.01 | -2.2 | 0.02 |  |  | 71.32 | 0.02 |  |  |  |  | 95.37 | 0.01 | 70.98 | 0.01 | 56.46 | 0.01 | 14.52 | 0.01 | 94.94 | 0.05 | 59.85 | 0.02 | 56.22 | 0.03 | 3.63 | 0.03 | [46 empty] | 95.99 | 0.03 | 59.97 | 0.02 | 56.8 | 0.01 | 3.17 | 0.03 | 96.62 | 0.03 | 57.16 | 0.01 | 0.27 | 0.2 |  |  | 72.26 | 0.03 |  |  |  |  | 95.79 | 0.02 | 56.69 | 0.01 | 14.17 | 0.03 | 95.76 | 0.02 | 60.82 | 0.01 | 56.67 | 0.01 | 4.15 | 0.02 | 59.85 | 0.06 | [28 empty] | 59.19 | 0.02 | 60.01 | 0.02 | 59.85 | 0.06 | 61.26 | 0.02 | 73.45 | 0.02 | 73.18 | 0.02 | 73.03 | 0.02 | 73.72 | 0.01 | 73.72 | 0.01 |  |  | 57.18 | 0.02 | 71.88 | 0.01 | 71.69 | 0.01 | 60.06 | 0.01 | 60.69 | 0.02 | 57.18 | 0.14 | 72.82 | 0.03 | 71.99 | 0.02 | 62.6 | 0.02 | 71.32 | 0.02 | 72.26 | 0.03 | 55.62 | 0.04 | 58.6 | 0.02 | 60.9 | 0.02 | 58 | 0.03 | 58.89 | 0.06 | 60.01 | 0.02 | 61.26 | 0.02 | [16 empty] | 57.77 | 0.02 | 56.91 | 0.2 | 59.19 | 0.02 | 59.85 | 0.06 | [16 empty] | 70.86 | 0.02 | [12 empty] | 58.77 | 0.01 | 56.07 | 0.06 | 55.74 | 0.04 | 75.32 | 0.02 | 72.75 | 0.04 | 74.77 | 0.02 | 73.71 | 0.05 | 75.75 | 1.07 | 75.73 | 0.02 | 75.35 | 0.02 | 70.81 | 0.09 | 71.71 | 0.05 | 71.55 | 0.04 | 70.67 | 0.08 | 72.03 | 0.1 | 71.87 | 0.08 | 72.11 | 0.05 | 72.77 | 0.04 | 73.6 | 0.05 | 72.73 | 0.05 | 73.34 | 0.06 | 74.74 | 0.02 | 74.63 | 0.02 | 74.65 | 0.01 | 74.52 | 0.03 | 74.84 | 0.02 | 74.57 | 0.02 | 71.55 | 0.15 | 69.66 | 0.1 |  |  | 73.21 | 0.06 | 75.67 | 0.02 | 75.54 | 0.02 | 74.86 | 0.03 | 73.17 |  | 75 | 0.02 | 68.53 | 0.08 |  |  | 71.14 | 0.08 | 73.81 | 0.05 | 74.76 | 0.02 | [62 empty] | Economizer test | 74.982 | 0.003 | 61.993 | 0.023 | 73.326 | 0.004 | 61.124 | 0.022 | 55.008 | 0.011 | 51.005 | 0.015 | 1999.8 | 1.9 | 1926.7 | 1.9 | 0.288 | 0.002 | -0.131 | 0.001 | 0.07 | 0.002 | 0.8123 | 0.0016 | 29.5 | 0.001 | 790 | 8 | 700 |  | 0.031841 | 61.3488 | 13.03 | 0.131 | 1.0159 | 8883.7287 | 65.1886 | 61.3481 | 282.4996 | 8601.2291 | 0.0087231 | 27.3869 | 72.3101 | 13.0297 | 13.5065 | 0.0069821 | 20.7805 | 0.0087803 | 27.6039 | 0.0086036 | 27.0067 | 74.3488 | 61.6784 | 26.7591
2 | T2-TRN-63A-55-T3E-DM-2 | 75T0070 | T2-TRN-63A-55-T3E-DM-2 | 30% open | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 11:47:07 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 3 | 0 | 5700 | 14 | 5495 | 41 | 2777 | 66 | 8479 | 71 | 10.6923 | 634 | 700 |  | 7.1879 | [35 empty] | Econo 30%-open (4.4V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--62.5% airflow (250 cfm/ton), 2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet--Meriam, adjust code tester | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.98 | 0.005 | 61.999 | 0.026 | 54.993 | 0.01 | 51.002 | 0.014 | 75 | 0.03 | 72.49 | 0.02 | 73.3 | 0.01 | 0.073 | 0.002 | 0.828 | 0.0015 | 5700 | 14 | 2777 | 66 | 10.696 | 0.143 | [6 empty] | 460 | 2 | 460.7 | 2 | 459.9 | 2 | 3 | 0 | 2.6 | 0 | 3 | 0 | 1128.9 | 15 | 1128.9 | 20.2 | -10 | 0 | 460 |  | 459 |  | 459 |  | 2.5 |  | 2.6 |  | 2.6 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 785 | [14 empty] | 96.34 | 0.02 | 58.38 | 0.03 | 57 | 0.01 | -1.38 | 0.03 | 95.75 | 0 | 59.13 | 0.02 | 56.67 | 0 | -2.46 | 0.02 |  |  | 71.45 | 0.01 |  |  |  |  | 95.85 | 0.01 | 70.87 | 0.02 | 56.72 | 0.01 | 14.14 | 0.02 | 95.4 | 0.02 | 60.91 | 0.02 | 56.47 | 0.01 | 4.43 | 0.02 | [46 empty] | 96.46 | 0.01 | 60.77 | 0.04 | 57.07 | 0.01 | 3.71 | 0.04 | 97.08 | 0.02 | 57.41 | 0.01 | 0.38 | 0.09 |  |  | 71.56 | 0.06 |  |  |  |  | 96.22 | 0.02 | 56.93 | 0.01 | 14.01 | 0.03 | 96.19 | 0.02 | 61.43 | 0.01 | 56.92 | 0.01 | 4.52 | 0.01 | 60.16 | 0.04 | [28 empty] | 59.69 | 0.02 | 60.43 | 0.02 | 60.16 | 0.04 | 61.64 | 0.02 | 72.7 | 0.02 | 72.15 | 0.02 | 71.95 | 0.02 | 72.93 | 0.02 | 72.89 | 0.02 |  |  | 57.74 | 0.02 | 72.06 | 0.02 | 71.62 | 0.02 | 60.97 | 0.02 | 61.44 | 0.05 | 57.4 | 0.1 | 72.15 | 0.06 | 72.01 | 0.02 | 62.96 | 0.03 | 71.45 | 0.01 | 71.56 | 0.06 | 55.49 | 0.02 | 59.32 | 0.02 | 61.3 | 0.02 | 58.47 | 0.08 | 59.13 | 0.04 | 60.43 | 0.02 | 61.64 | 0.02 | [16 empty] | 58.38 | 0.03 | 57.03 | 0.09 | 59.69 | 0.02 | 60.16 | 0.04 | [16 empty] | 70.94 | 0.03 | [12 empty] | 59.26 | 0.03 | 56.25 | 0.09 | 55.79 | 0.04 | 75.31 | 0.02 | 72.72 | 0.04 | 74.77 | 0.02 | 73.66 | 0.06 | 75.62 | 2.72 | 75.7 | 0.02 | 75.3 | 0.02 | 67.47 | 0.12 | 69.96 | 0.14 | 71.12 | 0.05 | 69.7 | 0.1 | 67.56 | 0.11 | 70.41 | 0.08 | 70.95 | 0.04 | 70.71 | 0.05 | 68.68 | 0.09 | 69.98 | 0.07 | 67.88 | 0.12 | 73.99 | 0.04 | 74.28 | 0.04 | 74.49 | 0.03 | 74.42 | 0.03 | 74.42 | 0.03 | 74.57 | 0.02 | 71.76 | 0.13 | 70.58 | 0.07 |  |  | 73.15 | 0.06 | 75.63 | 0.01 | 75.51 | 0.02 | 74.86 | 0.02 | 73.22 |  | 75 | 0.02 | 64.13 | 0.07 |  |  | 66.6 | 0.14 | 66.57 | 0.13 | 74.31 | 0.04 | [62 empty] | Economizer test | 74.98 | 0.005 | 61.999 | 0.026 | 72.385 | 0.005 | 60.641 | 0.022 | 54.993 | 0.01 | 51.002 | 0.014 | 2018 | 1.8 | 1946.8 | 1.7 | 0.279 | 0.002 | -0.119 | 0.001 | 0.073 | 0.002 | 0.828 | 0.0015 | 29.495 | 0.001 | 793 | 8 | 700 |  | 0.079302 | 154.3842 | 13.029 | 0.119 | 1.0071 | 8980.9091 | 63.8103 | 154.3863 | 710.9473 | 8269.9618 | 0.0086421 | 27.0676 | 71.3779 | 13.0293 | 13.4819 | 0.0069841 | 20.7789 | 0.0087847 | 27.6082 | 0.0085145 | 26.6799 | 73.4026 | 61.2114 | 26.4344
2 | T2-TRN-63A-55-TCE-DM-2 | 75T0071 | T2-TRN-63A-55-TCE-DM-2 | closed | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 8:04:48 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 3 | 0 | 2388 | 11 | 2066 | 40 | 1315 | 39 | 3705 | 41 | 4.6899 | 634 | 710 |  | 3.0228 | [35 empty] | Econo closed (2V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 62.5% airflow (250 cfm/ton), 2 HP fan motor, 5.5 turns, 7.25" AK74 pulley--(620 rpm), 100% inlet/outlet Meriam, adjust code tester speed to match tot | W/ECO: 2V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.003 | 0.005 | 61.996 | 0.011 | 55.001 | 0.01 | 51.003 | 0.017 | 75.05 | 0.02 | 74.1 | 0.02 | 74.41 | 0 | 0.083 | 0.002 | 0.8136 | 0.0013 | 2388 | 11 | 1315 | 39 | 4.688 | 0.074 | [6 empty] | 460.3 | 1.9 | 460.9 | 1.9 | 459.9 | 2 | 3 | 0 | 2.6 | 0 | 3 | 0 | 1132.3 | 14.4 | 1125.9 | 19.4 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.7 |  | 2.7 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 795 | [14 empty] | 95.83 | 0.02 | 57.74 | 0.03 | 56.71 | 0.01 | 1.03 | 0.04 | 95.23 | 0.01 | 59.08 | 0.02 | 56.38 | 0.01 | 2.7 | 0.02 |  |  | 71.13 | 0.02 |  |  |  |  | 95.3 | 0.02 | 71.03 | 0.01 | 56.41 | 0.01 | 14.62 | 0.02 | 95.13 | 0.03 | 59.85 | 0.02 | 56.32 | 0.02 | 3.53 | 0.03 | [46 empty] | 95.88 | 0.01 | 59.6 | 0.02 | 56.74 | 0.01 | 2.85 | 0.03 | 96.99 | 0.02 | 57.36 | 0.01 | 1.54 | 0.04 |  |  | 72.53 | 0.02 |  |  |  |  | 95.76 | 0.02 | 56.67 | 0.01 | 14.15 | 0.03 | 95.7 | 0.02 | 59.3 | 0.02 | 56.63 | 0.01 | 2.66 | 0.02 | 59.29 | 0.03 | [28 empty] | 58.95 | 0.03 | 59.74 | 0.02 | 59.29 | 0.03 | 60.59 | 0.02 | 74.16 | 0.02 | 73.88 | 0.02 | 73.67 | 0.02 | 74.38 | 0.03 | 74.37 | 0.02 |  |  | 57.11 | 0.02 | 71.67 | 0.02 | 71.74 | 0.02 | 60.02 | 0.02 | 60.38 | 0.02 | 58.85 | 0.01 | 73.14 | 0.01 | 71.99 | 0.01 | 61.19 | 0.02 | 71.13 | 0.02 | 72.53 | 0.02 | 55.74 | 0.02 | 58.44 | 0.02 | 60.58 | 0.02 | 59.3 | 0.02 | 59.88 | 0.04 | 59.74 | 0.02 | 60.59 | 0.02 | [16 empty] | 57.74 | 0.03 | 58.9 | 0.04 | 58.95 | 0.03 | 59.29 | 0.03 | [16 empty] | 70.82 | 0.03 | [12 empty] | 59.33 | 0.03 | 56.02 | 0.04 | 55.76 | 0.05 | 75.4 | 0.02 | 72.84 | 0.05 | 74.85 | 0.03 | 73.78 | 0.04 | 76.22 | 2.67 | 75.86 | 0.02 | 75.47 | 0.02 | 71.94 | 0.06 | 72.35 | 0.04 | 72.37 | 0.03 | 72.54 | 0.08 | 73.07 | 0.05 | 73.06 | 0.04 | 73.2 | 0.03 | 73.69 | 0.03 | 74.12 | 0.04 | 73.7 | 0.04 | 73.94 | 0.03 | 74.85 | 0.02 | 74.83 | 0.02 | 74.75 | 0.02 | 74.51 | 0.05 | 74.92 | 0.02 | 74.62 | 0.02 | 70.83 | 0.16 | 69.92 | 0.1 |  |  | 73.3 | 0.06 | 75.8 | 0.02 | 75.65 | 0.02 | 74.94 | 0.03 | 73.18 |  | 75.06 | 0.02 | 70.35 | 0.11 |  |  | 72.52 | 0.08 | 74.18 | 0.04 | 74.89 | 0.02 | [62 empty] | Economizer test | 75.003 | 0.005 | 61.996 | 0.011 | 73.906 | 0.003 | 61.408 | 0.009 | 55.001 | 0.01 | 51.003 | 0.017 | 2002.7 | 1.6 | 1926.9 | 1.6 | 0.287 | 0.002 | -0.141 | 0.001 | 0.083 | 0.002 | 0.8136 | 0.0013 | 29.484 | 0 | 790 | 8 | 710 |  | 0.0033497 | 6.4545 | 13.03 | 0.141 | 1.0319 | 8886.6899 | 64.969 | 6.4544 | 29.7218 | 8856.9681 | 0.0087713 | 27.5829 | 72.8741 | 13.0295 | 13.5216 | 0.0069827 | 20.7794 | 0.0087773 | 27.6057 | 0.0086511 | 27.2001 | 74.9363 | 61.963 | 26.9485
2 | T2-TRN-75A-55-TCE-DM-2 | 75T0209 | T2-TRN-75A-55-TCE-DM-2 | closed | off | off |  | unsealed | unsealed | [5 empty] | CUST 5 | 10/29/2014 | 21:13:07 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 3.2 | 0 | 2193 | 17 | 1877 | 62 | 1597 | 68 | 3792 | 71 | 3.5673 | 748 | 980 |  | 2.063 | [35 empty] | Econo closed (2V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor, 3 turns, 7.25" AK74 pulley (725 rpm),--100% inlet/outlet Meriam, adjust code tester speed to match total s | W/ECO: 2 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.01 | 0.006 | 61.988 | 0.02 | 54.992 | 0.013 | 51.028 | 0.013 | 75.01 | 0.03 | 74.29 | 0.02 | 74.41 | 0.02 | 0.12 | 0.002 | 1.1604 | 0.002 | 2193 | 17 | 1597 | 68 | 3.568 | 0.073 | [6 empty] | 460.2 | 2 | 460.3 | 2 | 459.9 | 2 | 3.2 | 0 | 2.8 | 0 | 3.1 | 0 | 1254.2 | 14.1 | 1119.9 | 19.2 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.8 |  | 0.39 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1065 | [14 empty] | 95.91 | 0.03 | 57.91 | 0.05 | 56.75 | 0.02 | -1.15 | 0.04 | 95.39 | 0.04 | 59.71 | 0.06 | 56.46 | 0.02 | -3.24 | 0.04 |  |  | 70.46 | 0.03 |  |  |  |  | 95.46 | 0.03 | 70.93 | 0.02 | 56.51 | 0.02 | 14.42 | 0.03 | 95.31 | 0.05 | 60.53 | 0.06 | 56.41 | 0.03 | 4.11 | 0.06 | [46 empty] | 96.15 | 0.05 | 60.66 | 0.06 | 56.89 | 0.02 | 3.76 | 0.03 | 97.31 | 0.04 | 57.53 | 0.02 | -1.41 | 0.05 |  |  | 72.68 | 0.02 |  |  |  |  | 95.94 | 0.05 | 56.77 | 0.03 | 13.75 | 0.04 | 95.96 | 0.05 | 60.45 | 0.06 | 56.78 | 0.02 | 3.67 | 0.04 | 60.47 | 0.02 | [28 empty] | 59.42 | 0.03 | 60.42 | 0.03 | 60.47 | 0.02 | 61.4 | 0.04 | 74.36 | 0.02 | 74.16 | 0.01 | 74.03 | 0.04 | 74.61 | 0.02 | 74.61 | 0.02 |  |  | 57.26 | 0.03 | 70.74 | 0.02 | 71.6 | 0.02 | 60.74 | 0.08 | 61.4 | 0.06 | 58.86 | 0.02 | 73.3 | 0.03 | 71.82 | 0.03 | 62.94 | 0.05 | 70.46 | 0.03 | 72.68 | 0.02 | 55.76 | 0.03 | 58.78 | 0.03 | 61.32 | 0.04 | 59.67 | 0.01 | 60.19 | 0.02 | 60.42 | 0.03 | 61.4 | 0.04 | [16 empty] | 57.91 | 0.05 | 58.94 | 0.06 | 59.42 | 0.03 | 60.47 | 0.02 | [16 empty] | 70.52 | 0.04 | [12 empty] | 59.88 | 0.06 | 56.07 | 0.07 | 55.76 | 0.04 | 75.43 | 0.02 | 72.98 | 0.04 | 74.85 | 0.03 | 73.95 | 0.04 | 75.85 | 0.28 | 75.85 | 0.03 | 75.47 | 0.03 | 72.37 | 0.04 | 72.75 | 0.03 | 72.61 | 0.03 | 72.93 | 0.06 | 73.29 | 0.05 | 73.22 | 0.04 | 73.43 | 0.03 | 73.95 | 0.05 | 74.19 | 0.04 | 73.86 | 0.05 | 74.05 | 0.04 | 74.78 | 0.02 | 74.8 | 0.02 | 74.8 | 0.02 | 73.68 | 0.14 | 74.77 | 0.02 | 74.58 | 0.02 | 69.63 | 0.1 | 69.64 | 0.07 |  |  | 73.41 | 0.06 | 75.85 | 0.02 | 75.69 | 0.02 | 74.98 | 0.03 | 73.3 |  | 75.12 | 0.02 | 71.27 | 0.08 |  |  | 72.74 | 0.05 | 74.23 | 0.04 | 74.82 | 0.02 | [62 empty] | Economizer test | 75.01 | 0.006 | 61.988 | 0.02 | 74.17 | 0.009 | 61.494 | 0.023 | 54.992 | 0.013 | 51.028 | 0.013 | 2395.2 | 2.1 | 2304.1 | 2 | 0.423 | 0.002 | -0.193 | 0.001 | 0.12 | 0.002 | 1.1604 | 0.002 | 29.476 | 0 | 1063 | 9 | 980 |  | 0 | 0 | 13.029 | 0.193 | 1.1583 | 10623.1352 | 114.5003 | 0 | 0 | 10623.1352 | 0.0087704 | 27.5998 | 73.0117 | 13.0294 | 13.5282 | 0.0069981 | 20.7939 | 0.0087704 | 27.5998 | 0.0086448 | 27.2576 | 75.01 | 61.988 | 26.9752
2 | T2-TRN-75A-55-T1E-DM | 75T0210 | T2-TRN-75A-55-T1E-DM | 10% open | off | off |  | unsealed | unsealed | [5 empty] | CUST 5 | 10/22/2014 | 0:59:37 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 3.2 | 0 | 2157 | 14 | 1842 | 82 | 2100 | 71 | 4259 | 72 | 3.9435 | 755 |  |  | 1.9972 | [35 empty] | Econo 10%-open (2.8V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor, 3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab,--100% inlet/outlet Meriam, adjust code tester spee | W/ECO: Eco set at 2.8v: No Compr:55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley:3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.994 | 0.001 | 62.002 | 0.034 | 54.997 | 0.01 | 51.007 | 0.016 | 74.87 | 0.05 | 74.18 | 0.04 | 74.56 | 0.01 | 0.115 | 0.003 | 1.1643 | 0.0016 | 2157 | 14 | 2100 | 71 | 3.946 | 0.075 | [6 empty] | 460.2 | 1.9 | 461.8 | 2 | 459.8 | 2 | 3.2 | 0 | 2.7 | 0 | 3.1 | 0 | 1276.6 | 14.4 | 1095.9 | 18.9 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.7 |  | 0.38 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1065 | [14 empty] | 96.85 | 0.03 | 55.54 | 0.04 | 57.26 | 0.01 | 1.71 | 0.04 | 96.07 | 0.01 | 57.23 | 0.01 | 56.83 | 0 | 0.4 | 0.02 |  |  | 68.64 | 0.02 |  |  |  |  | 96.46 | 0.02 | 70.97 | 0.01 | 57.04 | 0.01 | 13.93 | 0.02 | 95.67 | 0.03 | 56.89 | 0.02 | 56.6 | 0.02 | 0.29 | 0.02 | [46 empty] | 96.99 | 0.03 | 56.81 | 0.02 | 57.34 | 0.01 | 0.52 | 0.02 | 97.5 | 0.03 | 57.61 | 0.02 | 1.11 | 0.03 |  |  | 72.51 | 0.01 |  |  |  |  | 97.05 | 0.02 | 57.37 | 0.01 | 13.2 | 0.03 | 96.54 | 0.01 | 58.76 | 0.02 | 57.08 | 0.01 | 1.67 | 0.02 | 57.56 | 0.03 | [28 empty] | 56.58 | 0.03 | 58.1 | 0.04 | 57.56 | 0.03 | 59.33 | 0.05 | 74.22 | 0.02 | 74.01 | 0.02 | 73.94 | 0.02 | 74.5 | 0.02 | 74.48 | 0.02 |  |  | 55.03 | 0.01 | 69 | 0.03 | 71.15 | 0.02 | 57.3 | 0.02 | 57.3 | 0.01 | 56.74 | 0.02 | 73.04 | 0.01 | 71.74 | 0.02 | 60.63 | 0.02 | 68.64 | 0.02 | 72.51 | 0.01 | 55.24 | 0.04 | 55.98 | 0.01 | 59.06 | 0.02 | 57.1 | 0.01 | 57.68 | 0.01 | 58.1 | 0.04 | 59.33 | 0.05 | [16 empty] | 55.54 | 0.04 | 56.5 | 0.02 | 56.58 | 0.03 | 57.56 | 0.03 | [16 empty] | 70.57 | 0.03 | [12 empty] | 57.21 | 0.02 | 56.77 | 0.1 | 56.45 | 0.15 | 75.15 | 0.02 | 74.8 | 0.01 | 74.7 | 0.01 | 75.49 | 0.02 | 75.8 | 4.35 | 75.49 | 0.02 | 75.29 | 0.02 | 72.67 | 0.05 | 73.43 | 0.03 | 73.24 | 0.04 | 73 | 0.05 | 73.7 | 0.03 | 73.55 | 0.03 | 73.91 | 0.03 | 74.54 | 0.03 | 74.58 | 0.02 | 74.45 | 0.03 | 74.59 | 0.02 | 74.53 | 0.02 | 74.69 | 0.02 | 74.5 | 0.03 | 72.15 | 0.11 | 74.76 | 0.02 | 73.63 | 0.04 | 68.03 | 0.15 | 68.51 | 0.13 |  |  | 74.85 | 0.02 | 75.52 | 0.02 | 75.38 | 0.02 | 75.23 | 0.02 | 74.66 |  | 74.89 | 0.02 | 71.94 | 0.05 | 72.28 | 0.04 | 73.51 | 0.03 | 74.6 | 0.03 | 74.76 | 0.02 | [62 empty] | Economizer test | 74.994 | 0.001 | 62.002 | 0.034 | 74.175 | 0.006 | 61.446 | 0.03 | 54.997 | 0.01 | 51.007 | 0.016 | 2402.9 | 1.6 | 2304.5 | 1.6 | 0.403 | 0.002 | -0.191 | 0.001 | 0.115 | 0.003 | 1.1643 | 0.0016 | 29.396 | 0 | 1080 | 8 | 980 |  | 0 | 0 | 13.029 | 0.191 | 1.1617 | 10657.392 | 109.1056 | 0 | 0 | 10657.392 | 0.0087834 | 27.6102 | 73.0133 | 13.0295 | 13.5281 | 0.0069858 | 20.7818 | 0.0087834 | 27.6102 | 0.0086123 | 27.2233 | 74.994 | 62.002 | 26.94
2 | T2-TRN-75A-55-T2E-DM-2 | 75T0211 | T2-TRN-75A-55-T2E-DM-2 | 20% open | off | off |  | unsealed | unsealed | [5 empty] | CUST 5 | 10/29/2014 | 22:42:23 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.4 | 0 | 3.2 | 0 | 3830 | 15 | 3554 | 61 | 2345 | 81 | 6177 | 87 | 5.7891 | 748 | 980 |  | 3.5895 | [35 empty] | Econo 20%-open (3.6V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor, 3 turns, 7.25" AK74 pulley (725 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester spee | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.998 | 0.005 | 62.001 | 0.03 | 55 | 0.01 | 50.995 | 0.014 | 75.1 | 0.02 | 73.74 | 0.02 | 74 | 0 | 0.108 | 0.003 | 1.1674 | 0.0028 | 3830 | 15 | 2345 | 81 | 5.791 | 0.094 | [6 empty] | 460.4 | 2 | 460.6 | 2 | 459.6 | 2 | 3.2 | 0 | 2.7 | 0 | 3.1 | 0 | 1267.3 | 14.9 | 1109.6 | 19.3 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.7 |  | 0.39 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1065 | [14 empty] | 95.93 | 0.03 | 58.08 | 0.03 | 56.76 | 0.02 | -1.31 | 0.03 | 95.92 | 0.02 | 59.29 | 0.02 | 56.76 | 0.01 | -2.52 | 0.02 |  |  | 70.78 | 0.02 |  |  |  |  | 95.5 | 0.02 | 70.83 | 0.02 | 56.52 | 0.01 | 14.31 | 0.02 | 95.03 | 0.03 | 60.33 | 0.02 | 56.26 | 0.01 | 4.06 | 0.02 | [46 empty] | 96.25 | 0.03 | 60.38 | 0.05 | 56.94 | 0.02 | 3.43 | 0.04 | 96.93 | 0.03 | 57.32 | 0.02 | 0.37 | 0.26 |  |  | 72.49 | 0.06 |  |  |  |  | 96.02 | 0.03 | 56.81 | 0.02 | 13.88 | 0.03 | 96.02 | 0.03 | 60.61 | 0.06 | 56.81 | 0.02 | 3.8 | 0.07 | 60.53 | 0.05 | [28 empty] | 59.55 | 0.02 | 60.44 | 0.02 | 60.53 | 0.05 | 61.71 | 0.03 | 73.72 | 0.02 | 73.45 | 0.01 | 73.27 | 0.02 | 74.01 | 0.01 | 74 | 0.01 |  |  | 57.37 | 0.02 | 71.17 | 0.02 | 71.69 | 0.01 | 60.46 | 0.01 | 61.11 | 0.03 | 57.21 | 0.18 | 73.07 | 0.06 | 71.9 | 0.02 | 62.86 | 0.07 | 70.78 | 0.02 | 72.49 | 0.06 | 55.63 | 0.04 | 58.98 | 0.02 | 61.32 | 0.02 | 58.3 | 0.04 | 59.27 | 0.08 | 60.44 | 0.02 | 61.71 | 0.03 | [16 empty] | 58.08 | 0.03 | 56.96 | 0.25 | 59.55 | 0.02 | 60.53 | 0.05 | [16 empty] | 70.7 | 0.03 | [12 empty] | 59.57 | 0.01 | 56.26 | 0.09 | 55.84 | 0.05 | 75.46 | 0.02 | 73.01 | 0.04 | 74.87 | 0.02 | 74.02 | 0.04 | 75.63 | 1.39 | 75.94 | 0.02 | 75.53 | 0.02 | 70.71 | 0.06 | 71.82 | 0.05 | 71.78 | 0.04 | 71.23 | 0.08 | 72.09 | 0.07 | 71.73 | 0.05 | 71.96 | 0.04 | 73.03 | 0.04 | 73.49 | 0.06 | 72.56 | 0.06 | 73.27 | 0.06 | 74.81 | 0.02 | 74.78 | 0.02 | 74.79 | 0.02 | 74.23 | 0.11 | 74.85 | 0.01 | 74.65 | 0.01 | 70.11 | 0.1 | 69.01 | 0.08 |  |  | 73.43 | 0.05 | 75.9 | 0.02 | 75.73 | 0.02 | 75.03 | 0.03 | 73.39 |  | 75.14 | 0.02 | 68.16 | 0.09 |  |  | 71.3 | 0.07 | 74.04 | 0.05 | 74.83 | 0.01 | [62 empty] | Economizer test | 74.998 | 0.005 | 62.001 | 0.03 | 73.533 | 0.004 | 61.183 | 0.021 | 55 | 0.01 | 50.995 | 0.014 | 2401.6 | 2.9 | 2312.1 | 2.8 | 0.42 | 0.002 | -0.179 | 0.001 | 0.108 | 0.003 | 1.1674 | 0.0028 | 29.476 | 0.001 | 1067 | 9 | 980 |  | 0.015752 | 36.4192 | 13.029 | 0.179 | 1.1543 | 10664.574 | 114.083 | 36.4199 | 167.7115 | 10496.8625 | 0.0087534 | 27.5019 | 72.3787 | 13.0295 | 13.5117 | 0.0069787 | 20.7748 | 0.0087818 | 27.6094 | 0.0085929 | 27.0456 | 74.6845 | 61.8454 | 26.7641
2 | T2-TRN-75A-55-T3E-DM-2 | 75T0212 | T2-TRN-75A-55-T3E-DM-2 | 30% open | off | off |  | unsealed | unsealed | [5 empty] | CUST 5 | 10/29/2014 | 23:58:09 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 3.2 | 0 | 6506 | 14 | 6116 | 50 | 3501 | 63 | 10011 | 64 | 9.3039 | 748 | 990 |  | 6.0465 | [35 empty] | Econo 30%-open (4.4V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor, 3 turns, 7.25" AK74 pulley (725 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester spee | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.993 | 0.002 | 62 | 0.019 | 54.999 | 0.013 | 51.001 | 0.018 | 75.07 | 0.01 | 72.76 | 0.01 | 73.22 | 0 | 0.123 | 0.002 | 1.1992 | 0.002 | 6506 | 14 | 3501 | 63 | 9.306 | 0.089 | [6 empty] | 460.6 | 1.9 | 461.3 | 1.9 | 459.4 | 1.9 | 3.2 | 0 | 2.7 | 0 | 3.1 | 0 | 1286 | 14.6 | 1097.5 | 17.9 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.7 |  | 0.39 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1075 | [14 empty] | 96.39 | 0.02 | 58.6 | 0.01 | 57.01 | 0.01 | -1.58 | 0.02 | 96.42 | 0.03 | 59.76 | 0.02 | 57.05 | 0.02 | -2.71 | 0.03 |  |  | 71.18 | 0.02 |  |  |  |  | 96 | 0.01 | 70.75 | 0.02 | 56.8 | 0.01 | 13.95 | 0.02 | 95.65 | 0.03 | 61.27 | 0.02 | 56.61 | 0.01 | 4.66 | 0.03 | [46 empty] | 96.8 | 0.03 | 60.62 | 0.08 | 57.24 | 0.02 | 3.39 | 0.08 | 97.44 | 0.03 | 57.6 | 0.02 | 0.05 | 0.25 |  |  | 72.01 | 0.14 |  |  |  |  | 96.51 | 0.04 | 57.09 | 0.02 | 13.75 | 0.03 | 96.54 | 0.03 | 61.62 | 0.02 | 57.1 | 0.02 | 4.51 | 0.04 | 60.75 | 0.08 | [28 empty] | 59.87 | 0.02 | 60.73 | 0.02 | 60.75 | 0.08 | 61.98 | 0.02 | 73 | 0.01 | 72.33 | 0.02 | 72.14 | 0.02 | 73.27 | 0.01 | 73.21 | 0.02 |  |  | 57.9 | 0.03 | 71.59 | 0.02 | 71.74 | 0.02 | 61.37 | 0.02 | 61.35 | 0.07 | 57.72 | 0.16 | 72.58 | 0.12 | 72.05 | 0.02 | 63.65 | 0.04 | 71.18 | 0.02 | 72.01 | 0.14 | 55.6 | 0.04 | 59.59 | 0.02 | 61.64 | 0.02 | 58.62 | 0.09 | 59.53 | 0.06 | 60.73 | 0.02 | 61.98 | 0.02 | [16 empty] | 58.6 | 0.01 | 57.55 | 0.25 | 59.87 | 0.02 | 60.75 | 0.08 | [16 empty] | 70.84 | 0.02 | [12 empty] | 60.09 | 0.02 | 56.61 | 0.11 | 55.96 | 0.04 | 75.5 | 0.01 | 73.08 | 0.04 | 74.94 | 0.02 | 74.07 | 0.04 | 75.91 | 0.9 | 75.99 | 0.02 | 75.57 | 0.02 | 67.43 | 0.1 | 70.21 | 0.17 | 71.39 | 0.05 | 69.32 | 0.14 | 67 | 0.12 | 70.5 | 0.08 | 71.18 | 0.03 | 70.98 | 0.05 | 68.74 | 0.1 | 70.05 | 0.08 | 68.26 | 0.11 | 74.34 | 0.03 | 74.41 | 0.03 | 74.63 | 0.02 | 74.53 | 0.03 | 74.75 | 0.02 | 74.71 | 0.01 | 71.85 | 0.15 | 70.23 | 0.09 |  |  | 73.45 | 0.06 | 75.92 | 0.02 | 75.75 | 0.02 | 75.06 | 0.02 | 73.51 |  | 75.16 | 0.02 | 64.44 | 0.09 |  |  | 66.75 | 0.12 | 67.35 | 0.16 | 74.48 | 0.03 | [62 empty] | Economizer test | 74.993 | 0.002 | 62 | 0.019 | 72.534 | 0.005 | 60.675 | 0.018 | 54.999 | 0.013 | 51.001 | 0.018 | 2432.5 | 2 | 2345.8 | 1.9 | 0.404 | 0.002 | -0.164 | 0.001 | 0.123 | 0.002 | 1.1992 | 0.002 | 29.476 | 0.001 | 1076 | 8 | 990 |  | 0.06547 | 153.5787 | 13.029 | 0.164 | 1.1542 | 10822.6555 | 111.3365 | 153.5815 | 707.2339 | 10115.4216 | 0.0086646 | 27.1624 | 71.3798 | 13.0295 | 13.4856 | 0.0069821 | 20.7783 | 0.0087823 | 27.6087 | 0.0085011 | 26.7016 | 73.6904 | 61.3507 | 26.4203
2 | T2-TRN-100A-55-1E-DM | 75T0013 | T2-TRN-100A-55-1E-DM | 10% open | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 15:53:18 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 0 | 3.6 | 0 | 2984 | 20 | 2541 | 82 | 3203 | 80 | 6190 | 79 | 3.6758 | 944 | 1580 |  | 1.772 | [35 empty] | Econo 10%-open (2.8V), no compressor, 55/51 ambient, 100% airflow (400 cfm/ton),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-100A-55-1E-DM-SPWCT-SS | W/ECO: 2.8 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.986 | 0.009 | 61.995 | 0.025 | 55.005 | 0.009 | 51.015 | 0.016 | 74.96 | 0.04 | 74.21 | 0.04 | 74.25 | 0.01 | 0.199 | 0.004 | 1.9057 | 0.0029 | 2984 | 20 | 3203 | 80 | 3.675 | 0.052 | [6 empty] | 460.7 | 2 | 460.2 | 2 | 459.3 | 2 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1575.2 | 14.3 | 1093.6 | 18 | 108.9 | 9.8 | 460 |  | 459 |  | 459 |  | 3.1 |  | 3.1 |  | 3.1 |  | 0.54 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1665 | [14 empty] | 95.84 | 0.04 | 58.36 | 0.06 | 56.68 | 0.02 | -1.68 | 0.07 | 96.19 | 0.01 | 58.15 | 0.01 | 56.88 | 0.01 | -1.27 | 0.01 |  |  | 71.83 | 0.02 |  |  |  |  | 95.61 | 0.02 | 72.4 | 0.02 | 56.55 | 0.01 | 15.85 | 0.03 | 95.55 | 0.03 | 61.72 | 0.03 | 56.52 | 0.01 | 5.2 | 0.03 | [46 empty] | 96.33 | 0.02 | 60.88 | 0.05 | 56.95 | 0.02 | 3.92 | 0.05 | 96.74 | 0.03 | 57.18 | 0.02 | -0.18 | 0.23 |  |  | 73.55 | 0.06 |  |  |  |  | 96.03 | 0.03 | 56.78 | 0.02 | 15.4 | 0.04 | 96.1 | 0.03 | 61.91 | 0.03 | 56.82 | 0.02 | 5.08 | 0.04 | 61.28 | 0.14 | [28 empty] | 60.47 | 0.04 | 60.98 | 0.03 | 61.28 | 0.14 | 62.18 | 0.06 | 74.2 | 0.04 | 74.03 | 0.03 | 73.9 | 0.04 | 74.49 | 0.02 | 74.5 | 0.02 |  |  | 57.45 | 0.02 | 72.28 | 0.03 | 72.7 | 0.03 | 61.72 | 0.03 | 61.51 | 0.02 | 57.58 | 0.15 | 74.11 | 0.05 | 73.25 | 0.02 | 63.74 | 0.03 | 71.83 | 0.02 | 73.55 | 0.06 | 55.58 | 0.05 | 59.77 | 0.02 | 61.76 | 0.02 | 58.34 | 0.03 | 59.3 | 0.08 | 60.98 | 0.03 | 62.18 | 0.06 | [16 empty] | 58.36 | 0.06 | 57.35 | 0.23 | 60.47 | 0.04 | 61.28 | 0.14 | [16 empty] | 72.18 | 0.04 | [12 empty] | 58.17 | 0.03 | 56.27 | 0.1 | 55.76 | 0.05 | 75.34 | 0.01 | 73.16 | 0.04 | 74.75 | 0.02 | 74.05 | 0.04 | 75.71 | 1.9 | 75.69 | 0.02 | 75.33 | 0.02 | 69.35 | 0.1 | 71.77 | 0.05 | 71.82 | 0.03 | 72.56 | 0.07 | 72.48 | 0.06 | 72.41 | 0.05 | 72.66 | 0.03 | 73.38 | 0.03 | 73.95 | 0.03 | 73.42 | 0.04 | 73.9 | 0.03 | 74.72 | 0.02 | 74.73 | 0.02 | 74.64 | 0.02 | 73.96 | 0.07 | 74.79 | 0.02 | 74.58 | 0.03 | 69.24 | 0.15 | 70.4 | 0.07 |  |  | 73.57 | 0.04 | 75.66 | 0.01 | 75.51 | 0.02 | 74.88 | 0.03 | 73.33 |  | 75.01 | 0.01 | 68.82 | 0.09 |  |  | 71.93 | 0.06 | 74.1 | 0.03 | 74.76 | 0.02 | [62 empty] | Economizer test | 74.986 | 0.009 | 61.995 | 0.025 | 74.104 | 0.007 | 61.374 | 0.023 | 55.005 | 0.009 | 51.015 | 0.016 | 3081 | 2.4 | 2951.9 | 2.3 | 0.689 | 0.003 | -0.282 | 0.002 | 0.199 | 0.004 | 1.9057 | 0.0029 | 29.343 | 0 | 1684 | 10 | 1580 |  | 0 | 0 | 13.03 | 0.282 | 1.395 | 13666.9776 | 238.9384 | 0 | 0 | 13666.9776 | 0.0087806 | 27.6052 | 72.709 | 13.0297 | 13.526 | 0.0069881 | 20.7863 | 0.0087806 | 27.6052 | 0.0085822 | 27.173 | 74.986 | 61.995 | 26.8329
2 | T2-TRN-100A-55-1F-DM | 75T0014 | T2-TRN-100A-55-1F-DM | 1 finger | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 16:51:59 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 0 | 3.7 | 0 | 10949 | 26 | 10463 | 75 | 6837 | 80 | 17793 | 80 | 10.387 | 944 | 1600 |  | 6.3917 | [35 empty] | Econo 1F-open (5.1V), no compressor, 55/51 ambient, 100% airflow (400 cfm/ton), 2 HP fan motor,--3 turns, 5.75" AK59 pulley (950 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-100A-55-1F-DM-SPWC | W/ECO: 5.1 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.965 | 0.011 | 61.991 | 0.011 | 54.99 | 0.007 | 50.999 | 0.012 | 74.93 | 0.04 | 71.85 | 0.04 | 72.4 | 0.02 | 0.21 | 0.004 | 1.9786 | 0.0035 | 10949 | 26 | 6837 | 80 | 10.385 | 0.08 | [6 empty] | 460.8 | 2 | 460.7 | 2 | 459.2 | 2 | 3.7 | 0 | 3.2 | 0 | 3.4 | 0 | 1601.8 | 14.3 | 1084.8 | 17.6 | 111.5 | 10.1 | 460 |  | 459 |  | 459 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.55 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1685 | [14 empty] | 96.01 | 0.04 | 59.07 | 0.06 | 56.78 | 0.02 | -2.29 | 0.06 | 97.25 | 0.02 | 59.25 | 0.02 | 57.46 | 0.01 | -1.78 | 0.03 |  |  | 71.96 | 0.01 |  |  |  |  | 96.6 | 0.03 | 71.23 | 0.03 | 57.1 | 0.01 | 14.13 | 0.03 | 96.67 | 0.02 | 64.07 | 0.01 | 57.14 | 0.01 | 6.93 | 0.02 | [46 empty] | 97.64 | 0.06 | 61.56 | 0.08 | 57.67 | 0.02 | 3.87 | 0.08 | 97.98 | 0.05 | 57.86 | 0.03 | -0.43 | 0.22 |  |  | 72.28 | 0.09 |  |  |  |  | 97.11 | 0.04 | 57.38 | 0.02 | 14 | 0.05 | 97.31 | 0.06 | 62.94 | 0.02 | 57.49 | 0.03 | 5.45 | 0.03 | 62.43 | 0.08 | [28 empty] | 61.25 | 0.04 | 61.54 | 0.03 | 62.43 | 0.08 | 62.71 | 0.05 | 72.31 | 0.05 | 71.39 | 0.03 | 71.19 | 0.03 | 72.58 | 0.02 | 72.5 | 0.02 |  |  | 57.99 | 0.03 | 72.41 | 0.03 | 71.93 | 0.03 | 63.73 | 0.02 | 62.18 | 0.07 | 58.43 | 0.15 | 72.83 | 0.08 | 72.44 | 0.02 | 64.68 | 0.03 | 71.96 | 0.01 | 72.28 | 0.09 | 55.34 | 0.04 | 61.01 | 0.04 | 62.36 | 0.01 | 59.29 | 0.06 | 60.54 | 0.08 | 61.54 | 0.03 | 62.71 | 0.05 | [16 empty] | 59.07 | 0.06 | 58.3 | 0.21 | 61.25 | 0.04 | 62.43 | 0.08 | [16 empty] | 71.39 | 0.04 | [12 empty] | 59.39 | 0.03 | 57.16 | 0.16 | 55.94 | 0.06 | 75.35 | 0.02 | 73.12 | 0.04 | 74.8 | 0.02 | 74.1 | 0.05 | 75.69 | 1.09 | 75.67 | 0.02 | 75.3 | 0.02 | 63 | 0.17 | 67.29 | 0.16 | 68.46 | 0.23 | 63.77 | 0.13 | 65.37 | 0.14 | 68.68 | 0.08 | 70.62 | 0.04 | 69.64 | 0.06 | 67.63 | 0.12 | 68.85 | 0.06 | 67.77 | 0.15 | 71.06 | 0.08 | 73.72 | 0.08 | 73.97 | 0.05 | 73.6 | 0.05 | 71.62 | 0.08 | 74.11 | 0.03 | 73.08 | 0.04 | 70.02 | 0.06 |  |  | 73.47 | 0.05 | 75.64 | 0.03 | 75.48 | 0.03 | 74.89 | 0.03 | 73.52 |  | 74.99 | 0.03 | 63.7 | 0.1 |  |  | 62.99 | 0.09 | 65.28 | 0.26 | 73.73 | 0.09 | [62 empty] | Economizer test | 74.965 | 0.011 | 61.991 | 0.011 | 71.748 | 0.008 | 60.157 | 0.012 | 54.99 | 0.007 | 50.999 | 0.012 | 3133.9 | 2.8 | 3014.6 | 2.7 | 0.64 | 0.003 | -0.217 | 0.001 | 0.21 | 0.004 | 1.9786 | 0.0035 | 29.345 | 0 | 1713 | 11 | 1600 |  | 0.090964 | 274.2192 | 13.029 | 0.217 | 1.3981 | 13965.1456 | 226.6599 | 274.2219 | 1262.7972 | 12702.3483 | 0.0086202 | 26.9855 | 70.3499 | 13.0293 | 13.4645 | 0.0069832 | 20.7772 | 0.008783 | 27.6027 | 0.008356 | 26.3515 | 73.1641 | 61.0907 | 26.0107
2 | T2-TRN-100A-55-2E-DM | 75T0015 | T2-TRN-100A-55-2E-DM | 20% open | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 14:49:15 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 0 | 3.7 | 0 | 5691 | 22 | 5213 | 81 | 4376 | 94 | 10071 | 99 | 5.9451 | 944 | 1580 |  | 3.3595 | [35 empty] | Econo 20%-open (3.6V), no compressor, 55/51 ambient, 100% airflow (400 cfm/ton),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-100A-55-2E-DM-SPWCT-SS | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.987 | 0.008 | 61.997 | 0.023 | 55.003 | 0.01 | 51.007 | 0.015 | 75.02 | 0.02 | 73.48 | 0.03 | 73.61 | 0 | 0.199 | 0.004 | 1.9326 | 0.0035 | 5691 | 22 | 4376 | 94 | 5.946 | 0.069 | [6 empty] | 460.7 | 2 | 460.4 | 2 | 459.5 | 2.1 | 3.7 | 0 | 3.2 | 0 | 3.4 | 0 | 1581.4 | 14.4 | 1094.7 | 18.5 | 112.5 | 10.1 | 460 |  | 460 |  | 459 |  | 3.1 |  | 3.1 |  | 3.1 |  | 0.55 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1665 | [14 empty] | 96.36 | 0.02 | 59.31 | 0.04 | 56.97 | 0.01 | -2.34 | 0.04 | 96.68 | 0.01 | 58.57 | 0.02 | 57.15 | 0.01 | -1.43 | 0.02 |  |  | 72.01 | 0.02 |  |  |  |  | 96.28 | 0.02 | 72.2 | 0.02 | 56.92 | 0.01 | 15.28 | 0.02 | 96.07 | 0.02 | 62.66 | 0.02 | 56.81 | 0.01 | 5.85 | 0.02 | [46 empty] | 96.87 | 0.03 | 61.12 | 0.05 | 57.25 | 0.02 | 3.86 | 0.05 | 97.22 | 0.05 | 57.44 | 0.03 | -0.55 | 0.13 |  |  | 73.24 | 0.07 |  |  |  |  | 96.57 | 0.04 | 57.08 | 0.02 | 14.96 | 0.04 | 96.58 | 0.04 | 62.38 | 0.02 | 57.09 | 0.02 | 5.29 | 0.03 | 61.84 | 0.13 | [28 empty] | 60.88 | 0.03 | 61.2 | 0.02 | 61.84 | 0.13 | 62.48 | 0.04 | 73.56 | 0.04 | 73.2 | 0.03 | 73.02 | 0.03 | 73.84 | 0.02 | 73.84 | 0.02 |  |  | 58.77 | 0.02 | 72.53 | 0.03 | 72.59 | 0.02 | 62.55 | 0.02 | 61.79 | 0.04 | 58.07 | 0.1 | 73.78 | 0.07 | 73.01 | 0.01 | 64.11 | 0.03 | 72.01 | 0.02 | 73.24 | 0.07 | 55.38 | 0.02 | 60.7 | 0.02 | 61.99 | 0.02 | 58.81 | 0.11 | 59.82 | 0.12 | 61.2 | 0.02 | 62.48 | 0.04 | [16 empty] | 59.31 | 0.04 | 58 | 0.14 | 60.88 | 0.03 | 61.84 | 0.13 | [16 empty] | 72.04 | 0.04 | [12 empty] | 58.66 | 0.05 | 56.59 | 0.11 | 55.84 | 0.05 | 75.36 | 0.01 | 73.17 | 0.04 | 74.78 | 0.02 | 74.07 | 0.04 | 75.65 | 1.62 | 75.7 | 0.02 | 75.34 | 0.02 | 67.1 | 0.09 | 69.89 | 0.08 | 70.82 | 0.05 | 70.01 | 0.09 | 70.89 | 0.08 | 70.35 | 0.06 | 71.01 | 0.05 | 71.84 | 0.05 | 72.2 | 0.07 | 71.23 | 0.07 | 72.06 | 0.07 | 74.73 | 0.02 | 74.68 | 0.02 | 74.63 | 0.02 | 74.39 | 0.06 | 74.83 | 0.02 | 74.65 | 0.02 | 70.82 | 0.12 | 69.01 | 0.08 |  |  | 73.56 | 0.05 | 75.64 | 0.03 | 75.5 | 0.03 | 74.89 | 0.03 | 73.44 |  | 75.01 | 0.02 | 65.48 | 0.11 |  |  | 70.25 | 0.08 | 72.9 | 0.07 | 74.76 | 0.02 | [62 empty] | Economizer test | 74.987 | 0.008 | 61.997 | 0.023 | 73.301 | 0.003 | 60.969 | 0.016 | 55.003 | 0.01 | 51.007 | 0.015 | 3100.9 | 2.8 | 2974.9 | 2.7 | 0.677 | 0.003 | -0.26 | 0.002 | 0.199 | 0.004 | 1.9326 | 0.0035 | 29.343 | 0.001 | 1694 | 10 | 1580 |  | 0.014812 | 44.0638 | 13.03 | 0.26 | 1.3863 | 13776.5731 | 236.6062 | 44.0631 | 202.9061 | 13573.667 | 0.0087552 | 27.5061 | 71.9147 | 13.0296 | 13.5051 | 0.0069844 | 20.7817 | 0.0087817 | 27.6067 | 0.0085093 | 26.8975 | 74.6936 | 61.8515 | 26.5596
2 | T2-TRN-100A-55-2F-DM | 75T0016 | T2-TRN-100A-55-2F-DM | 2 finger | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 18:30:25 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 3.7 | 0 | 15905 | 32 | 15412 | 94 | 8992 | 139 | 24906 | 155 | 14.4802 | 944 | 1630 |  | 9.2471 | [35 empty] | Econo 2F-open (6V), no compressor, 55/51 ambient, 100% airflow (400 cfm/ton),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-100A-55-2F-DM-SPWCT- | W/ECO: 6 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75 | 0.009 | 62.001 | 0.027 | 55 | 0.012 | 50.999 | 0.012 | 74.93 | 0.08 | 70.42 | 0.08 | 71.16 | 0.01 | 0.195 | 0.004 | 1.9878 | 0.0031 | 15905 | 32 | 8992 | 139 | 14.475 | 0.128 | [6 empty] | 460.6 | 2.1 | 460.1 | 2.1 | 459.1 | 2.1 | 3.7 | 0 | 3.2 | 0 | 3.4 | 0 | 1595.4 | 14.9 | 1091.6 | 19 | 124.8 | 10.6 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1715 | [14 empty] | 97.08 | 0.03 | 59.85 | 0.08 | 57.37 | 0.01 | -2.46 | 0.08 | 98.01 | 0.02 | 60.56 | 0.02 | 57.88 | 0.01 | -2.68 | 0.02 |  |  | 71.16 | 0.02 |  |  |  |  | 97.59 | 0.03 | 69.31 | 0.03 | 57.65 | 0.01 | 11.66 | 0.04 | 97.37 | 0.02 | 65.28 | 0.02 | 57.53 | 0.01 | 7.75 | 0.02 | [46 empty] | 98.47 | 0.03 | 62.34 | 0.12 | 58.13 | 0.02 | 4.21 | 0.12 | 98.62 | 0.05 | 58.22 | 0.02 | -0.14 | 0.34 |  |  | 70.41 | 0.18 |  |  |  |  | 97.78 | 0.05 | 57.76 | 0.02 | 11.81 | 0.11 | 98.05 | 0.03 | 63.69 | 0.03 | 57.91 | 0.02 | 5.78 | 0.02 | 62.28 | 0.16 | [28 empty] | 61.61 | 0.06 | 62 | 0.05 | 62.28 | 0.16 | 62.99 | 0.08 | 71 | 0.08 | 69.91 | 0.05 | 69.7 | 0.03 | 71.24 | 0.03 | 71.14 | 0.03 |  |  | 59.15 | 0.08 | 71.44 | 0.05 | 70.05 | 0.05 | 64.78 | 0.04 | 62.88 | 0.09 | 58.72 | 0.16 | 71 | 0.16 | 70.62 | 0.05 | 65.3 | 0.04 | 71.16 | 0.02 | 70.41 | 0.18 | 55.1 | 0.04 | 62.14 | 0.01 | 62.79 | 0.01 | 59.58 | 0.1 | 60.53 | 0.11 | 62 | 0.05 | 62.99 | 0.08 | [16 empty] | 59.85 | 0.08 | 58.38 | 0.34 | 61.61 | 0.06 | 62.28 | 0.16 | [16 empty] | 69.57 | 0.1 | [12 empty] | 60.82 | 0.03 | 57.66 | 0.19 | 56.03 | 0.05 | 75.38 | 0.03 | 73.17 | 0.05 | 74.86 | 0.03 | 74.09 | 0.05 | 75.83 | 1.65 | 75.68 | 0.04 | 75.3 | 0.04 | 62.66 | 0.16 | 60.47 | 0.16 | 59.71 | 0.07 | 60.63 | 0.08 | 64.63 | 0.18 | 66.04 | 0.29 | 67.3 | 0.24 | 68.62 | 0.07 | 67.36 | 0.31 | 67.59 | 0.17 | 67.42 | 0.35 | 65.7 | 0.23 | 71.05 | 0.16 | 71.7 | 0.13 | 71.24 | 0.13 | 68.76 | 0.11 | 72.52 | 0.06 | 72.85 | 0.09 | 72.21 | 0.13 |  |  | 73.49 | 0.06 | 75.7 | 0.04 | 75.54 | 0.03 | 74.94 | 0.03 | 73.58 |  | 75.04 | 0.02 | 60.09 | 0.32 |  |  | 63.95 | 0.15 | 64.6 | 0.33 | 69.97 | 0.15 | [62 empty] | Economizer test | 75 | 0.009 | 62.001 | 0.027 | 70.337 | 0.004 | 59.398 | 0.016 | 55 | 0.012 | 50.999 | 0.012 | 3136.5 | 2.5 | 3026.8 | 2.4 | 0.614 | 0.004 | -0.178 | 0.001 | 0.195 | 0.004 | 1.9878 | 0.0031 | 29.365 | 0.001 | 1720 | 11 | 1630 |  | 0.16165 | 489.2822 | 13.029 | 0.178 | 1.432 | 14015.152 | 218.3319 | 489.2916 | 2253.1562 | 11761.9958 | 0.0084918 | 26.511 | 68.905 | 13.0295 | 13.4276 | 0.0069808 | 20.7771 | 0.0087813 | 27.6094 | 0.0082107 | 25.8489 | 71.7935 | 60.3873 | 25.5
2 | T2-TRN-100A-55-3E-DM | 75T0017 | T2-TRN-100A-55-3E-DM | 30% open | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 12:31:04 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.6 | 0 | 3.6 | 0 | 8294 | 25 | 7767 | 52 | 5606 | 97 | 13905 | 99 | 8.1506 | 944 | 1580 |  | 4.8617 | [35 empty] | Econo 30%-open (4.4V), no compressor, 55/51 ambient, 100% airflow (400 cfm/ton),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet Meriam, adjust--code tester speed to match total static of run T2-TRN-100A-55-3E-DM-SPWCT-SS | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.991 | 0.005 | 62.003 | 0.031 | 55.001 | 0.012 | 51.001 | 0.014 | 75.12 | 0.02 | 72.83 | 0.02 | 73 | 0 | 0.202 | 0.004 | 1.9585 | 0.0029 | 8294 | 25 | 5606 | 97 | 8.153 | 0.077 | [6 empty] | 459.6 | 2 | 460.2 | 2 | 460.3 | 2 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1564 | 14.2 | 1116.3 | 18.2 | 141.6 | 9.7 | 460 |  | 459 |  | 459 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.55 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1665 | [14 empty] | 96.4 | 0.05 | 59.45 | 0.03 | 56.99 | 0.03 | -2.46 | 0.04 | 97.02 | 0.02 | 60.13 | 0.01 | 57.35 | 0.01 | -2.78 | 0.01 |  |  | 72.28 | 0.02 |  |  |  |  | 96.56 | 0.04 | 71.84 | 0.01 | 57.09 | 0.02 | 14.75 | 0.03 | 96.37 | 0.01 | 63.49 | 0.01 | 56.98 | 0.01 | 6.51 | 0.02 | [46 empty] | 97.31 | 0.03 | 61.38 | 0.07 | 57.5 | 0.02 | 3.89 | 0.08 | 97.55 | 0.04 | 57.64 | 0.02 | -0.32 | 0.28 |  |  | 72.84 | 0.14 |  |  |  |  | 97.05 | 0.04 | 57.36 | 0.02 | 14.55 | 0.03 | 96.88 | 0.02 | 62.53 | 0.01 | 57.26 | 0.01 | 5.27 | 0.02 | 62.17 | 0.09 | [28 empty] | 61.22 | 0.02 | 61.45 | 0.01 | 62.17 | 0.09 | 62.68 | 0.02 | 73.18 | 0.02 | 72.35 | 0.02 | 72.08 | 0.02 | 73.4 | 0.01 | 73.34 | 0.02 |  |  | 58.81 | 0.05 | 72.63 | 0.02 | 72.46 | 0.01 | 63.26 | 0.01 | 62.06 | 0.06 | 58.16 | 0.18 | 73.36 | 0.13 | 73.05 | 0.01 | 64.41 | 0.03 | 72.28 | 0.02 | 72.84 | 0.14 | 55.53 | 0.03 | 61.27 | 0.02 | 62.26 | 0.01 | 59.1 | 0.05 | 60.14 | 0.08 | 61.45 | 0.01 | 62.68 | 0.02 | [16 empty] | 59.45 | 0.03 | 57.99 | 0.26 | 61.22 | 0.02 | 62.17 | 0.09 | [16 empty] | 71.92 | 0.01 | [12 empty] | 60.32 | 0.02 | 56.96 | 0.15 | 55.98 | 0.05 | 75.48 | 0.02 | 73.23 | 0.03 | 74.9 | 0.02 | 74.28 | 0.04 | 75.8 | 0.51 | 75.87 | 0.02 | 75.51 | 0.02 | 65.67 | 0.12 | 66.76 | 0.32 | 70.43 | 0.1 | 69.01 | 0.1 | 65.88 | 0.11 | 68.12 | 0.1 | 70.38 | 0.06 | 70.44 | 0.05 | 68.18 | 0.12 | 69.16 | 0.09 | 68.1 | 0.12 | 74.73 | 0.02 | 74.56 | 0.03 | 74.55 | 0.03 | 74.47 | 0.03 | 74.99 | 0.02 | 74.77 | 0.02 | 72.21 | 0.12 | 69.61 | 0.08 |  |  | 73.53 | 0.05 | 75.84 | 0.02 | 75.68 | 0.02 | 75.08 | 0.02 | 73.69 |  | 75.1 | 0.01 | 64.47 | 0.07 |  |  | 65.22 | 0.11 | 66.96 | 0.16 | 74.72 | 0.02 | [62 empty] | Economizer test | 74.991 | 0.005 | 62.003 | 0.031 | 72.545 | 0.009 | 60.575 | 0.029 | 55.001 | 0.012 | 51.001 | 0.014 | 3118.2 | 2.3 | 2998.6 | 2.2 | 0.661 | 0.003 | -0.24 | 0.001 | 0.202 | 0.004 | 1.9585 | 0.0029 | 29.375 | 0.001 | 1706 | 10 | 1580 |  | 0.053327 | 159.9053 | 13.03 | 0.24 | 1.3804 | 13873.7287 | 232.8547 | 159.9024 | 736.3387 | 13137.39 | 0.008689 | 27.2483 | 71.1646 | 13.0295 | 13.4853 | 0.0069816 | 20.7783 | 0.0087847 | 27.6109 | 0.0084344 | 26.6314 | 73.9333 | 61.4761 | 26.2949
2 | T2-TRN-100A-55-3F-DM | 75T0018 | T2-TRN-100A-55-3F-DM | 3 finger | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 19:33:47 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.8 | 0 | 3.6 | 0 | 21739 | 34 | 21347 | 130 | 11748 | 227 | 33498 | 237 | 19.3742 | 944 | 1630 |  | 12.5732 | [35 empty] | Econo 3F-open (6.9V), no compressor, 55/51 ambient, 100% airflow (400 cfm/ton),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-100A-55-3F-DM-SPWC | W/ECO: 6.9 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.967 | 0.013 | 61.99 | 0.034 | 54.998 | 0.012 | 50.936 | 0.016 | 74.89 | 0.05 | 68.65 | 0.05 | 69.8 | 0.01 | 0.18 | 0.004 | 1.9971 | 0.004 | 21739 | 34 | 11748 | 227 | 19.376 | 0.186 | [6 empty] | 459.8 | 2.1 | 460 | 2.1 | 460.2 | 2.1 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1575.4 | 14.7 | 1117.8 | 18.9 | 153.5 | 10.2 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.56 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1715 | [14 empty] | 97.54 | 0.04 | 60.79 | 0.05 | 57.64 | 0.02 | -3.15 | 0.06 | 98.25 | 0.05 | 60.91 | 0.01 | 58.03 | 0.02 | -2.87 | 0.03 |  |  | 69.23 | 0.03 |  |  |  |  | 97.92 | 0.05 | 66.85 | 0.03 | 57.86 | 0.03 | 9 | 0.05 | 97.78 | 0.06 | 65.94 | 0.02 | 57.77 | 0.03 | 8.17 | 0.04 | [46 empty] | 98.56 | 0.09 | 57.67 | 0.05 | 58.21 | 0.05 | -0.52 | 0.03 | 98.67 | 0.08 | 58.26 | 0.05 | -2.63 | 0.1 |  |  | 66.78 | 0.76 |  |  |  |  | 97.94 | 0.08 | 57.86 | 0.05 | 8.2 | 0.16 | 98.04 | 0.09 | 64.12 | 0.02 | 57.91 | 0.05 | 6.2 | 0.06 | 63.27 | 0.04 | [28 empty] | 61.75 | 0.04 | 62.08 | 0.03 | 63.27 | 0.04 | 62.37 | 0.68 | 69.4 | 0.05 | 68.09 | 0.04 | 67.87 | 0.04 | 69.59 | 0.03 | 69.43 | 0.03 |  |  | 60.65 | 0.02 | 69.28 | 0.05 | 67.9 | 0.05 | 65.32 | 0.03 | 58.48 | 0.04 | 60.86 | 0.13 | 67.39 | 0.68 | 67.31 | 0.07 | 65.89 | 0.02 | 69.23 | 0.03 | 66.78 | 0.76 | 54.89 | 0.07 | 63.03 | 0.01 | 62.9 | 0.02 | 62.45 | 0.13 | 64.1 | 0.13 | 62.08 | 0.03 | 62.37 | 0.68 | [16 empty] | 60.79 | 0.05 | 60.88 | 0.09 | 61.75 | 0.04 | 63.27 | 0.04 | [16 empty] | 66.06 | 0.13 | [12 empty] | 61.17 | 0.02 | 58.12 | 0.24 | 56.13 | 0.07 | 75.3 | 0.02 | 73.49 | 0.04 | 74.84 | 0.02 | 74.3 | 0.04 | 75.75 | 0.68 | 75.65 | 0.02 | 75.26 | 0.03 | 61.35 | 0.11 | 60.7 | 0.08 | 59.04 | 0.12 | 59.79 | 0.09 | 62.32 | 0.12 | 62.55 | 0.13 | 58.84 | 0.18 | 64.28 | 0.18 | 65.17 | 0.11 | 64.11 | 0.13 | 65.47 | 0.09 | 63.53 | 0.14 | 67.78 | 0.08 | 67.67 | 0.07 | 66.92 | 0.1 | 67.37 | 0.23 | 70.73 | 0.2 | 70.99 | 0.15 | 70.53 | 0.11 |  |  | 73.76 | 0.04 | 75.66 | 0.02 | 75.5 | 0.02 | 74.96 | 0.03 | 73.74 |  | 75.02 | 0.02 | 57.08 | 0.1 |  |  | 61.86 | 0.15 | 63.03 | 0.11 | 66.86 | 0.07 | [62 empty] | Economizer test | 74.967 | 0.013 | 61.99 | 0.034 | 68.617 | 0.012 | 58.462 | 0.021 | 54.998 | 0.012 | 50.936 | 0.016 | 3138.3 | 3.1 | 3040 | 3 | 0.584 | 0.003 | -0.135 | 0.003 | 0.18 | 0.004 | 1.9971 | 0.004 | 29.393 | 0.001 | 1729 | 11 | 1630 |  | 0.24588 | 747.4786 | 13.029 | 0.135 | 1.4362 | 14070.3096 | 208.5699 | 747.4841 | 3442.1972 | 10628.1124 | 0.0083332 | 25.9234 | 67.1808 | 13.0292 | 13.3826 | 0.0069478 | 20.7408 | 0.0087818 | 27.6019 | 0.0080366 | 25.2398 | 70.0941 | 59.502 | 24.89
2 | T2-TRN-100A-55-CE-DM-2 | 75T0019 | T2-TRN-100A-55-CE-DM-2 | closed | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 3:35:30 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 3.6 | 0 | 3290 | 20 | 2859 | 86 | 3438 | 84 | 6730 | 90 | 4.0036 | 945 | 1590 |  | 1.9572 | [35 empty] | Econo closed, no compressor, 55/51 ambient, 100% airflow (400 cfm/ton), 2 HP fan motor,--3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-100A-55-CE-DM-2-SPWCT-SS | W/ECO: 2 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.98 | 0.018 | 61.991 | 0.024 | 54.985 | 0.01 | 50.993 | 0.014 | 75.06 | 0.03 | 74.22 | 0.03 | 74.2 | 0.01 | 0.195 | 0.004 | 1.8973 | 0.0031 | 3290 | 20 | 3438 | 84 | 4.004 | 0.058 | [6 empty] | 460.2 | 2 | 461.2 | 2 | 459.9 | 2 | 3.6 | 0 | 3.1 | 0 | 3.4 | 0 | 1576.6 | 14.8 | 1096.1 | 17.9 | 104.7 | 9.8 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.55 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1675 | [14 empty] | 96.29 | 0.02 | 58.58 | 0.02 | 56.89 | 0.01 | -1.68 | 0.03 | 95.88 | 0.03 | 58.27 | 0.01 | 56.67 | 0.02 | -1.61 | 0.02 |  |  | 71.69 | 0.04 |  |  |  |  | 96.06 | 0.01 | 72.28 | 0.02 | 56.76 | 0.01 | 15.52 | 0.02 | 95.63 | 0.02 | 61.28 | 0.01 | 56.53 | 0.01 | 4.76 | 0.02 | [46 empty] | 96.58 | 0.02 | 60.68 | 0.07 | 57.06 | 0.01 | 3.62 | 0.07 | 97.26 | 0.03 | 57.43 | 0.02 | -2.35 | 0.24 |  |  | 73.4 | 0.08 |  |  |  |  | 96.33 | 0.03 | 56.92 | 0.01 | 15.11 | 0.03 | 96.25 | 0.01 | 60.66 | 0.03 | 56.87 | 0.01 | 3.79 | 0.03 | 61.25 | 0.06 | [28 empty] | 60.35 | 0.01 | 60.65 | 0.02 | 61.25 | 0.06 | 61.01 | 0.05 | 74.23 | 0.02 | 73.97 | 0.02 | 73.81 | 0.02 | 74.51 | 0.02 | 74.53 | 0.02 |  |  | 57.87 | 0.02 | 72.18 | 0.04 | 72.64 | 0.03 | 61.27 | 0.02 | 61.37 | 0.06 | 59.84 | 0.16 | 73.99 | 0.07 | 73.15 | 0.03 | 62.92 | 0.05 | 71.69 | 0.04 | 73.4 | 0.08 | 55.51 | 0.06 | 59.76 | 0.03 | 61.43 | 0.02 | 61.52 | 0.04 | 63.02 | 0.03 | 60.65 | 0.02 | 61.01 | 0.05 | [16 empty] | 58.58 | 0.02 | 59.82 | 0.19 | 60.35 | 0.01 | 61.25 | 0.06 | [16 empty] | 72.02 | 0.02 | [12 empty] | 58.36 | 0.02 | 56.43 | 0.11 | 55.83 | 0.06 | 75.45 | 0.02 | 73.16 | 0.03 | 74.85 | 0.03 | 74.18 | 0.04 | 75.71 | 0.91 | 75.82 | 0.03 | 75.46 | 0.03 | 68.88 | 0.1 | 71.9 | 0.05 | 71.65 | 0.04 | 70.66 | 0.11 | 71.91 | 0.08 | 72.25 | 0.05 | 72.76 | 0.03 | 73.32 | 0.04 | 73.95 | 0.04 | 73.34 | 0.04 | 73.77 | 0.04 | 74.81 | 0.04 | 74.84 | 0.04 | 74.76 | 0.02 | 74.53 | 0.06 | 74.96 | 0.05 | 74.76 | 0.03 | 68.37 | 0.13 | 68.66 | 0.05 |  |  | 73.52 | 0.05 | 75.82 | 0.02 | 75.66 | 0.03 | 75.04 | 0.03 | 73.51 |  | 75.11 | 0.03 | 68.46 | 0.09 |  |  | 70.87 | 0.09 | 73.98 | 0.04 | 74.87 | 0.04 | [62 empty] | Economizer test | 74.98 | 0.018 | 61.991 | 0.024 | 74.002 | 0.016 | 61.311 | 0.018 | 54.985 | 0.01 | 50.993 | 0.014 | 3080.5 | 2.6 | 2939.2 | 2.4 | 0.68 | 0.002 | -0.279 | 0.002 | 0.195 | 0.004 | 1.8973 | 0.0031 | 29.22 | 0.001 | 1681 | 10 | 1590 |  | 0 | 0 | 13.029 | 0.279 | 1.4096 | 13667.5086 | 234.8027 | 0 | 0 | 13667.5086 | 0.0087794 | 27.6024 | 72.5924 | 13.0291 | 13.5233 | 0.0069811 | 20.7738 | 0.0087794 | 27.6024 | 0.0085653 | 27.1297 | 74.98 | 61.991 | 26.786
2 | T2-TRN-100A-55-OE-DM | 75T0020 | T2-TRN-100A-55-OE-DM | open | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 4:33:32 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.1 | 0 | 3.7 | 0 | 42708 | 116 | 42141 | 389 | 22562 | 216 | 65291 | 218 | 37.7405 | 945 |  |  | 24.6867 | [35 empty] | Econo fully open, no compressor, 55/51 ambient, 2 HP fan motor, 100% airflow (400 cfm/ton),--3 turns, 5.75" pulley, (950 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-100A-55-OE-DM-SPWCT-SSR | W/ECO: 2 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.969 | 0.012 | 62.015 | 0.036 | 55.006 | 0.017 | 50.962 | 0.02 | 74.93 | 0.12 | 62.54 | 0.06 | 64.74 | 0.03 | 0.18 | 0.005 | 1.9576 | 0.0033 | 42708 | 116 | 22562 | 216 | 37.744 | 0.272 | [6 empty] | 460.1 | 2 | 461 | 2 | 459.9 | 2 | 3.7 | 0 | 3.2 | 0 | 3.5 | 0 | 1599.8 | 14.4 | 1098.8 | 17.7 | 130.2 | 10.3 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.3 |  | 3.1 |  | 0.56 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1725 | [14 empty] | 97.06 | 0.07 | 59.8 | 0.06 | 57.32 | 0.04 | -2.47 | 0.07 | 97.56 | 0.1 | 59.36 | 0.06 | 57.6 | 0.06 | -1.76 | 0.04 |  |  | 62.61 | 0.04 |  |  |  |  | 97.42 | 0.09 | 59.96 | 0.04 | 57.53 | 0.05 | 2.43 | 0.07 | 97.36 | 0.09 | 66.15 | 0.03 | 57.49 | 0.05 | 8.66 | 0.05 | [46 empty] | 98.15 | 0.09 | 56.99 | 0.06 | 57.92 | 0.04 | -0.94 | 0.03 | 97.17 | 0.1 | 57.38 | 0.05 | -4.54 | 0.07 |  |  | 60.21 | 0.03 |  |  |  |  | 94.64 | 0.23 | 55.97 | 0.13 | 3.34 | 0.17 | 94.94 | 0.23 | 62.63 | 0.04 | 56.14 | 0.13 | 6.49 | 0.1 | 60.73 | 0.12 | [28 empty] | 60.9 | 0.05 | 61.45 | 0.05 | 60.73 | 0.12 | 61.01 | 0.08 | 62.89 | 0.07 | 62.34 | 0.06 | 62 | 0.07 | 62.79 | 0.06 | 62.55 | 0.06 |  |  | 58.29 | 0.05 | 62.28 | 0.06 | 60.63 | 0.05 | 65.59 | 0.04 | 57.58 | 0.05 | 61.98 | 0.1 | 60.79 | 0.02 | 60.55 | 0.05 | 63.22 | 0.05 | 62.61 | 0.04 | 60.21 | 0.03 | 55.26 | 0.2 | 61.25 | 0.09 | 62.35 | 0.03 | 60.86 | 0.16 | 60.97 | 0.23 | 61.45 | 0.05 | 61.01 | 0.08 | [16 empty] | 59.8 | 0.06 | 61.93 | 0.09 | 60.9 | 0.05 | 60.73 | 0.12 | [16 empty] | 59.31 | 0.07 | [12 empty] | 59.37 | 0.06 | 58.98 | 0.36 | 56.91 | 0.11 | 75.27 | 0.05 | 74.77 | 0.05 | 74.87 | 0.06 | 75.65 | 0.06 | 75.67 | 0.06 | 75.66 | 0.06 | 75.44 | 0.07 | 54.54 | 0.1 | 58.07 | 0.12 | 59.05 | 0.18 | 54.5 | 0.12 | 59.03 | 0.24 | 62.29 | 0.15 | 58.87 | 0.21 | 60.55 | 0.23 | 61.81 | 0.13 | 62.42 | 0.13 | 60.63 | 0.2 | 59.21 | 0.17 | 62.72 | 0.13 | 61.36 | 0.12 | 59.89 | 0.13 | 63.69 | 0.19 | 65.04 | 0.21 | 64.47 | 0.14 | 65.33 | 0.16 |  |  | 75.04 | 0.07 | 75.68 | 0.05 | 75.53 | 0.06 | 75.33 | 0.06 | 74.93 |  | 75 | 0.06 | 54.57 | 0.12 |  |  | 57.37 | 0.15 | 58.26 | 0.16 | 62.4 | 0.15 | [62 empty] | Economizer test | 74.969 | 0.012 | 62.015 | 0.036 | 62.411 | 0.037 | 54.856 | 0.039 | 55.006 | 0.017 | 50.962 | 0.02 | 3100.3 | 2.6 | 3018.6 | 2.5 | 0.513 | 0.003 | -0.15 | 0.005 | 0.18 | 0.005 | 1.9576 | 0.0033 | 29.229 | 0.001 | 1730 | 11 | 1640 |  | 0.55543 | 1676.6136 | 13.029 | 0.15 | 1.4732 | 14070.8128 | 181.9232 | 1676.6448 | 7720.8488 | 6349.964 | 0.0077893 | 23.8534 | 60.9378 | 13.0295 | 13.2201 | 0.0069597 | 20.7557 | 0.0087978 | 27.6199 | 0.0073632 | 22.9951 | 64.0316 | 56.2499 | 22.6367
2 | T2-TRN-95-1ER-DM | 75T0021 | T2-TRN-95-1ER-DM | 10% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 14:20:40 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 1.4 | 15.3 | 0 | 57838 | 56 | 59392 | 503 | 7242 | 142 | 65088 | 164 | 7.5613 | 949 | 1670 |  | 6.7191 | [35 empty] | Econo 10%-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-TRN-95-1E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.998 | 0.015 | 62.003 | 0.027 | 94.979 | 0.048 | 74.996 | 0.027 | 75.02 | 0.15 | 56.89 | 0.07 | 59.93 | 0.02 | 0.206 | 0.004 | 1.2412 | 0.0024 | 57838 | 56 | 7242 | 142 | 7.562 | 0.026 | [6 empty] | 460.9 | 2.6 | 460.6 | 2.6 | 459.1 | 2.6 | 15.3 | 0.1 | 13.3 | 0 | 12.8 | 0.1 | 6963.1 | 58.3 | 3204.8 | 67.5 | 1644.8 | 48 | 460 |  | 460 |  | 460 |  | 3.3 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.5 |  | 3150 |  | 0.85 | 460 | 460 | 460 | 5 | 4.6 | 4.4 | 3002 | 0.81 | 459.9 |  | 1.6 |  | 706.1 |  | 85 |  | 8613.1 | [14 empty] | 217.06 | 0.39 | 106.72 | 0.16 | 106.97 | 0.13 | 0.25 | 0.11 | 245.7 | 0.42 | 173.71 | 0.12 | 115.8 | 0.12 | -57.9 | 0.1 | 210 | 0.12 | 99.32 | 0.13 | 104.73 | 0.15 | 5.41 | 0.16 | 75.92 | 0.06 | 50.36 | 0.44 | 44.74 | 0.04 | 5.62 | 0.45 | 75.24 | 0.03 | 57.08 | 0.16 | 44.31 | 0.02 | 12.77 | 0.15 | [46 empty] | 247.97 | 0.43 | 170.13 | 0.36 | 116.47 | 0.13 | 53.66 | 0.37 | 230.49 | 0.56 | 111.21 | 0.17 | 10.83 | 0.16 | 219.7 | 0.15 | 99.92 | 0.16 | 107.81 | 0.19 | 7.89 | 0.17 | 78.49 | 0.18 | 46.39 | 0.11 | 3.39 | 0.81 | 77.78 | 0.2 | 57.47 | 0.75 | 45.94 | 0.13 | 11.54 | 0.8 | 105.29 | 0.15 | [28 empty] | 105.7 | 0.15 | 105.29 | 0.15 | 101.1 | 0.16 | 101.39 | 0.16 | 57.31 | 0.07 | 57.04 | 0.06 | 56.68 | 0.06 | 57.44 | 0.03 | 57.2 | 0.04 | 57.3 | 0.05 | 105.97 | 0.11 | 100.69 | 0.13 | 51.19 | 0.65 | 57.05 | 0.22 | 169.05 | 0.4 | 101.52 | 0.16 | 100.32 | 0.16 | 49.4 | 0.16 | 59.24 | 1.13 | 99.32 | 0.13 | 99.92 | 0.16 | 92.32 | 0.08 | 106.49 | 0.14 | 106.32 | 0.12 | 101.51 | 0.14 | 101.53 | 0.18 | 101.1 | 0.16 | 101.39 | 0.16 | [12 empty] | 106.72 | 0.16 | 57.3 | 0.05 |  |  | 100.39 | 0.19 | 105.7 | 0.15 | 105.29 | 0.15 | [16 empty] | 49.75 | 0.71 | [12 empty] | 174.07 | 0.13 | 95.08 | 0.17 | 94.87 | 0.24 | 75.73 | 0.07 | 75.52 | 0.08 | 75.34 | 0.07 | 75.98 | 0.05 | 75.98 | 0.07 | 75.89 | 0.08 | 75.68 | 0.08 | 81.36 | 0.13 | 81.27 | 0.1 | 78.62 | 0.15 | 75.72 | 0.11 | 77.32 | 0.1 | 78.04 | 0.07 | 77.29 | 0.06 | 77.09 | 0.08 | 75.73 | 0.07 | 76.4 | 0.09 | 75.32 | 0.1 | 75.53 | 0.08 | 75.31 | 0.09 | 75.9 | 0.08 | 75.56 | 0.09 | 75.67 | 0.08 | 75.54 | 0.08 | 75.45 | 0.08 | 75.68 | 0.08 |  |  | 75.3 | 0.07 | 75.97 | 0.05 | 75.73 | 0.07 | 75.52 | 0.08 | 75.44 |  | 75.38 | 0.09 |  |  | 82.88 | 0.16 | 76.57 | 0.1 | 75.7 | 0.09 | 75.5 | 0.08 | [62 empty] | T2-TRN-100A-55-1E-DM | 74.998 | 0.015 | 62.003 | 0.027 | 57.339 | 0.012 | 54.604 | 0.022 | 94.979 | 0.048 | 74.996 | 0.027 | 2975.2 | 2.9 | 2936.3 | 2.9 | 0.648 | 0.003 | -0.273 | 0.002 | 0.206 | 0.004 | 1.2412 | 0.0024 | 29.4 | 0.001 | 8608 | 24 | 1670 |  | 0 | 0 | 13.03 | 0.282 | 1.5091 | 13626.9733 | 223.5324 | 0 | 0 | 13626.9733 | 0.0087831 | 27.6108 | 55.8299 | 14.0994 | 13.0999 | 0.013922 | 38.1536 | 0.0087831 | 27.6108 | 0.0084151 | 22.904 | 74.998 | 62.003 | 22.5362 | 69152.206 | 62688.6405 | 6938 | 0.34242 | 64215.4122 | 57751.8467 | 7.46 | 0.15711 | -5.0747 | -19.1681 | 52.257 | 69152.206 | 64140.0257 | 5012.1803 | 0 | 69152.206 | 100%
2 | T2-TRN-95-1FER-DM | 75T0022 | T2-TRN-95-1FER-DM | 1 finger | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 23:34:37 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1 | 15.5 | 0 | 52300 | 75 | 52369 | 543 | 0 | 0 | 52299 | 75 | 6.0594 | 950 | 1640 |  | 6.0596 | [35 empty] | Econo 1F-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-TRN-95-1FE-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;1F Open: Jade Control set to 5.1V | 74.903 | 0.015 | 61.981 | 0.02 | 94.995 | 0.023 | 74.994 | 0.023 | 75.08 | 0.16 | 59.18 | 0.03 | 61.5 | 0.03 | 0.182 | 0.004 | 1.2707 | 0.0029 | 52300 | 75 | 0 | 0 | 6.059 | 0.018 | [6 empty] | 461.1 | 2.4 | 461.3 | 2.4 | 458.9 | 2.4 | 15.5 | 0.1 | 13.2 | 0 | 12.8 | 0.1 | 7031.5 | 61.4 | 3156.2 | 66.4 | 1599.4 | 51.9 | 460 |  | 460 |  | 460 |  | 3.3 |  | 3.2 |  | 3.1 |  | 0.58 | 460 |  | 460 |  | 460 |  | 4.7 |  | 4.8 |  | 4.4 |  | 3150 |  | 0.86 | 460 | 460 | 460 | 5.1 | 4.6 | 4.4 | 3030 | 0.81 | 460.1 |  | 1.6 |  | 706.7 |  | 85 |  | 8611.7 | [14 empty] | 216.93 | 0.3 | 106.76 | 0.14 | 106.93 | 0.09 | 0.17 | 0.1 | 245.67 | 0.33 | 173.69 | 0.1 | 115.79 | 0.1 | 57.9 | 0.1 | 211.07 | 0.05 | 99.81 | 0.09 | 105.01 | 0.05 | 5.16 | 0.05 | 76.05 | 0.06 | 50.45 | 0.39 | 44.83 | 0.04 | 5.62 | 0.41 | 75.48 | 0.03 | 57.38 | 0.15 | 44.46 | 0.02 | 12.91 | 0.15 | [46 empty] | 249.38 | 0.33 | 169.09 | 0.12 | 116.88 | 0.1 | 52.2 | 0.11 | 230.22 | 0.46 | 111.12 | 0.14 | 10.21 | 0.1 | 219.03 | 0.05 | 100.19 | 0.13 | 107.6 | 0.05 | 7.41 | 0.05 | 82.58 | 0.04 | 48.94 | 0.02 | 2.84 | 0.32 | 81.66 | 0.07 | 60.12 | 0.2 | 48.37 | 0.04 | 11.75 | 0.21 | 105.42 | 0.13 | [28 empty] | 105.83 | 0.12 | 105.42 | 0.13 | 101.32 | 0.14 | 101.56 | 0.12 | 59.18 | 0.05 | 58.86 | 0.05 | 58.47 | 0.05 | 59.4 | 0.03 | 59.13 | 0.03 | 59.16 | 0.03 | 106.03 | 0.09 | 100.95 | 0.11 | 51.61 | 0.63 | 57.44 | 0.22 | 168.29 | 0.14 | 101.64 | 0.13 | 100.62 | 0.13 | 51.85 | 0.11 | 62.11 | 0.31 | 99.81 | 0.09 | 100.19 | 0.13 | 93.01 | 0.07 | 106.67 | 0.12 | 106.41 | 0.1 | 101.89 | 0.08 | 101.79 | 0.1 | 101.32 | 0.14 | 101.56 | 0.12 | [12 empty] | 106.76 | 0.14 | 59.16 | 0.03 |  |  | 100.91 | 0.13 | 105.83 | 0.12 | 105.42 | 0.13 | [16 empty] | 51.78 | 0.31 | [12 empty] | 174.23 | 0.11 | 94.96 | 0.15 | 94.86 | 0.23 | 75.79 | 0.08 | 75.57 | 0.09 | 75.35 | 0.07 | 76.13 | 0.05 | 76.11 | 0.08 | 76 | 0.08 | 75.78 | 0.09 | 84.33 | 0.21 | 86.91 | 0.28 | 85.47 | 0.36 | 76.4 | 0.12 | 85.05 | 0.25 | 82.19 | 0.23 | 80.48 | 0.16 | 79.53 | 0.08 | 81.41 | 0.21 | 79.93 | 0.11 | 76.8 | 0.16 | 75.45 | 0.09 | 76.5 | 0.12 | 78.66 | 0.09 | 78.03 | 0.11 | 75.51 | 0.09 | 75.71 | 0.09 | 76.75 | 0.11 | 77.16 | 0.09 |  |  | 75.37 | 0.08 | 76.04 | 0.07 | 75.78 | 0.09 | 75.56 | 0.1 | 75.46 |  | 75.37 | 0.1 |  |  | 83.9 | 0.16 | 83.33 | 0.14 | 75.72 | 0.11 | 75.41 | 0.1 | [62 empty] | T2-TRN-100A-55-1F-DM | 74.903 | 0.015 | 61.981 | 0.02 | 59.024 | 0.008 | 56.28 | 0.016 | 94.995 | 0.023 | 74.994 | 0.023 | 3016.1 | 3.5 | 2964.1 | 3.4 | 0.59 | 0.003 | -0.189 | 0.002 | 0.182 | 0.004 | 1.2707 | 0.0029 | 29.394 | 0 | 8631 | 24 | 1640 |  | 0.090964 | 274.2192 | 13.029 | 0.217 | 1.4816 | 13764.7268 | 205.4518 | 266.2251 | 1132.8928 | 12631.834 | 0.0092129 | 28.4651 | 57.5424 | 14.0998 | 13.1471 | 0.013917 | 38.1514 | 0.008791 | 27.5964 | 0.0089896 | 23.9393 | 76.5708 | 63.2033 | 23.5778 | 67272.3328 | 62861.1438 | 6991 | 0.35468 | 62376.2198 | 57965.0308 | 7.227 | 0.15271 | -4.8873 | -19.0285 | 54.1128 | 67272.3328 | 50338.4991 | 4976.0804 | 11957.7532 | 67272.3328 | 100%
2 | T2-TRN-95-2ER-DM | 75T0023 | T2-TRN-95-2ER-DM | 20% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 16:10:32 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 1.2 | 15.3 | 0 | 56639 | 72 | 58568 | 586 | 4996 | 115 | 61640 | 148 | 7.1566 | 949 | [38 empty] | Econo 20%-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static--of run T2-TRN-95-2E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.014 | 0.014 | 61.992 | 0.022 | 94.992 | 0.073 | 75.016 | 0.019 | 75.23 | 0.17 | 57.37 | 0.08 | 60.33 | 0.02 | 0.219 | 0.004 | 1.2495 | 0.0027 | 56639 | 72 | 4996 | 115 | 7.157 | 0.025 | [6 empty] | 461 | 2.5 | 460.4 | 2.4 | 458.9 | 2.4 | 15.3 | 0.1 | 13.3 | 0 | 12.8 | 0.1 | 6966.5 | 56.3 | 3201.6 | 64.4 | 1646.5 | 46.7 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.5 |  | 3160 |  | 0.85 | 460 | 460 | 460 | 5 | 4.6 | 4.5 | 3012 | 0.81 | 460.1 |  | 1.6 |  | 706.1 |  | 85 |  | 8613.1 | [14 empty] | 217 | 0.4 | 106.8 | 0.16 | 106.95 | 0.13 | 0.15 | 0.1 | 245.76 | 0.42 | 173.6 | 0.17 | 115.82 | 0.12 | -57.78 | 0.13 | 210 | 0.15 | 99.4 | 0.12 | 104.66 | 0.06 | 5.26 | 0.16 | 75.99 | 0.06 | 50.45 | 0.44 | 44.78 | 0.04 | 5.67 | 0.46 | 75.3 | 0.03 | 57.14 | 0.16 | 44.34 | 0.02 | 12.81 | 0.16 | [46 empty] | 248.42 | 0.42 | 169.95 | 0.21 | 116.6 | 0.12 | 53.35 | 0.2 | 230.58 | 0.56 | 111.23 | 0.17 | 10.56 | 0.13 | 219 | 0.37 | 99.94 | 0.15 | 104.66 | 0.15 | 4.72 | 0.11 | 79.47 | 0.1 | 47.01 | 0.06 | 3.1 | 0.43 | 78.72 | 0.11 | 58.16 | 0.37 | 46.53 | 0.07 | 11.63 | 0.4 | 105.39 | 0.15 | [28 empty] | 105.8 | 0.15 | 105.39 | 0.15 | 101.18 | 0.16 | 101.45 | 0.14 | 57.84 | 0.05 | 57.52 | 0.05 | 57.15 | 0.06 | 58.05 | 0.04 | 57.77 | 0.04 | 57.83 | 0.05 | 106.01 | 0.12 | 100.83 | 0.14 | 51.49 | 0.67 | 57.27 | 0.23 | 169.02 | 0.23 | 101.51 | 0.15 | 100.29 | 0.16 | 49.95 | 0.11 | 60.03 | 0.55 | 99.4 | 0.12 | 99.94 | 0.15 | 92.5 | 0.09 | 106.47 | 0.15 | 106.29 | 0.13 | 101.51 | 0.13 | 101.6 | 0.11 | 101.18 | 0.16 | 101.45 | 0.14 | [12 empty] | 106.8 | 0.16 | 57.83 | 0.05 |  |  | 100.67 | 0.16 | 105.8 | 0.15 | 105.39 | 0.15 | [16 empty] | 50.09 | 0.38 | [12 empty] | 174.09 | 0.16 | 95.12 | 0.19 | 94.93 | 0.26 | 75.86 | 0.08 | 75.64 | 0.09 | 75.42 | 0.08 | 76.13 | 0.06 | 76.13 | 0.08 | 76.04 | 0.09 | 75.83 | 0.09 | 82.08 | 0.16 | 83.49 | 0.21 | 81.49 | 0.17 | 75.78 | 0.12 | 78.41 | 0.11 | 79.5 | 0.09 | 78.09 | 0.08 | 78.05 | 0.07 | 76.18 | 0.09 | 77.78 | 0.09 | 75.43 | 0.11 | 75.54 | 0.09 | 75.32 | 0.1 | 76.4 | 0.09 | 75.85 | 0.1 | 75.63 | 0.09 | 75.57 | 0.09 | 75.52 | 0.09 | 75.73 | 0.09 |  |  | 75.41 | 0.08 | 76.08 | 0.07 | 75.83 | 0.09 | 75.61 | 0.1 | 75.5 |  | 75.45 | 0.11 |  |  | 83.19 | 0.17 | 77.21 | 0.12 | 75.82 | 0.1 | 75.51 | 0.09 | [62 empty] | T2-TRN-100A-55-2E-DM | 75.014 | 0.014 | 61.992 | 0.022 | 57.744 | 0.01 | 55.03 | 0.019 | 94.992 | 0.073 | 75.016 | 0.019 | 2988 | 3.2 | 2943.1 | 3.2 | 0.633 | 0.003 | -0.252 | 0.002 | 0.219 | 0.004 | 1.2495 | 0.0027 | 29.371 | 0.001 | 8613 | 23 | 1650 |  | 0.014812 | 44.0638 | 13.03 | 0.26 | 1.488 | 13673.6801 | 218.8637 | 45.1263 | 192.0292 | 13481.6509 | 0.0088446 | 27.7511 | 56.256 | 14.0998 | 13.1113 | 0.013937 | 38.1727 | 0.008772 | 27.6027 | 0.0085636 | 23.1641 | 75.2972 | 62.203 | 22.8013 | 67681.8898 | 62486.9661 | 6963 | 0.35112 | 62797.4218 | 57602.4981 | 7.291 | 0.15442 | -4.9498 | -19.0411 | 52.7788 | 67681.8898 | 60691.7293 | 4960.3971 | 2029.7635 | 67681.8898 | 100%
2 | T2-TRN-95-2FER-DM | 75T0024 | T2-TRN-95-2FER-DM | 2 finger | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 22:40:01 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.2 | 15.5 | 0 | 49024 | 84 | 49155 | 506 | 0 | 0 | 49018 | 84 | 5.6695 | 949 | 1650 | [37 empty] | Econo 2F-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-TRN-95-2FE-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;2F Open: Jade Control set to 5.95V | 75.013 | 0.013 | 61.992 | 0.025 | 95.03 | 0.021 | 74.903 | 0.016 | 75.06 | 0.15 | 60.04 | 0.03 | 62.17 | 0.01 | 0.162 | 0.004 | 1.267 | 0.0027 | 49024 | 84 | 0 | 0 | 5.669 | 0.017 | [6 empty] | 461.1 | 2.4 | 461.3 | 2.4 | 459 | 2.4 | 15.5 | 0.1 | 13.2 | 0 | 12.8 | 0.1 | 7035.9 | 59.9 | 3159.3 | 64.9 | 1610.7 | 50.4 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.7 |  | 4.8 |  | 4.4 |  | 3150 |  | 0.86 | 460 | 460 | 460 | 5 | 4.6 | 4.5 | 3040 | 0.81 | 460.2 |  | 1.6 |  | 706.8 |  | 85 |  | 8631.8 | [14 empty] | 217.23 | 0.32 | 106.76 | 0.13 | 107.03 | 0.1 | 0.26 | 0.08 | 246.48 | 0.34 | 173.78 | 0.07 | 116.03 | 0.1 | 57.76 | 0.07 | 210.37 | 0.05 | 99.57 | 0.09 | 104.79 | 0.05 | 5.25 | 0.05 | 76.8 | 0.06 | 51.3 | 0.37 | 45.31 | 0.04 | 5.99 | 0.39 | 76.14 | 0.03 | 57.99 | 0.12 | 44.89 | 0.02 | 13.1 | 0.13 | [46 empty] | 250.99 | 0.34 | 168.63 | 0.12 | 117.36 | 0.1 | 51.28 | 0.12 | 230.48 | 0.44 | 111.2 | 0.13 | 9.95 | 0.1 | 218.13 | 0.05 | 100.47 | 0.13 | 107.3 | 0.05 | 6.8 | 0.05 | 85.53 | 0.06 | 50.73 | 0.04 | 2.86 | 0.38 | 84.51 | 0.07 | 61.99 | 0.2 | 50.12 | 0.04 | 11.88 | 0.21 | 105.36 | 0.13 | [28 empty] | 105.77 | 0.13 | 105.36 | 0.13 | 101.5 | 0.14 | 101.76 | 0.13 | 60.1 | 0.05 | 59.82 | 0.05 | 59.43 | 0.05 | 60.26 | 0.04 | 59.99 | 0.03 | 60.04 | 0.03 | 105.97 | 0.09 | 100.64 | 0.13 | 52.44 | 0.58 | 57.94 | 0.19 | 167.77 | 0.14 | 101.85 | 0.13 | 100.9 | 0.12 | 53.46 | 0.11 | 63.98 | 0.27 | 99.57 | 0.09 | 100.47 | 0.13 | 92.96 | 0.08 | 106.67 | 0.12 | 106.42 | 0.11 | 102.22 | 0.08 | 101.81 | 0.43 | 101.5 | 0.14 | 101.76 | 0.13 | [12 empty] | 106.76 | 0.13 | 60.04 | 0.03 |  |  | 101.25 | 0.12 | 105.77 | 0.13 | 105.36 | 0.13 | [16 empty] | 53.59 | 0.35 | [12 empty] | 174.27 | 0.1 | 94.75 | 0.16 | 94.79 | 0.22 | 75.76 | 0.08 | 75.57 | 0.08 | 75.36 | 0.07 | 76.1 | 0.04 | 76.06 | 0.08 | 75.96 | 0.08 | 75.75 | 0.08 | 86.15 | 0.21 | 86.08 | 0.18 | 88.15 | 0.23 | 80.43 | 0.14 | 85.35 | 0.17 | 85.67 | 0.19 | 87.47 | 0.19 | 83.17 | 0.25 | 81.92 | 0.1 | 83.52 | 0.19 | 77.38 | 0.13 | 75.83 | 0.09 | 77.72 | 0.13 | 80.55 | 0.12 | 79.14 | 0.11 | 75.58 | 0.09 | 76.34 | 0.08 | 78.47 | 0.09 | 79.16 | 0.08 |  |  | 75.37 | 0.08 | 76.05 | 0.07 | 75.82 | 0.09 | 75.61 | 0.09 | 75.52 |  | 75.43 | 0.09 |  |  | 88.63 | 0.21 | 86.44 | 0.17 | 76.24 | 0.1 | 75.49 | 0.09 | [62 empty] | T2-TRN-100A-55-2F-DM | 75.013 | 0.013 | 61.992 | 0.025 | 60.038 | 0.009 | 57.255 | 0.015 | 95.03 | 0.021 | 74.903 | 0.016 | 3014.2 | 3.3 | 2956.1 | 3.2 | 0.557 | 0.002 | -0.124 | 0.001 | 0.162 | 0.004 | 1.267 | 0.0027 | 29.388 | 0 | 8647 | 23 | 1650 |  | 0.16165 | 489.2822 | 13.029 | 0.178 | 1.5086 | 13726.4365 | 193.4369 | 424.8278 | 1807.789 | 11918.6475 | 0.0094382 | 28.9803 | 58.5294 | 14.0999 | 13.1755 | 0.013829 | 38.0629 | 0.0087723 | 27.6027 | 0.0093308 | 24.5578 | 77.6703 | 63.9158 | 24.1895 | 65761.0193 | 63056.6995 | 6997 | 0.36314 | 60789.7696 | 58085.4497 | 7.0302 | 0.14895 | -4.7908 | -19.1409 | 55.1794 | 65761.0193 | 41795.5437 | 5055.5812 | 18909.8944 | 65761.0193 | 100%
2 | T2-TRN-95-3ER-DM | 75T0025 | T2-TRN-95-3ER-DM | 30% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 9:43:46 | 10 Ton | 0:15:00 | 75/62095/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.5 | 15.3 | 0 | 53836 | 91 | 56187 | 555 | 3212 | 167 | 57051 | 160 | 6.61 | 950 | [38 empty] | Econo 30%-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-TRN-95-3E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.665 | 0.019 | 61.975 | 0.02 | 94.906 | 0.022 | 74.919 | 0.024 | 75.51 | 0.17 | 58.46 | 0.04 | 60.88 | 0.03 | 0.223 | 0.005 | 1.2642 | 0.0034 | 53836 | 91 | 3212 | 167 | 6.61 | 0.025 | [6 empty] | 460.8 | 2.6 | 460.8 | 2.6 | 459.5 | 2.6 | 15.3 | 0.1 | 13.3 | 0 | 12.9 | 0.1 | 6959.5 | 63.5 | 3226.3 | 70.9 | 1670.9 | 52.7 | 460 |  | 459 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.7 |  | 3150 |  | 0.86 | 460 | 459 | 459 | 4.9 | 4.6 | 4.5 | 3030 | 0.82 | 459.9 |  | 1.6 |  | 707 |  | 85 |  | 8612 | [14 empty] | 217.37 | 0.32 | 107.51 | 0.14 | 107.08 | 0.1 | -0.44 | 0.09 | 246.04 | 0.35 | 173.84 | 0.09 | 115.91 | 0.1 | -57.93 | 0.08 | 210 | 0.05 | 99.74 | 0.09 | 104.66 | 0.04 | 4.92 | 0.03 | 76.16 | 0.06 | 49.97 | 0.27 | 44.91 | 0.04 | 5.07 | 0.28 | 75.25 | 0.03 | 57.5 | 0.13 | 44.32 | 0.02 | 13.18 | 0.13 | [46 empty] | 249.03 | 0.35 | 169.17 | 0.12 | 116.79 | 0.1 | 52.38 | 0.11 | 230.56 | 0.44 | 111.24 | 0.14 | 10.06 | 0.09 | 219 | 0.02 | 100.32 | 0.14 | 107.58 | 0.02 | 7.26 | 0.05 | 80.76 | 0.04 | 47.83 | 0.03 | 3.18 | 0.21 | 80 | 0.06 | 58.8 | 0.21 | 47.36 | 0.04 | 11.45 | 0.22 | 105.81 | 0.13 | [28 empty] | 106.32 | 0.12 | 105.81 | 0.13 | 101.36 | 0.15 | 102.15 | 0.14 | 58.96 | 0.04 | 58.5 | 0.04 | 57.93 | 0.04 | 59.11 | 0.04 | 58.79 | 0.04 | 58.76 | 0.04 | 106.47 | 0.1 | 101.33 | 0.11 | 51.42 | 0.45 | 57.78 | 0.18 | 168.94 | 0.14 | 101.86 | 0.15 | 100.48 | 0.15 | 50.8 | 0.1 | 60.65 | 0.32 | 99.74 | 0.09 | 100.32 | 0.14 | 92.6 | 0.09 | 106.86 | 0.12 | 106.67 | 0.1 | 102.07 | 0.08 | 101.74 | 0.09 | 101.36 | 0.15 | 102.15 | 0.14 | [12 empty] | 107.51 | 0.14 | 58.76 | 0.04 |  |  | 101.17 | 0.15 | 106.32 | 0.12 | 105.81 | 0.13 | [16 empty] | 51.02 | 0.2 | [12 empty] | 174.52 | 0.1 | 95.29 | 0.14 | 95.22 | 0.22 | 75.91 | 0.09 | 75.7 | 0.09 | 75.42 | 0.08 | 76.28 | 0.05 | 76.28 | 0.08 | 76.17 | 0.09 | 75.91 | 0.09 | 83.61 | 0.17 | 86.8 | 0.2 | 85.1 | 0.2 | 75.42 | 0.11 | 83.89 | 0.19 | 83.73 | 0.15 | 82.16 | 0.18 | 78.21 | 0.07 | 81.53 | 0.16 | 79.02 | 0.14 | 76.88 | 0.12 | 75.18 | 0.1 | 75.61 | 0.11 | 77.57 | 0.08 | 77.12 | 0.1 | 75.18 | 0.09 | 75.27 | 0.08 | 75.8 | 0.09 | 76.13 | 0.08 |  |  | 75.47 | 0.09 | 76.05 | 0.07 | 75.78 | 0.09 | 75.55 | 0.1 | 75.44 |  | 75.33 | 0.11 |  |  | 82.13 | 0.15 | 80.78 | 0.14 | 75.48 | 0.1 | 75.15 | 0.1 | [62 empty] | T2-TRN-100A-55-3E-DM | 74.665 | 0.019 | 61.975 | 0.02 | 58.337 | 0.009 | 55.594 | 0.018 | 94.906 | 0.022 | 74.919 | 0.024 | 3004.2 | 4 | 2961.1 | 3.9 | 0.613 | 0.002 | -0.223 | 0.002 | 0.223 | 0.005 | 1.2642 | 0.0034 | 29.431 | 0 | 8631 | 23 | 1640 |  | 0.053327 | 159.9053 | 13.03 | 0.24 | 1.4773 | 13730.5558 | 213.2449 | 160.3256 | 682.3757 | 13048.1801 | 0.0090932 | 28.1166 | 56.8597 | 14.0971 | 13.1278 | 0.013872 | 38.0806 | 0.0088433 | 27.5955 | 0.0087499 | 23.5112 | 75.6797 | 62.7123 | 23.1509 | 68181.6633 | 62017.9871 | 6991 | 0.34995 | 63312.1482 | 57148.4719 | 7.3354 | 0.15857 | -4.9657 | -18.8199 | 53.3129 | 68181.6633 | 56080.0235 | 4946.8899 | 7154.75 | 68181.6633 | 100%
2 | T2-TRN-95-3FER-DM | 75T0026 | T2-TRN-95-3FER-DM | 3 finger | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 21:20:18 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.3 | 15.4 | 0 | 45513 | 51 | 46106 | 529 | 0 | 0 | 45503 | 51 | 5.2508 | 949 | [38 empty] | Econo 3F-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-TRN-95-3FE-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;3F Open: Jade Control set to 6.9V | 75.009 | 0.011 | 61.998 | 0.008 | 95 | 0.025 | 75.004 | 0.025 | 74.97 | 0.15 | 60.83 | 0.06 | 63.04 | 0.01 | 0.118 | 0.003 | 1.2692 | 0.0021 | 45513 | 51 | 0 | 0 | 5.251 | 0.015 | [6 empty] | 460.8 | 2.7 | 460.9 | 2.7 | 459.1 | 2.6 | 15.4 | 0.1 | 13.3 | 0 | 12.9 | 0.1 | 7011.7 | 65.7 | 3189.4 | 69.8 | 1654.3 | 55.1 | 460 |  | 460 |  | 460 |  | 3.3 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.4 |  | 3170 |  | 0.85 | 460 | 460 | 460 | 5 | 4.6 | 4.5 | 3060 | 0.81 | 459.9 |  | 1.6 |  | 705.9 |  | 85 |  | 8660.9 | [14 empty] | 217.4 | 0.32 | 106.84 | 0.14 | 107.08 | 0.1 | 0.24 | 0.1 | 247.47 | 0.35 | 173.95 | 0.09 | 116.32 | 0.1 | 57.64 | 0.07 | 210.07 | 0.05 | 99.35 | 0.1 | 104.68 | 0.05 | 5.37 | 0.05 | 78.09 | 0.05 | 52.7 | 0.36 | 46.13 | 0.03 | 6.57 | 0.38 | 77.34 | 0.02 | 59.26 | 0.11 | 45.65 | 0.01 | 13.61 | 0.12 | [46 empty] | 252.11 | 0.36 | 168.42 | 0.1 | 117.67 | 0.1 | 50.75 | 0.06 | 230.8 | 0.46 | 111.3 | 0.14 | 9.78 | 0.1 | 218.2 | 0.05 | 100.61 | 0.13 | 107.33 | 0.05 | 6.83 | 0.05 | 87.24 | 0.05 | 51.74 | 0.03 | 3.07 | 0.32 | 86.21 | 0.06 | 63.13 | 0.14 | 51.13 | 0.04 | 12 | 0.14 | 105.33 | 0.14 | [28 empty] | 105.75 | 0.13 | 105.33 | 0.14 | 101.56 | 0.14 | 101.86 | 0.12 | 61.08 | 0.07 | 60.8 | 0.06 | 60.37 | 0.06 | 61.25 | 0.03 | 60.96 | 0.03 | 61.03 | 0.04 | 106.04 | 0.1 | 100.52 | 0.11 | 53.78 | 0.54 | 59.1 | 0.18 | 167.63 | 0.12 | 102.03 | 0.14 | 101.09 | 0.13 | 54.49 | 0.11 | 65.23 | 0.19 | 99.35 | 0.1 | 100.61 | 0.13 | 92.71 | 0.11 | 106.65 | 0.13 | 106.45 | 0.11 | 102.29 | 0.1 | 101.84 | 0.39 | 101.56 | 0.14 | 101.86 | 0.12 | [12 empty] | 106.84 | 0.14 | 61.03 | 0.04 |  |  | 101.52 | 0.14 | 105.75 | 0.13 | 105.33 | 0.14 | [16 empty] | 54.81 | 0.3 | [12 empty] | 174.36 | 0.11 | 94.57 | 0.17 | 94.76 | 0.23 | 75.68 | 0.07 | 75.54 | 0.09 | 75.3 | 0.07 | 76.03 | 0.05 | 75.98 | 0.08 | 75.9 | 0.08 | 75.69 | 0.09 | 89.25 | 0.34 | 87.71 | 0.21 | 89.74 | 0.18 | 81.77 | 0.17 | 86.97 | 0.21 | 86.74 | 0.17 | 88.85 | 0.27 | 87.44 | 0.23 | 85.4 | 0.16 | 85.45 | 0.16 | 80.61 | 0.22 | 77.79 | 0.09 | 80.97 | 0.15 | 83.31 | 0.11 | 82.91 | 0.12 | 75.58 | 0.08 | 78.11 | 0.08 | 81.8 | 0.13 | 82.36 | 0.13 |  |  | 75.29 | 0.08 | 76.02 | 0.07 | 75.78 | 0.09 | 75.58 | 0.1 | 75.51 |  | 75.37 | 0.1 |  |  | 90.52 | 0.25 | 87.73 | 0.22 | 77.36 | 0.11 | 76.59 | 0.1 | [62 empty] | T2-TRN-100A-55-3F-DM | 75.009 | 0.011 | 61.998 | 0.008 | 61.052 | 0.003 | 58.186 | 0.01 | 95 | 0.025 | 75.004 | 0.025 | 3020.9 | 2.5 | 2953.8 | 2.5 | 0.529 | 0.002 | -0.066 | 0.001 | 0.118 | 0.003 | 1.2692 | 0.0021 | 29.368 | 0 | 8666 | 24 | 1640 |  | 0.24588 | 747.4786 | 13.029 | 0.135 | 1.5083 | 13727.5085 | 183.5701 | 543.697 | 2313.6139 | 11413.8946 | 0.0096447 | 29.3858 | 59.5437 | 14.0999 | 13.2037 | 0.013924 | 38.161 | 0.0087772 | 27.6071 | 0.0096563 | 25.1596 | 78.4045 | 64.4664 | 24.7911 | 63073.6353 | 62138.7932 | 7026 | 0.38019 | 58102.8399 | 57167.9978 | 6.7047 | 0.15183 | -4.5947 | -18.8608 | 56.1675 | 63073.6353 | 33597.808 | 5058.1121 | 24417.7152 | 63073.6353 | 100%
2 | T2-TRN-95-CE-DM | 75T0027 | T2-TRN-95-CE-DM | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 18:33:50 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.2 | 15.3 | 0 | 57774 | 87 | 58787 | 558 | 7650 | 146 | 65432 | 152 | 7.6128 | 949 | 1620 |  | 6.7218 | [35 empty] | Econo closed, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-TRN-95-CE-DM-SPWCT-SS | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.953 | 0.011 | 62.008 | 0.027 | 94.986 | 0.042 | 75.005 | 0.043 | 75.14 | 0.18 | 57.16 | 0.06 | 59.96 | 0.02 | 0.205 | 0.003 | 1.2383 | 0.0027 | 57774 | 87 | 7650 | 146 | 7.613 | 0.029 | [6 empty] | 460.8 | 2.5 | 460.6 | 2.5 | 458.9 | 2.5 | 15.3 | 0.1 | 13.2 | 0 | 12.8 | 0.1 | 6964 | 58.8 | 3194.5 | 65.2 | 1630.9 | 47.9 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.5 |  | 3150 |  | 0.86 | 460 | 460 | 460 | 5 | 4.6 | 4.6 | 3010 | 0.82 | 459.9 |  | 1.6 |  | 705.4 |  | 85 |  | 8570.4 | [14 empty] | 216.77 | 0.37 | 106.72 | 0.14 | 106.87 | 0.12 | 0.15 | 0.1 | 245.44 | 0.4 | 173.41 | 0.14 | 115.72 | 0.12 | 57.69 | 0.1 | 209.77 | 0.05 | 99.32 | 0.1 | 104.58 | 0.05 | 5.28 | 0.05 | 75.95 | 0.06 | 50.27 | 0.44 | 44.75 | 0.04 | 5.53 | 0.45 | 75.31 | 0.03 | 57.04 | 0.16 | 44.33 | 0.02 | 12.71 | 0.15 | [46 empty] | 247.56 | 0.4 | 170.28 | 0.25 | 116.34 | 0.12 | 53.93 | 0.27 | 230.25 | 0.53 | 111.12 | 0.16 | 10.41 | 0.15 | 218.67 | 0.05 | 99.83 | 0.15 | 107.47 | 0.05 | 7.59 | 0.05 | 78.44 | 0.13 | 46.34 | 0.09 | 2.88 | 0.61 | 77.54 | 0.16 | 57.48 | 0.49 | 45.76 | 0.11 | 11.71 | 0.54 | 105.31 | 0.14 | [28 empty] | 105.71 | 0.13 | 105.31 | 0.14 | 101.03 | 0.16 | 101.3 | 0.14 | 57.35 | 0.06 | 57.06 | 0.05 | 56.71 | 0.05 | 57.55 | 0.04 | 57.3 | 0.04 | 57.37 | 0.04 | 105.95 | 0.12 | 100.71 | 0.12 | 51.34 | 0.64 | 57.18 | 0.22 | 169.37 | 0.29 | 101.39 | 0.16 | 100.25 | 0.16 | 49.25 | 0.1 | 59.37 | 0.72 | 99.32 | 0.1 | 99.83 | 0.15 | 92.56 | 0.07 | 106.43 | 0.14 | 106.25 | 0.12 | 101.35 | 0.13 | 101.54 | 0.12 | 101.03 | 0.16 | 101.3 | 0.14 | [12 empty] | 106.72 | 0.14 | 57.37 | 0.04 |  |  | 100.71 | 0.15 | 105.71 | 0.13 | 105.31 | 0.14 | [16 empty] | 49.24 | 0.53 | [12 empty] | 173.97 | 0.12 | 95.13 | 0.18 | 94.88 | 0.25 | 75.8 | 0.09 | 75.59 | 0.1 | 75.36 | 0.09 | 76.08 | 0.06 | 76.09 | 0.09 | 76.01 | 0.1 | 75.79 | 0.1 | 81.2 | 0.11 | 80.86 | 0.08 | 78.23 | 0.15 | 75.75 | 0.11 | 77.35 | 0.1 | 77.92 | 0.08 | 77.19 | 0.07 | 77.12 | 0.08 | 75.76 | 0.08 | 76.44 | 0.1 | 75.38 | 0.11 | 75.46 | 0.09 | 75.19 | 0.1 | 75.88 | 0.09 | 75.58 | 0.1 | 75.56 | 0.08 | 75.51 | 0.08 | 75.46 | 0.09 | 75.68 | 0.08 |  |  | 75.35 | 0.09 | 76.01 | 0.08 | 75.77 | 0.1 | 75.55 | 0.11 | 75.47 |  | 75.36 | 0.1 |  |  | 82.85 | 0.1 | 76.54 | 0.1 | 75.77 | 0.1 | 75.42 | 0.09 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.953 | 0.011 | 62.008 | 0.027 | 57.283 | 0.009 | 54.563 | 0.019 | 94.986 | 0.042 | 75.005 | 0.043 | 2974.7 | 3.3 | 2930 | 3.2 | 0.646 | 0.002 | -0.277 | 0.002 | 0.205 | 0.003 | 1.2383 | 0.0027 | 29.344 | 0 | 8595 | 24 | 1620 |  | 0 | 0 | 13.029 | 0.279 | 1.4582 | 13626.2415 | 222.3644 | 0 | 0 | 13626.2415 | 0.008797 | 27.6151 | 55.8248 | 14.0996 | 13.0984 | 0.013929 | 38.1622 | 0.008797 | 27.6151 | 0.0084049 | 22.8793 | 74.953 | 62.008 | 22.5239 | 69374.0997 | 62554.8976 | 6975 | 0.34315 | 64603.9693 | 57784.7673 | 7.5165 | 0.15906 | -5.0912 | -19.1282 | 52.2069 | 69374.0997 | 64531.2176 | 4842.8821 | 0 | 69374.0997 | 100%
2 | T2-TRN-95-OER-DM | 75T0028 | T2-TRN-95-OER-DM | open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 8:23:08 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 1.4 | 15.4 | 0 | 32789 | 170 | 36605 | 526 | 0 | 0 | 32766 | 171 | 3.7762 | 950 | 1650 | [37 empty] | Econo fully open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-TRN-95-OE-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.886 | 0.031 | 62.215 | 0.046 | 94.881 | 0.03 | 74.648 | 0.028 | 75.21 | 0.12 | 63.43 | 0.08 | 65.95 | 0.06 | 0.025 | 0.014 | 1.1893 | 0.0044 | 32789 | 170 | 0 | 0 | 3.776 | 0.022 | [6 empty] | 460.7 | 2.7 | 460.6 | 2.7 | 459.3 | 2.6 | 15.4 | 0.1 | 13.3 | 0 | 13 | 0.1 | 6979.8 | 67.2 | 3229.7 | 73.5 | 1697.5 | 56 | 460 |  | 459 |  | 459 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 459 |  | 459 |  | 4.6 |  | 4.9 |  | 4.5 |  | 3180 |  | 0.86 | 459 | 460 | 459 | 5 | 4.6 | 4.5 | 3060 | 0.81 | 459.8 |  | 1.6 |  | 705.9 |  | 85 |  | 8680.9 | [14 empty] | 217.25 | 0.35 | 107.18 | 0.13 | 107.03 | 0.11 | -0.15 | 0.07 | 251.21 | 0.33 | 174.58 | 0.21 | 117.42 | 0.09 | 57.16 | 0.22 | 208.7 | 0.01 | 99.73 | 0.02 | 104.23 | 0.02 | 4.5 | 0.01 | 84.08 | 0.17 | 59.46 | 0.99 | 49.87 | 0.1 | 9.6 | 0.97 | 82.82 | 0.16 | 64.75 | 0.45 | 49.1 | 0.1 | 15.66 | 0.43 | [46 empty] | 255.17 | 0.31 | 166.9 | 0.44 | 118.56 | 0.09 | 48.34 | 0.43 | 230.05 | 0.6 | 111.07 | 0.19 | 8.17 | 0.23 | 217 | 0.02 | 102.32 | 0.19 | 106.94 | 0.02 | 4.62 | 0.01 | 93.49 | 0.17 | 55.38 | 0.1 | 5.43 | 1.5 | 92.05 | 0.16 | 66.3 | 0.86 | 54.56 | 0.09 | 11.74 | 0.86 | 105.29 | 0.14 | [28 empty] | 105.78 | 0.13 | 105.29 | 0.14 | 102.94 | 0.2 | 103.42 | 0.19 | 64.53 | 0.13 | 64.24 | 0.13 | 63.81 | 0.14 | 64.86 | 0.13 | 64.64 | 0.12 | 64.54 | 0.13 | 106.18 | 0.1 | 101.11 | 0.13 | 61.17 | 0.95 | 65.12 | 0.48 | 166.84 | 0.45 | 103.41 | 0.19 | 102.63 | 0.19 | 59.37 | 1.38 | 68.95 | 0.95 | 99.73 | 0.12 | 102.32 | 0.19 | 93.36 | 0.11 | 106.71 | 0.14 | 106.59 | 0.11 | 103.74 | 0.12 | 103.21 | 0.14 | 102.94 | 0.2 | 103.42 | 0.19 | [12 empty] | 107.18 | 0.13 | 64.54 | 0.13 |  |  | 102.9 | 0.19 | 105.78 | 0.13 | 105.29 | 0.14 | [16 empty] | 60.85 | 1.49 | [12 empty] | 175.24 | 0.22 | 94.29 | 0.18 | 95 | 0.21 | 75.96 | 0.06 | 75.85 | 0.06 | 75.52 | 0.06 | 76.55 | 0.04 | 76.4 | 0.06 | 76.32 | 0.06 | 76.06 | 0.07 | 93.94 | 0.32 | 93.4 | 0.32 | 91.98 | 0.16 | 92.91 | 0.28 | 89.56 | 0.22 | 87.2 | 0.24 | 86.8 | 0.18 | 86.58 | 0.22 | 87.06 | 0.18 | 86 | 0.18 | 89.61 | 0.22 | 88.93 | 0.22 | 86.87 | 0.28 | 88.44 | 0.18 | 87.38 | 0.21 | 79.49 | 0.28 | 84.39 | 0.55 | 88.42 | 0.28 | 88.69 | 0.28 |  |  | 75.63 | 0.06 | 76.3 | 0.06 | 76.02 | 0.07 | 75.79 | 0.08 | 75.7 |  | 75.5 | 0.08 |  |  | 93.82 | 0.32 | 92.64 | 0.26 | 91.32 | 0.27 | 86.9 | 0.21 | [62 empty] | T2-TRN-100A-55-OE-DM | 74.886 | 0.031 | 62.215 | 0.046 | 64.309 | 0.062 | 61.289 | 0.09 | 94.881 | 0.03 | 74.648 | 0.028 | 2930.3 | 5.5 | 2848.4 | 5.4 | 0.409 | 0.006 | -0.148 | 0.022 | 0.025 | 0.014 | 1.1893 | 0.0044 | 29.421 | 0.001 | 8677 | 23 | 1650 |  | 0.55543 | 1676.6136 | 13.029 | 0.15 | 1.6268 | 13223.6974 | 136.8641 | 1732.1631 | 7373.7395 | 5849.9579 | 0.011566 | 33.3724 | 62.6822 | 14.0946 | 13.2957 | 0.013642 | 37.8203 | 0.0089497 | 27.7658 | 0.010849 | 27.2549 | 86.0774 | 69.5636 | 26.8566 | 86162.2793 | 74249.054 | 7027 | 0.27835 | 80997.9463 | 69084.721 | 9.3348 | 0.13355 | -6.5157 | -23.3952 | 59.0761 | 86162.2793 | 6756.4405 | 5266.4425 | 74139.3964 | 86162.2793 | 100%
2 | T2-CBASE-3000-95-CE | 75T0029 | T2-CBASE-3000-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/15/2014 | 13:22 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.1 | 1.3 | 15.1 | 0 | 57427 | 68 | 57232 | 586 | 8295 | 124 | 65729 | 123 | 7.6554 | 949 | [38 empty] | Factory charge, 2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), Econo closed unsealed cab,--adjust code tester speed to match total static of run T2-C-3000-95-CE-SPWCT-SS. Both stages. | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;Added 20.5 oz in circuit #1 | 74.909 | 0.016 | 62.195 | 0.019 | 94.972 | 0.025 | 75.007 | 0.009 | 74.74 | 0.18 | 57.51 | 0.02 | 60.12 | 0.01 | 0.283 | 0.003 | 1.2804 | 0.0031 | 57427 | 68 | 8295 | 124 | 7.656 | 0.025 | [6 empty] | 460.1 | 2.6 | 460 | 2.6 | 459.9 | 2.6 | 15.1 | 0.1 | 13.3 | 0 | 13 | 0.1 | 6837.5 | 61.8 | 3320.1 | 72.6 | 1747.9 | 52.2 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.2 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.7 |  | 4.9 |  | 4.4 |  | 3170 |  | 0.86 | 460 | 460 | 460 | 4.9 | 4.7 | 4.4 | 3000 | 0.81 | 459.2 |  | 1.6 |  | 697.7 |  | 85 |  | 8582.7 | [14 empty] | 215.95 | 0.24 | 106.58 | 0.09 | 106.6 | 0.08 | 0.02 | 0.06 | 245.94 | 0.26 | 174.25 | 0.22 | 115.86 | 0.07 | -58.39 | 0.21 | 208.9 | 0.05 | 98.87 | 0.13 | 104.28 | 0.03 | 5.41 | 0.12 | 76.18 | 0.05 | 51.57 | 0.41 | 44.88 | 0.03 | 6.69 | 0.41 | 75.6 | 0.05 | 58.11 | 0.13 | 44.5 | 0.03 | 13.61 | 0.12 | [46 empty] | 248.1 | 0.27 | 170.3 | 0.3 | 116.49 | 0.08 | 53.81 | 0.34 | 230.57 | 0.39 | 111.21 | 0.12 | 11.14 | 0.19 | 221 | 0.39 | 99.79 | 0.17 | 108.21 | 0.12 | 8.42 | 0.19 | 78.44 | 0.18 | 46.32 | 0.11 | 3.3 | 1.09 | 77.62 | 0.2 | 57.49 | 0.63 | 45.81 | 0.13 | 11.68 | 0.67 | 104.92 | 0.1 | [28 empty] | 105.36 | 0.1 | 104.92 | 0.1 | 100.92 | 0.15 | 101.26 | 0.14 | 57.57 | 0.04 | 57.34 | 0.04 |  |  | 57.6 | 0.04 | 57.58 | 0.03 | 57.5 | 0.04 | 105.63 | 0.09 | 100.04 | 0.08 | 52.47 | 0.5 | 58.11 | 0.16 | 169.7 | 0.33 | 101.19 | 0.15 | 100.22 | 0.14 | 49.45 | 0.19 | 59.02 | 0.97 | 98.87 | 0.07 | 99.79 | 0.14 | 94.11 | 0.08 | 106.23 | 0.1 | 105.83 | 0.13 | 101.48 | 0.1 | 101.65 | 0.11 | 100.92 | 0.15 | 101.26 | 0.14 | [12 empty] | 106.58 | 0.09 | 57.5 | 0.04 |  |  | 100.07 | 0.17 | 105.36 | 0.1 | 104.92 | 0.1 | [16 empty] | 49.65 | 1 | [12 empty] | 174.86 | 0.09 | 94.63 | 0.09 | 95.33 | 0.2 | 75.42 | 0.09 | 75.22 | 0.09 | 75.06 | 0.08 | 75.65 | 0.06 | 75.65 | 0.09 | 75.54 | 0.09 | 75.36 | 0.1 | 79.77 | 0.09 | 79.93 | 0.09 | 77.62 | 0.1 | 75.5 | 0.12 | 77.2 | 0.12 | 77.99 | 0.09 | 77.8 | 0.08 | 77.58 | 0.09 | 75.53 | 0.09 | 76.65 | 0.1 | 75.09 | 0.11 | 75.28 | 0.11 | 74.91 | 0.11 | 76.09 | 0.1 | 75.56 | 0.1 | 75.43 | 0.1 | 75.34 | 0.09 |  |  | 75.88 | 0.08 |  |  | 75.02 | 0.09 | 75.64 | 0.08 | 75.44 | 0.1 | 75.26 | 0.11 | 75.19 |  | 75.08 | 0.11 | 79.76 | 0.11 | 80.63 | 0.09 | 76.44 | 0.11 | 75.47 | 0.11 | 75.25 | 0.11 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.909 | 0.016 | 62.195 | 0.019 | 57.621 | 0.009 | 54.875 | 0.015 | 94.972 | 0.025 | 75.007 | 0.009 | 3027.7 | 3.7 | 2976.9 | 3.6 | 0.649 | 0.003 | -0.288 | 0.002 | 0.283 | 0.003 | 1.2804 | 0.0031 | 29.3 | 0 | 8586 | 22 | 1630 |  | 0 | 0 | 13.029 | 0.279 | 1.4392 | 13859.1442 | 226.9729 | 0 | 0 | 13859.1442 | 0.008931 | 27.751 | 56.1818 | 14.0993 | 13.1077 | 0.013934 | 38.1644 | 0.008931 | 27.751 | 0.0085036 | 23.0689 | 74.909 | 62.195 | 22.718 | 69752.5693 | 62290.3806 | 6956 | 0.34036 | 64964.0379 | 57501.8492 | 7.5663 | 0.16481 | -5.033 | -18.7272 | 52.4863 | 69752.5693 | 64890.1318 | 4862.4375 | 0 | 69752.5693 | 100%
2 | T2-MF0-100C1-100C2-100A-95-CCE | 75T0030 | T2-MF0-100C1-100C2-100A-95-CCE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 30 | 0 | CUST 5 | 10/9/2014 | 16:33:00 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 1.5 | 16.1 | 0 | 58645 | 62 | 58262 | 373 | 6524 | 81 | 65176 | 116 | 6.9603 | 949 | [38 empty] | MF0, 100% charge CK1 and CK2, 100% airflow (400 cfm/ton), closed damper,--30% condenser coil blockage, 2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm),--adjust code tester speed to match total static of run T2-MF0-100C1-100C2-100A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 1 turns open: AX 35 belt: 100% inlet-outlet Meriam, condenser coil blocked 28" of 62" coil | 74.994 | 0.016 | 61.998 | 0.015 | 95 | 0.02 | 74.998 | 0.023 | 75.02 | 0.13 | 57.53 | 0.08 | 60.88 | 0.02 | 0.199 | 0.003 | 1.9039 | 0.003 | 58645 | 62 | 6524 | 81 | 6.96 | 0.02 | [6 empty] | 460.9 | 2.8 | 461.4 | 2.8 | 459.1 | 2.7 | 16.1 | 0 | 13.9 | 0 | 13.6 | 0 | 7372.8 | 55.2 | 3174 | 65.2 | 1991.2 | 42.1 | 460 |  | 459 |  | 459 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 459 |  | 5.6 |  | 5.2 |  | 4.8 |  | 3540 |  | 0.85 | 459 | 459 | 460 | 5.5 | 5 | 4.7 | 3410 | 0.83 | 459.9 |  | 1.6 |  | 666.7 |  | 85 |  | 9331.7 | [14 empty] | 247.24 | 0.14 | 115.2 | 0.09 | 116.23 | 0.04 | 1.03 | 0.08 | 278.11 | 0.14 | 186.39 | 0.06 | 124.94 | 0.04 | 61.44 | 0.06 | 239 | 0.05 | 112.73 | 0.05 | 113.78 |  | 1.05 |  | 77.28 | 0.03 | 51.12 | 0.21 | 45.56 | 0.02 | 5.56 | 0.21 | 76.65 | 0.03 | 57.89 | 0.08 | 45.15 | 0.02 | 12.74 | 0.08 | [46 empty] | 284.41 | 0.17 | 186.17 | 0.16 | 126.63 | 0.04 | 59.54 | 0.18 | 268.5 | 0.27 | 122.3 | 0.07 | 22.49 | 0.08 | 256.7 | 0.05 | 106.11 | 0.06 | 118.98 | 0.05 | 12.87 | 0.05 | 79.04 | 0.13 | 46.68 | 0.08 | 3.08 | 0.62 | 78.69 | 0.1 | 59.09 | 0.07 | 46.46 | 0.06 | 12.63 | 0.09 | 105.82 | 0.07 | [28 empty] | 114.85 | 0.08 | 114.36 | 0.08 | 105.82 | 0.07 | 106.35 | 0.1 | 57.01 | 0.09 | 57.57 | 0.06 | 57.37 | 0.05 | 57.23 | 0.04 | 57.25 | 0.03 |  |  | 112.43 | 0.04 | 110.67 | 0.07 | 52.52 | 0.29 | 58.47 | 0.11 | 186.18 | 0.2 | 103.59 | 0.05 | 99.15 | 0.05 | 50.05 | 0.54 | 60.62 | 0.32 | 112.73 | 0.05 | 106.11 | 0.06 | 92.97 | 0.21 | 114.29 | 0.05 | 115.17 | 0.05 | 105.31 | 0.04 | 105.7 | 0.04 | 114.36 | 0.08 | 106.35 | 0.1 | [16 empty] | 115.2 | 0.09 | 99.82 | 0.06 | 114.85 | 0.08 | 105.82 | 0.07 | [16 empty] | 49.75 | 0.54 | [12 empty] | 187.73 | 0.08 | 93.98 | 0.1 | 93.14 | 0.09 | 75.33 | 0.05 | 75.62 | 0.05 | 75.14 | 0.05 | 75.84 | 0.06 | 75.7 | 0.05 | 75.74 | 0.07 | 75.53 | 0.06 | 79.34 | 0.11 | 76.86 | 0.06 | 76.95 | 0.05 | 77.96 | 0.09 | 78.21 | 0.07 | 77.45 | 0.07 | 76.86 | 0.06 | 75.64 | 0.06 | 75.39 | 0.07 | 75.66 | 0.07 | 75.1 | 0.06 | 75.35 | 0.06 | 75.27 | 0.06 | 75.27 | 0.06 | 75.67 | 0.05 | 75.42 | 0.06 | 75.3 | 0.03 | 76.37 | 0.07 | 76.42 | 0.08 |  |  | 75.16 | 0.06 | 75.4 | 0.05 | 75.6 | 0.06 | 75.4 | 0.06 | 75.55 |  | 75.16 | 0.06 | 81.15 | 0.06 | 81.35 | 0.07 | 78.76 | 0.07 | 75.42 | 0.07 | 75.32 | 0.06 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.994 | 0.016 | 61.998 | 0.015 | 57.392 | 0.008 | 54.758 | 0.015 | 95 | 0.02 | 74.998 | 0.023 | 3048.3 | 2.4 | 2982.6 | 2.3 | 0.673 | 0.003 | -0.298 | 0.002 | 0.199 | 0.003 | 1.9039 | 0.003 | 29.207 | 0.001 | 9364 | 22 | 1630 |  | 0 | 0 | 13.029 | 0.279 | 1.4198 | 13959.727 | 235.817 | 0 | 0 | 13959.727 | 0.0087807 | 27.6073 | 55.9722 | 14.0999 | 13.1018 | 0.013919 | 38.1552 | 0.0087807 | 27.6073 | 0.0084906 | 22.999 | 74.994 | 61.998 | 22.6528 | 69162.5973 | 63729.5398 | 7734 | 0.38165 | 64404.2509 | 58971.1933 | 6.8779 | 0.15257 | -4.9544 | -19.0218 | 52.5475 | 69162.5973 | 64330.9248 | 4831.6726 | 0 | 69162.5973 | 100%
2 | T2-MF13-115C1-115C2-100A-95-CCE | 75T0032 | T2-MF13-115C1-115C2-100A-95-CCE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 30 | 0 | CUST 5 | 10/9/2014 | 18:33:19 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.36 lbs/CK2: 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 460.9 | 1.6 | 16.4 | 0 | 59967 | 73 | 59460 | 366 | 7911 | 199 | 67885 | 202 | 7.0972 | 949 | [38 empty] | MF13, 115% charge CK1 and CK2, 100% airflow (400 cfm/ton), closed damper, 30% condenser coil blockage,--2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), adjust code tester speed--to match total static of run T2-MF0-100C1-100C2-100A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 1 turns open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 28` of 62` coil | 74.996 | 0.009 | 61.998 | 0.031 | 95.012 | 0.028 | 74.996 | 0.033 | 74.89 | 0.14 | 57.05 | 0.08 | 60.44 | 0.02 | 0.201 | 0.004 | 1.904 | 0.0026 | 59967 | 73 | 7911 | 199 | 7.097 | 0.025 | [6 empty] | 460.9 | 2.9 | 461.3 | 2.9 | 459.1 | 2.8 | 16.4 | 0 | 14.1 | 0 | 13.8 | 0 | 7479 | 57.2 | 3188.7 | 67 | 2086.2 | 43.9 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.55 | 460 |  | 460 |  | 460 |  | 5.6 |  | 5.2 |  | 4.9 |  | 3580 |  | 0.86 | 460 | 460 | 460 | 5.7 | 5.2 | 4.9 | 3560 | 0.85 | 459.8 |  | 1.6 |  | 665.2 |  | 85 |  | 9560.2 | [14 empty] | 260.27 | 0.21 | 105.75 | 0.13 | 119.99 | 0.06 | 14.24 | 0.12 | 281.85 | 0.21 | 186.5 | 0.21 | 125.95 | 0.05 | 60.55 | 0.22 | 254.5 | 0.05 | 104.72 | 0.1 | 118.34 | 0.05 | 13.5333 | 0.05 | 76.45 | 0.08 | 48.52 | 0.35 | 45.02 | 0.05 | 3.5 | 0.38 | 75.84 | 0.09 | 55.19 | 0.44 | 44.62 | 0.05 | 10.57 | 0.47 | [46 empty] | 297.69 | 0.21 | 191.76 | 0.15 | 130.12 | 0.05 | 61.64 | 0.15 | 282.76 | 0.27 | 126.2 | 0.07 | 29.68 | 0.07 | 270.9 | 0.05 | 102.45 | 0.06 | 122.96 | 0.05 | 20.4567 | 0.05 | 78.9 | 0.11 | 46.59 | 0.07 | 2.65 | 0.45 | 78.57 | 0.09 | 56.56 | 0.36 | 46.38 | 0.06 | 10.18 | 0.35 | 102.28 | 0.07 | [28 empty] | 106.13 | 0.13 | 106.24 | 0.11 | 102.28 | 0.07 | 102.86 | 0.09 | 56.52 | 0.08 | 57.15 | 0.06 | 56.97 | 0.05 | 56.75 | 0.05 | 56.77 | 0.05 |  |  | 104.24 | 0.08 | 102.86 | 0.12 | 49.48 | 0.65 | 55.76 | 0.46 | 191.75 | 0.19 | 100.15 | 0.06 | 96.02 | 0.04 | 49.7 | 0.35 | 60.21 | 0.28 | 104.72 | 0.1 | 102.45 | 0.06 | 92.93 | 0.21 | 105.71 | 0.09 | 106.82 | 0.09 | 102.16 | 0.04 | 102.6 | 0.04 | 106.24 | 0.11 | 102.86 | 0.09 | [16 empty] | 105.75 | 0.13 | 96.51 | 0.07 | 106.13 | 0.13 | 102.28 | 0.07 | [16 empty] | 49.24 | 0.39 | [12 empty] | 187.86 | 0.25 | 93.91 | 0.11 | 93.09 | 0.09 | 75.19 | 0.05 | 75.54 | 0.05 | 75.05 | 0.05 | 75.72 | 0.06 | 75.57 | 0.05 | 75.64 | 0.06 | 75.44 | 0.06 | 79.26 | 0.1 | 76.79 | 0.06 | 76.87 | 0.05 | 77.87 | 0.1 | 78.09 | 0.09 | 77.37 | 0.07 | 76.75 | 0.06 | 75.55 | 0.07 | 75.29 | 0.07 | 75.58 | 0.07 | 75 | 0.06 | 75.24 | 0.06 | 75.17 | 0.06 | 75.2 | 0.06 | 75.57 | 0.05 | 75.34 | 0.06 | 75.24 | 0.04 | 76.28 | 0.06 | 76.32 | 0.06 |  |  | 75.07 | 0.06 | 75.32 | 0.05 | 75.52 | 0.06 | 75.33 | 0.06 | 75.48 |  | 75.08 | 0.06 | 81.1 | 0.06 | 81.39 | 0.08 | 78.65 | 0.08 | 75.33 | 0.07 | 75.22 | 0.06 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.996 | 0.009 | 61.998 | 0.031 | 57.011 | 0.016 | 54.44 | 0.021 | 95.012 | 0.028 | 74.996 | 0.033 | 3047.7 | 2.1 | 2983.6 | 2.1 | 0.672 | 0.003 | -0.298 | 0.002 | 0.201 | 0.004 | 1.904 | 0.0026 | 29.195 | 0.001 | 9565 | 22 | 1670 |  | 0 | 0 | 13.029 | 0.279 | 1.46 | 13968.0312 | 235.5456 | 0 | 0 | 13968.0312 | 0.0087803 | 27.6073 | 55.551 | 14.1002 | 13.0915 | 0.013914 | 38.153 | 0.0087803 | 27.6073 | 0.0083991 | 22.8067 | 74.996 | 61.998 | 22.4508 | 72025.0647 | 65185.9683 | 7895 | 0.37411 | 67129.2718 | 60290.1753 | 7.0182 | 0.14638 | -5.1564 | -19.445 | 52.2166 | 72025.0647 | 67054.6562 | 4970.4085 | 0 | 72025.0647 | 100%
2 | T2-MF15-85C1-85C2-100A-95-CCE | 75T0033 | T2-MF15-85C1-85C2-100A-95-CCE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 30 | 0 | CUST 5 | 10/9/2014 | 20:29:51 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.44 lbs/CK2: 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 460.9 | 1.4 | 15.8 | 0 | 56270 | 48 | 55691 | 367 | 4735 | 109 | 61010 | 95 | 6.6904 | 949 | [38 empty] | MF15, 85% charge CK1 and CK2, 100% airflow (400 cfm/ton), closed damper, 30% condenser coil blockage,--2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), adjust code tester speed--to match total static of run T2-MF0-100C1-100C2-100A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 3 turns open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 28` of 62` coil | 75.008 | 0.008 | 61.992 | 0.017 | 95.011 | 0.031 | 74.989 | 0.028 | 74.78 | 0.12 | 58.03 | 0.09 | 61.3 | 0.01 | 0.196 | 0.004 | 1.9022 | 0.0025 | 56270 | 48 | 4735 | 109 | 6.691 | 0.018 | [6 empty] | 460.9 | 2.5 | 460.6 | 2.5 | 459.2 | 2.5 | 15.8 | 0 | 13.7 | 0 | 13.3 | 0 | 7180.3 | 51.1 | 3200.5 | 60.9 | 1938.4 | 39.5 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 5.4 |  | 5.1 |  | 4.7 |  | 3430 |  | 0.85 | 460 | 460 | 460 | 5.3 | 4.8 | 4.7 | 3270 | 0.82 | 459.9 |  | 1.6 |  | 667.8 |  | 85 |  | 9112.8 | [14 empty] | 234.99 | 0.17 | 111.56 | 0.08 | 112.56 | 0.05 | 1 | 0.09 | 269.78 | 0.16 | 199.07 | 0.05 | 122.66 | 0.04 | 76.41 | 0.07 | 223.1 | 0.05 | 107.92 | 0.04 | 108.86 | 0.05 | 0.89333 | 0.05 | 73.9 | 0.04 | 68 | 0.04 | 43.37 | 0.03 | 24.63 | 0.04 | 73.3 | 0.04 | 70.75 | 0.03 | 42.97 | 0.03 | 27.77 | 0.03 | [46 empty] | 272.77 | 0.15 | 181.49 | 0.13 | 123.49 | 0.04 | 58 | 0.13 | 250.16 | 0.24 | 117.09 | 0.07 | 10.74 | 0.1 | 239.2 | 0.05 | 113.24 | 0.12 | 113.83 | 0.05 | 0.53 | 0.05 | 79.42 | 0.08 | 46.92 | 0.05 | 3.19 | 0.44 | 79.07 | 0.06 | 71.47 | 0.04 | 46.7 | 0.04 | 24.77 | 0.06 | 112.9 | 0.12 | [28 empty] | 110.34 | 0.07 | 109.8 | 0.06 | 112.9 | 0.12 | 113.17 | 0.11 | 57.51 | 0.08 | 58.23 | 0.06 | 58.06 | 0.05 | 57.71 | 0.05 | 57.76 | 0.05 |  |  | 108.96 | 0.05 | 105.67 | 0.07 | 68.41 | 0.1 | 71.07 | 0.08 | 181.46 | 0.15 | 110.54 | 0.11 | 105.62 | 0.06 | 50.41 | 0.38 | 61.29 | 0.23 | 107.92 | 0.04 | 113.24 | 0.12 | 93.15 | 0.22 | 109.69 | 0.05 | 110.54 | 0.05 | 111.45 | 0.07 | 111.98 | 0.09 | 109.8 | 0.06 | 113.17 | 0.11 | [16 empty] | 111.56 | 0.08 | 106.36 | 0.07 | 110.34 | 0.07 | 112.9 | 0.12 | [16 empty] | 50.08 | 0.38 | [12 empty] | 200.53 | 0.08 | 93.82 | 0.09 | 93.14 | 0.1 | 75.14 | 0.05 | 75.5 | 0.04 | 75.02 | 0.05 | 75.64 | 0.05 | 75.5 | 0.04 | 75.58 | 0.06 | 75.38 | 0.05 | 79.4 | 0.12 | 76.83 | 0.05 | 76.93 | 0.06 | 77.99 | 0.08 | 78.17 | 0.07 | 77.41 | 0.06 | 76.84 | 0.06 | 75.59 | 0.06 | 75.3 | 0.07 | 75.62 | 0.07 | 75.03 | 0.06 | 75.29 | 0.06 | 75.2 | 0.06 | 75.23 | 0.06 | 75.63 | 0.06 | 75.41 | 0.06 | 75.38 | 0.04 | 76.41 | 0.06 | 76.43 | 0.07 |  |  | 75.04 | 0.05 | 75.38 | 0.05 | 75.56 | 0.06 | 75.37 | 0.06 | 75.49 |  | 75.11 | 0.06 | 81.2 | 0.07 | 81.52 | 0.07 | 78.72 | 0.07 | 75.36 | 0.06 | 75.27 | 0.06 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 75.008 | 0.008 | 61.992 | 0.017 | 58.085 | 0.01 | 55.234 | 0.014 | 95.011 | 0.031 | 74.989 | 0.028 | 3047.8 | 2 | 2980 | 2 | 0.674 | 0.003 | -0.297 | 0.002 | 0.196 | 0.004 | 1.9022 | 0.0025 | 29.216 | 0 | 9119 | 21 | 1660 |  | 0 | 0 | 13.029 | 0.279 | 1.4525 | 13937.8436 | 235.9616 | 0 | 0 | 13937.8436 | 0.0087735 | 27.6027 | 56.6325 | 14.1001 | 13.1203 | 0.013909 | 38.1463 | 0.0087735 | 27.6027 | 0.0086007 | 23.2875 | 75.008 | 61.992 | 22.9334 | 65081.1755 | 61467.6498 | 7459 | 0.39117 | 60220.9323 | 56607.4066 | 6.6039 | 0.16708 | -4.6694 | -18.3755 | 52.9463 | 65081.1755 | 60145.0465 | 4936.129 | 0 | 65081.1755 | 100%
2 | T2-MF31-115C1-115C2-100A-95-CE | 75T0039 | T2-MF31-115C1-115C2-100A-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 5 | 10/8/2014 | 20:33:46 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.36 lbs/CK2: 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 460.8 | 1.4 | 15.6 | 0 | 60962 | 75 | 60223 | 434 | 8434 | 140 | 69404 | 160 | 7.8591 | 948 |  |  | 6.9032 | [35 empty] | MF31, 115% charge CK1 and CK2, 100% airflow (400 cfm/ton), closed damper,--2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), adjust code tester speed--to match total static of run T2-MFBASE-3000-95-C-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 3 turns open: AX 35 belt: 100% inlet-outlet Meriam | 74.994 | 0.007 | 62 | 0.02 | 94.982 | 0.02 | 75.008 | 0.016 | 74.77 | 0.14 | 56.81 | 0.08 | 60.37 | 0.01 | 0.26 | 0.003 | 1.3014 | 0.0026 | 60962 | 75 | 8434 | 140 | 7.859 | 0.026 | [6 empty] | 460.8 | 2.6 | 461.3 | 2.6 | 459.3 | 2.6 | 15.6 | 0.1 | 13.4 | 0 | 13 | 0 | 7078.9 | 53.5 | 3164.8 | 61.7 | 1752.5 | 40.1 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 5.2 |  | 4.9 |  | 4.5 |  | 3220 |  | 0.83 | 460 | 460 | 460 | 5.2 | 4.8 | 4.5 | 3160 | 0.82 | 459.8 |  | 1.6 |  | 700.3 |  | 85 |  | 8825.3 | [14 empty] | 229.37 | 0.18 | 100.37 | 0.09 | 110.84 | 0.06 | 10.47 | 0.1 | 251.48 | 0.14 | 173.95 | 0.31 | 117.48 | 0.04 | 56.46 | 0.34 | 222.6 | 0.05 | 99.19 | 0.08 | 108.72 | 0.05 | 9.55 | 0.05 | 75.77 | 0.13 | 48.71 | 0.72 | 44.62 | 0.08 | 4.1 | 0.79 | 75.13 | 0.13 | 54.8 | 0.69 | 44.21 | 0.08 | 10.6 | 0.76 | [46 empty] | 263.19 | 0.14 | 177.09 | 0.3 | 120.83 | 0.04 | 56.26 | 0.32 | 247.19 | 0.28 | 116.22 | 0.08 | 17.55 | 0.09 | 236.7 | 0.05 | 92.67 | 0.05 | 113.1 | 0.05 | 20.43 | 0.05 | 78.24 | 0.17 | 46.2 | 0.11 | 3.67 | 1.15 | 77.9 | 0.16 | 56.27 | 0.6 | 45.98 | 0.1 | 10.29 | 0.6 | 98.18 | 0.06 | [28 empty] | 100.54 | 0.09 | 100.41 | 0.08 | 98.18 | 0.06 | 98.45 | 0.09 | 56.28 | 0.07 | 56.91 | 0.07 | 56.76 | 0.06 | 56.49 | 0.05 | 56.54 | 0.04 |  |  | 99.91 | 0.08 | 97.73 | 0.08 | 49.62 | 1.07 | 54.37 | 0.79 | 177.07 | 0.36 | 96.06 | 0.06 | 92.39 | 0.04 | 50.12 | 1.18 | 58.37 | 0.6 | 99.19 | 0.08 | 98.67 | 0.05 | 93.2 | 0.11 | 100.95 | 0.09 | 101.04 | 0.1 | 99.35 | 0.04 | 99.55 | 0.05 | 100.41 | 0.08 | 98.45 | 0.09 | [16 empty] | 100.37 | 0.09 | 98.67 | 0.05 | 100.54 | 0.09 | 98.18 | 0.06 | [16 empty] | 49.86 | 1.07 | [12 empty] | 174.99 | 0.38 | 95.61 | 0.06 | 95.31 | 0.06 | 75.15 | 0.05 | 75.5 | 0.05 | 75.05 | 0.05 | 75.65 | 0.06 | 75.51 | 0.05 | 75.6 | 0.06 | 75.4 | 0.07 | 78.82 | 0.08 | 76.93 | 0.06 | 76.98 | 0.06 | 77.94 | 0.1 | 78.14 | 0.09 | 77.47 | 0.06 | 76.79 | 0.07 | 75.55 | 0.07 | 75.31 | 0.07 | 75.56 | 0.08 | 75.04 | 0.07 | 75.17 | 0.08 | 75.1 | 0.08 | 75.21 | 0.07 | 76.59 | 0.07 | 75.27 | 0.09 | 75.53 | 0.06 | 79.69 | 0.12 | 79.46 | 0.16 |  |  | 75.06 | 0.06 | 75.4 | 0.05 | 75.57 | 0.07 | 75.36 | 0.07 | 75.47 |  | 75.08 | 0.07 | 81 | 0.06 | 81.14 | 0.06 | 78.72 | 0.08 | 75.36 | 0.08 | 75.16 | 0.08 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.994 | 0.007 | 62 | 0.02 | 56.82 | 0.01 | 54.288 | 0.016 | 94.982 | 0.02 | 75.008 | 0.016 | 3053.1 | 3.1 | 3001.4 | 3.1 | 0.666 | 0.003 | -0.306 | 0.002 | 0.26 | 0.003 | 1.3014 | 0.0026 | 29.304 | 0 | 8831 | 22 | 1660 |  | 0 | 0 | 13.029 | 0.279 | 1.4474 | 13998.2981 | 234.8352 | 0 | 0 | 13998.2981 | 0.008782 | 27.6087 | 55.3726 | 14.0995 | 13.0863 | 0.013932 | 38.1652 | 0.008782 | 27.6087 | 0.0083578 | 22.7153 | 74.994 | 62 | 22.3626 | 73437.3053 | 65919.8791 | 7171 | 0.33327 | 68573.2178 | 61055.7917 | 7.7651 | 0.14423 | -5.2462 | -19.6214 | 52.0656 | 73437.3053 | 68499.4566 | 4937.8487 | 0 | 73437.3053 | 100%
2 | T2-MF33-85C1-85C2-100A-95-CE | 75T0040 | T2-MF33-85C1-85C2-100A-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 5 | 10/8/2014 | 22:09:37 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.44 lbs/CK2: 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 461 | 1.4 | 15.3 | 0 | 57585 | 91 | 56745 | 342 | 5328 | 138 | 62919 | 167 | 7.365 | 948 | [38 empty] | MF33, 85% charge CK1 and CK2, 100% airflow (400 cfm/ton), 2 HP fan motor,--3 turns, 5.75" AK59 pulley (939 rpm), adjust code tester speed to match total--static of run T2-MFBASE-3000-95-C-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 3 turns open: AX 35 belt: 100% inlet-outlet Meriam | 75.041 | 0.009 | 61.995 | 0.021 | 95.003 | 0.016 | 75.003 | 0.013 | 74.88 | 0.13 | 57.85 | 0.1 | 61.12 | 0.02 | 0.232 | 0.003 | 1.2897 | 0.0027 | 57585 | 91 | 5328 | 138 | 7.365 | 0.027 | [6 empty] | 461 | 2.8 | 461.3 | 2.8 | 458.9 | 2.7 | 15.3 | 0.1 | 13.1 | 0 | 12.7 | 0.1 | 6942.7 | 56.8 | 3117.5 | 66.2 | 1600 | 42.5 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.7 |  | 4.4 |  | 3130 |  | 0.83 | 460 | 460 | 460 | 5 | 4.5 | 4.3 | 2980 | 0.81 | 460.1 |  | 1.6 |  | 702.4 |  | 85 |  | 8527.4 | [14 empty] | 211.29 | 0.13 | 104.78 | 0.11 | 105.08 | 0.04 | 0.3 | 0.1 | 243.39 | 0.13 | 189.3 | 0.23 | 115.11 | 0.04 | 74.2 | 0.23 | 199.7 | 0.05 | 100.74 | 0.05 | 101.2 | 0.05 | 0.42 | 0.05 | 72.13 | 0.05 | 68.34 | 0.09 | 42.23 | 0.04 | 26.11 | 0.07 | 71.52 | 0.05 | 70.64 | 0.09 | 41.82 | 0.04 | 28.81 | 0.06 | [46 empty] | 246.64 | 0.13 | 170.96 | 0.06 | 116.07 | 0.04 | 54.89 | 0.05 | 223.28 | 0.2 | 108.94 | 0.06 | 8.56 | 0.08 | 212 | 0.05 | 108.21 | 0.08 | 105.31 | 0.05 | -2.93 | 0.05 | 78.7 | 0.04 | 46.5 | 0.02 | 3.94 | 0.22 | 78.35 | 0.04 | 71.58 | 0.1 | 46.28 | 0.02 | 25.3 | 0.11 | 102.69 | 0.09 | [28 empty] | 103.28 | 0.1 | 102.69 | 0.09 | 106.81 | 0.07 | 106.86 | 0.11 | 57.3 | 0.09 | 57.94 | 0.07 | 57.77 | 0.06 | 57.49 | 0.05 | 57.55 | 0.04 |  |  | 103.33 | 0.04 | 99.3 | 0.1 | 68.8 | 0.14 | 70.28 | 0.13 | 171.01 | 0.07 | 104.06 | 0.05 | 99.73 | 0.05 | 50.31 | 0.25 | 59.82 | 0.07 | 100.74 | 0.05 | 108.21 | 0.08 | 93.46 | 0.1 | 104.68 | 0.06 | 103.16 | 0.04 | 107.78 | 0.04 | 107.58 | 0.05 | 106.81 | 0.07 | 106.86 | 0.11 | [16 empty] | 104.78 | 0.11 | 100.38 | 0.08 | 103.28 | 0.1 | 102.69 | 0.09 | [16 empty] | 50.44 | 0.22 | [12 empty] | 190.48 | 0.24 | 95.53 | 0.06 | 95.23 | 0.07 | 75.18 | 0.05 | 75.52 | 0.05 | 75.05 | 0.05 | 75.65 | 0.06 | 75.52 | 0.05 | 75.61 | 0.06 | 75.42 | 0.06 | 78.96 | 0.07 | 76.98 | 0.05 | 77.06 | 0.05 | 78.08 | 0.09 | 78.31 | 0.07 | 77.63 | 0.06 | 76.9 | 0.06 | 75.59 | 0.06 | 75.37 | 0.06 | 75.65 | 0.07 | 75.08 | 0.06 | 75.25 | 0.06 | 75.16 | 0.06 | 75.3 | 0.08 | 76.68 | 0.07 | 75.33 | 0.07 | 75.76 | 0.06 | 79.94 | 0.13 | 79.55 | 0.13 |  |  | 75.06 | 0.05 | 75.4 | 0.04 | 75.56 | 0.05 | 75.36 | 0.06 | 75.47 |  | 75.07 | 0.05 | 81.08 | 0.05 | 80.79 | 0.15 | 78.88 | 0.06 | 75.39 | 0.06 | 75.22 | 0.06 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 75.041 | 0.009 | 61.995 | 0.021 | 57.759 | 0.018 | 55.009 | 0.016 | 95.003 | 0.016 | 75.003 | 0.013 | 3040.8 | 3.2 | 2985.5 | 3.2 | 0.672 | 0.003 | -0.295 | 0.002 | 0.232 | 0.003 | 1.2897 | 0.0027 | 29.32 | 0.001 | 8543 | 21 | 1630 |  | 0 | 0 | 13.029 | 0.279 | 1.4245 | 13915.0292 | 235.6956 | 0 | 0 | 13915.0292 | 0.0087676 | 27.6044 | 56.3345 | 14.1 | 13.1116 | 0.013923 | 38.16 | 0.0087676 | 27.6044 | 0.008548 | 23.1508 | 75.041 | 61.995 | 22.8035 | 66805.664 | 62472.4551 | 6913 | 0.35317 | 62046.903 | 57713.6941 | 7.2629 | 0.16045 | -4.801 | -18.7065 | 52.7594 | 66805.664 | 61973.0657 | 4832.5983 | 0 | 66805.664 | 100%
2 | T2-MFB1-100C1-100C2-100A-95-CE | 75T0047 | T2-MFB1-100C1-100C2-100A-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 5 | 10/7/2014 | 20:32:40 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs CK2- 6.20 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.2 | 15.4 | 0 | 59712 | 76 | 59086 | 398 | 8060 | 122 | 67779 | 127 | 7.8584 | 949 |  |  | 6.9231 | [35 empty] | MFB1, 100% charge CK1 and CK2, 100% rated airflow (400 cfm/ton), closed damper,--2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), adjust code tester speed to match total static--of run T2-MFB1-100C1-100C2-100A-95-CE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 3 turns open: 100% inlet-outlet Meriam | 75 | 0.013 | 61.994 | 0.015 | 95.103 | 0.05 | 75.006 | 0.024 | 74.84 | 0.12 | 57.02 | 0.07 | 60.39 | 0.01 | 0.263 | 0.003 | 1.276 | 0.0025 | 59712 | 76 | 8060 | 122 | 7.858 | 0.024 | [6 empty] | 460.8 | 2.4 | 461.2 | 2.4 | 459.2 | 2.4 | 15.4 | 0.1 | 13.2 | 0 | 12.9 | 0 | 6995.2 | 50.1 | 3190.2 | 59.9 | 1630 | 39.1 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.8 |  | 4.4 |  | 3150 |  | 0.82 | 460 | 460 | 460 | 5 | 4.6 | 4.4 | 3040 | 0.82 | 459.8 |  | 1.6 |  | 702.9 |  | 85 |  | 8617.9 | [14 empty] | 219.27 | 0.15 | 107.15 | 0.1 | 107.65 | 0.05 | 0.5 | 0.08 | 248.58 | 0.16 | 173.95 | 0.06 | 116.62 | 0.05 | 57.33 | 0.05 | 211.8 | 0.05 | 104.3 | 0.06 | 105.29 | 0.05 | 0.99 | 0.05 | 76.26 | 0.04 | 50.99 | 0.32 | 44.91 | 0.03 | 6.09 | 0.32 | 75.62 | 0.04 | 56.96 | 0.11 | 44.49 | 0.02 | 12.46 | 0.1 | [46 empty] | 251.69 | 0.18 | 172.56 | 0.26 | 117.53 | 0.05 | 55.03 | 0.29 | 234.91 | 0.35 | 112.55 | 0.11 | 11.5 | 0.11 | 224.7 | 0.05 | 94.96 | 0.07 | 109.39 | 0.05 | 14.43 | 0.05 | 78.04 | 0.17 | 46.05 | 0.11 | 3.78 | 1.02 | 77.7 | 0.14 | 58.36 | 0.1 | 45.83 | 0.09 | 12.53 | 0.13 | 100.7 | 0.09 | [28 empty] | 106.46 | 0.09 | 105.9 | 0.08 | 100.7 | 0.09 | 100.95 | 0.1 | 56.44 | 0.06 | 57.02 | 0.04 | 56.88 | 0.04 | 56.68 | 0.03 | 56.73 | 0.03 |  |  | 105.76 | 0.06 | 103.56 | 0.08 | 52.07 | 0.41 | 56.69 | 0.12 | 172.6 | 0.32 | 98.36 | 0.08 | 94.46 | 0.04 | 49.94 | 1.02 | 58.76 | 0.52 | 104.3 | 0.06 | 101.05 | 0.08 | 92.49 | 0.16 | 107.01 | 0.07 | 106.54 | 0.06 | 101.63 | 0.05 | 101.71 | 0.05 | 105.9 | 0.08 | 100.95 | 0.1 | [16 empty] | 107.15 | 0.1 | 101.05 | 0.08 | 106.46 | 0.09 | 100.7 | 0.09 | [16 empty] | 49.85 | 0.93 | [12 empty] | 174.96 | 0.08 | 95.04 | 0.1 | 95.02 | 0.11 | 75.22 | 0.05 | 75.53 | 0.05 | 75.06 | 0.05 | 75.72 | 0.06 | 75.56 | 0.05 | 75.64 | 0.06 | 75.44 | 0.07 | 78.48 | 0.08 | 76.87 | 0.06 | 77 | 0.06 | 77.75 | 0.09 | 78.03 | 0.08 | 77.41 | 0.07 | 76.76 | 0.06 | 75.47 | 0.07 |  |  | 75.44 | 0.08 | 74.98 | 0.07 | 75.19 | 0.07 | 75.14 | 0.07 | 75.23 | 0.07 | 76.71 | 0.07 | 75.31 | 0.07 | 75.68 | 0.05 | 80.32 | 0.13 | 80.12 | 0.17 |  |  | 75.06 | 0.06 | 75.34 | 0.06 | 75.52 | 0.07 | 75.32 | 0.07 | 75.4 |  | 75.08 | 0.07 | 80.37 | 0.07 | 80.61 | 0.07 | 78.59 | 0.08 | 75.3 | 0.07 | 75.2 | 0.07 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 75 | 0.013 | 61.994 | 0.015 | 56.989 | 0.007 | 54.396 | 0.012 | 95.103 | 0.05 | 75.006 | 0.024 | 3027.7 | 3 | 2967.1 | 2.9 | 0.67 | 0.003 | -0.299 | 0.002 | 0.263 | 0.003 | 1.276 | 0.0025 | 29.216 | 0.001 | 8625 | 20 | 1640 |  | 0 | 0 | 13.029 | 0.279 | 1.4409 | 13877.1229 | 233.5458 | 0 | 0 | 13877.1229 | 0.0087767 | 27.6043 | 55.5481 | 14.1024 | 13.0908 | 0.013901 | 38.1611 | 0.0087767 | 27.6043 | 0.0083793 | 22.7798 | 75 | 61.994 | 22.4286 | 71823.9282 | 64784.6284 | 6985 | 0.33192 | 67023.7001 | 59984.4002 | 7.7709 | 0.14909 | -5.1757 | -19.4519 | 52.1398 | 71823.9282 | 66950.717 | 4873.2112 | 0 | 71823.9282 | 100%
2 | T2-HS-3000-95-CF-C | 75T0152 | T2-HS-3000-95+CF-1.5T-8575M-C | closed | on | on | 1.5 turns | unsealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 7/31/2014 | 1:51:56 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 1.1 | 15.9 | 0 | 55839 | 122 | 57328 | 361 | 5400 | 485 | 61244 | 477 | 6.4576 | 1144 |  |  | 5.8877 | 109.31 | 0.09 | 28.88 | [32 empty] | 100% airflow (400 cfm/ton), factory charge, closed damper, 3 HP fan motor,--1.5 turns, 5.75" pulley, 95F Test, adjust code tester speed to match total static of run T2-3000-95+CF-1.5T-8575M-C-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: AK59H BP: ID Blw M: MQC 56T17D5563B: Mtr Pulley 1.5 T/O: With econo: Supply Meriam @85% Return Meriam @75%: Horiz Air Disch: Max Mtr Amp 4.7 | 75.038 | 0.016 | 61.966 | 0.09 | 94.852 | 0.017 | 74.997 | 0.014 | 75.23 | 0.11 | 58.16 | 0.09 | 60.74 | 0.03 | 0.25 | 0.004 | 1.3109 | 0.0033 | 55839 | 122 | 5400 | 485 | 6.458 | 0.051 | 86121 | 213 | 9.08 | 0.027 | 28.88 | 0.44 | 459.7 | 2.4 | 460.1 | 2.4 | 460 | 2.4 | 15.9 | 0.1 | 14.1 | 0 | 13.8 | 0.1 | 7248.2 | 61.8 | 3248.4 | 65 | 2236 | 54.1 | 460 |  | 460 |  | 460 |  | 3.8 |  | 3.7 |  | 3.7 |  | 0.71 | 460 |  | 460 |  | 460 |  | 5.1 |  | 5 |  | 4.5 |  | 3180 |  | 0.82 | 460 | 460 | 460 | 5 | 4.7 | 4.5 | 3050 | 0.82 | 458.6 |  | 1.6 |  | 702.4 |  | 115 |  | 9477.4 | [14 empty] | 221.95 | 0.12 | 107.6 | 0.07 | 108.52 | 0.04 | 0.91 | 0.05 | 249.13 | 0.17 | 176.59 | 0.26 | 116.8 | 0.05 | -59.79 | 0.24 | 211.9 | 0.05 | 101.07 | 0.52 | 105.27 | 0.05 | 4.02 | 0.52 | 75.62 | 0.14 | 48.29 | 0.5 | 44.53 | 0.09 | 3.76 | 0.47 | 75.07 | 0.13 | 56.83 | 0.44 | 44.17 | 0.08 | 12.67 | 0.4 | 644.69 | 1.2 |  | 0.16 | 86121 | 213 | 44804 | 152 | [38 empty] | 251.68 | 0.2 | 171.52 | 0.23 | 117.54 | 0.06 | 53.98 | 0.24 | 233.53 | 0.19 | 112.19 | 0.05 | 10.23 | 0.05 | 221.83 | 0.05 | 99.53 | 0.08 | 108.48 | 0.06 | 8.88 | 0.08 | 79.25 | 0.16 | 46.85 | 0.1 | 2.4 | 0.35 | 78.87 | 0.17 | 56.81 | 0.46 | 46.61 | 0.1 | 10.21 | 0.47 | 105.89 | 0.04 | 643.58 | 1.79 | 39.33 | 0.03 | 109.26 | 0.06 | 86121 | 213 | 45001 | 101 | [18 empty] | 106.47 | 0.06 | 105.89 | 0.04 | 101.42 | 0.08 | 101.59 | 0.08 | 58.51 | 0.09 | 58.29 | 0.09 |  |  | 58.73 | 0.09 | 58.69 | 0.09 | 58.53 | 0.09 | 107.23 | 0.1 | 101.93 | 0.04 | 50.03 | 0.62 | 56.42 | 0.52 | 170.4 | 0.19 | 101.44 | 0.06 | 101.11 | 0.08 | 49.85 | 0.13 | 56.84 | 0.71 |  |  |  |  | 92.94 | 0.06 | [8 empty] | 101.42 | 0.08 | 101.59 | 0.08 | [14 empty] | 58.53 | 0.09 | 107.6 | 0.07 | 101.91 | 0.09 | 106.47 | 0.06 | 105.89 | 0.04 | [16 empty] | 49.24 | 0.31 | [12 empty] | 175.73 | 0.25 | 94.15 | 0.14 | 94.3 | 0.13 | 76 | 0.12 | 75.8 | 0.13 | 75.52 | 0.12 | 76.37 | 0.11 | 76.36 | 0.11 | 76.24 | 0.12 | 76.06 | 0.11 | 81.09 | 0.11 | 80.53 | 0.11 | 77.81 | 0.12 | 78.91 | 0.46 | 80.13 | 0.21 | 79.74 | 0.16 | 78.79 | 0.2 | 76.54 | 0.11 | 76.16 | 0.12 | 76.42 | 0.15 | 75.68 | 0.09 | 75.36 | 0.13 | 75.33 | 0.14 | 75.69 | 0.15 | 75.46 | 0.12 | 75.52 | 0.1 | 75.5 | 0.1 | 75.77 | 0.1 | 76.19 | 0.11 |  |  | 75.65 | 0.09 | 76.43 | 0.15 | 76.11 | 0.13 | 75.87 | 0.13 | 75.7 |  | 75.57 | 0.15 | 82.27 | 0.16 | 82.43 | 0.13 | 79.71 | 0.2 | 75.99 | 0.11 | 75.35 | 0.12 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 75.038 | 0.016 | 61.966 | 0.09 | 58.41 | 0.043 | 55.248 | 0.069 | 94.852 | 0.017 | 74.997 | 0.014 | 3064.5 | 3.9 | 3011.7 | 3.8 | 1.084 | 0.003 | -0.466 | 0.003 | 0.25 | 0.004 | 1.3109 | 0.0033 | 29.325 | 0.004 | 9484 | 20 | 2430 |  | 0 | 0 | 13.029 | 0.279 | 2.0772 | 14005.9948 | 383.536 | 0 | 0 | 14005.9948 | 0.0087492 | 27.5836 | 56.3328 | 14.0964 | 13.1279 | 0.013954 | 38.1569 | 0.0087492 | 27.5836 | 0.008532 | 23.2921 | 75.038 | 61.966 | 22.7857 | 67199.3384 | 62876.539 | 7054 | 0.35827 | 60214.7566 | 55891.9573 | 6.3491 | 0.16229 | -4.7979 | -18.7052 | 52.7091 | 67199.3384 | 60106.59 | 7092.7484 | 0 | 67199.3384 | 100%
2 | T2-3000-95-CF | 75T0157 | T2-3000-95-CF | closed | on | on | 3 turns | unsealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 7/30/2014 | 12:11:54 | 10 Ton | 0:05:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 1.5 | 15.1 | 0 | 57015 | 213 | 59693 | 478 | 8928 | 699 | 65953 | 580 | 7.629 | 939 |  |  |  | 109.25 | 0.04 | 23.09 | [32 empty] | 100% airflow, 2 HP fan motor, 3 turns, 5.75" pulley, both stages, closed damper | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: AK59 5.75 diam BP: ID Blw M: MQC 56T17D5563B: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch | 74.52 | 0.134 | 62.065 | 0.077 | 95.008 | 0.047 | 75 | 0.013 | 75.14 | 0.21 | 56.79 | 0.13 | 59.75 | 0.04 | 0.208 | 0.004 | 1.2213 | 0.0028 | 57015 | 213 | 8928 | 699 | 7.631 | 0.067 | 85783 | 139 | 9.923 | 0.026 | 23.09 | 0.64 | 459.7 | 2.6 | 460.5 | 2.6 | 460.3 | 2.6 | 15.1 | 0.1 | 13.2 | 0 | 13.2 | 0.1 | 6870.5 | 66.8 | 3328.2 | 77.1 | 1774.4 | 57.2 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.57 | 458 |  | 460 |  | 459 |  | 50.2 |  | 5 |  | 4.5 |  | 3180 |  | 0.82 | 460 | 460 | 460 | 5 | 4.7 | 4.5 | 3050 | 0.82 | 458.8 |  | 1.6 |  | 702.5 |  | 115 |  | 8637.5 | [14 empty] | 222.31 | 0.36 | 107.6 | 0.1 |  |  |  |  | 249.09 | 0.31 | 177 | 0.27 | 116.8 | 0.09 | -60.2 | 0.19 |  |  | 101.53 | 0.35 | 108.64 | 0.11 | 7.12 | 0.29 | 75.14 | 0.06 | 47.77 | 0.22 | 44.24 | 0.03 | 3.53 | 0.2 | 74.57 | 0.05 | 56.89 | 0.29 | 43.87 | 0.03 | 13.02 | 0.26 | 643.26 | 0.94 |  | 0.11 | 85783 | 139 | 44571 | 92 | [38 empty] | 251.12 | 0.35 | 168.97 | 0.3 | 117.39 | 0.1 | 51.57 | 0.39 | 232.68 | 0.27 | [6 empty] | 100.08 | 0.12 | 111.88 | 0.08 | 11.8 | 0.11 | 78.5 | 0.14 | 46.4 | 0.09 | 2.47 | 0.32 | 78.11 | 0.14 | 55.96 | 0.46 | 46.15 | 0.09 | 9.82 | 0.51 | 106.08 | 0.11 | 643.83 | 1.71 | 39.5 | 0.04 | 109.23 | 0.06 | 85783 | 139 | 44894 | 102 | [18 empty] | 106.8 | 0.13 | 106.08 | 0.11 | 101.83 | 0.14 | 102.07 | 0.11 | 57.35 | 0.06 | 57.08 | 0.07 | 56.71 | 0.1 | 57.5 | 0.04 | 57.26 | 0.05 | 57.39 | 0.05 | 107.07 | 0.09 | 101.9 | 0.06 | 49.27 | 0.29 | 56.19 | 0.33 | 167.59 | 0.4 | 101.92 | 0.12 | 101.54 | 0.16 | 49.37 | 0.13 | 55.8 | 0.67 |  |  |  |  | 93.39 | 0.11 | [8 empty] | 101.83 | 0.14 | 102.07 | 0.11 | [12 empty] | 101.53 | 0.35 | 57.39 | 0.05 | 107.6 | 0.1 | 102.41 | 0.16 | 106.8 | 0.13 | 106.08 | 0.11 | [16 empty] | 48.87 | 0.28 | [12 empty] | 176.07 | 0.35 | 94.14 | 0.1 | 94.29 | 0.09 | 75.69 | 0.22 | 75.45 | 0.21 | 75.25 | 0.2 | 75.93 | 0.21 | 75.98 | 0.22 | 75.87 | 0.23 | 75.66 | 0.23 | 79.87 | 0.13 | 79.27 | 0.12 | 78.2 | 0.12 | 76.03 | 0.17 | 77.52 | 0.19 | 77.6 | 0.18 | 77.02 | 0.2 | 75.77 | 0.21 | 75.59 | 0.2 | 75.37 | 0.2 | 75.3 | 0.19 | 75.41 | 0.22 | 75.37 | 0.22 | 76.23 | 0.24 | 75.53 | 0.25 | 75.64 | 0.18 | 75.62 | 0.18 | 76.43 | 0.17 | 76.52 | 0.19 |  |  | 75.21 | 0.2 | 76.1 | 0.2 | 75.81 | 0.2 | 75.55 | 0.2 | 75.42 |  | 75.35 | 0.19 | 83.91 | 0.11 | 82.14 | 0.16 | 76.93 | 0.17 | 75.66 | 0.2 | 75.42 | 0.21 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.52 | 0.134 | 62.065 | 0.077 | 56.994 | 0.116 | 54.509 | 0.066 | 95.008 | 0.047 | 75 | 0.013 | 2950.7 | 3.3 | 2912.9 | 3.5 | 0.608 | 0.003 | -0.287 | 0.002 | 0.208 | 0.004 | 1.2213 | 0.0028 | 29.399 | 0 | 8645 | 20 | 1590 |  | 0 | 0 | 13.029 | 0.279 | 1.4528 | 13523.5635 | 208.0627 | 0 | 0 | 13523.5635 | 0.008937 | 27.6626 | 55.5412 | 14.1001 | 13.0914 | 0.013919 | 38.157 | 0.008937 | 27.6626 | 0.0084424 | 22.8496 | 74.52 | 62.065 | 22.4955 | 69878.2768 | 61598.5236 | 7055 | 0.34458 | 65161.7249 | 56881.9716 | 7.5375 | 0.14617 | -5.1671 | -18.9788 | 52.2922 | 69878.2768 | 65089.4633 | 4788.8135 | 0 | 69878.2768 | 100%
2 | T2-R-3000-115-CE | 75T0167 | T2-R-3000-115-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/16/2014 | 1:44:58 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 115 | 80 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1 | 16.8 | 0 | 45413 | 60 | 45304 | 438 | 2445 | 242 | 47860 | 256 | 4.7575 | 949 | [38 empty] | Restriction 115F OAT (leave restriction from run T2-R-3000-95-CE only move outdoor room conditions),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), Econo closed unsealed cab,--adjust code tester speed to match total static of run T2-C-3000-95-CE-S | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .; | 74.882 | 0.006 | 62.119 | 0.049 | 114.952 | 0.017 | 80.008 | 0.023 | 74.82 | 0.14 | 61.04 | 0.04 | 63.09 | 0.02 | 0.272 | 0.005 | 1.2731 | 0.0034 | 45413 | 60 | 2445 | 242 | 4.758 | 0.027 | [6 empty] | 460.8 | 2.5 | 460.6 | 2.5 | 459.2 | 2.5 | 16.8 | 0.1 | 14.9 | 0 | 14.5 | 0.1 | 7714.8 | 66.9 | 3334.8 | 69 | 2345.1 | 58.6 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.9 |  | 5.7 |  | 5.3 |  | 3820 |  | 0.85 | 460 | 460 | 460 | 5.8 | 5.4 | 5.3 | 3790 | 0.85 | 459.9 |  | 1.6 |  | 683.3 |  | 85 |  | 10008.3 | [14 empty] | 290.06 | 0.25 | 116.08 | 0.1 | 128.14 | 0.06 | 12.06 | 0.08 | 301.96 | 0.27 | 242.02 | 0.07 | 131.22 | 0.07 | 110.8 | 0.06 | 177.13 | 0.05 | 89.37 | 0.06 | 93.17 | 0.05 | 3.74 | 0.05 | 63.88 | 0.04 | 71.83 | 0.04 | 36.47 | 0.03 | 35.35 | 0.04 | 63.5 | 0.05 | 76.56 | 0.04 | 36.2 | 0.03 | 40.37 | 0.05 | [46 empty] | 311.72 | 0.27 | 194.7 | 0.2 | 133.69 | 0.06 | 61.02 | 0.2 | 295.56 | 0.35 | 129.57 | 0.09 | 11.97 | 0.11 | 283.17 | 0.05 | 116.05 | 0.12 | 126.31 | 0.05 | 10.22 | 0.05 | 80.88 | 0.13 | 47.84 | 0.08 | 2.87 | 0.36 | 80.06 | 0.14 | 59.3 | 0.42 | 47.33 | 0.09 | 11.97 | 0.43 | 95.16 | 0.07 | [28 empty] | 96.23 | 0.07 | 95.16 | 0.07 | 117.5 | 0.13 | 117.77 | 0.13 | 61.18 | 0.05 | 60.91 | 0.04 |  |  | 61.3 | 0.05 | 61.24 | 0.04 | 61.13 | 0.04 | 116.18 | 0.07 | 90.67 | 0.08 | 72.33 | 0.06 | 76.79 | 0.05 | 191.61 | 0.22 | 118.14 | 0.13 | 116.43 | 0.12 | 51.21 | 0.07 | 60.93 | 0.83 | 89.37 | 0.06 | 116.05 | 0.12 | 114.41 | 0.04 | 116.69 | 0.07 | 96.27 | 0.06 | 117.87 | 0.1 | 118.78 | 0.08 | 117.5 | 0.13 | 117.77 | 0.13 | [12 empty] | 116.08 | 0.1 | 61.13 | 0.04 |  |  | 117.6 | 0.13 | 96.23 | 0.07 | 95.16 | 0.07 | [16 empty] | 50.7 | 0.3 | [12 empty] | 243.67 | 0.08 | 114.61 | 0.16 | 114.87 | 0.15 | 75.47 | 0.07 | 75.27 | 0.07 | 75.08 | 0.06 | 75.78 | 0.05 | 75.79 | 0.07 | 75.7 | 0.08 | 75.49 | 0.08 | 88.06 | 0.17 | 89.52 | 0.31 | 82.05 | 0.13 | 78.85 | 0.11 | 81.42 | 0.11 | 80.91 | 0.11 | 79.5 | 0.09 | 80.65 | 0.1 | 78.76 | 0.1 | 80.63 | 0.12 | 75.5 | 0.09 | 75.38 | 0.08 | 75.42 | 0.09 | 76.74 | 0.09 | 76.36 | 0.08 | 75.57 | 0.07 | 75.66 | 0.05 |  |  | 82.75 | 0.35 |  |  | 75.11 | 0.07 | 75.7 | 0.06 | 75.48 | 0.07 | 75.27 | 0.08 | 75.14 |  | 75.05 | 0.07 | 85.1 | 1.03 | 86.78 | 0.14 | 80.8 | 0.11 | 75.65 | 0.09 | 75.33 | 0.08 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.882 | 0.006 | 62.119 | 0.049 | 61.068 | 0.013 | 56.851 | 0.033 | 114.952 | 0.017 | 80.008 | 0.023 | 3031 | 4.1 | 2955.1 | 4 | 0.653 | 0.003 | -0.288 | 0.002 | 0.272 | 0.005 | 1.2731 | 0.0034 | 29.239 | 0 | 10060 | 21 | 1630 |  | 0 | 0 | 13.029 | 0.279 | 1.4478 | 13779.6153 | 226.6994 | 0 | 0 | 13779.6153 | 0.0088871 | 27.6964 | 59.6202 | 14.6059 | 13.1978 | 0.013786 | 42.9194 | 0.0088871 | 27.6964 | 0.0088448 | 24.2805 | 74.882 | 62.119 | 23.9273 | 51935.9202 | 50472.4467 | 8430 | 0.55398 | 47146.4554 | 45682.982 | 4.6865 | 0.27777 | -3.769 | -15.2618 | 53.7504 | 51935.9202 | 47069.5123 | 4866.4079 | 0 | 51935.9202 | 100%
2 | T2-R-3000-75-CE | 75T0168 | T2-R-3000-75-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/16/2014 | 3:54:57 | 10 Ton | 0:15:07 | 75/62 75/62 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 75 | 62 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 0.9 | 13.8 | 0 | 57445 | 71 | 57432 | 511 | 14367 | 162 | 71825 | 151 | 10.1706 | 949 | [38 empty] | Restriction 75F OAT (leave restriction from run T2-R-3000-95-CE only move outdoor room conditions),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), Econo closed unsealed cab,--adjust code tester speed to match total static of run T2-C-3000-95-CE-SP | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .; | 74.899 | 0.018 | 62.105 | 0.023 | 74.904 | 0.023 | 61.904 | 0.018 | 74.69 | 0.15 | 57.44 | 0.04 | 60.14 | 0.01 | 0.279 | 0.004 | 1.2819 | 0.0025 | 57445 | 71 | 14367 | 162 | 10.17 | 0.036 | [6 empty] | 460.9 | 2.3 | 460.7 | 2.3 | 459.2 | 2.2 | 13.8 | 0.1 | 11.6 | 0 | 11.3 | 0.1 | 6144.4 | 67.8 | 3134.3 | 66.5 | 918.2 | 57.2 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.2 |  | 4 |  | 3.6 |  | 2350 |  | 0.75 | 460 | 460 | 460 | 4.2 | 3.8 | 3.7 | 2300 | 0.75 | 460 |  | 1.7 |  | 717 |  | 85 |  | 7062 | [14 empty] | 163.37 | 0.14 | 76.88 | 0.07 | 87.93 | 0.05 | 11.04 | 0.06 | 172.18 | 0.15 | 192.95 | 0.08 | 91.31 | 0.05 | 101.63 | 0.07 | 100.7 | 0.05 | 60.07 | 0.06 | 59.31 | 0.05 | -0.76 | 0.05 | 44.8 | 0.05 | 69.29 | 0.04 | 21.23 | 0.05 | 48.07 | 0.04 | 44.52 | 0.06 | 72.59 | 0.04 | 20.97 | 0.05 | 51.62 | 0.06 | [46 empty] | 184.91 | 0.17 | 140.66 | 0.29 | 96 | 0.06 | 44.66 | 0.31 | 165.5 | 0.25 | 88.76 | 0.1 | 8.86 | 0.15 | 159.3 | 0.05 | 79.53 | 0.11 | 86.31 | 0.05 | 6.77 | 0.05 | 72.76 | 0.09 | 42.61 | 0.06 | 4.67 | 1.5 | 71.94 | 0.12 | 54.09 | 0.6 | 42.06 | 0.08 | 12.03 | 0.63 | 61.46 | 0.05 | [28 empty] | 62.4 | 0.07 | 61.46 | 0.05 | 79.87 | 0.11 | 80.19 | 0.12 | 57.31 | 0.04 | 57.25 | 0.05 |  |  | 57.46 | 0.04 | 57.63 | 0.04 | 57.62 | 0.04 | 77.05 | 0.05 | 59.8 | 0.08 | 69.84 | 0.06 | 72.52 | 0.04 | 137.88 | 0.3 | 80.45 | 0.11 | 80.05 | 0.11 | 46.95 | 0.64 | 55.4 | 0.76 | 60.07 | 0.06 | 79.53 | 0.11 | 74.01 | 0.07 | 77.46 | 0.05 | 62.74 | 0.05 | 80.31 | 0.12 | 81.36 | 0.08 | 79.87 | 0.11 | 80.19 | 0.12 | [12 empty] | 76.88 | 0.07 | 57.62 | 0.04 |  |  | 79.9 | 0.11 | 62.4 | 0.07 | 61.46 | 0.05 | [16 empty] | 47.27 | 1.46 | [12 empty] | 194.82 | 0.07 | 75.04 | 0.1 | 74.85 | 0.1 | 75.52 | 0.09 | 75.36 | 0.08 | 75.18 | 0.08 | 75.75 | 0.06 | 75.8 | 0.08 | 75.72 | 0.09 | 75.51 | 0.09 | 75.06 | 0.06 | 74.93 | 0.05 | 74.97 | 0.06 | 75.23 | 0.09 | 74.98 | 0.07 | 74.87 | 0.07 | 74.88 | 0.06 | 74.97 | 0.07 | 74.9 | 0.08 | 74.74 | 0.07 | 74.88 | 0.09 | 75.23 | 0.09 | 74.99 | 0.09 | 75.02 | 0.08 | 75 | 0.09 | 75.4 | 0.08 | 75.11 | 0.06 |  |  | 74.76 | 0.07 |  |  | 75.14 | 0.08 | 75.92 | 0.07 | 75.68 | 0.09 | 75.48 | 0.1 | 75.38 |  | 75.27 | 0.09 |  |  | 75.2 | 0.05 | 75.04 | 0.07 | 75.18 | 0.1 | 75.23 | 0.09 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.899 | 0.018 | 62.105 | 0.023 | 57.646 | 0.004 | 54.054 | 0.015 | 74.904 | 0.023 | 61.904 | 0.018 | 3033.2 | 2.9 | 2976.4 | 2.9 | 0.657 | 0.003 | -0.294 | 0.002 | 0.279 | 0.004 | 1.2819 | 0.0025 | 29.224 | 0 | 7062 | 20 | 1610 |  | 0 | 0 | 13.029 | 0.279 | 1.413 | 13887.5569 | 229.7321 | 0 | 0 | 13887.5569 | 0.0088738 | 27.686 | 56.233 | 13.5476 | 13.1047 | 0.0087401 | 27.5408 | 0.0088738 | 27.686 | 0.0080305 | 22.5609 | 74.899 | 62.105 | 22.2168 | 75953.8491 | 62213.9583 | 5452 | 0.24499 | 71242.995 | 57503.1042 | 10.0882 | 0.23981 | -5.4692 | -18.666 | 50.3445 | 75953.8491 | 71174.4094 | 4779.4397 | 0 | 75953.8491 | 100%
2 | T2-R-3000-95-CE | 75T0169 | T2-R-3000-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/16/2014 | 0:11:23 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 1.4 | 15 | 0 | 51341 | 66 | 51361 | 506 | 5557 | 142 | 56904 | 127 | 6.7542 | 949 | [38 empty] | Restriction 95F OAT (reduce SP by 50% from CK1 baseline T2-R-3000-95-CE),--2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm), Econo closed unsealed cab,--adjust code tester speed to match total static of run T2-C-3000-95-CE-SPWCT-SS | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .; | 74.905 | 0.015 | 62.204 | 0.03 | 95.001 | 0.01 | 75.002 | 0.017 | 74.77 | 0.16 | 59.22 | 0.04 | 61.62 | 0.02 | 0.278 | 0.003 | 1.2766 | 0.0029 | 51341 | 66 | 5557 | 142 | 6.754 | 0.023 | [6 empty] | 460.7 | 2.5 | 460.5 | 2.5 | 459.4 | 2.5 | 15 | 0.1 | 13.1 | 0 | 12.7 | 0.1 | 6817.4 | 61.7 | 3241.8 | 71.9 | 1607.6 | 51.8 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.5 |  | 4.7 |  | 4.3 |  | 3050 |  | 0.84 | 460 | 460 | 460 | 4.9 | 4.5 | 4.4 | 2970 | 0.8 | 459.8 |  | 1.6 |  | 697.7 |  | 85 |  | 8422.7 | [14 empty] | 222.99 | 0.24 | 96.94 | 0.11 | 108.84 | 0.07 | 11.89 | 0.09 | 233.31 | 0.25 | 216.32 | 0.09 | 112.05 | 0.07 | 104.26 | 0.09 | 136.9 | 0.05 | 75.62 | 0.05 | 76.94 | 0.05 | 1.31 | 0.05 | 54.41 | 0.03 | 70.75 | 0.05 | 29.31 | 0.03 | 41.44 | 0.05 | 54.06 | 0.04 | 74.82 | 0.04 | 29.03 | 0.03 | 45.79 | 0.05 | [46 empty] | 244.51 | 0.25 | 166.74 | 0.28 | 115.43 | 0.07 | 51.32 | 0.3 | 227.04 | 0.39 | 110.11 | 0.12 | 10.88 | 0.14 | 217.17 | 0.05 | 98.34 | 0.12 | 106.98 | 0.05 | 8.67 | 0.05 | 77.87 | 0.19 | 45.94 | 0.12 | 3.36 | 0.91 | 77.01 | 0.19 | 57.44 | 0.6 | 45.4 | 0.12 | 12.04 | 0.65 | 78.91 | 0.08 | [28 empty] | 79.91 | 0.07 | 78.91 | 0.08 | 99.27 | 0.12 | 99.51 | 0.11 | 59.33 | 0.06 | 59.14 | 0.06 |  |  | 59.45 | 0.05 | 59.45 | 0.05 | 59.39 | 0.05 | 97.1 | 0.08 | 75.98 | 0.06 | 71.19 | 0.05 | 74.84 | 0.05 | 164.22 | 0.32 | 99.81 | 0.12 | 98.82 | 0.12 | 49.56 | 0.17 | 58.96 | 0.93 | 75.62 | 0.05 | 98.34 | 0.12 | 94.43 | 0.06 | 97.64 | 0.08 | 80.1 | 0.07 | 99.68 | 0.09 | 100.26 | 0.13 | 99.27 | 0.12 | 99.51 | 0.11 | [12 empty] | 96.94 | 0.11 | 59.39 | 0.05 |  |  | 99.23 | 0.12 | 79.91 | 0.07 | 78.91 | 0.08 | [16 empty] | 49.3 | 0.82 | [12 empty] | 217.83 | 0.11 | 94.8 | 0.12 | 95.38 | 0.2 | 75.51 | 0.09 | 75.34 | 0.09 | 75.13 | 0.08 | 75.81 | 0.06 | 75.82 | 0.09 | 75.74 | 0.09 | 75.53 | 0.09 | 81.81 | 0.11 | 82.67 | 0.17 | 78.87 | 0.09 | 77.25 | 0.1 | 78.49 | 0.11 | 78.17 | 0.1 | 77.42 | 0.09 | 78.12 | 0.09 | 77.05 | 0.1 | 77.97 | 0.09 | 75.31 | 0.11 | 75.38 | 0.1 | 75.19 | 0.12 | 76.02 | 0.09 | 75.79 | 0.09 | 75.57 | 0.09 | 75.45 | 0.06 |  |  | 78.87 | 0.19 |  |  | 75.13 | 0.09 | 75.83 | 0.07 | 75.59 | 0.1 | 75.38 | 0.1 | 75.29 |  | 75.18 | 0.1 | 71.5 | 4.78 | 81.26 | 0.08 | 78.22 | 0.1 | 75.55 | 0.11 | 75.35 | 0.1 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.905 | 0.015 | 62.204 | 0.03 | 59.367 | 0.012 | 55.911 | 0.028 | 95.001 | 0.01 | 75.002 | 0.017 | 3030.6 | 3.5 | 2964.7 | 3.4 | 0.652 | 0.003 | -0.289 | 0.002 | 0.278 | 0.003 | 1.2766 | 0.0029 | 29.247 | 0 | 8425 | 21 | 1620 |  | 0 | 0 | 13.029 | 0.279 | 1.4325 | 13824.2089 | 227.0876 | 0 | 0 | 13824.2089 | 0.0089379 | 27.7576 | 57.9345 | 14.1 | 13.1534 | 0.013922 | 38.159 | 0.0089379 | 27.7576 | 0.0086915 | 23.6988 | 74.905 | 62.204 | 23.3495 | 60937.7621 | 56304.7508 | 6805 | 0.38113 | 56183.7521 | 51550.7408 | 6.6687 | 0.22111 | -4.408 | -16.9705 | 53.117 | 60937.7621 | 56108.7266 | 4829.0355 | 0 | 60937.7621 | 100%
2 | T2-RBASE-3000-115-CE | 75T0170 | T2-RBASE-3000-115-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/16/2014 | 5:32:41 | 10 Ton | 0:15:00 | 75/62 115/80 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 115 | 80 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 1.3 | 17 | 0 | 50172 | 59 | 50109 | 462 | 2204 | 233 | 52379 | 228 | 5.1717 | 949 | [38 empty] | Factory charge baseline, 2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm),--Econo closed unsealed cab, adjust code tester speed to match total static of--run T2-R-3000-95-CE-SPWCT-SS. Both stages. | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .; | 74.896 | 0.015 | 62.1 | 0.025 | 115.018 | 0.034 | 79.801 | 0.078 | 74.88 | 0.13 | 59.6 | 0.04 | 61.84 | 0.01 | 0.262 | 0.003 | 1.2639 | 0.0027 | 50172 | 59 | 2204 | 233 | 5.172 | 0.025 | [6 empty] | 460.9 | 2.4 | 460.7 | 2.4 | 459.1 | 2.4 | 17 | 0.1 | 15 | 0 | 14.5 | 0.1 | 7782.5 | 59.9 | 3326.9 | 67.1 | 2345.7 | 51.3 | 460 |  | 460 |  | 460 |  | 3.3 |  | 3.1 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 5.3 |  | 5.8 |  | 5.3 |  | 3880 |  | 0.9 | 460 | 460 | 460 | 5.8 | 5.4 | 5.3 | 3790 | 0.86 | 459.9 |  | 1.6 |  | 684.3 |  | 85 |  | 10079.3 | [14 empty] | 281.67 | 0.35 | 125.87 | 0.09 | 125.9 | 0.09 | 0.04 | 0.05 | 310.18 | 0.35 | 201.29 | 0.14 | 133.3 | 0.09 | 67.98 | 0.11 | 273.7 | 0.05 | 114.87 | 0.1 | 123.74 | 0.05 | 8.74 | 0.05 | 78.97 | 0.03 | 50.35 | 0.07 | 46.64 | 0.02 | 3.71 | 0.07 | 78.42 | 0.03 | 57.78 | 0.11 | 46.3 | 0.02 | 11.48 | 0.12 | [46 empty] | 314.9 | 0.34 | 195.22 | 0.21 | 134.48 | 0.09 | 60.74 | 0.22 | 298.59 | 0.47 | 130.36 | 0.12 | 11.98 | 0.32 | 287.13 | 0.05 | 117.62 | 0.12 | 127.36 | 0.05 | 9.75 | 0.05 | 81.13 | 0.11 | 48 | 0.07 | 2.8 | 0.39 | 80.55 | 0.13 | 59.46 | 0.42 | 47.64 | 0.08 | 11.82 | 0.43 | 124.37 | 0.1 | [28 empty] | 124.72 | 0.1 | 124.37 | 0.1 | 119.22 | 0.13 | 119.6 | 0.12 | 59.72 | 0.04 | 59.47 | 0.04 |  |  | 59.73 | 0.04 | 59.76 | 0.05 | 59.59 | 0.04 | 124.92 | 0.08 | 117.46 | 0.1 | 50.93 | 0.16 | 58.1 | 0.15 | 191.73 | 0.24 | 119.67 | 0.12 | 117.98 | 0.12 | 51.07 | 0.06 | 60.94 | 0.82 | 114.87 | 0.1 | 117.62 | 0.12 | 113.67 | 0.07 | 125.49 | 0.08 | 125.14 | 0.1 | 119.47 | 0.09 | 119.99 | 0.1 | 119.22 | 0.13 | 119.6 | 0.12 | [12 empty] | 125.87 | 0.09 | 59.59 | 0.04 |  |  | 118.38 | 0.34 | 124.72 | 0.1 | 124.37 | 0.1 | [16 empty] | 50.8 | 0.33 | [12 empty] | 202.28 | 0.15 | 114.91 | 0.16 | 115.12 | 0.15 | 75.3 | 0.08 | 75.06 | 0.08 | 74.88 | 0.08 | 75.55 | 0.06 | 75.57 | 0.08 | 75.48 | 0.09 | 75.29 | 0.09 | 87.88 | 0.19 | 89.17 | 0.27 | 81.58 | 0.14 | 78.88 | 0.11 | 81.41 | 0.11 | 80.73 | 0.1 | 79.27 | 0.08 | 80.41 | 0.09 | 78.66 | 0.1 | 80.38 | 0.12 | 75.42 | 0.09 | 75.37 | 0.08 | 75.39 | 0.09 | 76.54 | 0.1 | 76.14 | 0.1 | 75.51 | 0.07 | 75.48 | 0.05 |  |  | 82.25 | 0.31 |  |  | 74.93 | 0.08 | 75.51 | 0.06 | 75.31 | 0.08 | 75.1 | 0.08 | 75.02 |  | 74.9 | 0.09 |  |  | 86.55 | 0.14 | 80.84 | 0.12 | 75.62 | 0.09 | 75.31 | 0.08 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.896 | 0.015 | 62.1 | 0.025 | 59.6 | 0.01 | 56.287 | 0.014 | 115.018 | 0.034 | 79.801 | 0.078 | 3016.6 | 3.2 | 2947.8 | 3.1 | 0.653 | 0.003 | -0.288 | 0.002 | 0.262 | 0.003 | 1.2639 | 0.0027 | 29.238 | 0.001 | 10128 | 21 | 1640 |  | 0 | 0 | 13.029 | 0.279 | 1.4615 | 13752.817 | 226.1394 | 0 | 0 | 13752.817 | 0.0088712 | 27.6824 | 58.1385 | 14.6058 | 13.1606 | 0.013569 | 42.694 | 0.0088712 | 27.6824 | 0.0088574 | 23.9361 | 74.896 | 62.1 | 23.5796 | 56425.2191 | 55311.2337 | 8488 | 0.51341 | 51599.713 | 50485.7276 | 5.0948 | 0.20463 | -4.1028 | -16.7575 | 53.8272 | 56425.2191 | 51522.0782 | 4903.1409 | 0 | 56425.2191 | 100%
2 | T2-RBASE-3000-75-CE | 75T0171 | T2-RBASE-3000-75-CE | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/16/2014 | 4:21:45 | 10 Ton | 0:15:00 | 75/62 75/62 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 75 | 62 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 1.5 | 14 | 0 | 67164 | 132 | 67347 | 585 | 19391 | 171 | 86573 | 180 | 11.9017 | 949 | [38 empty] | Factory charge baseline, 2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm),--Econo closed unsealed cab, adjust code tester speed to match total static of run--T2-R-3000-95-CE-SPWCT-SS. Both stages. | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .; | 74.818 | 0.022 | 62.126 | 0.023 | 74.972 | 0.029 | 61.876 | 0.025 | 74.74 | 0.18 | 54.63 | 0.05 | 57.69 | 0.02 | 0.286 | 0.003 | 1.2859 | 0.0025 | 67164 | 132 | 19391 | 171 | 11.902 | 0.043 | [6 empty] | 460.9 | 2.6 | 460.7 | 2.6 | 459.1 | 2.5 | 14 | 0.1 | 11.9 | 0 | 11.5 | 0.1 | 6269 | 66.1 | 3135 | 66.5 | 1005.5 | 53.4 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.4 |  | 4.2 |  | 3.7 |  | 2540 |  | 0.77 | 460 | 460 | 460 | 4.3 | 3.9 | 3.8 | 2310 | 0.75 | 460 |  | 1.7 |  | 715 |  | 85 |  | 7260 | [14 empty] | 157.82 | 0.11 | 85.78 | 0.07 | 85.73 | 0.04 | -0.05 | 0.04 | 188.73 | 0.11 | 155.3 | 0.18 | 97.37 | 0.04 | 57.94 | 0.18 | 151.17 |  | 79.62 | 0.07 | 83.02 |  | 3.31 |  | 73.37 | 0.05 | 60.93 | 0.1 | 43.02 | 0.03 | 17.91 | 0.08 | 72.79 | 0.05 | 62.94 | 0.08 | 42.64 | 0.04 | 20.3 | 0.07 | [46 empty] | 188.78 | 0.12 | 142.24 | 0.07 | 97.39 | 0.04 | 44.86 | 0.08 | 169.93 | 0.13 | 90.46 | 0.05 | 9.02 | 0.05 | 163 | 0.05 | 80.92 | 0.05 | 87.78 | 0.05 | 6.79 | 0.05 | 73.19 | 0.04 | 42.9 | 0.03 | 3.91 | 0.27 | 72.44 | 0.05 | 54.26 | 0.14 | 42.41 | 0.03 | 11.85 | 0.14 | 84.08 | 0.07 | [28 empty] | 84.57 | 0.06 | 84.08 | 0.07 | 81.42 | 0.06 | 81.78 | 0.06 | 54.53 | 0.06 | 54.35 | 0.05 |  |  | 54.52 | 0.05 | 54.57 | 0.05 | 54.52 | 0.05 | 85.15 | 0.04 | 80.41 | 0.07 | 60.98 | 0.13 | 62.99 | 0.1 | 139.39 | 0.09 | 81.95 | 0.05 | 81.44 | 0.05 | 46.55 | 0.15 | 55.58 | 0.16 | 79.62 | 0.07 | 80.92 | 0.05 | 73.73 | 0.05 | 85.58 | 0.05 | 85.37 | 0.05 | 82.17 | 0.04 | 82.88 | 0.04 | 81.42 | 0.06 | 81.78 | 0.06 | [12 empty] | 85.78 | 0.07 | 54.52 | 0.05 |  |  | 81.44 | 0.05 | 84.57 | 0.06 | 84.08 | 0.07 | [16 empty] | 46.81 | 0.26 | [12 empty] | 156.15 | 0.18 | 75 | 0.09 | 74.81 | 0.08 | 75.49 | 0.1 | 75.33 | 0.1 | 75.13 | 0.09 | 75.68 | 0.07 | 75.75 | 0.09 | 75.68 | 0.1 | 75.47 | 0.1 | 75.02 | 0.06 | 74.89 | 0.06 | 74.93 | 0.08 | 75.18 | 0.11 | 74.9 | 0.1 | 74.8 | 0.1 | 74.84 | 0.09 | 74.9 | 0.09 | 74.82 | 0.12 | 74.66 | 0.1 | 74.85 | 0.12 | 75.27 | 0.1 | 75.06 | 0.12 | 75.04 | 0.09 | 75.03 | 0.09 | 75.44 | 0.09 | 75.09 | 0.06 |  |  | 74.78 | 0.07 |  |  | 75.08 | 0.09 | 75.91 | 0.08 | 75.68 | 0.1 | 75.49 | 0.11 | 75.37 |  | 75.25 | 0.1 |  |  | 75.18 | 0.05 | 74.98 | 0.1 | 75.12 | 0.13 | 75.27 | 0.1 | [62 empty] | T2-TRN-100A-55-CE-DM-2 | 74.818 | 0.022 | 62.126 | 0.023 | 54.765 | 0.015 | 52.31 | 0.019 | 74.972 | 0.029 | 61.876 | 0.025 | 3030.6 | 2.9 | 2989.5 | 2.9 | 0.655 | 0.003 | -0.297 | 0.002 | 0.286 | 0.003 | 1.2859 | 0.0025 | 29.224 | 0 | 7274 | 21 | 1610 |  | 0 | 0 | 13.029 | 0.279 | 1.4058 | 13955.7575 | 230.0408 | 0 | 0 | 13955.7575 | 0.0089068 | 27.7024 | 53.3592 | 13.549 | 13.0295 | 0.0087056 | 27.5197 | 0.0089068 | 27.7024 | 0.0077421 | 21.5462 | 74.818 | 62.126 | 21.204 | 90690.0833 | 71873.5739 | 5664 | 0.21316 | 85980.2827 | 67163.7733 | 11.8202 | 0.15035 | -6.4984 | -21.4588 | 49.5621 | 90690.0833 | 85914.225 | 4775.8584 | 0 | 90690.0833 | 100%
2 | T2-TRN-63A-55-1E-DM-2 | 75T0057 | T2-TRN-63A-55-1E-DM-2 | 10% open | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 2:02:29 | 10 Ton | 0:20:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.1 | 0 | 3458 | 17 | 3145 | 52 | 1864 | 54 | 5323 | 54 | 6.738 | 634 | 700 |  | 4.3772 | [35 empty] | Econo 10%-open (2.8V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton),--2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-1E-DM-2 | W/ECO: 2.8 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.016 | 0.014 | 62.006 | 0.028 | 55 | 0.009 | 51.025 | 0.014 | 75.09 | 0.03 | 73.65 | 0.01 | 74.06 | 0.01 | 0.07 | 0.002 | 0.8129 | 0.0017 | 3458 | 17 | 1864 | 54 | 6.74 | 0.099 | [6 empty] | 460.5 | 2.1 | 461.4 | 2.1 | 459.5 | 2.1 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1147.1 | 15.7 | 1112.5 | 19.8 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.6 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 785 | [14 empty] | 95.61 | 0.02 | 57.83 | 0.02 | 56.59 | 0.01 | -1.24 | 0.02 | 95.24 | 0.01 | 58.92 | 0.02 | 56.37 | 0.01 | -2.54 | 0.02 |  |  | 71.51 | 0.03 |  |  |  |  | 95.29 | 0.01 | 71.06 | 0.02 | 56.4 | 0.01 | 14.65 | 0.02 | 94.95 | 0.03 | 59.78 | 0.03 | 56.22 | 0.02 | 3.56 | 0.04 | [46 empty] | 96.05 | 0.02 | 60.07 | 0.02 | 56.84 | 0.01 | 3.25 | 0.02 | 96.71 | 0.03 | 57.19 | 0.02 | 0.45 | 0.12 |  |  | 72.64 | 0.03 |  |  |  |  | 95.81 | 0.02 | 56.7 | 0.01 | 14.35 | 0.02 | 95.76 | 0.02 | 60.79 | 0.02 | 56.67 | 0.01 | 4.12 | 0.02 | 59.91 | 0.06 | [28 empty] | 59.29 | 0.02 | 60.23 | 0.01 | 59.91 | 0.06 | 61.6 | 0.02 | 73.6 | 0.02 | 73.37 | 0.02 | 73.19 | 0.02 | 73.93 | 0.02 | 73.92 | 0.02 |  |  | 57.32 | 0.03 | 71.96 | 0.02 | 71.97 | 0.02 | 60.11 | 0.02 | 60.81 | 0.02 | 57.1 | 0.07 | 73.26 | 0.04 | 72.47 | 0.02 | 62.99 | 0.03 | 71.51 | 0.03 | 72.64 | 0.03 | 55.99 | 0.04 | 58.81 | 0.01 | 61.22 | 0.02 | 58.15 | 0.03 | 58.99 | 0.05 | 60.23 | 0.01 | 61.6 | 0.02 | [16 empty] | 57.83 | 0.02 | 56.75 | 0.11 | 59.29 | 0.02 | 59.91 | 0.06 | [16 empty] | 71.05 | 0.02 | [12 empty] | 59.28 | 0.02 | 56.27 | 0.06 | 55.94 | 0.05 | 75.52 | 0.02 | 72.95 | 0.05 | 74.9 | 0.02 | 73.99 | 0.05 | 75.98 | 1.48 | 76.03 | 0.02 | 75.6 | 0.02 | 69.81 | 0.09 | 71.66 | 0.06 | 71.77 | 0.04 | 72.51 | 0.08 | 72.8 | 0.06 | 72.63 | 0.06 | 72.85 | 0.04 | 73.59 | 0.04 | 74.18 | 0.04 | 73.57 | 0.04 | 74.02 | 0.04 | 74.9 | 0.02 | 74.88 | 0.02 | 74.82 | 0.02 | 74.61 | 0.06 | 75 | 0.02 | 74.67 | 0.02 | 70.97 | 0.13 | 70.39 | 0.09 |  |  | 73.43 | 0.07 | 76 | 0.02 | 75.8 | 0.02 | 75.09 | 0.03 | 73.32 |  | 75.2 | 0.02 | 69.27 | 0.08 |  |  | 72.19 | 0.06 | 74.33 | 0.04 | 74.96 | 0.02 | [62 empty] | Economizer test | 75.016 | 0.014 | 62.006 | 0.028 | 73.427 | 0.011 | 61.154 | 0.025 | 55 | 0.009 | 51.025 | 0.014 | 2001.7 | 2.1 | 1926.4 | 2 | 0.287 | 0.002 | -0.133 | 0.001 | 0.07 | 0.002 | 0.8129 | 0.0017 | 29.471 | 0 | 790 | 8 | 700 |  | 0.028427 | 54.7623 | 13.03 | 0.133 | 1.0155 | 8890.5077 | 64.9521 | 54.7614 | 252.1708 | 8638.3369 | 0.0087301 | 27.4193 | 72.4115 | 13.0296 | 13.509 | 0.0069946 | 20.7921 | 0.0087808 | 27.6127 | 0.0085992 | 27.0265 | 74.4501 | 61.7256 | 26.7789
2 | T2-TRN-63A-55-1F-DM-2 | 75T0058 | T2-TRN-63A-55-1F-DM-2 | 1 finger | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 4:02:19 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.1 | 0 | 8771 | 13 | 8467 | 58 | 4151 | 84 | 12926 | 85 | 16.198 | 634 | 710 |  | 10.9912 | [35 empty] | Econo 1F-open (5.1V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton), 2 HP fan motor,--5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-1F-DM-2- | W/ECO: 5.1 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.995 | 0.01 | 62 | 0.018 | 55 | 0.008 | 50.991 | 0.013 | 75.1 | 0.02 | 71.28 | 0.02 | 72.3 | 0.02 | 0.074 | 0.002 | 0.8442 | 0.0013 | 8771 | 13 | 4151 | 84 | 16.199 | 0.198 | [6 empty] | 460.5 | 2 | 461.5 | 2 | 459.5 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1153.2 | 15.5 | 1109.9 | 19.4 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 795 | [14 empty] | 96.4 | 0.01 | 59.15 | 0.03 | 57.03 | 0.01 | -2.13 | 0.03 | 95.96 | 0.01 | 59.65 | 0.02 | 56.78 | 0.01 | -2.86 | 0.02 |  |  | 71.36 | 0.02 |  |  |  |  | 96.06 | 0.01 | 69.9 | 0.01 | 56.84 | 0.01 | 13.06 | 0.02 | 95.83 | 0.02 | 61.98 | 0.02 | 56.7 | 0.01 | 5.27 | 0.02 | [46 empty] | 97.11 | 0.03 | 60.81 | 0.02 | 57.42 | 0.01 | 3.38 | 0.02 | 97.57 | 0.03 | 57.67 | 0.02 | -0.37 | 0.09 |  |  | 71.01 | 0.02 |  |  |  |  | 96.68 | 0.03 | 57.18 | 0.02 | 12.83 | 0.04 | 96.7 | 0.02 | 61.97 | 0.02 | 57.19 | 0.01 | 4.78 | 0.02 | 61.19 | 0.04 | [28 empty] | 60.3 | 0.02 | 60.96 | 0.01 | 61.19 | 0.04 | 62.26 | 0.03 | 71.68 | 0.03 | 70.8 | 0.03 | 70.51 | 0.02 | 71.9 | 0.02 | 71.78 | 0.02 |  |  | 58.64 | 0.02 | 71.88 | 0.02 | 70.94 | 0.01 | 61.99 | 0.02 | 61.53 | 0.01 | 58.12 | 0.05 | 71.53 | 0.01 | 71.22 | 0.02 | 64 | 0.01 | 71.36 | 0.02 | 71.01 | 0.02 | 55.59 | 0.02 | 60.4 | 0.01 | 61.82 | 0.02 | 58.68 | 0.03 | 59.66 | 0.03 | 60.96 | 0.01 | 62.26 | 0.03 | [16 empty] | 59.15 | 0.03 | 58.04 | 0.09 | 60.3 | 0.02 | 61.19 | 0.04 | [16 empty] | 70.01 | 0.03 | [12 empty] | 59.89 | 0.03 | 56.78 | 0.1 | 55.99 | 0.04 | 75.45 | 0.02 | 72.88 | 0.05 | 74.89 | 0.02 | 73.87 | 0.06 | 75.8 | 0.4 | 75.87 | 0.01 | 75.44 | 0.02 | 63.18 | 0.16 | 67.28 | 0.19 | 66.67 | 0.45 | 64.55 | 0.17 | 66.17 | 0.18 | 68.7 | 0.11 | 69.68 | 0.04 | 69.74 | 0.04 | 67.76 | 0.11 | 69.07 | 0.06 | 66.97 | 0.13 | 69.27 | 0.18 | 73.52 | 0.1 | 73.54 | 0.1 | 73.15 | 0.05 | 70.11 | 0.09 | 73.79 | 0.04 | 73.05 | 0.05 | 71.2 | 0.06 |  |  | 73.36 | 0.06 | 75.82 | 0.02 | 75.68 | 0.01 | 74.99 | 0.03 | 73.32 |  | 75.08 | 0.01 | 63.8 | 0.11 |  |  | 64.01 | 0.12 | 63.58 | 0.14 | 73.36 | 0.1 | [62 empty] | Economizer test | 74.995 | 0.01 | 62 | 0.018 | 71.042 | 0.008 | 59.919 | 0.018 | 55 | 0.008 | 50.991 | 0.013 | 2036.8 | 1.6 | 1967.2 | 1.6 | 0.266 | 0.002 | -0.103 | 0.001 | 0.074 | 0.002 | 0.8442 | 0.0013 | 29.468 | 0.001 | 798 | 8 | 710 |  | 0.14669 | 288.562 | 13.029 | 0.103 | 1.0145 | 9088.2858 | 61.4745 | 288.5672 | 1328.8366 | 7759.4491 | 0.0085179 | 26.6092 | 70.0275 | 13.0295 | 13.4468 | 0.0069766 | 20.7725 | 0.0087818 | 27.6087 | 0.0083719 | 26.1967 | 72.0797 | 60.5337 | 25.9495
2 | T2-TRN-63A-55-2E-DM-2 | 75T0059 | T2-TRN-63A-55-2E-DM-2 | 20% open | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 2:43:50 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 3.1 | 0 | 4732 | 13 | 4446 | 45 | 2475 | 56 | 7210 | 53 | 9.0806 | 633 | 710 |  | 5.9597 | [35 empty] | Econo 20%-open (3.6V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton),--2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-2E-DM-2 | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.991 | 0.009 | 61.996 | 0.025 | 54.987 | 0.011 | 50.982 | 0.014 | 75.1 | 0.02 | 73.08 | 0.02 | 73.62 | 0.01 | 0.073 | 0.002 | 0.8271 | 0.0016 | 4732 | 13 | 2475 | 56 | 9.082 | 0.115 | [6 empty] | 460.3 | 2.1 | 461.4 | 2.1 | 459.5 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1148.5 | 15.4 | 1111.7 | 19.8 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.7 |  | 2.5 |  | 0.29 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 795 | [14 empty] | 95.83 | 0.02 | 58.24 | 0.02 | 56.71 | 0.01 | -1.54 | 0.02 | 95.43 | 0.01 | 59.27 | 0.02 | 56.48 | 0 | -2.78 | 0.01 |  |  | 71.61 | 0.02 |  |  |  |  | 95.52 | 0.01 | 70.98 | 0.02 | 56.53 | 0.01 | 14.44 | 0.02 | 95.17 | 0.02 | 60.36 | 0.02 | 56.34 | 0.01 | 4.02 | 0.02 | [46 empty] | 96.38 | 0.02 | 60.27 | 0.02 | 57.01 | 0.01 | 3.26 | 0.03 | 96.98 | 0.03 | 57.35 | 0.01 | 0.35 | 0.19 |  |  | 72.44 | 0.05 |  |  |  |  | 96.09 | 0.02 | 56.85 | 0.01 | 14.16 | 0.03 | 96.06 | 0.02 | 61.17 | 0.02 | 56.83 | 0.01 | 4.33 | 0.02 | 60.32 | 0.11 | [28 empty] | 59.62 | 0.02 | 60.48 | 0.02 | 60.32 | 0.11 | 61.87 | 0.03 | 73.08 | 0.02 | 72.75 | 0.03 | 72.55 | 0.02 | 73.4 | 0.01 | 73.39 | 0.02 |  |  | 57.66 | 0.03 | 72.11 | 0.02 | 71.9 | 0.02 | 60.62 | 0.02 | 61.02 | 0.02 | 57.27 | 0.13 | 72.99 | 0.04 | 72.35 | 0.02 | 63.34 | 0.02 | 71.61 | 0.02 | 72.44 | 0.05 | 55.84 | 0.02 | 59.23 | 0.02 | 61.45 | 0.02 | 58.29 | 0.04 | 59.29 | 0.1 | 60.48 | 0.02 | 61.87 | 0.03 | [16 empty] | 58.24 | 0.02 | 57.01 | 0.19 | 59.62 | 0.02 | 60.32 | 0.11 | [16 empty] | 71.01 | 0.02 | [12 empty] | 59.64 | 0.02 | 56.38 | 0.06 | 55.96 | 0.04 | 75.49 | 0.01 | 72.93 | 0.05 | 74.89 | 0.02 | 73.94 | 0.05 | 75.94 | 0.09 | 75.99 | 0.02 | 75.56 | 0.02 | 67.01 | 0.18 | 70.98 | 0.07 | 71.04 | 0.04 | 70.74 | 0.08 | 71.82 | 0.08 | 71.59 | 0.09 | 71.81 | 0.06 | 72.67 | 0.04 | 73.74 | 0.05 | 72.6 | 0.06 | 73.57 | 0.06 | 74.89 | 0.02 | 74.78 | 0.02 | 74.78 | 0.02 | 74.64 | 0.04 | 75.02 | 0.02 | 74.7 | 0.02 | 71.72 | 0.17 | 70.09 | 0.1 |  |  | 73.4 | 0.06 | 75.92 | 0.02 | 75.75 | 0.01 | 75.05 | 0.03 | 73.32 |  | 75.15 | 0.02 | 67.29 | 0.06 |  |  | 70.89 | 0.08 | 74.16 | 0.05 | 74.92 | 0.02 | [62 empty] | Economizer test | 74.991 | 0.009 | 61.996 | 0.025 | 72.836 | 0.006 | 60.845 | 0.024 | 54.987 | 0.011 | 50.982 | 0.014 | 2018.5 | 2 | 1944.2 | 1.9 | 0.282 | 0.002 | -0.126 | 0.001 | 0.073 | 0.002 | 0.8271 | 0.0016 | 29.469 | 0 | 794 | 8 | 710 |  | 0.056739 | 110.3113 | 13.029 | 0.126 | 1.0226 | 8975.3948 | 64.4103 | 110.3118 | 507.9934 | 8467.4014 | 0.0086779 | 27.2188 | 71.8134 | 13.0291 | 13.4936 | 0.0069748 | 20.7675 | 0.0087801 | 27.6059 | 0.0085391 | 26.8168 | 73.8623 | 61.4334 | 26.5675
2 | T2-TRN-63A-55-2F-DM-2 | 75T0060 | T2-TRN-63A-55-2F-DM-2 | 2 finger | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 4:42:00 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 3.1 | 0 | 11896 | 14 | 11571 | 57 | 5593 | 97 | 17495 | 99 | 21.8414 | 633 | 720 |  | 14.8514 | [35 empty] | Econo 2F-open (6V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton),--2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-2F-DM-2-SP | W/ECO: 6 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.984 | 0.01 | 61.996 | 0.033 | 54.995 | 0.009 | 50.991 | 0.014 | 75.09 | 0.04 | 69.9 | 0.02 | 71.28 | 0.02 | 0.075 | 0.002 | 0.8519 | 0.0013 | 11896 | 14 | 5593 | 97 | 21.851 | 0.265 | [6 empty] | 460.6 | 2 | 461.4 | 2 | 459.4 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1154.9 | 15.2 | 1108.9 | 19.5 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.6 |  | 2.5 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 795 | [14 empty] | 96.8 | 0.02 | 59.66 | 0.03 | 57.25 | 0.01 | -2.41 | 0.03 | 96.41 | 0.01 | 60.54 | 0.02 | 57.03 | 0.01 | -3.51 | 0.02 |  |  | 70.56 | 0.02 |  |  |  |  | 96.61 | 0.07 | 68.35 | 0.01 | 57.14 | 0.04 | 11.21 | 0.04 | 96.27 | 0.02 | 63.11 | 0.02 | 56.95 | 0.01 | 6.15 | 0.02 | [46 empty] | 97.66 | 0.04 | 61.32 | 0.04 | 57.72 | 0.02 | 3.6 | 0.04 | 97.9 | 0.03 | 57.85 | 0.02 | -0.12 | 0.14 |  |  | 69.59 | 0.05 |  |  |  |  | 97.12 | 0.03 | 57.42 | 0.02 | 10.83 | 0.03 | 97.15 | 0.04 | 62.47 | 0.02 | 57.44 | 0.02 | 5.04 | 0.02 | 61.5 | 0.06 | [28 empty] | 60.69 | 0.04 | 61.25 | 0.02 | 61.5 | 0.06 | 62.48 | 0.04 | 70.45 | 0.03 | 69.34 | 0.03 | 68.99 | 0.02 | 70.6 | 0.02 | 70.43 | 0.03 |  |  | 59.18 | 0.02 | 70.98 | 0.02 | 69.44 | 0.01 | 62.93 | 0.02 | 62.03 | 0.03 | 58.12 | 0.13 | 70.14 | 0.05 | 69.45 | 0.03 | 64.4 | 0.03 | 70.56 | 0.02 | 69.59 | 0.05 | 55.47 | 0.04 | 61.22 | 0.02 | 62.12 | 0.02 | 59.08 | 0.05 | 60.14 | 0.06 | 61.25 | 0.02 | 62.48 | 0.04 | [16 empty] | 59.66 | 0.03 | 57.98 | 0.15 | 60.69 | 0.04 | 61.5 | 0.06 | [16 empty] | 68.25 | 0.03 | [12 empty] | 60.9 | 0.03 | 57.09 | 0.14 | 56.02 | 0.05 | 75.4 | 0.02 | 72.95 | 0.06 | 74.88 | 0.02 | 73.8 | 0.06 | 75.98 | 0.59 | 75.86 | 0.02 | 75.42 | 0.03 | 63.17 | 0.16 | 60.99 | 0.12 | 59.69 | 0.06 | 60.96 | 0.1 | 65.22 | 0.29 | 64.5 | 0.28 | 65.6 | 0.48 | 68.29 | 0.13 | 66.89 | 0.12 | 66.96 | 0.2 | 66.57 | 0.22 | 66.13 | 0.14 | 70.63 | 0.09 | 71.25 | 0.06 | 70.98 | 0.05 | 68.92 | 0.12 | 72.44 | 0.08 | 72.57 | 0.13 | 72.9 | 0.06 |  |  | 73.4 | 0.08 | 75.78 | 0.01 | 75.65 | 0.02 | 74.96 | 0.03 | 73.29 |  | 75.06 | 0.02 | 60.9 | 0.12 |  |  | 63.92 | 0.16 | 63.83 | 0.33 | 69.3 | 0.1 | [62 empty] | Economizer test | 74.984 | 0.01 | 61.996 | 0.033 | 69.653 | 0.009 | 59.176 | 0.023 | 54.995 | 0.009 | 50.991 | 0.014 | 2044.4 | 1.6 | 1978.4 | 1.5 | 0.252 | 0.002 | -0.086 | 0.001 | 0.075 | 0.002 | 0.8519 | 0.0013 | 29.461 | 0.001 | 801 | 8 | 710 |  | 0.21617 | 427.6685 | 13.029 | 0.086 | 1.0125 | 9146.8873 | 58.5706 | 427.6742 | 1969.4351 | 7177.4521 | 0.0083933 | 26.1347 | 68.6405 | 13.0293 | 13.4105 | 0.0069777 | 20.7726 | 0.0087818 | 27.606 | 0.0082336 | 25.7072 | 70.6912 | 59.8218 | 25.4605
2 | T2-TRN-63A-55-3E-DM-2 | 75T0061 | T2-TRN-63A-55-3E-DM-2 | 30% open | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 3:21:59 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.4 | 0 | 3.1 | 0 | 6808 | 16 | 6491 | 41 | 3347 | 82 | 10158 | 79 | 12.7453 | 634 | 710 |  | 8.542 | [35 empty] | Econo 30%-open (4.4V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton),--2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-3E-DM-2 | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.995 | 0.008 | 61.998 | 0.03 | 54.985 | 0.01 | 51.007 | 0.016 | 75.1 | 0.02 | 72.17 | 0.01 | 72.95 | 0.02 | 0.078 | 0.002 | 0.8414 | 0.0014 | 6808 | 16 | 3347 | 82 | 12.751 | 0.163 | [6 empty] | 460.4 | 2 | 461.5 | 2 | 459.5 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1151.7 | 15.3 | 1110.1 | 19.6 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.6 |  | 2.5 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 795 | [14 empty] | 96.18 | 0.01 | 58.67 | 0.03 | 56.9 | 0.01 | -1.76 | 0.03 | 95.75 | 0.01 | 59.62 | 0.03 | 56.66 | 0 | -2.97 | 0.02 |  |  | 71.66 | 0.02 |  |  |  |  | 95.85 | 0.01 | 70.65 | 0.01 | 56.72 | 0.01 | 13.93 | 0.01 | 95.57 | 0.03 | 61.1 | 0.03 | 56.56 | 0.01 | 4.54 | 0.03 | [46 empty] | 96.77 | 0.03 | 60.7 | 0.05 | 57.24 | 0.01 | 3.46 | 0.05 | 97.34 | 0.03 | 57.55 | 0.01 | 0.38 | 0.12 |  |  | 71.68 | 0.07 |  |  |  |  | 96.42 | 0.02 | 57.04 | 0.01 | 13.8 | 0.03 | 96.41 | 0.02 | 61.56 | 0.02 | 57.03 | 0.01 | 4.53 | 0.02 | 60.44 | 0.12 | [28 empty] | 59.93 | 0.02 | 60.72 | 0.02 | 60.44 | 0.12 | 62.03 | 0.03 | 72.47 | 0.02 | 71.72 | 0.02 | 71.43 | 0.02 | 72.69 | 0.01 | 72.59 | 0.02 |  |  | 58.11 | 0.03 | 72.18 | 0.01 | 71.66 | 0.01 | 61.24 | 0.02 | 61.42 | 0.04 | 57.47 | 0.08 | 72.21 | 0.06 | 72.06 | 0.02 | 63.54 | 0.03 | 71.66 | 0.02 | 71.68 | 0.07 | 55.66 | 0.02 | 59.76 | 0.01 | 61.64 | 0.01 | 58.46 | 0.03 | 59.4 | 0.06 | 60.72 | 0.02 | 62.03 | 0.03 | [16 empty] | 58.67 | 0.03 | 57.18 | 0.12 | 59.93 | 0.02 | 60.44 | 0.12 | [16 empty] | 70.84 | 0.03 | [12 empty] | 59.97 | 0.04 | 56.54 | 0.1 | 55.96 | 0.04 | 75.45 | 0.02 | 72.89 | 0.05 | 74.91 | 0.02 | 73.9 | 0.04 | 76.07 | 1.39 | 75.91 | 0.02 | 75.5 | 0.02 | 65.87 | 0.11 | 67.11 | 0.25 | 70.13 | 0.08 | 69.36 | 0.13 | 65.97 | 0.11 | 68.24 | 0.11 | 70.17 | 0.06 | 70.32 | 0.07 | 68.23 | 0.1 | 69.09 | 0.09 | 67.87 | 0.13 | 74.44 | 0.04 | 74.44 | 0.04 | 74.57 | 0.03 | 74.48 | 0.03 | 74.83 | 0.02 | 74.75 | 0.02 | 72.36 | 0.16 | 70.95 | 0.09 |  |  | 73.36 | 0.06 | 75.83 | 0.02 | 75.68 | 0.02 | 75.01 | 0.03 | 73.36 |  | 75.09 | 0.02 | 63.77 | 0.08 |  |  | 65.8 | 0.14 | 66.39 | 0.18 | 74.58 | 0.04 | [62 empty] | Economizer test | 74.995 | 0.008 | 61.998 | 0.03 | 71.921 | 0.008 | 60.378 | 0.028 | 54.985 | 0.01 | 51.007 | 0.016 | 2034.6 | 1.6 | 1962.6 | 1.6 | 0.275 | 0.002 | -0.115 | 0.001 | 0.078 | 0.002 | 0.8414 | 0.0014 | 29.47 | 0 | 797 | 8 | 710 |  | 0.10315 | 202.4391 | 13.029 | 0.115 | 1.0143 | 9063.0054 | 63.4059 | 202.4405 | 932.2483 | 8130.7571 | 0.0085962 | 26.9052 | 70.9067 | 13.0292 | 13.4697 | 0.0069886 | 20.7819 | 0.0087805 | 27.6073 | 0.0084558 | 26.5027 | 72.9427 | 60.9726 | 26.2555
2 | T2-TRN-63A-55-3F-DM-2 | 75T0062 | T2-TRN-63A-55-3F-DM-2 | 3 finger | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 5:36:23 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.1 | 0 | 15748 | 25 | 15445 | 59 | 7295 | 126 | 23050 | 141 | 28.6692 | 633 | 700 |  | 19.5871 | [35 empty] | Econo 3F-open (6.9V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton),--2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet--Meriam, adjust code tester speed to match total static of run T2-TRN-63A-55-3F-DM-2- | W/ECO: 6.9 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.977 | 0.006 | 61.994 | 0.033 | 54.996 | 0.011 | 51.001 | 0.016 | 75.11 | 0.03 | 68.23 | 0.03 | 69.97 | 0.01 | 0.077 | 0.002 | 0.8596 | 0.0015 | 15748 | 25 | 7295 | 126 | 28.685 | 0.341 | [6 empty] | 460.5 | 2.1 | 461.2 | 2.1 | 459.5 | 2.1 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1151.7 | 15.6 | 1112.3 | 20.4 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.6 |  | 2.6 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 785 | [14 empty] | 97.31 | 0.02 | 60.23 | 0.03 | 57.52 | 0.01 | 2.7 | 0.03 | 96.88 | 0.02 | 61.03 | 0.06 | 57.29 | 0.01 | 3.75 | 0.05 |  |  | 68.36 | 0.02 |  |  |  |  | 97.12 | 0.03 | 66.36 | 0.02 | 57.42 | 0.01 | 8.94 | 0.03 | 96.74 | 0.03 | 64.3 | 0.02 | 57.21 | 0.01 | 7.1 | 0.02 | [46 empty] | 98.03 | 0.05 | 56.91 | 0.04 | 57.92 | 0.02 | 1.02 | 0.03 | 98.29 | 0.06 | 58.06 | 0.03 | 1.69 | 0.08 |  |  | 66.98 | 0.03 |  |  |  |  | 97.43 | 0.05 | 57.59 | 0.03 | 7.86 | 0.17 | 97.53 | 0.04 | 63.04 | 0.01 | 57.64 | 0.02 | 5.4 | 0.03 | 62.15 | 0.06 | [28 empty] | 61.04 | 0.03 | 61.46 | 0.02 | 62.15 | 0.06 | 62.62 | 0.05 | 68.86 | 0.04 | 67.59 | 0.04 | 67.23 | 0.03 | 69.01 | 0.03 | 68.82 | 0.03 |  |  | 59.87 | 0.03 | 68.57 | 0.03 | 67.41 | 0.01 | 64.01 | 0.02 | 57.56 | 0.03 | 59.67 | 0.06 | 67.47 | 0.03 | 66.76 | 0.14 | 64.98 | 0.02 | 68.36 | 0.02 | 66.98 | 0.03 | 55.38 | 0.03 | 62.07 | 0.02 | 62.36 | 0.02 | 61.2 | 0.14 | 62.6 | 0.21 | 61.46 | 0.02 | 62.62 | 0.05 | [16 empty] | 60.23 | 0.03 | 59.76 | 0.08 | 61.04 | 0.03 | 62.15 | 0.06 | [16 empty] | 65.45 | 0.17 | [12 empty] | 61.3 | 0.08 | 57.4 | 0.17 | 56.08 | 0.06 | 75.43 | 0.02 | 73.34 | 0.06 | 74.96 | 0.02 | 74.33 | 0.06 | 75.87 | 0.37 | 75.86 | 0.02 | 75.43 | 0.03 | 61.44 | 0.19 | 61.24 | 0.21 | 59.45 | 0.2 | 60.01 | 0.13 | 62.86 | 0.15 | 62.49 | 0.2 | 59.52 | 0.37 | 64.67 | 0.15 | 64.73 | 0.22 | 63.68 | 0.25 | 64.85 | 0.14 | 64.59 | 0.29 | 67.43 | 0.24 | 67.17 | 0.17 | 66.68 | 0.12 | 66.99 | 0.2 | 70.38 | 0.12 | 70.9 | 0.1 | 70.23 | 0.08 |  |  | 73.82 | 0.07 | 75.81 | 0.02 | 75.7 | 0.02 | 75.09 | 0.03 | 73.59 |  | 75.1 | 0.02 | 57.49 | 0.27 |  |  | 62.25 | 0.14 | 63.53 | 0.15 | 66.61 | 0.26 | [62 empty] | Economizer test | 74.977 | 0.006 | 61.994 | 0.033 | 67.964 | 0.005 | 58.266 | 0.018 | 54.996 | 0.011 | 51.001 | 0.016 | 2051.2 | 1.8 | 1990.2 | 1.7 | 0.234 | 0.002 | -0.067 | 0.001 | 0.077 | 0.002 | 0.8596 | 0.0015 | 29.459 | 0 | 804 | 8 | 700 |  | 0.30094 | 598.9226 | 13.029 | 0.067 | 0.99634 | 9207.5817 | 54.7114 | 598.9321 | 2758.0619 | 6449.5198 | 0.0082431 | 25.5599 | 66.9677 | 13.0294 | 13.3664 | 0.0069828 | 20.7783 | 0.0087821 | 27.6046 | 0.0080706 | 25.1178 | 69.0056 | 58.9455 | 24.8751
2 | T2-TRN-63A-55-CE-DM-2 | 75T0063 | T2-TRN-63A-55-CE-DM-2 | closed | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 1:31:40 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.1 | 0 | 3406 | 8 | 3108 | 52 | 1874 | 54 | 5282 | 57 | 6.6776 | 634 | 700 |  | 4.3059 | [35 empty] | Econo closed (2V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton),--2 HP fan motor, 5.5 turns, 7.25" AK74 pulley (620 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-CE-DM-2-SPWCT-SS | W/ECO: 2 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.979 | 0.004 | 61.986 | 0.03 | 54.982 | 0.01 | 50.941 | 0.013 | 75.06 | 0.02 | 73.64 | 0.02 | 74.06 | 0.01 | 0.071 | 0.002 | 0.8125 | 0.0017 | 3406 | 8 | 1874 | 54 | 6.681 | 0.099 | [6 empty] | 460.5 | 2 | 461.4 | 2 | 459.6 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1146.7 | 15 | 1113.7 | 19.1 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.6 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 785 | [14 empty] | 95.52 | 0.01 | 57.83 | 0.01 | 56.52 | 0 | -1.3 | 0.02 | 95.28 | 0.03 | 58.88 | 0.02 | 56.4 | 0.02 | -2.47 | 0.02 |  |  | 71.56 | 0.02 |  |  |  |  | 95.21 | 0.01 | 71.39 | 0.02 | 56.36 | 0.01 | 15.02 | 0.01 | 94.88 | 0.03 | 59.86 | 0.02 | 56.18 | 0.01 | 3.68 | 0.02 | [46 empty] | 96.02 | 0.02 | 59.82 | 0.02 | 56.82 | 0.01 | 3 | 0.02 | 96.69 | 0.02 | 57.19 | 0.01 | 0.45 | 0.09 |  |  | 72.97 | 0.02 |  |  |  |  | 95.79 | 0.02 | 56.69 | 0.01 | 14.71 | 0.03 | 95.73 | 0.02 | 60.78 | 0.01 | 56.66 | 0.01 | 4.13 | 0.01 | 59.71 | 0.05 | [28 empty] | 59.25 | 0.01 | 60.17 | 0.01 | 59.71 | 0.05 | 61.54 | 0.02 | 73.58 | 0.02 | 73.36 | 0.01 | 73.18 | 0.01 | 73.87 | 0.02 | 73.87 | 0.01 |  |  | 57.24 | 0.02 | 72.07 | 0.02 | 72.25 | 0.02 | 60.15 | 0.01 | 60.55 | 0.02 | 56.94 | 0.06 | 73.6 | 0.01 | 72.72 | 0.02 | 63.01 | 0.01 | 71.56 | 0.02 | 72.97 | 0.02 | 55.91 | 0.02 | 58.78 | 0.01 | 61.13 | 0.02 | 58.09 | 0.03 | 59.15 | 0.06 | 60.17 | 0.01 | 61.54 | 0.02 | [16 empty] | 57.83 | 0.01 | 56.74 | 0.08 | 59.25 | 0.01 | 59.71 | 0.05 | [16 empty] | 71.4 | 0.03 | [12 empty] | 59.17 | 0.01 | 56.22 | 0.07 | 55.89 | 0.04 | 75.48 | 0.02 | 72.91 | 0.04 | 74.87 | 0.03 | 73.88 | 0.05 | 76 | 0.59 | 76 | 0.02 | 75.57 | 0.03 | 69.86 | 0.09 | 71.7 | 0.04 | 71.83 | 0.04 | 72.45 | 0.09 | 72.79 | 0.07 | 72.6 | 0.06 | 72.8 | 0.03 | 73.49 | 0.03 | 74.11 | 0.03 | 73.51 | 0.04 | 73.99 | 0.03 | 74.82 | 0.01 | 74.82 | 0.01 | 74.8 | 0.02 | 74.7 | 0.04 | 74.86 | 0.02 | 74.61 | 0.02 | 72.29 | 0.13 | 71.09 | 0.06 |  |  | 73.38 | 0.06 | 75.93 | 0.02 | 75.75 | 0.01 | 75.03 | 0.02 | 73.26 |  | 75.15 | 0.02 | 69.39 | 0.08 |  |  | 72.2 | 0.07 | 74.26 | 0.04 | 74.86 | 0.02 | [62 empty] | Economizer test | 74.979 | 0.004 | 61.986 | 0.03 | 73.415 | 0.005 | 61.141 | 0.027 | 54.982 | 0.01 | 50.941 | 0.013 | 2001 | 2.1 | 1926.1 | 2.1 | 0.287 | 0.002 | -0.132 | 0.001 | 0.071 | 0.002 | 0.8125 | 0.0017 | 29.477 | 0 | 791 | 8 | 700 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.0158 | 8887.6282 | 64.942 | 52.3974 | 241.2992 | 8646.3291 | 0.0087269 | 27.4127 | 72.3992 | 13.0288 | 13.5087 | 0.0069542 | 20.7439 | 0.0087764 | 27.5988 | 0.0085936 | 27.0175 | 74.4378 | 61.7163 | 26.7698
2 | T2-TRN-63A-55-OE-DM-2 | 75T0066 | T2-TRN-63A-55-OE-DM-2 | open | off | off | 5.5 turns | unsealed | unsealed | 620 | 7.25 |  | 0 | 0 | CUST 5 | 10/30/2014 | 6:28:28 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 3.1 | 0 | 29997 | 64 | 29702 | 154 | 14212 | 181 | 44223 | 180 | 55.2788 | 633 | 710 |  | 37.4963 | [35 empty] | Econo fully open (10V), no compressor, 55/51 ambient, 62.5% airflow (250 cfm/ton), 2 HP fan motor,--5.5 turns, 7.25" AK74 pulley (620 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-63A-55-OE-DM- | W/ECO: 10 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 5.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.932 | 0.031 | 61.99 | 0.029 | 55.015 | 0.007 | 50.994 | 0.016 | 75.11 | 0.06 | 61.58 | 0.03 | 65.36 | 0.09 | 0.063 | 0.002 | 0.8075 | 0.0014 | 29997 | 64 | 14212 | 181 | 55.288 | 0.602 | [6 empty] | 460.3 | 2 | 461 | 2 | 459.7 | 2 | 3.1 | 0 | 2.6 | 0 | 3 | 0 | 1141.6 | 14.6 | 1121.4 | 19.5 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.6 |  | 2.6 |  | 2.6 |  | 0.3 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 795 | [14 empty] | 95.74 | 0.08 | 60.03 | 0.04 | 56.65 | 0.04 | 3.37 | 0.06 | 95.92 | 0.05 | 60.29 | 0.02 | 56.75 | 0.03 | 3.54 | 0.03 |  |  | 63.71 | 0.03 |  |  |  |  | 95.69 | 0.07 | 61.71 | 0.04 | 56.63 | 0.03 | 5.08 | 0.05 | 95.31 | 0.05 | 64.68 | 0.02 | 56.41 | 0.02 | 8.26 | 0.04 | [46 empty] | 96.2 | 0.07 | 56.07 | 0.05 | 56.92 | 0.03 | 0.85 | 0.03 | 96.48 | 0.06 | 57.07 | 0.03 | 2.57 | 0.17 |  |  | 62.03 | 0.04 |  |  |  |  | 95.28 | 0.06 | 56.4 | 0.03 | 4.25 | 0.1 | 95.45 | 0.07 | 61.86 | 0.04 | 56.5 | 0.03 | 5.36 | 0.06 | 56.88 | 0.05 | [28 empty] | 60.5 | 0.03 | 60.54 | 0.02 | 56.88 | 0.05 | 59.86 | 0.05 | 61.26 | 0.04 | 61.18 | 0.03 | 60.89 | 0.03 | 61.35 | 0.03 | 61.27 | 0.02 |  |  | 59.76 | 0.03 | 63.75 | 0.02 | 62.64 | 0.03 | 64.27 | 0.01 | 56.87 | 0.07 | 59.49 | 0.23 | 62.55 | 0.04 | 61.92 | 0.07 | 62.57 | 0.03 | 63.71 | 0.03 | 62.03 | 0.04 | 55.34 | 0.11 | 61.89 | 0.03 | 61.37 | 0.04 | 58.88 | 0.07 | 58.9 | 0.05 | 60.54 | 0.02 | 59.86 | 0.05 | [16 empty] | 60.03 | 0.04 | 59.63 | 0.19 | 60.5 | 0.03 | 56.88 | 0.05 | [16 empty] | 60.64 | 0.09 | [12 empty] | 60.5 | 0.02 | 58.05 | 0.21 | 56.46 | 0.08 | 75.23 | 0.03 | 74.6 | 0.03 | 74.93 | 0.03 | 75.7 | 0.03 | 75.72 | 0.03 | 75.78 | 0.03 | 75.55 | 0.03 | 54.94 | 0.06 | 58.15 | 0.18 | 58.35 | 0.17 | 54.65 | 0.09 | 58.7 | 0.15 | 60.69 | 0.32 | 57.8 | 0.25 | 61.01 | 0.21 | 61.85 | 0.2 | 62.09 | 0.24 | 59.77 | 0.17 | 60.05 | 0.13 | 63.56 | 0.12 | 63.74 | 0.15 | 62.35 | 0.23 | 64.72 | 0.19 | 65.81 | 0.15 | 65.07 | 0.14 | 66.31 | 0.18 |  |  | 75.15 | 0.03 | 75.64 | 0.03 | 75.58 | 0.03 | 75.38 | 0.03 | 74.82 |  | 75.02 | 0.03 | 55.07 | 0.08 |  |  | 57.09 | 0.09 | 59 | 0.13 | 62.77 | 0.15 | [62 empty] | Economizer test | 74.932 | 0.031 | 61.99 | 0.029 | 61.263 | 0.033 | 54.389 | 0.029 | 55.015 | 0.007 | 50.994 | 0.016 | 1978.6 | 1.8 | 1939.2 | 1.7 | 0.195 | 0.002 | -0.032 | 0.001 | 0.063 | 0.002 | 0.8075 | 0.0014 | 29.463 | 0.001 | 800 | 8 | 710 |  | 0.63358 | 1228.6371 | 13.03 | 0.032 | 1.0514 | 8999.7062 | 44.4245 | 1228.629 | 5657.6138 | 3342.0924 | 0.0076488 | 23.3098 | 60.2116 | 13.0298 | 13.1911 | 0.0069746 | 20.774 | 0.0087901 | 27.6024 | 0.0073677 | 22.7206 | 62.4267 | 55.3596 | 22.4649
2 | T2-MF2-100C1-100C2-63A-95-CCE | 75T0034 | T2-MF2-100C1-100C2-63A-95-CCE | closed | on | on | 3 turns | unsealed | unsealed | 650 | 9.25 |  | 30 | 0 | CUST 5 | 10/10/2014 | 15:07:09 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.5 | 15.1 | 0 | 50992 | 63 | 49661 | 282 | 17573 | 128 | 68580 | 136 | 8.176 | 648 |  |  | 6.0792 | [35 empty] | MF2, 100% charge CK1 and CK2, 62.5% airflow (250 cfm/ton), 30% condenser--coil blockage, 2 HP fan motor, 3 turns, 9.25" AK94 pulley (650 rpm), adjust code--tester speed to match total static of run T2-MF2-100C1-100C2-63A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 9.25` mtr. pulley: 3 turns open: AX 38 belt: 100% inlet-outlet Meriam: condenser coil blocked 33.5` of 62` coil | 74.998 | 0.02 | 62 | 0.021 | 95.008 | 0.015 | 75.009 | 0.031 | 74.66 | 0.12 | 52.3 | 0.07 | 58.36 | 0.02 | 0.062 | 0.002 | 0.8218 | 0.0016 | 50992 | 63 | 17573 | 128 | 8.176 | 0.025 | [6 empty] | 460.8 | 2.6 | 461 | 2.6 | 459.1 | 2.6 | 15.1 | 0.1 | 12.9 | 0 | 12.7 | 0.1 | 6861.4 | 53.7 | 3212.2 | 65.5 | 1526.8 | 39.7 | 460 |  | 460 |  | 459 |  | 2.7 |  | 2.7 |  | 2.7 |  | 0.31 | 460 |  | 459 |  | 459 |  | 5.5 |  | 5.2 |  | 4.8 |  | 3490 |  | 0.85 | 459 | 459 | 459 | 5.4 | 5 | 4.8 | 3350 | 0.84 | 459.8 |  | 1.6 |  | 695.3 |  | 85 |  | 8380.3 | [14 empty] | 245.64 | 0.12 | 115.03 | 0.07 | 115.75 | 0.04 | 0.73 | 0.07 | 273.57 | 0.12 | 189.68 | 0.09 | 123.7 | 0.03 | 65.97 | 0.1 | 239 | 0.04 | 112.32 | 0.04 | 113.77 | 0.04 | 1.45 | 0.04 | 71.27 | 0.04 | 45.64 | 0.15 | 41.6 | 0.03 | 4.03 | 0.14 | 70.69 | 0.04 | 54.55 | 0.12 | 41.21 | 0.03 | 13.34 | 0.11 | [46 empty] | 278.63 | 0.16 | 189.62 | 0.19 | 125.08 | 0.04 | 64.53 | 0.22 | 264.92 | 0.25 | 121.31 | 0.07 | 15.77 | 0.09 | 254 | 0.07 | 98.94 | 0.08 | 118.2 | 0.07 | 19.26 | 0.07 | 72.02 | 0.17 | 42.1 | 0.11 | 2.64 | 0.57 | 71.72 | 0.13 | 56.42 | 0.09 | 41.91 | 0.08 | 14.51 | 0.13 | 105.6 | 0.07 | [28 empty] | 114.8 | 0.07 | 114.41 | 0.06 | 105.6 | 0.07 | 106.13 | 0.08 | 51.52 | 0.08 | 52.06 | 0.05 | 51.94 | 0.04 | 51.87 | 0.04 | 51.94 | 0.04 |  |  | 114.92 | 0.04 | 110.4 | 0.05 | 46.77 | 0.34 | 54.92 | 0.13 | 189.8 | 0.25 | 103.03 | 0.06 | 98.44 | 0.05 | 45.25 | 0.43 | 56.09 | 0.51 | 112.32 | 0.04 | 105.54 | 0.07 | 93.33 | 0.19 | 114.19 | 0.05 | 114.97 | 0.05 | 106.42 | 0.06 | 106.86 | 0.07 | 114.41 | 0.06 | 106.13 | 0.08 | [16 empty] | 115.03 | 0.07 | 105.54 | 0.07 | 114.8 | 0.07 | 105.6 | 0.07 | [16 empty] | 44.74 | 0.47 | [12 empty] | 190.87 | 0.11 | 94.36 | 0.08 | 93.89 | 0.09 | 74.82 | 0.06 | 75.39 | 0.05 | 74.76 | 0.06 | 75.46 | 0.06 | 75.22 | 0.06 | 75.38 | 0.08 | 75.19 | 0.07 | 78.14 | 0.09 | 76.36 | 0.06 | 76.22 | 0.06 | 77.13 | 0.1 | 77.22 | 0.08 | 76.89 | 0.07 | 76.12 | 0.06 | 75.31 | 0.07 | 75.06 | 0.08 | 75.28 | 0.08 | 74.8 | 0.08 | 74.93 | 0.07 | 74.88 | 0.07 | 75.01 | 0.07 | 75.39 | 0.07 | 75.03 | 0.07 | 74.8 | 0.05 | 76.21 | 0.08 | 76.31 | 0.09 |  |  | 74.84 | 0.07 | 74.88 | 0.06 | 75.27 | 0.07 | 75.11 | 0.08 | 75.31 |  | 74.86 | 0.08 | 76.96 | 0.31 | 79.72 | 0.07 | 77.62 | 0.07 | 75.12 | 0.08 | 74.93 | 0.07 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 74.998 | 0.02 | 62 | 0.021 | 52.028 | 0.01 | 49.96 | 0.016 | 95.008 | 0.015 | 75.009 | 0.031 | 1992.1 | 2 | 1961.4 | 1.9 | 0.289 | 0.002 | -0.14 | 0.001 | 0.062 | 0.002 | 0.8218 | 0.0016 | 29.194 | 0.001 | 8388 | 20 | 760 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.0685 | 9225.9386 | 66.5931 | 56.1367 | 238.8766 | 8987.0621 | 0.0089143 | 27.882 | 50.9595 | 14.1002 | 12.9554 | 0.013927 | 38.1657 | 0.0087811 | 27.6087 | 0.0071324 | 20.219 | 75.5208 | 62.3878 | 19.9591 | 73095.8751 | 54384.3048 | 7628 | 0.35617 | 70729.2773 | 52017.707 | 8.4322 | 0.13726 | -7.9229 | -24.5613 | 47.0519 | 73095.8751 | 68176.9292 | 2397.1224 | 2521.8235 | 73095.8751 | 100%
2 | T2-MF21-115C1-115C2-63A-95-CE | 75T0035 | T2-MF21-115C1-115C2-63A-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 650 | 9.25 |  | 0 | 0 | CUST 5 | 10/8/2014 | 1:00:19 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 7.36 lbs/CK2- 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 461.2 | 1.4 | 14.7 | 0 | 52203 | 59 | 51484 | 238 | 19179 | 107 | 71401 | 141 | 9.1434 | 648 |  |  | 6.685 | [35 empty] | MF21, 115% charge CK1 and CK2, 62.5% airflow (250 cfm/ton), closed damper, 2 HP fan motor,--3 turns, 9.25" AK94 pulley (650 rpm), adjust code tester speed to match total static of run--T2-MF20-115C1-100C2-63A-95-CE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 9.25` mtr. pulley: 3 turns open: AX 38 belt: 100% inlet-outlet Meriam | 74.985 | 0.011 | 62.001 | 0.02 | 95 | 0.012 | 74.998 | 0.022 | 74.85 | 0.1 | 51.74 | 0.06 | 57.28 | 0.02 | 0.08 | 0.002 | 1.5194 | 0.0023 | 52203 | 59 | 19179 | 107 | 9.143 | 0.029 | [6 empty] | 461.2 | 2.6 | 461.9 | 2.6 | 458.9 | 2.6 | 14.7 | 0.1 | 12.3 | 0 | 12.1 | 0.1 | 6632 | 55.8 | 3158.4 | 64.1 | 1177 | 41.5 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.6 |  | 0.32 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.8 |  | 4.4 |  | 3140 |  | 0.83 | 460 | 460 | 460 | 5.2 | 4.6 | 4.4 | 3110 | 0.82 | 460.3 |  | 1.6 |  | 702.5 |  | 85 |  | 7807.5 | [14 empty] | 227.15 | 0.12 | 98.81 | 0.08 | 110.15 | 0.04 | 11.33 | 0.08 | 245.66 | 0.13 | 175.52 | 0.12 | 115.77 | 0.04 | 59.75 | 0.13 | 221.6 | 0.05 | 97.36 | 0.05 | 108.4 | 0.05 | 11.08 | 0.05 | 69.56 | 0.05 | 44.1 | 0.19 | 40.47 | 0.03 | 3.63 | 0.2 | 68.98 | 0.05 | 50.95 | 0.25 | 40.08 | 0.03 | 10.87 | 0.27 | [46 empty] | 255.51 | 0.13 | 178.54 | 0.14 | 118.64 | 0.04 | 59.89 | 0.15 | 242.15 | 0.22 | 114.74 | 0.07 | 17.14 | 0.08 | 232.5 | 0.05 | 91.52 | 0.04 | 111.8 | 0.05 | 20.28 | 0.05 | 71.07 | 0.13 | 41.49 | 0.09 | 2.79 | 0.35 | 70.73 | 0.11 | 52.61 | 0.2 | 41.27 | 0.07 | 11.34 | 0.21 | 97.33 | 0.05 | [28 empty] | 98.93 | 0.08 | 98.8 | 0.06 | 97.33 | 0.05 | 97.71 | 0.07 | 50.9 | 0.07 | 51.48 | 0.05 | 51.37 | 0.04 | 51.18 | 0.05 | 51.28 | 0.04 |  |  | 98.34 | 0.05 | 96.89 | 0.07 | 44.93 | 0.42 | 50.63 | 0.27 | 178.59 | 0.17 | 95.04 | 0.06 | 91.08 | 0.03 | 44.31 | 0.24 | 54.46 | 0.28 | 97.36 | 0.05 | 97.6 | 0.07 | 93.08 | 0.2 | 98.61 | 0.1 | 99.28 | 0.06 | 98.05 | 0.05 | 98.37 | 0.05 | 98.8 | 0.06 | 97.71 | 0.07 | [16 empty] | 98.81 | 0.08 | 97.6 | 0.07 | 98.93 | 0.08 | 97.33 | 0.05 | [16 empty] | 44.26 | 0.27 | [12 empty] | 176.54 | 0.16 | 95.36 | 0.08 | 95.29 | 0.09 | 75.2 | 0.06 | 75.72 | 0.04 | 75.12 | 0.06 | 75.83 | 0.06 | 75.6 | 0.06 | 75.76 | 0.07 | 75.55 | 0.06 | 78.43 | 0.07 | 76.81 | 0.05 | 76.71 | 0.05 | 77.36 | 0.07 | 77.59 | 0.07 | 77.35 | 0.06 | 76.57 | 0.07 | 75.72 | 0.06 | 75.55 | 0.1 | 75.67 | 0.07 | 75.16 | 0.07 | 75.37 | 0.06 | 75.3 | 0.06 | 75.64 | 0.11 | 76.85 | 0.09 | 75.46 | 0.06 | 76.34 | 0.08 | 80.39 | 0.19 | 80.41 | 0.24 |  |  | 75.14 | 0.06 | 75.17 | 0.06 | 75.59 | 0.07 | 75.38 | 0.07 | 75.57 |  | 75.19 | 0.06 | 80.08 | 0.06 | 80.25 | 0.07 | 77.9 | 0.06 | 75.51 | 0.07 | 75.37 | 0.06 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 74.985 | 0.011 | 62.001 | 0.02 | 51.542 | 0.005 | 49.417 | 0.01 | 95 | 0.012 | 74.998 | 0.022 | 1989.8 | 1.5 | 1969.2 | 1.5 | 0.292 | 0.002 | -0.139 | 0.001 | 0.08 | 0.002 | 1.5194 | 0.0023 | 29.273 | 0.001 | 7809 | 20 | 770 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.0825 | 9224.9701 | 67.5519 | 55.9353 | 238.0242 | 8986.946 | 0.0089173 | 27.8817 | 50.4595 | 14.0999 | 12.9418 | 0.013919 | 38.1552 | 0.0087848 | 27.6096 | 0.0069648 | 19.9191 | 75.5061 | 62.3871 | 19.656 | 75881.9544 | 55453.1677 | 7039 | 0.3166 | 73484.4992 | 53055.7125 | 9.4102 | 0.14505 | -8.2257 | -25.0467 | 46.2101 | 75881.9544 | 70944.2097 | 2427.6347 | 2510.1101 | 75881.9544 | 100%
2 | T2-MF24-85C1-85C2-63A-95-CE | 75T0036 | T2-MF24-85C1-85C2-63A-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 650 | 9.25 |  | 0 | 0 | CUST 5 | 10/8/2014 | 2:49:12 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 5.44 lbs/CK2- 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 461.1 | 1.4 | 14.4 | 0 | 49876 | 57 | 49041 | 227 | 16667 | 98 | 66559 | 98 | 8.8064 | 648 |  |  | 6.5991 | [35 empty] | MF24, 85% charge CK1 and CK2, 62.5% airflow (250 cfm/ton), 2 HP fan motor, 3 turns,--9.25" AK94 pulley (650 rpm), adjust code tester speed to match total static of run--T2-MF20-115C1-100C2-63A-95-CE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 9.25` mtr. pulley: 3 turns open: AX 38 belt: 100% inlet-outlet Meriam | 74.995 | 0.009 | 62.002 | 0.019 | 94.992 | 0.013 | 74.999 | 0.021 | 74.82 | 0.09 | 52.71 | 0.06 | 58.02 | 0.03 | 0.072 | 0.003 | 1.512 | 0.0017 | 49876 | 57 | 16667 | 98 | 8.807 | 0.028 | [6 empty] | 461.1 | 2.6 | 461.8 | 2.6 | 458.9 | 2.6 | 14.4 | 0.1 | 12 | 0 | 11.9 | 0.1 | 6489.5 | 56.9 | 3142.2 | 65 | 1067.9 | 42.6 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.6 |  | 0.31 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.7 |  | 4.3 |  | 3060 |  | 0.82 | 460 | 460 | 460 | 5 | 4.5 | 4.3 | 2940 | 0.8 | 460.3 |  | 1.6 |  | 703.5 |  | 85 |  | 7558.5 | [14 empty] | 207.99 | 0.13 | 103.72 | 0.07 | 103.99 | 0.04 | 0.26 | 0.06 | 239.25 | 0.13 | 188.82 | 0.08 | 113.86 | 0.04 | 74.96 | 0.07 | 196.1 | 0.05 | 99.56 | 0.04 | 99.96 | 0.05 | 0.43 | 0.05 | 68.88 | 0.03 | 64.07 | 0.06 | 40.02 | 0.03 | 24.05 | 0.05 | 68.31 | 0.03 | 66.5 | 0.06 | 39.62 | 0.02 | 26.89 | 0.06 | [46 empty] | 240.8 | 0.14 | 172.31 | 0.1 | 114.33 | 0.04 | 57.99 | 0.12 | 220.82 | 0.22 | 108.16 | 0.07 | 1.43 | 0.07 | 210.9 | 0.05 | 99.47 | 0.06 | 104.96 | 0.05 | 5.49 | 0.05 | 71.64 | 0.08 | 41.89 | 0.06 | 3.09 | 0.29 | 71.32 | 0.08 | 67.55 | 0.06 | 41.67 | 0.05 | 25.88 | 0.07 | 106.22 | 0.12 | [28 empty] | 102.24 | 0.07 | 101.68 | 0.06 | 106.22 | 0.12 | 106.35 | 0.08 | 51.82 | 0.07 | 52.51 | 0.06 | 52.43 | 0.05 | 52.16 | 0.05 | 52.29 | 0.05 |  |  | 102.26 | 0.05 | 98.93 | 0.07 | 64.52 | 0.07 | 66.17 | 0.05 | 172.4 | 0.11 | 103.4 | 0.06 | 98.95 | 0.04 | 45.04 | 0.25 | 55.5 | 0.18 | 99.56 | 0.04 | 106.73 | 0.13 | 93.3 | 0.16 | 103.6 | 0.05 | 102.11 | 0.05 | 106.36 | 0.07 | 106.49 | 0.08 | 101.68 | 0.06 | 106.35 | 0.08 | [16 empty] | 103.72 | 0.07 | 106.73 | 0.13 | 102.24 | 0.07 | 106.22 | 0.12 | [16 empty] | 44.98 | 0.25 | [12 empty] | 189.94 | 0.08 | 95.4 | 0.08 | 95.31 | 0.09 | 75.18 | 0.05 | 75.67 | 0.05 | 75.1 | 0.05 | 75.84 | 0.05 | 75.61 | 0.05 | 75.72 | 0.06 | 75.51 | 0.06 | 78.46 | 0.07 | 76.82 | 0.05 | 76.74 | 0.04 | 77.4 | 0.08 | 77.63 | 0.06 | 77.39 | 0.05 | 76.65 | 0.05 | 75.72 | 0.05 | 76.78 | 1.18 | 75.67 | 0.07 | 75.14 | 0.05 | 75.35 | 0.06 | 75.28 | 0.06 | 75.58 | 0.12 | 76.88 | 0.08 | 75.45 | 0.06 | 76.3 | 0.08 | 80.46 | 0.17 | 80.43 | 0.21 |  |  | 75.13 | 0.05 | 75.18 | 0.05 | 75.57 | 0.06 | 75.36 | 0.06 | 75.55 |  | 75.17 | 0.06 | 80.14 | 0.06 | 79.97 | 0.07 | 77.95 | 0.06 | 75.5 | 0.06 | 75.35 | 0.05 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 74.995 | 0.009 | 62.002 | 0.019 | 52.504 | 0.016 | 50.323 | 0.019 | 94.992 | 0.013 | 74.999 | 0.021 | 1985.7 | 1.1 | 1963 | 1.2 | 0.295 | 0.002 | -0.139 | 0.001 | 0.072 | 0.003 | 1.512 | 0.0017 | 29.294 | 0.001 | 7558 | 21 | 770 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.0862 | 9187.3237 | 68.0311 | 55.9349 | 238.0257 | 8949.298 | 0.0089163 | 27.8834 | 51.4178 | 14.0997 | 12.9681 | 0.013922 | 38.1563 | 0.0087831 | 27.6102 | 0.0072105 | 20.4194 | 75.5178 | 62.3897 | 20.1552 | 71001.156 | 53139.5801 | 6788 | 0.3263 | 68605.3362 | 50743.7602 | 9.0772 | 0.14514 | -7.7282 | -24.1 | 47.326 | 71001.156 | 66063.8351 | 2427.0674 | 2510.2535 | 71001.156 | 100%
2 | T2-MF38-100C1-100C2-63A-95-CE | 75T0041 | T2-MF38-100C1-100C2-63A-95-CE | closed | on | on | 3 turns | unsealed | unsealed | 640 | 9.25 |  | 0 | 0 | CUST 5 | 10/9/2014 | 8:19:09 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.5 | 14.5 | 0 | 51586 | 78 | 50860 | 259 | 18106 | 91 | 69709 | 135 | 9.059 | 647 |  |  | 6.7038 | [35 empty] | MF38, 100% charge CK1 and CK2, 62.5% airflow (250 cfm/ton), 2 HP fan motor,--3 turns, 9.25" AK94 pulley (640 rpm), adjust code tester speed to match total--static of run T2-MF38-100C1-100C2-63A-95-CE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 9.25` mtr. pulley: 3 turns open: AX 38 belt: 100% inlet-outlet Meriam | 74.998 | 0.018 | 61.997 | 0.016 | 94.995 | 0.01 | 74.996 | 0.021 | 74.7 | 0.1 | 51.83 | 0.09 | 57.63 | 0.02 | 0.078 | 0.002 | 1.5137 | 0.0025 | 51586 | 78 | 18106 | 91 | 9.059 | 0.028 | [6 empty] | 461.1 | 2.7 | 461.7 | 2.7 | 459.2 | 2.7 | 14.5 | 0.1 | 12.2 | 0 | 12.1 | 0.1 | 6539.2 | 57.2 | 3190.4 | 68 | 1156.2 | 42.6 | 460 |  | 459 |  | 459 |  | 2.8 |  | 2.8 |  | 2.6 |  | 0.32 | 460 |  | 459 |  | 459 |  | 5.1 |  | 4.8 |  | 4.4 |  | 3140 |  | 0.83 | 460 | 459 | 459 | 5 | 4.6 | 4.3 | 3000 | 0.81 | 460.3 |  | 1.6 |  | 702.6 |  | 85 |  | 7677.6 | [14 empty] | 217.6 | 0.1 | 106.63 | 0.08 | 107.13 | 0.03 | 0.5 | 0.08 | 244.34 | 0.09 | 176.48 | 0.08 | 115.39 | 0.03 | 61.09 | 0.09 | 210 | 0.03 | 103.55 | 0.04 | 104.65 | 0.04 | 1.1 | 0.04 | 70.37 | 0.03 | 45.93 | 0.25 | 41.04 | 0.02 | 4.89 | 0.25 | 69.76 | 0.03 | 53.41 | 0.17 | 40.63 | 0.02 | 12.77 | 0.16 | [46 empty] | 247.69 | 0.11 | 175.7 | 0.15 | 116.38 | 0.03 | 59.32 | 0.16 | 233.56 | 0.2 | 112.14 | 0.06 | 11.47 | 0.06 | 223.6 | 0.03 | 94.2 | 0.04 | 109.04 | 0.04 | 14.84 | 0.04 | 71.2 | 0.14 | 41.6 | 0.09 | 2.89 | 0.36 | 70.9 | 0.11 | 55.07 | 0.15 | 41.4 | 0.07 | 13.67 | 0.14 | 100.17 | 0.06 | [28 empty] | 105.9 | 0.08 | 105.39 | 0.07 | 100.17 | 0.06 | 100.49 | 0.08 | 51.12 | 0.08 | 51.67 | 0.06 | 51.55 | 0.06 | 51.25 | 0.06 | 51.37 | 0.05 |  |  | 105.24 | 0.04 | 101.96 | 0.08 | 47.08 | 0.4 | 52.73 | 0.18 | 175.64 | 0.18 | 97.95 | 0.06 | 93.77 | 0.04 | 44.53 | 0.24 | 54.87 | 0.28 | 103.55 | 0.04 | 100.67 | 0.04 | 93.49 | 0.08 | 106.47 | 0.05 | 106.08 | 0.05 | 101.02 | 0.05 | 101.37 | 0.04 | 105.39 | 0.07 | 100.49 | 0.08 | [16 empty] | 106.63 | 0.08 | 100.67 | 0.04 | 105.9 | 0.08 | 100.17 | 0.06 | [16 empty] | 44.49 | 0.28 | [12 empty] | 177.39 | 0.1 | 95.39 | 0.07 | 95.16 | 0.06 | 75.03 | 0.07 | 75.6 | 0.06 | 75.06 | 0.06 | 75.56 | 0.07 | 75.38 | 0.07 | 75.54 | 0.08 | 75.38 | 0.07 | 78.43 | 0.08 | 76.87 | 0.07 | 76.67 | 0.07 | 77.44 | 0.1 | 77.56 | 0.08 | 77.28 | 0.07 | 76.37 | 0.08 | 75.71 | 0.07 | 75.1 | 0.07 | 75.5 | 0.08 | 75.16 | 0.07 | 75.45 | 0.07 | 75.34 | 0.07 | 76 | 0.11 | 76.72 | 0.1 | 75.55 | 0.07 | 76.73 | 0.11 | 80.27 | 0.2 | 80.88 | 0.17 |  |  | 75.07 | 0.06 | 75.26 | 0.06 | 75.66 | 0.07 | 75.44 | 0.07 | 75.66 |  | 75.2 | 0.06 | 80.14 | 0.07 | 79.82 | 0.13 | 77.98 | 0.08 | 75.46 | 0.08 | 75.42 | 0.07 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 74.998 | 0.018 | 61.997 | 0.016 | 51.793 | 0.011 | 49.715 | 0.018 | 94.995 | 0.01 | 74.996 | 0.021 | 1985 | 1.6 | 1966.3 | 1.6 | 0.297 | 0.002 | -0.138 | 0.001 | 0.078 | 0.002 | 1.5137 | 0.0025 | 29.323 | 0.001 | 7695 | 20 | 750 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.0532 | 9197.6772 | 68.6075 | 55.7334 | 237.1675 | 8960.5097 | 0.0089116 | 27.8785 | 50.7398 | 14.0998 | 12.9489 | 0.013918 | 38.1533 | 0.0087791 | 27.6065 | 0.0070601 | 20.0835 | 75.5183 | 62.3829 | 19.8274 | 74051.0568 | 54697.2207 | 6945 | 0.32009 | 71725.4641 | 52371.6279 | 9.321 | 0.14013 | -8.0511 | -24.7785 | 46.7017 | 74051.0568 | 69194.4106 | 2355.2776 | 2501.3687 | 74051.0568 | 100%
2 | T2-MF4-85C1-85C2-63A-95-CCE | 75T0043 | T2-MF4-85C1-85C2-63A-95-CCE | closed | on | on | 3 turns | unsealed | unsealed | 650 | 9.25 |  | 30 | 0 | CUST 5 | 10/10/2014 | 18:24:45 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.44 lbs/CK2: 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 461.2 | 1.6 | 15 | 0 | 49191 | 64 | 47853 | 252 | 15717 | 133 | 64923 | 168 | 7.9349 | 648 |  |  | 6.0121 | [35 empty] | MF4, 85% charge CK1 and CK2, 62.5% airflow (250 cfm/ton), 30% condenser coil blockage,--2 HP fan motor, 3 turns, 9.25" AK94 pulley (650 rpm), adjust code tester speed to match total--static of run T2-MF2-100C1-100C2-63A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 9.25` mtr. pulley: 3 turns open: AX 38 belt: 100% inlet-outlet Meriam: condenser coil blocked 33.5` of 62` coil | 75.009 | 0.014 | 61.999 | 0.026 | 95.015 | 0.029 | 74.991 | 0.021 | 74.64 | 0.12 | 52.96 | 0.08 | 58.86 | 0.02 | 0.055 | 0.002 | 0.8147 | 0.0017 | 49191 | 64 | 15717 | 133 | 7.935 | 0.028 | [6 empty] | 461.2 | 2.5 | 461.4 | 2.5 | 458.8 | 2.5 | 15 | 0.1 | 12.7 | 0 | 12.4 | 0.1 | 6795 | 53.7 | 3160.5 | 61.9 | 1386.8 | 40 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.6 |  | 0.32 | 460 |  | 460 |  | 460 |  | 5.4 |  | 5 |  | 4.7 |  | 3390 |  | 0.85 | 460 | 460 | 460 | 5.3 | 5.4 | 4.6 | 3240 | 0.82 | 460.2 |  | 1.6 |  | 696.6 |  | 85 |  | 8181.6 | [14 empty] | 232.84 | 0.16 | 111.34 | 0.08 | 111.9 | 0.05 | 0.56 | 0.07 | 266.69 | 0.15 | 200.41 | 0.12 | 121.8 | 0.04 | 78.61 | 0.12 | 220.3 | 0.05 | 107.07 | 0.06 | 107.97 | 0.05 | 0.90333 | 0.05 | 69.65 | 0.04 | 63.95 | 0.08 | 40.5 | 0.02 | 23.46 | 0.06 | 69.09 | 0.04 | 67.27 | 0.08 | 40.12 | 0.03 | 27.16 | 0.06 | [46 empty] | 268.73 | 0.21 | 185.07 | 0.25 | 122.36 | 0.06 | 62.7 | 0.28 | 248.98 | 0.35 | 116.73 | 0.1 | 4.71 | 0.25 | 238.3 | 0.05 | 105.76 | 0.12 | 113.55 | 0.05 | 7.6833 | 0.05 | 72.4 | 0.19 | 42.36 | 0.13 | 3.28 | 1.06 | 72.09 | 0.15 | 56.65 | 0.63 | 42.22 | 0.1 | 14.43 | 0.12 | 112.26 | 0.2 | [28 empty] | 110.08 | 0.08 | 109.63 | 0.07 | 112.26 | 0.2 | 112.7 | 0.2 | 52.13 | 0.08 | 52.75 | 0.06 | 52.65 | 0.05 | 52.45 | 0.05 | 52.55 | 0.06 |  |  | 110.81 | 0.05 | 105.14 | 0.07 | 64.43 | 0.1 | 67.49 | 0.08 | 185.21 | 0.3 | 112.33 | 0.2 | 104.56 | 0.11 | 46.06 | 0.96 | 56.65 | 0.63 | 107.07 | 0.06 | 105.76 | 0.12 | 93.47 | 0.14 | 110.52 | 0.09 | 109.94 | 0.06 | 112.13 | 0.14 | 112.45 | 0.15 | 109.63 | 0.07 | 112.7 | 0.2 | [16 empty] | 111.34 | 0.08 | 112.03 | 0.21 | 110.08 | 0.08 | 112.26 | 0.2 | [16 empty] | 45.63 | 0.95 | [12 empty] | 201.69 | 0.13 | 94.34 | 0.09 | 93.89 | 0.09 | 74.8 | 0.07 | 75.38 | 0.06 | 74.72 | 0.08 | 75.46 | 0.08 | 75.22 | 0.07 | 75.37 | 0.09 | 75.18 | 0.09 | 78.15 | 0.11 | 76.33 | 0.08 | 76.2 | 0.08 | 77.1 | 0.11 | 77.21 | 0.1 | 76.91 | 0.09 | 76.14 | 0.08 | 75.3 | 0.08 | 75.08 | 0.09 | 75.3 | 0.1 | 74.79 | 0.09 | 74.96 | 0.09 | 74.9 | 0.08 | 75.04 | 0.08 | 75.36 | 0.07 | 75.07 | 0.08 | 74.76 | 0.07 | 76.13 | 0.06 | 76.22 | 0.09 |  |  | 74.8 | 0.08 | 74.83 | 0.07 | 75.24 | 0.09 | 75.08 | 0.09 | 75.29 |  | 74.83 | 0.09 | 78.44 | 0.52 | 80 | 0.09 | 77.63 | 0.1 | 75.12 | 0.1 | 74.95 | 0.08 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 75.009 | 0.014 | 61.999 | 0.026 | 52.713 | 0.017 | 50.611 | 0.021 | 95.015 | 0.029 | 74.991 | 0.021 | 1985.1 | 2.1 | 1950.9 | 2 | 0.291 | 0.002 | -0.139 | 0.001 | 0.055 | 0.002 | 0.8147 | 0.0017 | 29.176 | 0 | 8182 | 20 | 770 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.0891 | 9180.2398 | 66.695 | 55.9359 | 238.0216 | 8942.2182 | 0.0089109 | 27.8811 | 51.6239 | 14.1002 | 12.9742 | 0.013909 | 38.1482 | 0.0087778 | 27.6078 | 0.007313 | 20.5814 | 75.5324 | 62.3868 | 20.3165 | 69444.655 | 52676.7504 | 7412 | 0.36428 | 67044.2749 | 50276.3703 | 8.1941 | 0.13622 | -7.5646 | -23.9086 | 47.8535 | 69444.655 | 64503.677 | 2432.1423 | 2508.8356 | 69444.655 | 100%
2 | T2-MF6-115C1-115C2-63A-95-CCE | 75T0044 | T2-MF6-115C1-115C2-63A-95-CCE | closed | on | on | 3 turns | unsealed | unsealed | 650 | 9.25 |  | 30 | 0 | CUST 5 | 10/10/2014 | 19:41:42 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.36 lbs/CK2: 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 461.2 | 1.4 | 15.5 | 0 | 51917 | 66 | 50493 | 250 | 18894 | 114 | 70829 | 150 | 8.2388 | 648 |  |  | 6.039 | [35 empty] | MF6, 115% charge CK1 and CK2, 62.5% airflow (250 cfm/ton), 30% condenser coil blockage,--2 HP fan motor, 3 turns, 9.25" AK94 pulley (650 rpm), adjust code tester speed to match--total static of run T2-MF2-100C1-100C2-63A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 9.25` mtr. pulley: 3 turns open: AX 38 belt: 100% inlet-outlet Meriam: condenser coil blocked 33.5` of 62` coil | 75.004 | 0.014 | 61.999 | 0.018 | 94.984 | 0.037 | 75.001 | 0.04 | 74.43 | 0.1 | 51.62 | 0.05 | 58.01 | 0.02 | 0.057 | 0.002 | 0.8157 | 0.0017 | 51917 | 66 | 18894 | 114 | 8.239 | 0.024 | [6 empty] | 461.2 | 2.6 | 462 | 2.6 | 458.9 | 2.6 | 15.5 | 0.1 | 13.1 | 0 | 12.9 | 0.1 | 7054.6 | 55.3 | 3160.1 | 63.4 | 1542.5 | 41.8 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.6 |  | 0.32 | 460 |  | 460 |  | 460 |  | 5.5 |  | 5.2 |  | 4.8 |  | 3540 |  | 0.85 | 460 | 460 | 460 | 5.6 | 5.1 | 4.9 | 3500 | 0.84 | 460.2 |  | 1.6 |  | 695.4 |  | 85 |  | 8590.4 | [14 empty] | 258.61 | 0.27 | 104.82 | 0.07 | 119.51 | 0.08 | 14.69 | 0.1 | 277.52 | 0.19 | 190.45 | 0.21 | 124.78 | 0.05 | 65.68 | 0.22 | 253.2 | 0.05 | 103.66 | 0.07 | 117.96 | 0.05 | 14.2533 | 0.05 | 70.18 | 0.12 | 44.08 | 0.27 | 40.86 | 0.08 | 3.22 | 0.34 | 69.63 | 0.13 | 51.59 | 0.62 | 40.49 | 0.09 | 11.11 | 0.68 | [46 empty] | 291.61 | 0.25 | 195.29 | 0.22 | 128.54 | 0.07 | 66.76 | 0.23 | 279.02 | 0.38 | 125.18 | 0.1 | 23.62 | 0.1 | 268.8 | 0.05 | 96.22 | 0.05 | 122.38 | 0.05 | 26.1033 | 0.05 | 71.71 | 0.18 | 41.89 | 0.12 | 2.37 | 0.57 | 71.4 | 0.13 | 53.79 | 0.49 | 41.69 | 0.09 | 12.1 | 0.48 | 101.99 | 0.07 | [28 empty] | 105.43 | 0.09 | 105.7 | 0.08 | 101.99 | 0.07 | 102.58 | 0.06 | 50.81 | 0.05 | 51.48 | 0.05 | 51.41 | 0.05 | 51.17 | 0.04 | 51.26 | 0.04 |  |  | 105.14 | 0.08 | 101.73 | 0.09 | 44.77 | 0.74 | 51.94 | 0.65 | 195.37 | 0.28 | 101.95 | 0.06 | 95.36 | 0.05 | 44.9 | 0.43 | 55.35 | 0.58 | 103.66 | 0.07 | 96.22 | 0.05 | 93.37 | 0.19 | 105.81 | 0.08 | 106.04 | 0.08 | 103.61 | 0.07 | 104.04 | 0.07 | 105.7 | 0.08 | 102.58 | 0.06 | [16 empty] | 104.82 | 0.07 | 101.57 | 0.06 | 105.43 | 0.09 | 101.99 | 0.07 | [16 empty] | 44.27 | 0.47 | [12 empty] | 191.64 | 0.27 | 94.23 | 0.1 | 93.77 | 0.12 | 74.65 | 0.06 | 75.27 | 0.05 | 74.63 | 0.06 | 75.32 | 0.06 | 75.06 | 0.05 | 75.22 | 0.07 | 75.04 | 0.06 | 78.1 | 0.09 | 76.32 | 0.06 | 76.15 | 0.07 | 77.07 | 0.09 | 77.14 | 0.07 | 76.81 | 0.05 | 75.99 | 0.07 | 75.21 | 0.06 | 75.02 | 0.07 | 75.18 | 0.07 | 74.71 | 0.07 | 74.87 | 0.06 | 74.81 | 0.06 | 74.93 | 0.06 | 75.29 | 0.06 | 75 | 0.06 | 74.76 | 0.05 | 76.14 | 0.07 | 76.24 | 0.09 |  |  | 74.68 | 0.06 | 74.77 | 0.06 | 75.19 | 0.07 | 75.03 | 0.07 | 75.27 |  | 74.79 | 0.07 | 77.48 | 0.25 | 79.77 | 0.08 | 77.54 | 0.08 | 75.04 | 0.07 | 74.86 | 0.06 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 75.004 | 0.014 | 61.999 | 0.018 | 51.548 | 0.008 | 49.473 | 0.016 | 94.984 | 0.037 | 75.001 | 0.04 | 1984.6 | 2.1 | 1954.3 | 2.1 | 0.291 | 0.002 | -0.139 | 0.001 | 0.057 | 0.002 | 0.8157 | 0.0017 | 29.173 | 0 | 8597 | 19 | 770 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.0866 | 9200.6031 | 66.8112 | 55.9346 | 238.0271 | 8962.576 | 0.0089122 | 27.8808 | 50.4614 | 14.0995 | 12.9422 | 0.013925 | 38.1584 | 0.008779 | 27.6079 | 0.0069923 | 19.9504 | 75.5256 | 62.3863 | 19.6863 | 75394.716 | 55345.3254 | 7827 | 0.35432 | 72994.7327 | 52945.3421 | 8.4907 | 0.13947 | -8.1945 | -25.0642 | 46.3992 | 75394.716 | 70453.0891 | 2430.3168 | 2511.3101 | 75394.716 | 100%
2 | T2-TRN-88A-55-1ER-DM | 75T0083 | T2-TRN-88A-55-1ER-DM | 10% open | off | off | 3.5 turns | unsealed | unsealed | 864 | 6.25 |  | 0 | 0 | CUST 5 | 10/21/2014 | 2:14:58 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.1 | 0 | 3.4 | 0 | 3274 | 17 | 2912 | 93 | 3018 | 69 | 6294 | 65 | 4.4702 | 862 | 1310 |  | 2.3253 | [35 empty] | Econo 10%-open (2.8V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor,--3.5 turns, 6.25" AK64 pulley (864 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-88A-55-1E-DM-S | W/ECO: Eco set at 2.8v: No Compr:55/51 amb:2HP blwr mtr 6.25` AK64 mtr. pulley:3.5 turns open: AX38 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.995 | 0.012 | 61.996 | 0.01 | 55.007 | 0.014 | 51.009 | 0.014 | 74.92 | 0.04 | 73.97 | 0.04 | 74.3 | 0.01 | 0.147 | 0.003 | 1.5532 | 0.0031 | 3274 | 17 | 3018 | 69 | 4.471 | 0.077 | [6 empty] | 460.1 | 2 | 461.8 | 2 | 459.9 | 2 | 3.4 | 0 | 2.9 | 0 | 3.3 | 0 | 1437.6 | 17 | 1089.2 | 18.4 | -9.8 | 1.2 | 460 |  | 460 |  | 460 |  | 3 |  | 3 |  | 2.8 |  | 0.48 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1395 | [14 empty] | 96.66 | 0.02 | 55.62 | 0.06 | 57.15 | 0.01 | 1.53 | 0.06 | 96.22 | 0.03 | 57.11 | 0.02 | 56.9 | 0.01 | 0.22 | 0.02 |  |  | 70.06 | 0.03 |  |  |  |  | 96.25 | 0.02 | 71.41 | 0.03 | 56.92 | 0.01 | 14.49 | 0.03 | 95.8 | 0.01 | 57.08 | 0.01 | 56.66 | 0.01 | 0.43 | 0.02 | [46 empty] | 96.37 | 0.03 | 56.74 | 0.02 | 56.98 | 0.02 | 0.24 | 0.02 | 97.01 | 0.04 | 57.33 | 0.02 | 1.03 | 0.04 |  |  | 73.05 | 0.02 |  |  |  |  | 96.18 | 0.04 | 56.87 | 0.02 | 14.26 | 0.05 | 96.27 | 0.04 | 58.91 | 0.02 | 56.92 | 0.02 | 1.99 | 0.03 | 58.19 | 0.03 | [28 empty] | 56.84 | 0.04 | 58.3 | 0.02 | 58.19 | 0.03 | 59.71 | 0.05 | 73.93 | 0.04 | 73.83 | 0.03 | 73.74 | 0.03 | 74.23 | 0.02 | 74.25 | 0.02 |  |  | 55.11 | 0.02 | 70.45 | 0.04 | 71.66 | 0.04 | 57.58 | 0.02 | 57.33 | 0.02 | 56.48 | 0.02 | 73.6 | 0.02 | 72.36 | 0.02 | 60.87 | 0.03 | 70.06 | 0.03 | 73.05 | 0.02 | 55.23 | 0.03 | 56.18 | 0.02 | 59.26 | 0.02 | 56.95 | 0.02 | 57.69 | 0.01 | 58.3 | 0.02 | 59.71 | 0.05 | [16 empty] | 55.62 | 0.06 | 56.31 | 0.05 | 56.84 | 0.04 | 58.19 | 0.03 | [16 empty] | 71.13 | 0.05 | [12 empty] | 57.22 | 0.02 | 56.76 | 0.12 | 56.64 | 0.15 | 75.28 | 0.02 | 74.93 | 0.02 | 74.83 | 0.02 | 75.64 | 0.02 | 75.62 | 0.02 | 75.61 | 0.02 | 75.41 | 0.03 | 67.14 | 0.12 | 67.27 | 0.18 | 73.87 | 0.04 | 70.4 | 0.14 | 70.81 | 0.1 | 72.49 | 0.04 | 73.9 | 0.05 | 74.27 | 0.05 | 73.36 | 0.05 | 73.2 | 0.07 | 73.76 | 0.05 | 74.74 | 0.03 | 74.71 | 0.03 | 74.4 | 0.05 | 72.34 | 0.08 | 74.68 | 0.02 | 73.77 | 0.07 | 67.24 | 0.11 | 67.43 | 0.14 |  |  | 75.03 | 0.02 | 75.62 | 0.02 | 75.44 | 0.02 | 75.29 | 0.02 | 74.8 |  | 74.96 | 0.03 | 67.54 | 0.11 | 68.86 | 0.09 | 71.15 | 0.08 | 73.79 | 0.04 | 74.77 | 0.03 | [62 empty] | Economizer test | 74.995 | 0.012 | 61.996 | 0.01 | 73.918 | 0.008 | 61.284 | 0.009 | 55.007 | 0.014 | 51.009 | 0.014 | 2778.2 | 2.8 | 2664.5 | 2.6 | 0.537 | 0.002 | -0.237 | 0.002 | 0.147 | 0.003 | 1.5532 | 0.0031 | 29.378 | 0 | 1408 | 19 | 1310 |  | 0 | 0 | 13.03 | 0.237 | 1.3168 | 12328.1929 | 168.0951 | 0 | 0 | 12328.1929 | 0.0087792 | 27.6058 | 72.6012 | 13.0297 | 13.5212 | 0.0069845 | 20.7828 | 0.0087792 | 27.6058 | 0.0085676 | 27.1117 | 74.995 | 61.996 | 26.7906
2 | T2-TRN-88A-55-1F-DM-2 | 75T0084 | T2-TRN-88A-55-1F-DM-2 | 1 finger | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 5:47:35 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.4 | 0 | 11168 | 28 | 10677 | 63 | 6094 | 85 | 17268 | 91 | 12.4769 | 858 | 1280 |  | 8.0694 | [35 empty] | Econo 1F-open (5.1V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor,--4.5 turns, 5.75" AK59 pulley (866 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-88A-55-1F-DM-2- | W/ECO: 5.1 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.004 | 0.008 | 61.998 | 0.021 | 55.007 | 0.009 | 50.993 | 0.01 | 75.13 | 0.02 | 71.66 | 0.02 | 72.15 | 0 | 0.156 | 0.003 | 1.6201 | 0.0028 | 11168 | 28 | 6094 | 85 | 12.479 | 0.117 | [6 empty] | 460.5 | 2 | 461 | 2 | 459.4 | 2 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1430 | 15.1 | 1092 | 18.7 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1365 | [14 empty] | 96.21 | 0.04 | 59.4 | 0.03 | 56.93 | 0.02 | 2.47 | 0.04 | 97.25 | 0.02 | 58.79 | 0.02 | 57.51 | 0.01 | 1.28 | 0.02 |  |  | 71.79 | 0.01 |  |  |  |  | 96.95 | 0.07 | 70.66 | 0.01 | 57.33 | 0.04 | 13.32 | 0.04 | 96.61 | 0.02 | 63.51 | 0.02 | 57.14 | 0.01 | 6.36 | 0.02 | [46 empty] | 97.96 | 0.04 | 61.19 | 0.02 | 57.9 | 0.03 | 3.29 | 0.02 | 97.84 | 0.04 | 57.83 | 0.02 | 0.75 | 0.07 |  |  | 71.91 | 0.01 |  |  |  |  | 97.15 | 0.04 | 57.44 | 0.02 | 13.43 | 0.04 | 97.21 | 0.02 | 62.62 | 0.02 | 57.48 | 0.02 | 5.14 | 0.03 | 62.19 | 0.03 | [28 empty] | 60.86 | 0.03 | 61.59 | 0.02 | 62.19 | 0.03 | 62.92 | 0.03 | 72.16 | 0.02 | 71.13 | 0.03 | 70.82 | 0.02 | 72.39 | 0.02 | 72.26 | 0.02 |  |  | 58.65 | 0.03 | 72.1 | 0.02 | 71.66 | 0.01 | 63.33 | 0.02 | 61.9 | 0.02 | 58.63 | 0.05 | 72.42 | 0.02 | 72.15 | 0.01 | 64.75 | 0.02 | 71.79 | 0.01 | 71.91 | 0.01 | 55.61 | 0.04 | 60.96 | 0.02 | 62.53 | 0.01 | 59.82 | 0.08 | 61 | 0.07 | 61.59 | 0.02 | 62.92 | 0.03 | [16 empty] | 59.4 | 0.03 | 58.58 | 0.06 | 60.86 | 0.03 | 62.19 | 0.03 | [16 empty] | 70.87 | 0.04 | [12 empty] | 59.05 | 0.02 | 57.25 | 0.15 | 56.04 | 0.05 | 75.46 | 0.01 | 73.18 | 0.04 | 74.89 | 0.02 | 74.17 | 0.04 | 75.98 | 1.14 | 75.88 | 0.02 | 75.49 | 0.02 | 63.99 | 0.14 | 67.53 | 0.14 | 68.3 | 0.47 | 65.35 | 0.17 | 64.26 | 0.12 | 68.33 | 0.09 | 70.01 | 0.05 | 70.04 | 0.04 | 66.85 | 0.14 | 69.37 | 0.06 | 66.27 | 0.2 | 71.14 | 0.15 | 73.72 | 0.11 | 73.5 | 0.14 | 73.71 | 0.05 | 70.61 | 0.14 | 74.2 | 0.04 | 73.24 | 0.07 | 70.42 | 0.06 |  |  | 73.52 | 0.05 | 75.87 | 0.02 | 75.7 | 0.02 | 75.05 | 0.03 | 73.61 |  | 75.12 | 0.02 | 63.13 | 0.1 |  |  | 62.69 | 0.16 | 63.7 | 0.15 | 73.84 | 0.07 | [62 empty] | Economizer test | 75.004 | 0.008 | 61.998 | 0.021 | 71.378 | 0.002 | 60.014 | 0.019 | 55.007 | 0.009 | 50.993 | 0.01 | 2826.4 | 2.4 | 2733.4 | 2.3 | 0.528 | 0.002 | -0.181 | 0.001 | 0.156 | 0.003 | 1.6201 | 0.0028 | 29.491 | 0 | 1384 | 11 | 1280 |  | 0.11882 | 324.7766 | 13.03 | 0.181 | 1.2526 | 12603.6781 | 169.5517 | 324.7721 | 1495.5387 | 11108.1394 | 0.0085645 | 26.7963 | 70.1254 | 13.0296 | 13.4551 | 0.006976 | 20.7736 | 0.0087784 | 27.6071 | 0.0083527 | 26.2576 | 72.638 | 60.8118 | 25.9524
2 | T2-TRN-88A-55-2E-DM-2 | 75T0085 | T2-TRN-88A-55-2E-DM-2 | 20% open | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 4:26:33 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 0 | 3.4 | 0 | 5686 | 24 | 5292 | 63 | 3715 | 90 | 9404 | 90 | 6.8492 | 858 | 1280 |  | 4.1413 | [35 empty] | Econo 20%-open (3.6V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton),--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (866 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-88A-55-2E-DM-2 | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.996 | 0.011 | 62.004 | 0.027 | 54.998 | 0.006 | 51.001 | 0.015 | 75.11 | 0.02 | 73.39 | 0.01 | 73.57 | 0 | 0.159 | 0.004 | 1.5926 | 0.0023 | 5686 | 24 | 3715 | 90 | 6.853 | 0.084 | [6 empty] | 460.7 | 2 | 461.4 | 2 | 459.4 | 2 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1430.1 | 14.9 | 1088 | 18.6 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.9 |  | 2.9 |  | 2.9 |  | 0.47 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1365 | [14 empty] | 95.23 | 0.03 | 58.39 | 0.02 | 56.37 | 0.02 | -2.01 | 0.03 | 96.5 | 0.04 | 58.16 | 0.02 | 57.09 | 0.01 | -1.07 | 0.02 |  |  | 71.49 | 0.02 |  |  |  |  | 96.07 | 0.01 | 71.42 | 0.02 | 56.85 | 0.01 | 14.57 | 0.02 | 95.8 | 0.03 | 61.33 | 0.03 | 56.69 | 0.01 | 4.64 | 0.03 | [46 empty] | 96.96 | 0.02 | 60.77 | 0.05 | 57.34 | 0.01 | 3.43 | 0.04 | 97.04 | 0.02 | 57.39 | 0.01 | -0.46 | 0.08 |  |  | 72.99 | 0.06 |  |  |  |  | 96.39 | 0.02 | 57.02 | 0.01 | 14.17 | 0.04 | 96.42 | 0.02 | 61.7 | 0.02 | 57.04 | 0.01 | 4.67 | 0.03 | 61.05 | 0.08 | [28 empty] | 60.03 | 0.01 | 61.04 | 0.01 | 61.05 | 0.08 | 62.42 | 0.02 | 73.44 | 0.02 | 73.07 | 0.02 | 72.82 | 0.01 | 73.75 | 0.03 | 73.73 | 0.03 |  |  | 57.54 | 0.02 | 71.86 | 0.03 | 72.2 | 0.03 | 61.47 | 0.01 | 61.49 | 0.05 | 58.06 | 0.05 | 73.55 | 0.06 | 72.5 | 0.02 | 63.82 | 0.03 | 71.49 | 0.02 | 72.99 | 0.06 | 55.73 | 0.04 | 59.47 | 0.02 | 61.97 | 0.02 | 58.92 | 0.04 | 59.9 | 0.06 | 61.04 | 0.01 | 62.42 | 0.02 | [16 empty] | 58.39 | 0.02 | 57.85 | 0.08 | 60.03 | 0.01 | 61.05 | 0.08 | [16 empty] | 71.2 | 0.03 | [12 empty] | 58.45 | 0.03 | 56.62 | 0.13 | 55.92 | 0.06 | 75.45 | 0.02 | 73.2 | 0.04 | 74.85 | 0.02 | 74.2 | 0.04 | 76 | 1.5 | 75.89 | 0.02 | 75.51 | 0.02 | 67.18 | 0.11 | 70.93 | 0.08 | 71.07 | 0.04 | 70.22 | 0.09 | 71.33 | 0.07 | 70.79 | 0.05 | 71.09 | 0.04 | 72.34 | 0.05 | 72.96 | 0.06 | 71.7 | 0.07 | 72.78 | 0.06 | 74.89 | 0.02 | 74.86 | 0.02 | 74.83 | 0.03 | 73.99 | 0.11 | 75.07 | 0.02 | 74.85 | 0.02 | 70.13 | 0.08 | 69.06 | 0.07 |  |  | 73.62 | 0.05 | 75.87 | 0.02 | 75.69 | 0.02 | 75.04 | 0.03 | 73.53 |  | 75.12 | 0.02 | 66.33 | 0.08 |  |  | 70.07 | 0.08 | 73.62 | 0.06 | 74.94 | 0.03 | [62 empty] | Economizer test | 74.996 | 0.011 | 62.004 | 0.027 | 73.137 | 0.008 | 60.937 | 0.021 | 54.998 | 0.006 | 51.001 | 0.015 | 2806.2 | 2 | 2705.4 | 2 | 0.555 | 0.003 | -0.222 | 0.002 | 0.159 | 0.004 | 1.5926 | 0.0023 | 29.486 | 0.001 | 1373 | 10 | 1280 |  | 0.029953 | 81.0348 | 13.029 | 0.222 | 1.2581 | 12470.9935 | 176.3963 | 81.0363 | 373.1679 | 12097.8256 | 0.0087303 | 27.4071 | 71.8789 | 13.0295 | 13.5011 | 0.0069823 | 20.7783 | 0.0087842 | 27.6116 | 0.0085273 | 26.8773 | 74.3995 | 61.7076 | 26.5706
2 | T2-TRN-88A-55-2F-DM-2 | 75T0086 | T2-TRN-88A-55-2F-DM-2 | 2 finger | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 6:58:39 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 3.4 | 0 | 15551 | 30 | 15000 | 90 | 7929 | 105 | 23487 | 107 | 16.9093 | 857 | 1290 |  | 11.1958 | [35 empty] | Econo 2F-open (6V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor,--4.5 turns, 5.75" AK59 pulley (866 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-88A-55-2F-DM-2-SP | W/ECO: 6V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.077 | 0.032 | 62.005 | 0.023 | 54.976 | 0.009 | 50.995 | 0.015 | 75.09 | 0.05 | 70.23 | 0.04 | 71.22 | 0.05 | 0.145 | 0.003 | 1.6264 | 0.0024 | 15551 | 30 | 7929 | 105 | 16.906 | 0.153 | [6 empty] | 460.3 | 2.1 | 460.7 | 2.1 | 459.8 | 2.1 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1421.7 | 15.1 | 1103 | 20 | -9.9 | 0.6 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.48 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1375 | [14 empty] | 97.07 | 0.03 | 60.04 | 0.02 | 57.41 | 0.01 | 2.63 | 0.03 | 97.84 | 0.03 | 59.15 | 0.02 | 57.83 | 0.02 | 1.31 | 0.02 |  |  | 71.35 | 0.03 |  |  |  |  | 97.55 | 0.02 | 68.96 | 0.04 | 57.67 | 0.01 | 11.29 | 0.04 | 97.18 | 0.03 | 64.63 | 0.03 | 57.47 | 0.02 | 7.17 | 0.04 | [46 empty] | 98.62 | 0.04 | 61.86 | 0.09 | 58.25 | 0.02 | 3.62 | 0.12 | 98.34 | 0.06 | 58.11 | 0.03 | -0.36 | 0.13 |  |  | 70.69 | 0.13 |  |  |  |  | 97.71 | 0.05 | 57.76 | 0.03 | 11.22 | 0.05 | 97.8 | 0.04 | 63.18 | 0.02 | 57.81 | 0.02 | 5.37 | 0.03 | 62.47 | 0.1 | [28 empty] | 61.19 | 0.02 | 61.93 | 0.02 | 62.47 | 0.1 | 63.17 | 0.02 | 70.85 | 0.04 | 69.6 | 0.04 | 69.29 | 0.04 | 71.17 | 0.03 | 71.01 | 0.04 |  |  | 59.75 | 0.03 | 71.36 | 0.02 | 69.99 | 0.03 | 64.3 | 0.04 | 62.55 | 0.09 | 58.79 | 0.08 | 71.29 | 0.12 | 70.5 | 0.04 | 65.5 | 0.04 | 71.35 | 0.03 | 70.69 | 0.13 | 55.83 | 0.04 | 62.07 | 0.03 | 63.09 | 0.02 | 60.77 | 0.15 | 61.99 | 0.2 | 61.93 | 0.02 | 63.17 | 0.02 | [16 empty] | 60.04 | 0.02 | 58.47 | 0.12 | 61.19 | 0.02 | 62.47 | 0.1 | [16 empty] | 68.98 | 0.06 | [12 empty] | 59.53 | 0.04 | 57.68 | 0.19 | 56.21 | 0.06 | 75.58 | 0.04 | 73.39 | 0.05 | 75.02 | 0.04 | 74.37 | 0.05 | 76.72 | 3.1 | 76.04 | 0.04 | 75.61 | 0.04 | 62.8 | 0.13 | 61.12 | 0.12 | 59.75 | 0.07 | 60.96 | 0.09 | 64.59 | 0.16 | 65.68 | 0.26 | 66.93 | 0.28 | 68.7 | 0.1 | 67.3 | 0.27 | 67.42 | 0.16 | 67.36 | 0.26 | 66.31 | 0.19 | 70.96 | 0.14 | 71.59 | 0.1 | 71.24 | 0.11 | 69.41 | 0.12 | 72.67 | 0.06 | 73.07 | 0.09 | 72.86 | 0.09 |  |  | 73.72 | 0.05 | 76.14 | 0.03 | 75.92 | 0.04 | 75.26 | 0.04 | 73.81 |  | 75.27 | 0.04 | 60.3 | 0.27 |  |  | 64 | 0.14 | 64.53 | 0.29 | 69.74 | 0.12 | [62 empty] | Economizer test | 75.077 | 0.032 | 62.005 | 0.023 | 70.041 | 0.027 | 59.28 | 0.021 | 54.976 | 0.009 | 50.995 | 0.015 | 2828.9 | 2.1 | 2742.4 | 2 | 0.503 | 0.003 | -0.149 | 0.001 | 0.145 | 0.003 | 1.6264 | 0.0024 | 29.504 | 0.001 | 1389 | 11 | 1290 |  | 0.18735 | 513.7992 | 13.029 | 0.149 | 1.2679 | 12647.7633 | 162.0555 | 513.7976 | 2366.1104 | 10281.653 | 0.0084325 | 26.3323 | 68.7731 | 13.0289 | 13.4201 | 0.0069843 | 20.7751 | 0.0087657 | 27.6111 | 0.0082069 | 25.7726 | 71.3265 | 60.1207 | 25.4636
2 | T2-TRN-88A-55-3E-DM-2 | 75T0087 | T2-TRN-88A-55-3E-DM-2 | 30% open | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 2:59:29 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 3.4 | 0 | 8381 | 16 | 7931 | 60 | 4891 | 74 | 13276 | 81 | 9.5994 | 858 | 1290 |  | 6.06 | [35 empty] | Econo 30%-open (4.4V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor,--4.5 turns, 5.75" AK59 pulley (866 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-88A-55-3E-DM-2 | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.99 | 0.009 | 62.002 | 0.016 | 55.015 | 0.012 | 51.003 | 0.012 | 75.09 | 0.02 | 72.51 | 0.03 | 72.89 | 0.01 | 0.162 | 0.004 | 1.6146 | 0.0025 | 8381 | 16 | 4891 | 74 | 9.603 | 0.096 | [6 empty] | 460.6 | 2.1 | 461.2 | 2.1 | 459.4 | 2 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1433.5 | 15.8 | 1088.5 | 18.5 | -10 | 0 | 460 |  | 460 |  | 460 |  | 3 |  | 3 |  | 2.9 |  | 0.48 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1375 | [14 empty] | 95.99 | 0.05 | 58.82 | 0.02 | 56.8 | 0.02 | -2.02 | 0.03 | 96.86 | 0.03 | 59 | 0.02 | 57.29 | 0.02 | -1.71 | 0.02 |  |  | 71.88 | 0.03 |  |  |  |  | 96.43 | 0.02 | 71.24 | 0.03 | 57.05 | 0.01 | 14.2 | 0.03 | 96.21 | 0.03 | 62.39 | 0.02 | 56.92 | 0.02 | 5.47 | 0.03 | [46 empty] | 97.31 | 0.03 | 60.79 | 0.02 | 57.53 | 0.02 | 3.25 | 0.02 | 97.43 | 0.05 | 57.6 | 0.03 | -1.05 | 0.11 |  |  | 72.64 | 0.02 |  |  |  |  | 96.74 | 0.03 | 57.22 | 0.02 | 14.12 | 0.03 | 96.8 | 0.02 | 62.18 | 0.02 | 57.25 | 0.01 | 4.93 | 0.02 | 61.58 | 0.04 | [28 empty] | 60.38 | 0.01 | 61.21 | 0.02 | 61.58 | 0.04 | 62.61 | 0.02 | 72.89 | 0.03 | 72.06 | 0.03 | 71.77 | 0.02 | 73.16 | 0.03 | 73.07 | 0.02 |  |  | 57.89 | 0.03 | 72.22 | 0.02 | 72.14 | 0.02 | 62.34 | 0.02 | 61.51 | 0.01 | 58.79 | 0.07 | 73.18 | 0.02 | 72.61 | 0.02 | 64.33 | 0.02 | 71.88 | 0.03 | 72.64 | 0.02 | 55.68 | 0.03 | 60.15 | 0.02 | 62.2 | 0.02 | 59.09 | 0.03 | 60.14 | 0.06 | 61.21 | 0.02 | 62.61 | 0.02 | [16 empty] | 58.82 | 0.02 | 58.64 | 0.1 | 60.38 | 0.01 | 61.58 | 0.04 | [16 empty] | 71.34 | 0.04 | [12 empty] | 59.12 | 0.03 | 56.92 | 0.14 | 56 | 0.05 | 75.47 | 0.02 | 73.17 | 0.04 | 74.88 | 0.02 | 74.22 | 0.05 | 76.23 | 2.14 | 75.88 | 0.01 | 75.49 | 0.02 | 65.89 | 0.12 | 67.05 | 0.25 | 70.5 | 0.08 | 68.85 | 0.14 | 65.88 | 0.11 | 68.17 | 0.13 | 70.32 | 0.06 | 70.39 | 0.06 | 68.2 | 0.1 | 69.05 | 0.09 | 67.88 | 0.13 | 74.54 | 0.03 | 74.51 | 0.03 | 74.6 | 0.03 | 74.52 | 0.03 | 74.97 | 0.02 | 74.81 | 0.02 | 72 | 0.16 | 70.16 | 0.09 |  |  | 73.54 | 0.05 | 75.88 | 0.02 | 75.7 | 0.02 | 75.05 | 0.03 | 73.59 |  | 75.12 | 0.02 | 64.22 | 0.08 |  |  | 65.57 | 0.12 | 66.72 | 0.17 | 74.63 | 0.03 | [62 empty] | Economizer test | 74.99 | 0.009 | 62.002 | 0.016 | 72.265 | 0.009 | 60.489 | 0.012 | 55.015 | 0.012 | 51.003 | 0.012 | 2824.1 | 2.2 | 2726 | 2.1 | 0.54 | 0.002 | -0.202 | 0.001 | 0.162 | 0.004 | 1.6146 | 0.0025 | 29.48 | 0.001 | 1383 | 11 | 1290 |  | 0.073342 | 199.9294 | 13.03 | 0.202 | 1.2632 | 12571.7283 | 172.9357 | 199.9284 | 920.6313 | 11651.097 | 0.0086521 | 27.11 | 71.0018 | 13.0299 | 13.4783 | 0.0069794 | 20.7792 | 0.0087843 | 27.6102 | 0.0084455 | 26.5753 | 73.5317 | 61.2737 | 26.2674
2 | T2-TRN-88A-55-3F-DM-2 | 75T0088 | T2-TRN-88A-55-3F-DM-2 | 3 finger | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 8:09:38 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 3.4 | 0 | 20657 | 36 | 20011 | 103 | 10459 | 161 | 31126 | 167 | 22.217 | 858 | 1290 |  | 14.7445 | [35 empty] | Econo 3F-open (6.9V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton),--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (866 rpm), unsealed cab, 100% inlet/outlet--Meriam, adjust code tester speed to match total static of run T2-TRN-88A-55-3F-DM-2- | W/ECO: 6.9 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.951 | 0.025 | 61.985 | 0.025 | 55.001 | 0.011 | 50.998 | 0.014 | 75.07 | 0.04 | 68.68 | 0.02 | 69.84 | 0.05 | 0.166 | 0.003 | 1.6646 | 0.003 | 20657 | 36 | 10459 | 161 | 22.212 | 0.212 | [6 empty] | 460.3 | 2.1 | 460.6 | 2.1 | 459.7 | 2.1 | 3.4 | 0 | 3 | 0 | 3.2 | 0 | 1425.9 | 15.5 | 1104.4 | 19.9 | -9.6 | 1.5 | 460 |  | 459 |  | 459 |  | 2.9 |  | 2.8 |  | 2.9 |  | 0.48 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1375 | [14 empty] | 97.36 | 0.03 | 60.61 | 0.04 | 57.57 | 0.02 | -3.04 | 0.04 | 98.11 | 0.04 | 59.46 | 0.03 | 57.98 | 0.02 | -1.48 | 0.02 |  |  | 69.34 | 0.03 |  |  |  |  | 97.64 | 0.03 | 66.62 | 0.04 | 57.73 | 0.01 | 8.89 | 0.05 | 97.47 | 0.04 | 65.72 | 0.02 | 57.64 | 0.02 | 8.09 | 0.02 | [46 empty] | 98.39 | 0.04 | 57.45 | 0.02 | 58.14 | 0.02 | -0.69 | 0.02 | 98.13 | 0.08 | 58 | 0.05 | -1.52 | 0.13 |  |  | 67.55 | 0.06 |  |  |  |  | 97.64 | 0.08 | 57.73 | 0.04 | 8.96 | 0.17 | 97.53 | 0.07 | 63.91 | 0.02 | 57.68 | 0.04 | 6.24 | 0.05 | 61.52 | 0.14 | [28 empty] | 61.43 | 0.02 | 62.12 | 0.03 | 61.52 | 0.14 | 62.86 | 0.04 | 69.41 | 0.03 | 67.95 | 0.03 | 67.57 | 0.03 | 69.6 | 0.03 | 69.42 | 0.03 |  |  | 60.27 | 0.04 | 69.36 | 0.05 | 67.71 | 0.04 | 65.41 | 0.01 | 58.48 | 0.03 | 59.17 | 0.16 | 68.04 | 0.05 | 68.02 | 0.17 | 66.04 | 0.02 | 69.34 | 0.03 | 67.55 | 0.06 | 55.32 | 0.04 | 62.58 | 0.02 | 63.17 | 0.03 | 60.18 | 0.14 | 60.98 | 0.15 | 62.12 | 0.03 | 62.86 | 0.04 | [16 empty] | 60.61 | 0.04 | 59.51 | 0.15 | 61.43 | 0.02 | 61.52 | 0.14 | [16 empty] | 66.69 | 0.19 | [12 empty] | 59.79 | 0.02 | 58.18 | 0.28 | 56.35 | 0.07 | 75.48 | 0.03 | 73.7 | 0.05 | 74.98 | 0.03 | 74.62 | 0.06 | 76.13 | 1.65 | 75.92 | 0.04 | 75.51 | 0.03 | 61.49 | 0.1 | 61.14 | 0.1 | 59.43 | 0.11 | 60.09 | 0.09 | 62.58 | 0.13 | 62.9 | 0.14 | 59.51 | 0.21 | 64.57 | 0.19 | 65.25 | 0.1 | 64.19 | 0.15 | 65.3 | 0.09 | 63.61 | 0.14 | 67.5 | 0.09 | 67.49 | 0.09 | 66.82 | 0.13 | 67.75 | 0.19 | 70.67 | 0.15 | 71.04 | 0.12 | 70.79 | 0.08 |  |  | 74 | 0.06 | 75.89 | 0.04 | 75.7 | 0.03 | 75.12 | 0.04 | 73.89 |  | 75.1 | 0.03 | 57.25 | 0.07 |  |  | 62.17 | 0.15 | 63.29 | 0.12 | 66.49 | 0.08 | [62 empty] | Economizer test | 74.951 | 0.025 | 61.985 | 0.025 | 68.352 | 0.022 | 58.382 | 0.022 | 55.001 | 0.011 | 50.998 | 0.014 | 2856.8 | 2.6 | 2780.4 | 2.5 | 0.469 | 0.002 | -0.118 | 0.001 | 0.166 | 0.003 | 1.6646 | 0.003 | 29.532 | 0.001 | 1401 | 11 | 1290 |  | 0.26762 | 744.088 | 13.03 | 0.118 | 1.2612 | 12814.5531 | 153.1952 | 744.0742 | 3426.4089 | 9388.1443 | 0.0083004 | 25.7744 | 67.0908 | 13.0295 | 13.376 | 0.00698 | 20.7765 | 0.0087823 | 27.5985 | 0.0080501 | 25.1899 | 69.6295 | 59.2743 | 24.8827
2 | T2-TRN-88A-55-CE-DM-2 | 75T0089 | T2-TRN-88A-55-CE-DM-2 | closed | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 21:08:49 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.8 | 0 | 3.3 | 0 | 3732 | 15 | 3380 | 79 | 2777 | 73 | 6512 | 78 | 4.8024 | 857 | 1270 |  | 2.7522 | [35 empty] | Econo closed (2V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton),--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (866 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-88A-55-CE-DM-2-SPWCT-SS | W/ECO: 2 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.994 | 0.007 | 61.987 | 0.026 | 54.997 | 0.009 | 51.012 | 0.014 | 74.97 | 0.03 | 73.85 | 0.03 | 74.06 | 0.01 | 0.142 | 0.003 | 1.5498 | 0.0019 | 3732 | 15 | 2777 | 73 | 4.802 | 0.072 | [6 empty] | 459.8 | 2 | 460 | 2 | 460.1 | 2 | 3.3 | 0 | 2.9 | 0 | 3.2 | 0 | 1383.8 | 14.6 | 1118.8 | 18.6 | -9.9 | 0.4 | 460 |  | 460 |  | 460 |  | 2.8 |  | 2.9 |  | 2.9 |  | 0.48 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1355 | [14 empty] | 95.19 | 0.03 | 57.41 | 0.04 | 56.33 | 0.01 | -1.07 | 0.04 | 96.09 | 0.01 | 58.12 | 0.02 | 56.83 | 0.01 | -1.29 | 0.02 |  |  | 71.34 | 0.03 |  |  |  |  | 95.56 | 0.02 | 71.87 | 0.02 | 56.54 | 0.01 | 15.33 | 0.02 | 95.57 | 0.02 | 60.55 | 0.03 | 56.54 | 0.01 | 4.01 | 0.02 | [46 empty] | 96.59 | 0.03 | 56.44 | 0.02 | 57.1 | 0.01 | -0.67 | 0.02 | 96.59 | 0.02 | 57.11 | 0.02 | -0.07 | 0.18 |  |  | 73.2 | 0.08 |  |  |  |  | 96.03 | 0.02 | 56.8 | 0.01 | 14.78 | 0.06 | 96.33 | 0.02 | 61.26 | 0.02 | 56.97 | 0.01 | 4.3 | 0.03 | 60.43 | 0.08 | [28 empty] | 59.42 | 0.02 | 60.53 | 0.02 | 60.43 | 0.08 | 61.66 | 0.04 | 73.88 | 0.04 | 73.68 | 0.03 | 73.56 | 0.03 | 74.18 | 0.02 | 74.18 | 0.02 |  |  | 56.77 | 0.02 | 71.68 | 0.02 | 72.35 | 0.02 | 60.68 | 0.01 | 56.96 | 0.01 | 57.47 | 0.1 | 73.81 | 0.08 | 72.84 | 0.02 | 63.3 | 0.04 | 71.34 | 0.03 | 73.2 | 0.08 | 55.73 | 0.04 | 58.53 | 0.02 | 61.44 | 0.02 | 58.31 | 0.04 | 59.31 | 0.1 | 60.53 | 0.02 | 61.66 | 0.04 | [16 empty] | 57.41 | 0.04 | 57.18 | 0.17 | 59.42 | 0.02 | 60.43 | 0.08 | [16 empty] | 71.58 | 0.05 | [12 empty] | 58.22 | 0.02 | 56.25 | 0.09 | 55.78 | 0.07 | 75.36 | 0.02 | 73.03 | 0.05 | 74.77 | 0.02 | 74.01 | 0.04 | 75.9 | 1.6 | 75.75 | 0.03 | 75.38 | 0.03 | 69.42 | 0.12 | 71.68 | 0.05 | 71.71 | 0.04 | 72.41 | 0.07 | 72.46 | 0.06 | 72.38 | 0.06 | 72.69 | 0.04 | 73.47 | 0.04 | 74.01 | 0.03 | 73.44 | 0.04 | 73.94 | 0.03 | 74.85 | 0.02 | 74.85 | 0.02 | 74.76 | 0.02 | 73.99 | 0.17 | 74.99 | 0.02 | 74.72 | 0.02 | 69.28 | 0.16 | 69.65 | 0.12 |  |  | 73.48 | 0.06 | 75.78 | 0.02 | 75.61 | 0.02 | 74.94 | 0.03 | 73.33 |  | 75.06 | 0.02 | 69.01 | 0.12 |  |  | 71.89 | 0.07 | 74.18 | 0.03 | 74.9 | 0.02 | [62 empty] | Economizer test | 74.994 | 0.007 | 61.987 | 0.026 | 73.758 | 0.006 | 61.25 | 0.029 | 54.997 | 0.009 | 51.012 | 0.014 | 2773.1 | 1.7 | 2663.4 | 1.6 | 0.566 | 0.003 | -0.231 | 0.002 | 0.142 | 0.003 | 1.5498 | 0.0019 | 29.407 | 0 | 1356 | 11 | 1270 |  | 0 | 0 | 13.029 | 0.231 | 1.2623 | 12309.1379 | 177.0997 | 0 | 0 | 12309.1379 | 0.0087735 | 27.5993 | 72.4957 | 13.0295 | 13.5173 | 0.0069884 | 20.7846 | 0.0087735 | 27.5993 | 0.0085833 | 27.0899 | 74.994 | 61.987 | 26.7821
2 | T2-TRN-88A-55-OE-DM-2 | 75T0092 | T2-TRN-88A-55-OE-DM-2 | open | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 9:34:23 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 3.4 | 0 | 40506 | 83 | 40009 | 312 | 19600 | 239 | 60124 | 275 | 43.0072 | 858 | 1290 |  | 28.9742 | [35 empty] | Econo fully open (10V), no compressor, 55/51 ambient, 87.5% airflow (350 cfm/ton),--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (866 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-88A-55-OE-DM- | W/ECO: 10 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.959 | 0.021 | 61.99 | 0.041 | 55.001 | 0.009 | 51.004 | 0.013 | 75.16 | 0.1 | 62.23 | 0.05 | 64.6 | 0.02 | 0.141 | 0.003 | 1.603 | 0.0029 | 40506 | 83 | 19600 | 239 | 43.026 | 0.392 | [6 empty] | 460.2 | 2 | 460.6 | 2 | 459.9 | 2 | 3.4 | 0 | 3 | 0 | 3.2 | 0 | 1420.1 | 14.6 | 1109.6 | 18.9 | -9.4 | 2 | 460 |  | 459 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.48 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1375 | [14 empty] | 97.72 | 0.07 | 60.8 | 0.04 | 57.79 | 0.03 | -3.02 | 0.05 | 97.84 | 0.08 | 59.3 | 0.05 | 57.85 | 0.04 | -1.45 | 0.05 |  |  | 63.21 | 0.03 |  |  |  |  | 97.25 | 0.08 | 60.45 | 0.03 | 57.52 | 0.04 | 2.92 | 0.06 | 97.18 | 0.1 | 66.35 | 0.04 | 57.49 | 0.05 | 8.87 | 0.07 | [46 empty] | 98.25 | 0.09 | 57.1 | 0.06 | 58.07 | 0.05 | -0.97 | 0.03 | 97.15 | 0.13 | 57.47 | 0.07 | -4.81 | 0.06 |  |  | 60.52 | 0.12 |  |  |  |  | 95.23 | 0.14 | 56.4 | 0.08 | 3.14 | 0.11 | 95.88 | 0.11 | 64 | 0.05 | 56.76 | 0.06 | 7.24 | 0.07 | 63.07 | 0.04 | [28 empty] | 61.36 | 0.04 | 62.18 | 0.03 | 63.07 | 0.04 | 63.27 | 0.06 | 62.44 | 0.07 | 61.94 | 0.06 | 61.51 | 0.06 | 62.38 | 0.06 | 62.18 | 0.06 |  |  | 60.21 | 0.03 | 63.07 | 0.04 | 61.32 | 0.04 | 66.05 | 0.02 | 57.85 | 0.06 | 62.41 | 0.07 | 61.05 | 0.11 | 60.78 | 0.03 | 65.53 | 0.04 | 63.21 | 0.03 | 60.52 | 0.12 | 55.05 | 0.11 | 62.73 | 0.02 | 63.11 | 0.03 | 63.76 | 0.09 | 65.17 | 0.08 | 62.18 | 0.03 | 63.27 | 0.06 | [16 empty] | 60.8 | 0.04 | 62.28 | 0.09 | 61.36 | 0.04 | 63.07 | 0.04 | [16 empty] | 59.54 | 0.05 | [12 empty] | 59.47 | 0.05 | 58.95 | 0.25 | 56.96 | 0.1 | 75.39 | 0.05 | 74.87 | 0.05 | 75.02 | 0.06 | 75.84 | 0.06 | 75.84 | 0.05 | 75.85 | 0.06 | 75.63 | 0.06 | 55.06 | 0.09 | 57.7 | 0.11 | 59.07 | 0.16 | 55 | 0.12 | 59.65 | 0.26 | 61.79 | 0.34 | 58.24 | 0.27 | 59.63 | 0.27 | 61.6 | 0.19 | 61.95 | 0.32 | 60.64 | 0.29 | 59.74 | 0.22 | 62.87 | 0.18 | 61.62 | 0.16 | 60.55 | 0.24 | 64.59 | 0.22 | 65.15 | 0.17 | 64.87 | 0.15 | 66.21 | 0.24 |  |  | 75.2 | 0.06 | 75.74 | 0.05 | 75.61 | 0.06 | 75.41 | 0.06 | 74.98 |  | 75.04 | 0.06 | 54.9 | 0.13 |  |  | 56.44 | 0.17 | 58.62 | 0.15 | 62.24 | 0.23 | [62 empty] | Economizer test | 74.959 | 0.021 | 61.99 | 0.041 | 61.862 | 0.024 | 54.674 | 0.027 | 55.001 | 0.009 | 51.004 | 0.013 | 2787.4 | 2.6 | 2745.8 | 2.5 | 0.421 | 0.002 | -0.065 | 0.001 | 0.141 | 0.003 | 1.603 | 0.0029 | 29.564 | 0.001 | 1398 | 11 | 1290 |  | 0.59109 | 1623.0185 | 13.03 | 0.065 | 1.2957 | 12663.8314 | 135.8051 | 1622.9899 | 7473.7391 | 5190.0923 | 0.0077211 | 23.5759 | 60.5663 | 13.0295 | 13.2064 | 0.0069832 | 20.78 | 0.0087837 | 27.602 | 0.0073886 | 22.8891 | 63.1964 | 55.797 | 22.5739
2 | T2-MFB3-100C1-100C2-90A-95-CE-3 | 75T0172 | T2-MFB3-100C1-100C2-90A-95-CE-3 | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 11/4/2014 | 20:02:33 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 14.9 | 0 | 57202 | 64 | 56963 | 564 | 9911 | 165 | 67122 | 150 | 8.1419 | 854 | 1310 |  | 6.9386 | [35 empty] | Econo closed (2.0V), factory charge NC baseline, 90% airflow (350 cfm/ton),--4.5 turns, 5.75" AK59 pulley (866 rpm), unsealed cab, adjust code tester speed--to match total static of run T2-MFB3-100C1-100C2-90A-95-CE-2-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.931 | 0.018 | 61.995 | 0.025 | 95.008 | 0.017 | 75.008 | 0.018 | 75.13 | 0.2 | 56.21 | 0.04 | 59.85 | 0.03 | 0.16 | 0.003 | 1.5277 | 0.0026 | 57202 | 64 | 9911 | 165 | 8.142 | 0.025 | [6 empty] | 460.2 | 2.1 | 461.3 | 2.1 | 459.8 | 2.1 | 14.9 | 0 | 12.6 | 0 | 12.7 | 0.1 | 6756.6 | 43.2 | 3185 | 52.5 | 1487.8 | 34.1 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.8 |  | 4.4 |  | 3150 |  | 0.82 | 460 | 460 | 460 | 5 | 4.6 | 4.2 | 2980 | 0.8 | 459.3 |  | 1.6 |  | 701.2 |  | 85 |  | 8226.2 | [14 empty] | 221.12 | 0.24 | 106.31 | 0.12 | 108.29 | 0.08 | 1.99 | 0.11 | 248.3 | 0.29 | 174.42 | 0.08 | 116.58 | 0.09 | 57.83 | 0.09 | 214.8 | 0.05 | 105.63 | 0.1 | 106.26 | 0.05 | 0.63 | 0.05 | 74.24 | 0.05 | 48.57 | 0.13 | 43.7 | 0.03 | 4.88 | 0.15 | 73.61 | 0.05 | 55.38 | 0.15 | 43.28 | 0.03 | 12.1 | 0.15 | [46 empty] | 249.31 | 0.33 | 171.79 | 0.3 | 116.88 | 0.1 | 54.91 | 0.32 | 231.88 | 0.44 | 111.65 | 0.13 | 11.35 | 0.18 | 222.1 | 0.05 | 96.38 | 0.08 | 108.6 | 0.05 | 12.22 | 0.05 | 77.09 | 0.18 | 45.54 | 0.11 | 3.41 | 1.62 | 76.69 | 0.17 | 56.95 | 0.78 | 45.28 | 0.11 | 11.67 | 0.83 | 101.23 | 0.13 | [28 empty] | 106.6 | 0.11 | 106.3 | 0.09 | 101.23 | 0.13 | 101.45 | 0.12 | 55.45 | 0.05 | 56.1 | 0.05 | 56 | 0.05 | 55.82 | 0.04 | 55.87 | 0.04 |  |  | 106.16 | 0.12 | 102.2 | 0.12 | 49.54 | 0.34 | 55.22 | 0.18 | 172.1 | 0.35 | 101.3 | 0.13 | 95.25 | 0.07 | 50.33 | 1.4 | 57.83 | 0.76 | 105.63 | 0.1 | 96.38 | 0.08 | 92.57 | 0.16 | 106.75 | 0.1 | 107.05 | 0.11 | 101.92 | 0.09 | 102.27 | 0.1 | 106.3 | 0.09 | 101.45 | 0.12 | [16 empty] | 106.31 | 0.12 | 100.31 | 0.15 | 106.6 | 0.11 | 101.23 | 0.13 | [16 empty] | 48.94 | 1.5 | [12 empty] | 175.36 | 0.11 | 94.65 | 0.29 | 95.62 | 0.09 | 75.54 | 0.09 | 77.2 | 0.08 | 75.3 | 0.09 | 77.39 | 0.09 |  |  | 76 | 0.1 | 75.89 | 0.1 | 79.75 | 0.12 | 77.89 | 0.09 | 77.58 | 0.08 | 76.18 | 0.11 | 77.46 | 0.11 | 77.36 | 0.1 | 77.41 | 0.09 | 77.05 | 0.09 | 75.91 | 0.11 | 76.51 | 0.1 | 75.57 | 0.11 | 75.42 | 0.11 | 75.37 | 0.11 | 75.3 | 0.1 | 75.66 | 0.11 | 75.6 | 0.1 | 75.41 | 0.08 | 81.11 | 0.09 | 80.61 | 0.12 |  |  | 76.55 | 0.1 | 75.47 | 0.08 | 75.74 | 0.1 | 75.87 | 0.11 | 76.77 |  | 75.21 | 0.1 | 80.26 | 0.11 | 80.27 | 0.11 | 77.52 | 0.1 | 75.84 | 0.11 | 75.43 | 0.11 | [12 empty] | 75.56 | 0.1 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.931 | 0.018 | 61.995 | 0.025 | 55.933 | 0.015 | 53.574 | 0.022 | 95.008 | 0.017 | 75.008 | 0.018 | 2710.5 | 2.3 | 2688.7 | 2.4 | 0.532 | 0.002 | -0.247 | 0.002 | 0.16 | 0.003 | 1.5277 | 0.0026 | 29.534 | 0.003 | 8244 | 19 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.304 | 12450.3031 | 168.0425 | 0 | 0 | 12450.3031 | 0.0087936 | 27.606 | 54.629 | 14.1002 | 13.0623 | 0.013926 | 38.1647 | 0.0087936 | 27.606 | 0.008165 | 22.2898 | 74.931 | 61.995 | 21.9721 | 70144.5983 | 60663.7648 | 6934 | 0.33739 | 66247.0973 | 56766.2638 | 8.0358 | 0.13927 | -5.634 | -20.302 | 51.3441 | 70144.5983 | 66189.3838 | 3955.2145 | 0 | 70144.5983 | 100%
2 | T2-NC1-CK1-100C1-100C2-90A-CE | 75T0173 | T2-NC1-CK1-100C1-100C2-90A-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 11/4/2014 | 22:16:03 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 15.4 | 0 | 54956 | 76 | 54861 | 399 | 7943 | 187 | 62907 | 169 | 7.2133 | 854 | 1310 |  | 6.3016 | [35 empty] | 0.5% NC 1st Circuit 0.5 oz. Nitrogen added to CK1, 95F OAT, 2 HP fan motor, 90% airflow--(350 cfm/ton), 4.5 turns, 5.75" AK59 pulley (866 rpm), Econo closed unsealed cab,--adjust code tester speed to match total static of run T2-NC102-CK1-100C1-100C2-90A- | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.95 | 0.011 | 61.992 | 0.03 | 95.023 | 0.018 | 75 | 0.018 | 75.21 | 0.13 | 56.98 | 0.03 | 60.46 | 0.03 | 0.156 | 0.003 | 1.5295 | 0.0026 | 54956 | 76 | 7943 | 187 | 7.213 | 0.022 | [6 empty] | 460.2 | 2 | 461.3 | 2 | 459.9 | 2 | 15.4 | 0 | 13.2 | 0 | 13.2 | 0 | 7000.7 | 41.7 | 3220.4 | 50.6 | 1720.4 | 32.4 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.7 |  | 5.5 |  | 5 |  | 3680 |  | 0.86 | 460 | 460 | 460 | 4.9 | 4.6 | 4.1 | 2890 | 0.79 | 459.3 |  | 1.6 |  | 702.4 |  | 85 |  | 8667.4 | [14 empty] | 259.87 | 0.28 | 95.44 | 0.07 | 119.93 | 0.08 | 24.49 | 0.09 | 292.94 | 0.16 | 212.09 | 0.06 | 128.93 | 0.04 | 83.15 | 0.06 | 242.9 | 0.05 | 92.67 | 0.06 | 114.99 | 0.05 | 22.32 | 0.05 | 75.27 | 0.06 | 69.09 | 0.05 | 44.37 | 0.04 | 24.71 | 0.06 | 74.72 | 0.06 | 72.01 | 0.04 | 44.02 | 0.04 | 27.99 | 0.05 | [46 empty] | 243.18 | 0.22 | 169.74 | 0.38 | 115.08 | 0.07 | 54.66 | 0.41 | 226.02 | 0.34 | 109.84 | 0.11 | 11.59 | 0.15 | 216 | 0.05 | 94.16 | 0.07 | 106.65 | 0.05 | 12.49 | 0.05 | 76.68 | 0.21 | 45.29 | 0.13 | 3.6 | 1.92 | 76.25 | 0.2 | 56.78 | 1 | 45.01 | 0.13 | 11.77 | 1.07 | 98.54 | 0.12 | [28 empty] | 94.21 | 0.07 | 93.92 | 0.06 | 98.54 | 0.12 | 98.75 | 0.12 | 56.27 | 0.06 | 56.93 | 0.05 | 56.79 | 0.04 | 56.69 | 0.03 | 56.71 | 0.03 |  |  | 94.83 | 0.08 | 89.95 | 0.06 | 70.52 | 0.05 | 71.94 | 0.04 | 170.08 | 0.43 | 98.75 | 0.12 | 93.11 | 0.07 | 50.38 | 1.69 | 57.71 | 0.95 | 92.67 | 0.06 | 94.16 | 0.07 | 92.75 | 0.16 | 96.4 | 0.05 | 94.31 | 0.07 | 99.32 | 0.08 | 99.51 | 0.1 | 93.92 | 0.06 | 98.75 | 0.12 | [16 empty] | 95.44 | 0.07 | 98.25 | 0.13 | 94.21 | 0.07 | 98.54 | 0.12 | [16 empty] | 48.89 | 1.79 | [12 empty] | 213.23 | 0.08 | 94.47 | 0.17 | 95.68 | 0.08 | 75.58 | 0.06 | 77.27 | 0.06 | 75.36 | 0.06 | 77.46 | 0.06 |  |  | 76.06 | 0.06 | 75.96 | 0.06 | 79.86 | 0.11 | 78.01 | 0.06 | 77.66 | 0.05 | 76.24 | 0.07 | 77.57 | 0.08 | 77.48 | 0.07 | 77.55 | 0.06 | 77.19 | 0.06 | 76.03 | 0.07 | 76.64 | 0.07 | 75.67 | 0.07 | 75.51 | 0.07 | 75.47 | 0.06 | 75.38 | 0.06 | 75.73 | 0.07 | 75.7 | 0.06 | 75.51 | 0.05 | 81.35 | 0.07 | 80.78 | 0.09 |  |  | 76.63 | 0.07 | 75.52 | 0.05 | 75.77 | 0.06 | 75.92 | 0.07 | 76.84 |  | 75.24 | 0.06 | 80.35 | 0.07 | 80.4 | 0.08 | 77.63 | 0.07 | 75.93 | 0.07 | 75.53 | 0.07 | [12 empty] | 75.67 | 0.06 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.95 | 0.011 | 61.992 | 0.03 | 56.687 | 0.015 | 54.136 | 0.022 | 95.023 | 0.018 | 75 | 0.018 | 2712.3 | 2.3 | 2689.7 | 2.4 | 0.534 | 0.002 | -0.247 | 0.002 | 0.156 | 0.003 | 1.5295 | 0.0026 | 29.567 | 0.001 | 8721 | 17 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3043 | 12439.3564 | 168.737 | 0 | 0 | 12439.3564 | 0.0087872 | 27.6036 | 55.3827 | 14.1005 | 13.0825 | 0.013915 | 38.1567 | 0.0087872 | 27.6036 | 0.0083031 | 22.6235 | 74.95 | 61.992 | 22.3056 | 65903.1368 | 58417.1812 | 7411 | 0.3838 | 62008.006 | 54522.0504 | 7.1102 | 0.15337 | -5.298 | -19.5673 | 51.838 | 65903.1368 | 61949.3325 | 3953.8043 | 0 | 65903.1368 | 100%
2 | T2-NC2-CK1-CK2-100C1-100C2-90A-CE | 75T0174 | T2-NC2-CK1-CK2-100C1-100C2-90A-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 11/4/2014 | 23:35:14 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 15.8 | 0 | 54743 | 58 | 54597 | 377 | 7918 | 118 | 62669 | 126 | 6.9118 | 854 | 1310 |  | 6.0376 | [35 empty] | 0.5% NC Both Circuits, 0.5 oz. Nitrogen added to CK1 and CK2, 95F OAT, 2 HP fan motor,--90% airflow (350 cfm/ton), 4.5 turns, 5.75" AK59 pulley (866 rpm), Econo closed unsealed cab,--adjust code tester speed to match total static of run T2-NC202-CK1-CK2-1 | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.97 | 0.008 | 61.998 | 0.016 | 95.011 | 0.013 | 75.005 | 0.021 | 75.3 | 0.12 | 57.14 | 0.03 | 60.5 | 0.02 | 0.156 | 0.003 | 1.5285 | 0.0025 | 54743 | 58 | 7918 | 118 | 6.912 | 0.02 | [6 empty] | 460.3 | 2.1 | 461.5 | 2.1 | 459.9 | 2 | 15.8 | 0 | 13.5 | 0 | 13.6 | 0 | 7195 | 43.7 | 3232.9 | 49.4 | 1871.8 | 33.9 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.6 |  | 5.4 |  | 4.9 |  | 3640 |  | 0.85 | 460 | 460 | 460 | 5.4 | 5 | 4.6 | 3310 | 0.82 | 459.3 |  | 1.6 |  | 701.6 |  | 85 |  | 9046.6 | [14 empty] | 256.58 | 0.25 | 94.27 | 0.07 | 118.99 | 0.07 | 24.72 | 0.08 | 289.73 | 0.19 | 210.77 | 0.07 | 128.09 | 0.05 | 82.68 | 0.08 | 239.8 | 0.05 | 91.38 | 0.05 | 114.06 | 0.05 | 22.68 | 0.05 | 75.06 | 0.06 | 69.37 | 0.04 | 44.23 | 0.04 | 25.14 | 0.06 | 74.51 | 0.06 | 72.39 | 0.05 | 43.88 | 0.04 | 28.51 | 0.06 | [46 empty] | 279.91 | 0.2 | 185.77 | 0.11 | 125.47 | 0.05 | 60.29 | 0.12 | 253.07 | 0.4 | 117.97 | 0.11 | 24.38 | 0.13 | 234.8 | 0.05 | 88.04 | 0.05 | 112.55 | 0.05 | 24.51 | 0.05 | 81.61 | 0.05 | 48.39 | 0.03 | 8.66 | 0.72 | 81.21 | 0.04 | 62.74 | 0.2 | 48.14 | 0.03 | 14.6 | 0.21 | 92.26 | 0.08 | [28 empty] | 92.93 | 0.07 | 92.58 | 0.06 | 92.26 | 0.08 | 92.33 | 0.08 | 56.45 | 0.04 | 57.08 | 0.03 | 56.85 | 0.04 | 56.77 | 0.04 | 56.8 | 0.03 |  |  | 93.53 | 0.07 | 88.79 | 0.06 | 70.75 | 0.06 | 72.32 | 0.04 | 186.08 | 0.13 | 93.67 | 0.08 | 87.19 | 0.05 | 58.4 | 0.67 | 63.14 | 0.23 | 91.38 | 0.05 | 88.04 | 0.05 | 92.75 | 0.18 | 94.95 | 0.05 | 92.99 | 0.07 | 94 | 0.06 | 93.93 | 0.06 | 92.58 | 0.06 | 92.33 | 0.08 | [16 empty] | 94.27 | 0.07 | 93.59 | 0.08 | 92.93 | 0.07 | 92.26 | 0.08 | [16 empty] | 57.03 | 0.7 | [12 empty] | 211.9 | 0.08 | 94.39 | 0.18 | 95.66 | 0.09 | 75.62 | 0.05 | 77.28 | 0.05 | 75.37 | 0.06 | 77.48 | 0.06 |  |  | 76.06 | 0.06 | 75.97 | 0.06 | 79.86 | 0.12 | 78.02 | 0.06 | 77.67 | 0.05 | 76.24 | 0.07 | 77.54 | 0.06 | 77.43 | 0.06 | 77.52 | 0.05 | 77.17 | 0.06 | 75.99 | 0.06 | 76.6 | 0.06 | 75.65 | 0.06 | 75.46 | 0.07 | 75.42 | 0.06 | 75.39 | 0.06 | 75.72 | 0.06 | 75.63 | 0.06 | 75.51 | 0.05 | 81.32 | 0.09 | 80.69 | 0.13 |  |  | 76.63 | 0.06 | 75.5 | 0.05 | 75.77 | 0.06 | 75.92 | 0.07 | 76.83 |  | 75.26 | 0.07 | 80.31 | 0.08 | 80.39 | 0.08 | 77.62 | 0.07 | 75.9 | 0.07 | 75.47 | 0.06 | [12 empty] | 75.6 | 0.06 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.97 | 0.008 | 61.998 | 0.016 | 56.763 | 0.008 | 54.173 | 0.01 | 95.011 | 0.013 | 75.005 | 0.021 | 2712.7 | 2.2 | 2687.5 | 2.3 | 0.536 | 0.003 | -0.248 | 0.002 | 0.156 | 0.003 | 1.5285 | 0.0025 | 29.542 | 0.002 | 9067 | 16 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3038 | 12439.3379 | 169.2304 | 0 | 0 | 12439.3379 | 0.0087864 | 27.6076 | 55.4592 | 14.1002 | 13.0845 | 0.013923 | 38.1618 | 0.0087864 | 27.6076 | 0.0083061 | 22.6453 | 74.97 | 61.998 | 22.3275 | 65680.7924 | 58248.2318 | 7757 | 0.40308 | 61787.3457 | 54354.7852 | 6.8145 | 0.15635 | -5.2801 | -19.5108 | 51.8433 | 65680.7924 | 61728.676 | 3952.1164 | 0 | 65680.7924 | 100%
2 | T2-NC3-CK1-100C1-100C2-90A-CE | 75T0175 | T2-NC3-CK1-100C1-100C2-90A-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 11/5/2014 | 0:35:13 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 16.2 | 0 | 53915 | 51 | 53690 | 405 | 7234 | 142 | 61156 | 152 | 6.4928 | 854 | 1310 |  | 5.7241 | [35 empty] | 1.0% NC 1st Circuit 1.0 oz. (total) Nitrogen added to CK1, 0.5% NC 2nd Circuit 0.5 oz.--(total) Nitrogen added to CK2, 95F OAT, 2 HP fan motor, 90% airflow (350 cfm/ton), 4.5 turns,--5.75" AK59 pulley (866 rpm), Econo closed unsealed cab, adjust code test | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.977 | 0.013 | 62.001 | 0.021 | 94.995 | 0.011 | 75.001 | 0.019 | 75.29 | 0.13 | 57.42 | 0.03 | 60.67 | 0.02 | 0.153 | 0.003 | 1.5291 | 0.0024 | 53915 | 51 | 7234 | 142 | 6.493 | 0.019 | [6 empty] | 460.2 | 2 | 461.5 | 2 | 459.7 | 2 | 16.2 | 0 | 13.9 | 0 | 14 | 0 | 7395.3 | 41.7 | 3246.8 | 48.6 | 2023.5 | 32.1 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 6.1 |  | 5.8 |  | 5.4 |  | 4010 |  | 0.87 | 460 | 460 | 460 | 5.4 | 5 | 4.6 | 3300 | 0.83 | 459.3 |  | 1.6 |  | 701.4 |  | 85 |  | 9406.4 | [14 empty] | 282.05 | 0.38 | 93.96 | 0.07 | 126.05 | 0.1 | 32.09 | 0.1 | 318.1 | 0.23 | 222.91 | 0.09 | 135.31 | 0.06 | 87.6 | 0.1 | 263 | 0.05 | 91.14 | 0.07 | 120.81 | 0.05 | 29.67 | 0.05 | 77.09 | 0.09 | 69.62 | 0.04 | 45.54 | 0.06 | 24.07 | 0.07 | 76.56 | 0.08 | 72.76 | 0.04 | 45.2 | 0.05 | 27.56 | 0.06 | [46 empty] | 278.64 | 0.26 | 185.44 | 0.11 | 125.13 | 0.07 | 60.31 | 0.12 | 251.59 | 0.5 | 117.55 | 0.15 | 24.19 | 0.14 | 234 | 0.05 | 87.82 | 0.06 | 112.3 | 0.05 | 24.48 | 0.05 | 81.64 | 0.06 | 48.4 | 0.04 | 8.72 | 0.73 | 81.21 | 0.06 | 62.81 | 0.19 | 48.14 | 0.04 | 14.68 | 0.21 | 92.04 | 0.07 | [28 empty] | 92.65 | 0.07 | 92.3 | 0.06 | 92.04 | 0.07 | 92.08 | 0.07 | 56.75 | 0.04 | 57.34 | 0.03 | 57.1 | 0.03 | 57.09 | 0.03 | 57.11 | 0.03 |  |  | 93.26 | 0.07 | 88.52 | 0.08 | 71.14 | 0.04 | 72.74 | 0.04 | 185.74 | 0.12 | 93.47 | 0.07 | 87.01 | 0.06 | 58.6 | 0.67 | 63.36 | 0.22 | 91.14 | 0.07 | 87.82 | 0.06 | 92.75 | 0.12 | 94.77 | 0.06 | 92.72 | 0.08 | 93.87 | 0.06 | 93.78 | 0.06 | 92.3 | 0.06 | 92.08 | 0.07 | [16 empty] | 93.96 | 0.07 | 93.36 | 0.08 | 92.65 | 0.07 | 92.04 | 0.07 | [16 empty] | 57.1 | 0.7 | [12 empty] | 224.17 | 0.14 | 94.45 | 0.28 | 95.65 | 0.08 | 75.6 | 0.06 | 77.25 | 0.06 | 75.35 | 0.06 | 77.49 | 0.06 |  |  | 76.06 | 0.06 | 75.96 | 0.06 | 79.87 | 0.1 | 78.05 | 0.06 | 77.69 | 0.05 | 76.26 | 0.07 | 77.57 | 0.07 | 77.46 | 0.07 | 77.53 | 0.06 | 77.18 | 0.06 | 76.02 | 0.08 | 76.61 | 0.07 | 75.65 | 0.07 | 75.49 | 0.07 | 75.45 | 0.07 | 75.4 | 0.07 | 75.75 | 0.07 | 75.69 | 0.06 | 75.55 | 0.05 | 81.41 | 0.06 | 80.84 | 0.1 |  |  | 76.61 | 0.06 | 75.6 | 0.06 | 75.82 | 0.07 | 75.96 | 0.08 | 76.86 |  | 75.27 | 0.07 | 80.4 | 0.09 | 80.44 | 0.08 | 77.64 | 0.07 | 75.92 | 0.08 | 75.51 | 0.07 | [12 empty] | 75.66 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.977 | 0.013 | 62.001 | 0.021 | 57.034 | 0.012 | 54.378 | 0.014 | 94.995 | 0.011 | 75.001 | 0.019 | 2714.1 | 2.1 | 2687 | 2.1 | 0.536 | 0.003 | -0.249 | 0.002 | 0.153 | 0.003 | 1.5291 | 0.0024 | 29.533 | 0.001 | 9419 | 18 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3039 | 12438.8435 | 169.1989 | 0 | 0 | 12438.8435 | 0.0087867 | 27.6097 | 55.7301 | 14.0998 | 13.0917 | 0.013923 | 38.1582 | 0.0087867 | 27.6097 | 0.0083584 | 22.7681 | 74.977 | 62.001 | 22.4503 | 64176.7382 | 57458.0537 | 8109 | 0.43125 | 60283.1841 | 53564.4996 | 6.4002 | 0.16115 | -5.1594 | -19.2469 | 52.0326 | 64176.7382 | 60224.1364 | 3952.6018 | 0 | 64176.7382 | 100%
2 | T2-NC4-CK1-CK2-100C1-100C2-90A-CE | 75T0176 | T2-NC4-CK1-CK2-100C1-100C2-90A-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 11/5/2014 | 1:30:10 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 16.7 | 0 | 53274 | 60 | 52989 | 435 | 6583 | 188 | 59863 | 218 | 6.0695 | 854 | 1320 |  | 5.4014 | [35 empty] | 1.0% NC Both Circuits, 1.0 oz. (total) Nitrogen added to CK1 and CK2, 95F OAT,--2 HP fan motor, 90% airflow (350 cfm/ton), 4.5 turns, 5.75" AK59 pulley (866 rpm),--Econo closed unsealed cab, adjust code tester speed to match total static of run T2-NC404-C | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.97 | 0.013 | 61.993 | 0.038 | 94.992 | 0.019 | 74.998 | 0.019 | 75.28 | 0.14 | 57.72 | 0.03 | 60.89 | 0.02 | 0.167 | 0.003 | 1.544 | 0.0029 | 53274 | 60 | 6583 | 188 | 6.069 | 0.025 | [6 empty] | 460.2 | 2.1 | 461.6 | 2.1 | 459.8 | 2.1 | 16.7 | 0 | 14.4 | 0 | 14.5 | 0 | 7635.3 | 42.1 | 3277.1 | 49.1 | 2228.1 | 33.7 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 6 |  | 5.8 |  | 5.3 |  | 3960 |  | 0.87 | 460 | 460 | 460 | 5.9 | 5.5 | 5.1 | 3780 | 0.85 | 459.2 |  | 1.6 |  | 701.6 |  | 85 |  | 9846.6 | [14 empty] | 279.8 | 0.38 | 93.68 | 0.07 | 125.44 | 0.1 | 31.76 | 0.1 | 315.59 | 0.25 | 222.82 | 0.07 | 134.69 | 0.06 | 88.14 | 0.1 | 263 | 0.05 | 90.76 | 0.06 | 120.81 | 0.05 | 30.05 | 0.05 | 76.42 | 0.11 | 69.85 | 0.05 | 45.11 | 0.07 | 24.74 | 0.07 | 75.89 | 0.11 | 73 | 0.05 | 44.77 | 0.07 | 28.23 | 0.07 | [46 empty] | 320.28 | 0.24 | 202.78 | 0.06 | 135.84 | 0.06 | 66.94 | 0.09 | 288.11 | 0.67 | 127.66 | 0.18 | 35.3 | 0.18 | 264.2 | 0.05 | 86.65 | 0.04 | 86.69 | 0.05 | 0.04 | 0.05 | 85.94 | 0.07 | 51.02 | 0.04 | 11.36 | 0.27 | 85.53 | 0.07 | 66.66 | 0.12 | 50.77 | 0.04 | 15.89 | 0.13 | 90.87 | 0.07 | [28 empty] | 92.34 | 0.07 | 92.03 | 0.06 | 90.87 | 0.07 | 90.9 | 0.07 | 57.1 | 0.05 | 57.65 | 0.05 | 57.4 | 0.04 | 57.38 | 0.05 | 57.4 | 0.05 |  |  | 92.94 | 0.07 | 88.23 | 0.07 | 71.33 | 0.06 | 73 | 0.05 | 203.05 | 0.08 | 92.41 | 0.06 | 85.9 | 0.04 | 63.53 | 0.23 | 67.15 | 0.13 | 90.76 | 0.06 | 86.65 | 0.04 | 92.71 | 0.17 | 94.39 | 0.06 | 92.35 | 0.07 | 92.87 | 0.04 | 92.73 | 0.05 | 92.03 | 0.06 | 90.9 | 0.07 | [16 empty] | 93.68 | 0.07 | 92.36 | 0.08 | 92.34 | 0.07 | 90.87 | 0.07 | [16 empty] | 62.37 | 0.26 | [12 empty] | 224.11 | 0.12 | 94.4 | 0.15 | 95.72 | 0.1 | 75.58 | 0.06 | 77.22 | 0.06 | 75.32 | 0.07 | 77.47 | 0.06 |  |  | 76 | 0.08 | 75.9 | 0.08 | 79.82 | 0.09 | 77.99 | 0.06 | 77.67 | 0.05 | 76.24 | 0.08 | 77.56 | 0.07 | 77.45 | 0.06 | 77.5 | 0.06 | 77.16 | 0.07 | 76.01 | 0.07 | 76.59 | 0.07 | 75.64 | 0.07 | 75.46 | 0.08 | 75.42 | 0.07 | 75.38 | 0.08 | 75.75 | 0.08 | 75.65 | 0.07 | 75.53 | 0.06 | 81.41 | 0.07 | 80.83 | 0.1 |  |  | 76.58 | 0.07 | 75.55 | 0.07 | 75.78 | 0.08 | 75.93 | 0.08 | 76.81 |  | 75.25 | 0.08 | 80.38 | 0.08 | 80.42 | 0.08 | 77.64 | 0.07 | 75.9 | 0.08 | 75.48 | 0.08 | [12 empty] | 75.62 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.97 | 0.013 | 61.993 | 0.038 | 57.315 | 0.014 | 54.577 | 0.026 | 94.992 | 0.019 | 74.998 | 0.019 | 2727.9 | 2.6 | 2699.5 | 2.6 | 0.534 | 0.002 | -0.251 | 0.002 | 0.167 | 0.003 | 1.544 | 0.0029 | 29.535 | 0.001 | 9863 | 16 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.3092 | 12494.9454 | 169.3518 | 0 | 0 | 12494.9454 | 0.0087831 | 27.604 | 56.0058 | 14.0997 | 13.0992 | 0.013921 | 38.1553 | 0.0087831 | 27.604 | 0.0084053 | 22.8876 | 74.97 | 61.993 | 22.5685 | 62919.071 | 56869.5943 | 8543 | 0.46341 | 58991.9085 | 52942.4318 | 5.9811 | 0.16703 | -5.0356 | -18.9642 | 52.2032 | 62919.071 | 58932.0102 | 3987.0608 | 0 | 62919.071 | 100%
2 | 3T-75629575-E3-Retest | 75T0181 | 3T-75629575-E3-Retest | closed | on | on | 3 turns | unsealed | sealed |  | 5.375 |  | 0 | 0 | CUST 8 | 2/21/2014 | 11:10:22 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU4 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.8 | 0 | 15.1 | 0 | 59126 | 208 | 57446 | 380 | 6936 | 189 | 66069 | 286 | 7.6735 | 928 |  | 32.3 | [36 empty] | Factory charge, 3 turns, Econo closed damper unsealed cab, 75% Meriam,--adjust code tester speed to match total static of run 3T-75629575-E3-SPWCT-SS | R22 CK1 : 6.4 lbs /Ck2 : 6.2 lbs: Unsealed cab/ Sealed ductwork: 5.375` blower pulley with AX35 (notched) belt : motor pulley 3 turns opened. with econo Closed: Meriam set @ 75%: Horiz airflow. set on floor. | 74.995 | 0.026 | 61.999 | 0.031 | 95.006 | 0.024 | 75.005 | 0.02 | 74.63 | 0.13 | 56.57 | 0.06 | 61.52 | 0.03 | 0.164 | 0.012 | 1.1605 | 0.0079 | 59126 | 208 | 6936 | 189 | 7.674 | 0.037 | [6 empty] | 459.8 | 2.1 | 461 | 2.1 | 460.3 | 2.1 | 15.1 | 0 | 13 | 0 | 13.1 | 0.1 | 6857 | 42.9 | 3193.8 | 50.9 | 1752.8 | 34 | 460 |  | 459 |  | 460 |  | 2.8 |  | 2.8 |  | 3 |  | 0.65 | 460 |  | 461 |  | 459 |  | 5.1 |  | 5 |  | 4.5 |  | 3210 |  | 0.73 | 460 | 461 | 459 | 5.1 | 4.8 | 4.4 | 3100 | 0.82 | 458.9 |  | 1.7 |  | 714.8 |  | 115 |  | 8609.8 | [22 empty] | 249.44 | 0.34 | 175.28 | 0.2 | 116.91 | 0.1 | 58.37 | 0.19 |  |  | 100.33 | 0.13 | [6 empty] | 48.32 | 0.47 |  |  |  |  | 74.82 | 0.07 | 56.21 | 0.34 | 44.05 | 0.04 | 12.16 | 0.34 | [46 empty] | 257.79 | 0.37 | 174.76 | 0.38 | 119.32 | 0.1 | 55.44 | 0.42 | [8 empty] | 97.98 | 0.12 | [10 empty] | 78.93 | 0.21 | 56.2 | 1.59 | 46.69 | 0.13 | 9.51 | 1.66 | 99.34 | 0.09 | [36 empty] | 56.58 | 0.08 | 56.82 | 0.08 | 57.01 | 0.07 | 56.59 | 0.07 | 56.89 | 0.06 | 56.77 | 0.06 | [32 empty] | 103.46 | 0.13 | 99.44 | 0.12 | 93.04 | 0.14 | 93.14 | 0.13 | 93.13 | 0.13 | 93.21 | 0.14 | 93.27 | 0.17 | 93.3 | 0.16 | [8 empty] | 103.74 | 0.14 | 99.34 | 0.09 | [16 empty] | 49.25 | 0.9 | [14 empty] | 96.01 | 0.27 | 95.39 | 0.13 | 74.81 | 0.13 | 74.81 | 0.11 | 74.71 | 0.12 | 74.84 | 0.15 | 74.83 | 0.15 | 74.85 | 0.14 | 74.77 | 0.12 | 77.05 | 0.11 | 77.44 | 0.11 | 76.89 | 0.11 | 76.22 | 0.1 | 78.86 | 0.16 | 77.72 | 0.11 | 77.08 | 0.1 | 76.31 | 0.09 | 84.48 | 0.16 | 80.62 | 0.22 | 76.03 | 0.1 | 75.21 | 0.1 | 82.44 | 0.27 | 76.23 | 0.12 | 75.35 | 0.1 | 74.75 | 0.09 | 75.71 | 0.09 | 74.92 | 0.08 | 74.96 | 0.09 | 74.98 | 0.09 | [84 empty] | T2-TRN-88A-55-CE-DM-2 | 74.995 | 0.026 | 61.999 | 0.031 | 56.414 | 0.021 | 54.24 | 0.031 | 95.006 | 0.024 | 75.005 | 0.02 | 2877.2 | 9.7 | 2837.5 | 9.7 | 0.92 | 0.007 | -0.47 | 0.005 | 0.164 | 0.012 | 1.1605 | 0.0079 | 29.469 | 0.001 | 8610 | 22 | 1470 |  | 0 | 0 | 13.029 | 0.231 | 1.2528 | 13201.6449 | 306.6824 | 0 | 0 | 13201.6449 | 0.0087811 | 27.608 | 55.1612 | 14.1001 | 13.0766 | 0.013924 | 38.1619 | 0.0087811 | 27.608 | 0.0084265 | 22.6909 | 74.995 | 61.999 | 22.3856 | 68944.1435 | 62841.1831 | 7140 | 0.35346 | 64973.7404 | 58870.78 | 7.5463 | 0.12407 | -5.2224 | -19.8338 | 52.3519 | 68944.1435 | 64913.0271 | 4031.1164 | 0 | 68944.1435 | 100%
2 | T2-RC10-130C1-130C2-90A-95-CE | 75T0186 | T2-RC10-130C1-130C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/8/2014 | 6:28:09 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 8.3 lbs/CK2: 8.1 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 8.3 | 8.1 | 6.4 | 6.2 | 460.3 | 0 | 15.2 | 0 | 58449 | 51 | 58642 | 386 | 11739 | 138 | 70199 | 146 | 8.2384 | 854 | 1310 |  | 6.8594 | [35 empty] | RC6, 130% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC6-70C1-70C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75 | 0.01 | 61.994 | 0.025 | 95.007 | 0.012 | 75.006 | 0.023 | 75.28 | 0.13 | 55.59 | 0.04 | 59.31 | 0.02 | 0.152 | 0.003 | 1.4999 | 0.0022 | 58449 | 51 | 11739 | 138 | 8.239 | 0.026 | [6 empty] | 460.3 | 2 | 461.8 | 2 | 459.9 | 2 | 15.2 | 0.1 | 12.9 | 0 | 13 | 0 | 6912.4 | 45.8 | 3174.9 | 49.6 | 1608.1 | 35.4 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.8 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.2 |  | 5 |  | 4.4 |  | 3240 |  | 0.83 | 460 | 460 | 460 | 5.3 | 4.9 | 4.3 | 3150 | 0.81 | 459.4 |  | 1.6 |  | 698 |  | 85 |  | 8493 | [14 empty] | 235.03 | 0.34 | 96.84 | 0.13 | 112.59 | 0.1 | 15.75 | 0.12 | 253.87 | 0.34 | 175.94 | 0.38 | 118.18 | 0.1 | 57.75 | 0.46 | 229.7 | 0.05 | 96.19 | 0.12 | 110.95 | 0.05 | 14.76 | 0.05 | 73.52 | 0.21 | 48.39 | 0.75 | 43.17 | 0.13 | 5.23 | 0.86 | 72.9 | 0.21 | 53.33 | 0.98 | 42.76 | 0.14 | 10.58 | 1.07 | [46 empty] | 267.19 | 0.31 | 178.31 | 0.41 | 121.97 | 0.08 | 56.35 | 0.46 | 251.89 | 0.38 | 117.61 | 0.11 | 22.29 | 0.15 | 241.9 | 0.05 | 91.09 | 0.09 | 114.66 | 0.05 | 23.57 | 0.05 | 76.78 | 0.15 | 45.28 | 0.1 | 2.19 | 0.59 | 76.39 | 0.13 | 54.39 | 1.24 | 45.03 | 0.08 | 9.35 | 1.29 | 95.54 | 0.15 | [28 empty] | 97.02 | 0.14 | 96.94 | 0.12 | 95.54 | 0.15 | 95.84 | 0.13 | 54.84 | 0.06 | 55.52 | 0.05 | 55.44 | 0.05 | 55.2 | 0.05 | 55.28 | 0.05 |  |  | 96.81 | 0.14 | 93.52 | 0.13 | 48.82 | 1.34 | 53.25 | 1.19 | 178.44 | 0.44 | 95.76 | 0.14 | 90.16 | 0.09 | 48.59 | 0.48 | 55.42 | 1.09 | 96.19 | 0.12 | 91.09 | 0.09 | 92.21 | 0.11 | 97.68 | 0.11 | 97.4 | 0.12 | 96.22 | 0.1 | 96.48 | 0.13 | 96.94 | 0.12 | 95.84 | 0.13 | [16 empty] | 96.84 | 0.13 | 95.32 | 0.13 | 97.02 | 0.14 | 95.54 | 0.15 | [16 empty] | 47.48 | 0.52 | [12 empty] | 176.83 | 0.48 | 93.9 | 0.21 | 95.73 | 0.1 | 75.49 | 0.06 | 77.13 | 0.06 | 75.28 | 0.06 | 77.24 | 0.06 | 75.73 | 0.06 | 75.87 | 0.07 | 75.8 | 0.07 | 79.77 | 0.11 | 77.88 | 0.06 | 77.58 | 0.05 | 76.11 | 0.09 | 77.38 | 0.08 | 77.3 | 0.07 | 77.41 | 0.06 | 76.98 | 0.07 | 75.9 | 0.07 | 76.45 | 0.07 | 75.56 | 0.07 | 75.34 | 0.08 | 75.34 | 0.07 | 75.3 | 0.07 | 75.67 | 0.08 | 75.41 | 0.07 | 75.29 | 0.05 | 80.81 | 0.09 | 79.78 | 0.12 |  |  | 76.44 | 0.07 | 75.27 | 0.06 | 75.63 | 0.07 | 75.79 | 0.07 | 76.69 |  | 75.22 | 0.08 | 80.14 | 0.09 | 80.27 | 0.08 | 77.44 | 0.07 | 75.77 | 0.08 | 75.36 | 0.07 | [12 empty] | 75.45 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 75 | 0.01 | 61.994 | 0.025 | 55.379 | 0.014 | 53.08 | 0.022 | 95.007 | 0.012 | 75.006 | 0.023 | 2692.1 | 2 | 2657.9 | 2 | 0.537 | 0.002 | -0.246 | 0.002 | 0.152 | 0.003 | 1.4999 | 0.0022 | 29.361 | 0 | 8521 | 19 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.3233 | 12380.1494 | 167.6787 | 0 | 0 | 12380.1494 | 0.0087767 | 27.6043 | 54.0557 | 14.1001 | 13.0472 | 0.013924 | 38.1628 | 0.0087767 | 27.6043 | 0.0080207 | 21.9981 | 75 | 61.994 | 21.6758 | 73395.524 | 62230.3391 | 7201 | 0.33486 | 69462.6516 | 58297.4666 | 8.1519 | 0.13391 | -5.9285 | -20.9443 | 50.8174 | 73395.524 | 69405.464 | 3990.06 | 0 | 73395.524 | 100%
2 | T2-RC11-140C1-140C2-90A-95-CE | 75T0187 | T2-RC11-140C1-140C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/8/2014 | 7:18:38 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 9.0 lbs/CK2: 8.7 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 9 | 8.7 | 6.4 | 6.2 | 460 | 0 | 15.2 | 0 | 58510 | 56 | 58786 | 364 | 11904 | 191 | 70424 | 189 | 8.1717 | 854 | 1310 |  | 6.7893 | [35 empty] | RC8, 140% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC8-60C1-60C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.972 | 0.012 | 62.004 | 0.03 | 94.998 | 0.015 | 74.999 | 0.028 | 75.24 | 0.13 | 55.54 | 0.04 | 59.32 | 0.02 | 0.152 | 0.003 | 1.5029 | 0.0022 | 58510 | 56 | 11904 | 191 | 8.171 | 0.027 | [6 empty] | 460 | 2 | 461.6 | 2 | 460 | 2 | 15.2 | 0.1 | 13 | 0 | 13.2 | 0 | 6943.1 | 44.2 | 3197.9 | 48.8 | 1675 | 33.1 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.8 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.2 |  | 5 |  | 4.5 |  | 3290 |  | 0.84 | 460 | 460 | 460 | 5.3 | 5 | 4.4 | 3230 | 0.82 | 459.2 |  | 1.6 |  | 698 |  | 85 |  | 8613 | [14 empty] | 237.98 | 0.3 | 96.18 | 0.1 | 113.49 | 0.09 | 17.31 | 0.09 | 256.39 | 0.32 | 176.78 | 0.35 | 118.91 | 0.09 | 57.86 | 0.4 | 233.4 | 0.05 | 95.64 | 0.1 | 112.1 | 0.05 | 16.46 | 0.05 | 73.55 | 0.17 | 48.17 | 0.68 | 43.19 | 0.12 | 4.98 | 0.77 | 72.94 | 0.18 | 53.21 | 0.85 | 42.79 | 0.12 | 10.42 | 0.92 | [46 empty] | 273.27 | 0.36 | 181.04 | 0.18 | 123.65 | 0.1 | 57.39 | 0.22 | 258.7 | 0.42 | 119.57 | 0.11 | 25 | 0.14 | 248.6 | 0.05 | 90.53 | 0.07 | 116.65 |  | 26.12 | 0.05 | 76.73 | 0.09 | 45.26 | 0.06 | 2.01 | 0.27 | 76.35 | 0.08 | 54.54 | 0.61 | 45.02 | 0.05 | 9.52 | 0.64 | 94.85 | 0.1 | [28 empty] | 96.38 | 0.11 | 96.3 | 0.09 | 94.85 | 0.1 | 95.08 | 0.1 | 54.77 | 0.06 | 55.48 | 0.05 | 55.44 | 0.05 | 55.18 | 0.03 | 55.27 | 0.04 |  |  | 96.21 | 0.1 | 92.92 | 0.1 | 48.58 | 1.09 | 53.05 | 0.98 | 181.13 | 0.19 | 95.02 | 0.1 | 89.66 | 0.06 | 48.54 | 0.18 | 55.68 | 0.49 | 95.64 | 0.1 | 90.53 | 0.07 | 92.36 | 0.11 | 97.16 | 0.09 | 96.83 | 0.11 | 95.61 | 0.08 | 95.78 | 0.07 | 96.3 | 0.09 | 95.08 | 0.1 | [16 empty] | 96.18 | 0.1 | 94.57 | 0.11 | 96.38 | 0.11 | 94.85 | 0.1 | [16 empty] | 47.27 | 0.23 | [12 empty] | 177.72 | 0.42 | 93.94 | 0.22 | 95.76 | 0.11 | 75.48 | 0.06 | 77.1 | 0.06 | 75.26 | 0.06 | 77.22 | 0.06 | 75.71 | 0.06 | 75.82 | 0.07 | 75.74 | 0.07 | 79.79 | 0.11 | 77.91 | 0.06 | 77.59 | 0.05 | 76.15 | 0.07 | 77.39 | 0.06 | 77.3 | 0.06 | 77.41 | 0.05 | 76.99 | 0.06 | 75.9 | 0.07 | 76.44 | 0.07 | 75.56 | 0.07 | 75.34 | 0.07 | 75.34 | 0.07 | 75.31 | 0.07 | 75.68 | 0.07 | 75.42 | 0.07 | 75.29 | 0.05 | 80.81 | 0.07 | 79.79 | 0.08 |  |  | 76.41 | 0.07 | 75.32 | 0.06 | 75.65 | 0.07 | 75.8 | 0.07 | 76.7 |  | 75.22 | 0.07 | 80.2 | 0.08 | 80.3 | 0.08 | 77.46 | 0.06 | 75.78 | 0.07 | 75.37 | 0.07 | [12 empty] | 75.46 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.972 | 0.012 | 62.004 | 0.03 | 55.361 | 0.011 | 53.07 | 0.018 | 94.998 | 0.015 | 74.999 | 0.028 | 2693.8 | 2 | 2661.7 | 2 | 0.537 | 0.003 | -0.247 | 0.002 | 0.152 | 0.003 | 1.5029 | 0.0022 | 29.384 | 0.001 | 8618 | 19 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3106 | 12388.4097 | 167.9185 | 0 | 0 | 12388.4097 | 0.0087899 | 27.6119 | 54.0504 | 14.0999 | 13.0467 | 0.01392 | 38.1562 | 0.0087899 | 27.6119 | 0.0080194 | 21.9923 | 74.972 | 62.004 | 21.6731 | 73572.5524 | 62204.5669 | 7308 | 0.33902 | 69674.6282 | 58306.6427 | 8.0848 | 0.13432 | -5.9388 | -20.9216 | 50.8041 | 73572.5524 | 69617.9581 | 3954.5943 | 0 | 73572.5524 | 100%
2 | T2-RC2-95C1-95C2-90A-95-CE | 75T0188 | T2-RC2-95C1-95C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/7/2014 | 20:19:24 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.1 lbs/CK2: 5.9 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.1 | 5.9 | 6.4 | 6.2 | 460.3 | 0 | 14.8 | 0 | 56523 | 51 | 56633 | 335 | 9423 | 122 | 65955 | 128 | 8.0188 | 853 | 1320 |  | 6.8721 | [35 empty] | RC2, 95% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC2-95C1-95C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.978 | 0.015 | 61.979 | 0.012 | 95.065 | 0.01 | 75 | 0.019 | 75.47 | 0.11 | 56.55 | 0.03 | 60 | 0.03 | 0.163 | 0.003 | 1.5175 | 0.0026 | 56523 | 51 | 9423 | 122 | 8.019 | 0.022 | [6 empty] | 460.3 | 2.1 | 461.3 | 2.1 | 459.9 | 2.1 | 14.8 | 0 | 12.6 | 0 | 12.7 | 0 | 6724.7 | 44.2 | 3180.3 | 52.9 | 1500 | 33.4 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.9 |  | 4.4 |  | 3160 |  | 0.83 | 460 | 460 | 460 | 5 | 4.6 | 4.2 | 2930 | 0.8 | 459.4 |  | 1.6 |  | 699.2 |  | 85 |  | 8194.2 | [14 empty] | 217.3 | 0.16 | 107.28 | 0.06 | 107.04 | 0.05 | -0.24 | 0.04 | 247.21 | 0.18 | 176.53 | 0.07 | 116.25 | 0.05 | 60.28 | 0.09 | 209.4 | 0.05 | 104.33 | 0.06 | 104.47 | 0.05 | 0.14 | 0.05 | 74.02 | 0.04 | 50.94 | 0.24 | 43.51 | 0.02 | 7.44 | 0.25 | 73.38 | 0.03 | 57.4 | 0.1 | 43.08 | 0.02 | 14.32 | 0.1 | [46 empty] | 247.97 | 0.21 | 170.96 | 0.17 | 116.47 | 0.06 | 54.49 | 0.19 | 227.8 | 0.25 | 110.37 | 0.08 | 6.7 | 0.13 | 217.6 | 0.05 | 98.47 | 0.07 | 107.14 | 0.05 | 8.67 | 0.05 | 77.22 | 0.06 | 45.58 | 0.04 | 2.51 | 0.34 | 76.82 | 0.07 | 56.58 | 0.44 | 45.33 | 0.05 | 11.25 | 0.47 | 103.78 | 0.11 | [28 empty] | 106.34 | 0.06 | 105.72 | 0.06 | 103.78 | 0.11 | 104.19 | 0.11 | 55.75 | 0.05 | 56.33 | 0.05 | 56.15 | 0.04 | 56.06 | 0.03 | 56.13 | 0.03 |  |  | 106.76 | 0.07 | 101.32 | 0.08 | 52.18 | 0.32 | 57.21 | 0.11 | 171.13 | 0.18 | 103.99 | 0.12 | 97.21 | 0.07 | 49.17 | 0.28 | 57.22 | 0.36 | 104.33 | 0.06 | 98.47 | 0.07 | 92.59 | 0.11 | 106.99 | 0.05 | 106.16 | 0.06 | 103.99 | 0.08 | 104.42 | 0.09 | 105.72 | 0.06 | 104.19 | 0.11 | [16 empty] | 107.28 | 0.06 | 103.66 | 0.12 | 106.34 | 0.06 | 103.78 | 0.11 | [16 empty] | 48.09 | 0.32 | [12 empty] | 177.41 | 0.07 | 94.28 | 0.19 | 95.98 | 0.09 | 75.63 | 0.04 | 77.3 | 0.05 | 75.4 | 0.05 | 77.47 | 0.05 | 75.94 | 0.05 | 76.05 | 0.06 | 75.95 | 0.05 | 79.93 | 0.11 | 77.99 | 0.05 | 77.66 | 0.05 | 76.21 | 0.07 | 77.48 | 0.07 | 77.39 | 0.06 | 77.47 | 0.05 | 77.07 | 0.06 | 75.99 | 0.06 | 76.54 | 0.06 | 75.63 | 0.06 | 75.33 | 0.06 | 75.33 | 0.06 | 75.39 | 0.06 | 75.74 | 0.06 | 75.38 | 0.06 | 75.36 | 0.05 | 80.56 | 0.06 | 79.51 | 0.08 |  |  | 76.62 | 0.05 | 75.46 | 0.05 | 75.78 | 0.06 | 75.92 | 0.06 | 76.82 |  | 75.3 | 0.06 | 80.4 | 0.09 | 80.46 | 0.09 | 77.57 | 0.07 | 75.86 | 0.07 | 75.35 | 0.06 | [12 empty] | 75.43 | 0.06 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.978 | 0.015 | 61.979 | 0.012 | 56.092 | 0.006 | 53.689 | 0.01 | 95.065 | 0.01 | 75 | 0.019 | 2708.2 | 2.4 | 2672.7 | 2.3 | 0.533 | 0.002 | -0.249 | 0.002 | 0.163 | 0.003 | 1.5175 | 0.0026 | 29.396 | 0.001 | 8225 | 17 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.3177 | 12435.7045 | 167.3565 | 0 | 0 | 12435.7045 | 0.008772 | 27.5938 | 54.7743 | 14.1014 | 13.0666 | 0.013905 | 38.156 | 0.008772 | 27.5938 | 0.0081919 | 22.3577 | 74.978 | 61.979 | 22.0366 | 69107.3954 | 60299.3913 | 6905 | 0.34102 | 65173.423 | 56365.4189 | 7.9238 | 0.14119 | -5.5572 | -20.2037 | 51.4528 | 69107.3954 | 65114.9739 | 3992.4215 | 0 | 69107.3954 | 100%
2 | T2-RC3-90C1-90C2-90A-95-CE | 75T0189 | T2-RC3-90C1-90C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/7/2014 | 21:20:36 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.8 lbs/CK2: 5.6 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.8 | 5.6 | 6.4 | 6.2 | 460 | 0 | 14.7 | 0 | 55947 | 74 | 55998 | 382 | 8995 | 142 | 64951 | 167 | 7.9334 | 854 | 1320 |  | 6.8336 | [35 empty] | RC3, 90% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester--speed to match total static of run T2-RC3-90C1-90C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.963 | 0.011 | 61.993 | 0.025 | 95.011 | 0.014 | 74.995 | 0.018 | 75.28 | 0.13 | 56.55 | 0.04 | 60.04 | 0.01 | 0.163 | 0.003 | 1.5174 | 0.002 | 55947 | 74 | 8995 | 142 | 7.934 | 0.026 | [6 empty] | 460 | 2 | 461.2 | 2 | 459.9 | 2 | 14.7 | 0.1 | 12.6 | 0 | 12.7 | 0 | 6689.8 | 43.6 | 3186.7 | 51.1 | 1497.2 | 33.9 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.9 |  | 4.4 |  | 3140 |  | 0.82 | 460 | 460 | 460 | 5 | 4.6 | 4.2 | 2920 | 0.8 | 459.2 |  | 1.6 |  | 699.1 |  | 85 |  | 8164.1 | [14 empty] | 213.63 | 0.23 | 105.93 | 0.07 | 105.86 | 0.07 | -0.07 | 0.06 | 246.03 | 0.24 | 178.46 | 0.08 | 115.89 | 0.07 | 62.57 | 0.08 | 203.5 | 0.05 | 102.61 | 0.07 | 102.5 | 0.05 | -0.11 | 0.05 | 73.94 | 0.04 | 55.23 | 0.24 | 43.44 | 0.03 | 11.78 | 0.24 | 73.29 | 0.04 | 59.82 | 0.09 | 43.01 | 0.03 | 16.81 | 0.08 | [46 empty] | 246.25 | 0.25 | 170.25 | 0.1 | 115.96 | 0.08 | 54.29 | 0.11 | 222.86 | 0.31 | 108.81 | 0.1 | 1.71 | 0.1 | 211.6 | 0.05 | 101.29 | 0.05 | 105.19 | 0.05 | 3.9 | 0.05 | 77.55 | 0.04 | 45.78 | 0.03 | 2.57 | 0.31 | 77.17 | 0.06 | 57.06 | 0.23 | 45.54 | 0.04 | 11.52 | 0.24 | 107.29 | 0.11 | [28 empty] | 104.66 | 0.07 | 104.04 | 0.07 | 107.29 | 0.11 | 107.19 | 0.08 | 55.79 | 0.05 | 56.41 | 0.05 | 56.3 | 0.06 | 56.14 | 0.04 | 56.21 | 0.04 |  |  | 105.4 | 0.08 | 99.48 | 0.09 | 55.44 | 0.22 | 59.61 | 0.1 | 170.38 | 0.1 | 107.44 | 0.12 | 100.04 | 0.05 | 49.61 | 0.25 | 57.79 | 0.22 | 102.61 | 0.07 | 101.29 | 0.05 | 92.72 | 0.11 | 105.89 | 0.06 | 104.6 | 0.08 | 107.32 | 0.07 | 107.75 | 0.09 | 104.04 | 0.07 | 107.19 | 0.08 | [16 empty] | 105.93 | 0.07 | 107.1 | 0.13 | 104.66 | 0.07 | 107.29 | 0.11 | [16 empty] | 48.33 | 0.27 | [12 empty] | 179.37 | 0.09 | 94.17 | 0.16 | 95.92 | 0.1 | 75.52 | 0.04 | 77.18 | 0.05 | 75.3 | 0.05 | 77.35 | 0.06 | 75.83 | 0.04 | 75.92 | 0.06 | 75.83 | 0.05 | 79.93 | 0.1 | 77.99 | 0.05 | 77.65 | 0.05 | 76.19 | 0.07 | 77.45 | 0.07 | 77.33 | 0.06 | 77.44 | 0.05 | 77.05 | 0.06 | 75.92 | 0.06 | 76.48 | 0.06 | 75.58 | 0.06 | 75.33 | 0.06 | 75.33 | 0.06 | 75.36 | 0.06 | 75.7 | 0.06 | 75.38 | 0.06 | 75.34 | 0.04 | 80.52 | 0.08 | 79.49 | 0.1 |  |  | 76.52 | 0.06 | 75.44 | 0.05 | 75.75 | 0.06 | 75.89 | 0.06 | 76.78 |  | 75.24 | 0.06 | 80.4 | 0.09 | 80.47 | 0.07 | 77.55 | 0.07 | 75.82 | 0.06 | 75.35 | 0.06 | [12 empty] | 75.43 | 0.06 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.963 | 0.011 | 61.993 | 0.025 | 56.254 | 0.014 | 53.839 | 0.022 | 95.011 | 0.014 | 74.995 | 0.018 | 2709.1 | 1.8 | 2671.5 | 1.8 | 0.534 | 0.002 | -0.249 | 0.002 | 0.163 | 0.003 | 1.5174 | 0.002 | 29.377 | 0.001 | 8187 | 17 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.3175 | 12435.5908 | 167.5952 | 0 | 0 | 12435.5908 | 0.0087848 | 27.6041 | 54.9365 | 14.1001 | 13.071 | 0.013914 | 38.1521 | 0.0087848 | 27.6041 | 0.0082379 | 22.4471 | 74.963 | 61.993 | 22.1261 | 68122.7454 | 59769.7976 | 6867 | 0.34404 | 64189.5877 | 55836.64 | 7.8404 | 0.14216 | -5.478 | -20.0265 | 51.6177 | 68122.7454 | 64130.8162 | 3991.9292 | 0 | 68122.7454 | 100%
2 | T2-RC4-80C1-80C2-90A-95-CE | 75T0190 | T2-RC4-80C1-80C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/7/2014 | 22:20:57 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.1 lbs/CK2: 5.0 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.1 | 5 | 6.4 | 6.2 | 460.1 | 0 | 14.7 | 0 | 54459 | 80 | 54403 | 424 | 7785 | 167 | 62250 | 168 | 7.6975 | 854 | 1310 |  | 6.7341 | [35 empty] | RC4, 80% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC4-80C1-80C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.999 | 0.011 | 62.001 | 0.032 | 94.991 | 0.026 | 74.993 | 0.017 | 75.43 | 0.14 | 57.21 | 0.03 | 60.39 | 0.01 | 0.159 | 0.004 | 1.5177 | 0.0026 | 54459 | 80 | 7785 | 167 | 7.698 | 0.026 | [6 empty] | 460.1 | 2.1 | 461.4 | 2.1 | 459.7 | 2.1 | 14.7 | 0.1 | 12.4 | 0 | 12.6 | 0.1 | 6663.9 | 45.3 | 3149 | 52.1 | 1423 | 33.8 | 460 |  | 460 |  | 460 |  | 2.9 |  | 2.9 |  | 2.8 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5 |  | 4.8 |  | 4.3 |  | 3090 |  | 0.83 | 460 | 460 | 460 | 4.9 | 4.6 | 4.1 | 2880 | 0.8 | 459.3 |  | 1.6 |  | 699.4 |  | 85 |  | 8064.4 | [14 empty] | 209.59 | 0.23 | 104.77 | 0.07 | 104.53 | 0.08 | -0.24 | 0.04 | 241.55 | 0.22 | 190.58 | 0.07 | 114.56 | 0.07 | -76.02 | 0.06 | 199 | 0.05 | 101.08 | 0.08 | 100.97 | 0.05 | -0.11 | 0.05 | 71.4 | 0.04 | 67.92 | 0.05 | 41.76 | 0.03 | 26.17 | 0.04 | 70.81 | 0.04 | 70.94 | 0.05 | 41.35 | 0.03 | 29.59 | 0.05 | [46 empty] | 242.72 | 0.22 | 173.86 | 0.07 | 114.91 | 0.07 | 58.95 | 0.06 | 213.9 | 0.3 | 105.94 | 0.1 | 0.29 | 0.07 | 198.5 | 0.05 | 97.36 | 0.06 | 100.98 | 0.05 | 3.62 | 0.05 | 77.38 | 0.04 | 45.68 | 0.02 | 10.86 | 0.4 | 77.01 | 0.05 | 62.27 | 0.11 | 45.44 | 0.03 | 16.84 | 0.11 | 103.14 | 0.08 | [28 empty] | 103.3 | 0.08 | 102.65 | 0.08 | 103.14 | 0.08 | 103.03 | 0.07 | 56.36 | 0.04 | 57.05 | 0.04 | 56.85 | 0.04 | 56.7 | 0.03 | 56.77 | 0.03 |  |  | 104.12 | 0.07 | 97.95 | 0.08 | 69.18 | 0.05 | 70.89 | 0.05 | 174.1 | 0.06 | 105.43 | 0.06 | 96.24 | 0.05 | 57.97 | 0.35 | 62.64 | 0.12 | 101.08 | 0.08 | 97.36 | 0.06 | 92.76 | 0.11 | 104.61 | 0.06 | 103.05 | 0.08 | 104.44 | 0.06 | 104.28 | 0.06 | 102.65 | 0.08 | 103.03 | 0.07 | [16 empty] | 104.77 | 0.07 | 105.66 | 0.07 | 103.3 | 0.08 | 103.14 | 0.08 | [16 empty] | 56.54 | 0.39 | [12 empty] | 191.68 | 0.07 | 94.31 | 0.18 | 95.96 | 0.09 | 75.65 | 0.06 | 77.33 | 0.05 | 75.42 | 0.07 | 77.51 | 0.07 | 75.98 | 0.06 | 76.08 | 0.07 | 75.99 | 0.07 | 79.94 | 0.1 | 78.04 | 0.05 | 77.71 | 0.05 | 76.25 | 0.07 | 77.53 | 0.08 | 77.41 | 0.07 | 77.51 | 0.05 | 77.16 | 0.07 | 75.98 | 0.07 | 76.55 | 0.07 | 75.62 | 0.07 | 75.35 | 0.07 | 75.35 | 0.07 | 75.4 | 0.08 | 75.74 | 0.08 | 75.41 | 0.07 | 75.4 | 0.06 | 80.72 | 0.07 | 79.61 | 0.09 |  |  | 76.67 | 0.07 | 75.5 | 0.06 | 75.81 | 0.07 | 75.95 | 0.07 | 76.83 |  | 75.31 | 0.07 | 80.47 | 0.08 | 80.54 | 0.08 | 77.62 | 0.07 | 75.9 | 0.08 | 75.37 | 0.07 | [12 empty] | 75.47 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.999 | 0.011 | 62.001 | 0.032 | 56.768 | 0.014 | 54.209 | 0.023 | 94.991 | 0.026 | 74.993 | 0.017 | 2710.8 | 2.3 | 2670.3 | 2.3 | 0.536 | 0.002 | -0.248 | 0.002 | 0.159 | 0.004 | 1.5177 | 0.0026 | 29.37 | 0.001 | 8087 | 17 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3059 | 12430.3629 | 168.1473 | 0 | 0 | 12430.3629 | 0.0087815 | 27.6094 | 55.4621 | 14.0997 | 13.0847 | 0.013917 | 38.1505 | 0.0087815 | 27.6094 | 0.0083253 | 22.6673 | 74.999 | 62.001 | 22.3491 | 65387.3502 | 58284.3085 | 6777 | 0.35374 | 61490.207 | 54387.1653 | 7.6036 | 0.15326 | -5.2603 | -19.5369 | 51.9258 | 65387.3502 | 61431.3432 | 3956.007 | 0 | 65387.3502 | 100%
2 | T2-RC5-70C1-70C2-90A-95-CE | 75T0191 | T2-RC5-70C1-70C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/8/2014 | 0:34:56 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 4.5 lbs/CK2: 4.3 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 4.5 | 4.3 | 6.4 | 6.2 | 460.3 | 0 | 14.6 | 0 | 50338 | 72 | 50140 | 342 | 5289 | 111 | 55633 | 101 | 7.0049 | 854 | 1310 |  | 6.3382 | [35 empty] | RC5, 70% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC5-70C1-70C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.956 | 0.008 | 61.961 | 0.022 | 95.013 | 0.013 | 75.006 | 0.029 | 75.39 | 0.11 | 58.54 | 0.03 | 61.54 | 0.02 | 0.152 | 0.003 | 1.5149 | 0.0028 | 50338 | 72 | 5289 | 111 | 7.005 | 0.019 | [6 empty] | 460.3 | 2 | 461.6 | 2 | 459.6 | 2 | 14.6 | 0.1 | 12.3 | 0 | 12.4 | 0 | 6600.3 | 43.4 | 3126.1 | 50.1 | 1341.9 | 33.1 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 4.9 |  | 4.7 |  | 4.2 |  | 3010 |  | 0.82 | 460 | 460 | 460 | 4.9 | 4.5 | 4.1 | 2810 | 0.79 | 459.5 |  | 1.6 |  | 700.3 |  | 85 |  | 7915.3 | [14 empty] | 204.11 | 0.19 | 103.09 | 0.07 | 102.7 | 0.06 | -0.39 | 0.04 | 234.5 | 0.2 | 199.35 | 0.06 | 112.43 | 0.06 | 86.92 | 0.06 | 192.8 | 0.05 | 99.34 | 0.06 | 98.82 | 0.05 | -0.52 | 0.05 | 64.65 | 0.03 | 70.34 | 0.03 | 37.06 | 0.03 | 33.28 | 0.04 | 64.13 | 0.04 | 73.92 | 0.04 | 36.69 | 0.03 | 37.23 | 0.05 | [46 empty] | 235.83 | 0.22 | 187.84 | 0.05 | 112.83 | 0.06 | 75 | 0.06 | 207.3 | 0.29 | 103.77 | 0.1 | 0.24 | 0.07 | 190.3 | 0.05 | 94.91 | 0.06 | 97.94 | 0.05 | 3.03 | 0.05 | 73.45 | 0.04 | 43.11 | 0.03 | 27.62 | 0.06 | 72.99 | 0.05 | 74.59 | 0.05 | 42.81 | 0.03 | 31.78 | 0.07 | 100.65 | 0.07 | [28 empty] | 101.51 | 0.08 | 100.9 | 0.07 | 100.65 | 0.07 | 100.52 | 0.08 | 57.86 | 0.04 | 58.38 | 0.04 | 58.13 | 0.04 | 58.18 | 0.02 | 58.23 | 0.03 |  |  | 102.4 | 0.07 | 96.41 | 0.07 | 72.05 | 0.04 | 73.94 | 0.04 | 188.07 | 0.05 | 103.18 | 0.07 | 93.9 | 0.04 | 71.28 | 0.05 | 75.01 | 0.04 | 99.34 | 0.06 | 94.91 | 0.06 | 92.99 | 0.11 | 102.95 | 0.06 | 101.22 | 0.07 | 102.37 | 0.05 | 102.1 | 0.05 | 100.9 | 0.07 | 100.52 | 0.08 | [16 empty] | 103.09 | 0.07 | 103.53 | 0.08 | 101.51 | 0.08 | 100.65 | 0.07 | [16 empty] | 70.73 | 0.05 | [12 empty] | 200.53 | 0.07 | 94.46 | 0.17 | 96 | 0.08 | 75.68 | 0.04 | 77.38 | 0.05 | 75.44 | 0.06 | 77.56 | 0.06 | 76.03 | 0.04 | 76.1 | 0.06 | 76.01 | 0.06 | 79.99 | 0.1 | 78.03 | 0.05 | 77.71 | 0.05 | 76.29 | 0.07 | 77.56 | 0.06 | 77.43 | 0.05 | 77.53 | 0.05 | 77.18 | 0.06 | 75.99 | 0.06 | 76.57 | 0.06 | 75.64 | 0.06 | 75.36 | 0.06 | 75.34 | 0.06 | 75.39 | 0.06 | 75.74 | 0.06 | 75.42 | 0.06 | 75.43 | 0.05 | 80.81 | 0.09 | 79.68 | 0.11 |  |  | 76.71 | 0.06 | 75.56 | 0.05 | 75.81 | 0.06 | 75.95 | 0.06 | 76.85 |  | 75.29 | 0.06 | 80.5 | 0.08 | 80.58 | 0.08 | 77.66 | 0.05 | 75.91 | 0.07 | 75.37 | 0.06 | [12 empty] | 75.47 | 0.06 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.956 | 0.008 | 61.961 | 0.022 | 58.039 | 0.009 | 55.033 | 0.016 | 95.013 | 0.013 | 75.006 | 0.029 | 2712.7 | 2.5 | 2662.9 | 2.5 | 0.54 | 0.002 | -0.249 | 0.002 | 0.152 | 0.003 | 1.5149 | 0.0028 | 29.342 | 0.001 | 7942 | 16 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3075 | 12407.2805 | 168.9327 | 0 | 0 | 12407.2805 | 0.0087653 | 27.5812 | 56.7315 | 14.1003 | 13.1183 | 0.013923 | 38.1627 | 0.0087653 | 27.5812 | 0.0084956 | 23.1621 | 74.956 | 61.961 | 22.8434 | 58782.6832 | 54267.873 | 6632 | 0.38506 | 54888.2205 | 50373.4103 | 6.9111 | 0.18729 | -4.7378 | -18.2245 | 52.5317 | 58782.6832 | 54828.1707 | 3954.5124 | 0 | 58782.6832 | 100%
2 | T2-RC6-60C1-60C2-90A-95-CE | 75T0192 | T2-RC6-60C1-60C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/8/2014 | 1:38:56 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 3.8 lbs/CK2: 3.7 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 3.8 | 3.7 | 6.4 | 6.2 | 460.2 | 0 | 14.3 | 0 | 42340 | 35 | 42047 | 317 | 603 | 49 | 42944 | 65 | 5.5613 | 854 | 1310 |  | 5.483 | [35 empty] | RC6, 60% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC6-60C1-60C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.982 | 0.006 | 61.99 | 0.01 | 94.988 | 0.009 | 74.983 | 0.013 | 75.37 | 0.11 | 61.21 | 0.02 | 63.64 | 0.01 | 0.163 | 0.004 | 1.5257 | 0.0021 | 42340 | 35 | 603 | 49 | 5.561 | 0.015 | [6 empty] | 460.2 | 2 | 461.5 | 2 | 459.8 | 2 | 14.3 | 0.1 | 12 | 0 | 12.2 | 0.1 | 6459 | 44.2 | 3132.4 | 50.5 | 1263.3 | 32.9 | 460 |  | 460 |  | 460 |  | 3 |  | 2.9 |  | 2.8 |  | 0.49 | 460 |  | 460 |  | 460 |  | 4.8 |  | 4.6 |  | 4.1 |  | 2910 |  | 0.81 | 460 | 460 | 460 | 4.7 | 4.4 | 3.9 | 2710 | 0.78 | 459.5 |  | 1.6 |  | 702.4 |  | 85 |  | 7717.4 | [14 empty] | 195.01 | 0.21 | 100.05 | 0.05 | 99.6 | 0.07 | -0.45 | 0.06 | 223.11 | 0.15 | 212.46 | 0.07 | 108.89 | 0.05 | 103.57 | 0.07 | 183.6 | 0.05 | 96.27 | 0.06 | 95.55 | 0.05 | -0.72 | 0.05 | 53.39 | 0.05 | 71.25 | 0.03 | 28.54 | 0.04 | 42.71 | 0.06 | 52.99 | 0.06 | 75.08 | 0.03 | 28.22 | 0.04 | 46.86 | 0.05 | [46 empty] | 225.43 | 0.16 | 199.44 | 0.05 | 109.62 | 0.05 | 89.82 | 0.07 | 198.07 | 0.36 | 100.65 | 0.12 | 0.23 | 0.1 | 181.4 | 0.05 | 92.29 | 0.05 | 94.75 | 0.05 | 2.46 | 0.05 | 63.47 | 0.08 | 36.22 | 0.06 | 37.75 | 0.07 | 62.92 | 0.08 | 78.16 | 0.03 | 35.82 | 0.06 | 42.35 | 0.07 | 97.4 | 0.06 | [28 empty] | 98.33 | 0.06 | 97.74 | 0.06 | 97.4 | 0.06 | 97.24 | 0.05 | 60.55 | 0.03 | 61.1 | 0.03 | 60.88 | 0.03 | 60.83 | 0.02 | 60.87 | 0.02 |  |  | 99.32 | 0.06 | 93.46 | 0.07 | 72.93 | 0.04 | 75.04 | 0.03 | 199.62 | 0.06 | 100.04 | 0.05 | 91.56 | 0.04 | 74.59 | 0.03 | 78.76 | 0.03 | 96.27 | 0.06 | 92.29 | 0.05 | 93.47 | 0.08 | 100.04 | 0.05 | 98.01 | 0.06 | 99.36 | 0.04 | 99.15 | 0.04 | 97.74 | 0.06 | 97.24 | 0.05 | [16 empty] | 100.05 | 0.05 | 100.43 | 0.05 | 98.33 | 0.06 | 97.4 | 0.06 | [16 empty] | 73.97 | 0.04 | [12 empty] | 213.75 | 0.07 | 94.63 | 0.14 | 95.9 | 0.07 | 75.69 | 0.03 | 77.47 | 0.04 | 75.45 | 0.04 | 77.61 | 0.05 | 76.06 | 0.03 | 76.15 | 0.05 | 76.06 | 0.05 | 80.11 | 0.1 | 78.07 | 0.05 | 77.73 | 0.05 | 76.35 | 0.06 | 77.62 | 0.06 | 77.48 | 0.05 | 77.55 | 0.05 | 77.22 | 0.05 | 76.03 | 0.05 | 76.58 | 0.05 | 75.67 | 0.05 | 75.38 | 0.05 | 75.35 | 0.05 | 75.39 | 0.05 | 75.8 | 0.06 | 75.46 | 0.05 | 75.45 | 0.04 | 80.94 | 0.08 | 79.82 | 0.1 |  |  | 76.75 | 0.05 | 75.63 | 0.04 | 75.85 | 0.05 | 76 | 0.05 | 76.92 |  | 75.3 | 0.05 | 80.6 | 0.08 | 80.68 | 0.08 | 77.74 | 0.06 | 75.96 | 0.06 | 75.39 | 0.05 | [12 empty] | 75.51 | 0.05 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.982 | 0.006 | 61.99 | 0.01 | 60.723 | 0.005 | 56.727 | 0.013 | 94.988 | 0.009 | 74.983 | 0.013 | 2727.4 | 1.9 | 2666.3 | 1.9 | 0.535 | 0.003 | -0.249 | 0.002 | 0.163 | 0.004 | 1.5257 | 0.0021 | 29.356 | 0.001 | 7722 | 17 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.309 | 12407.544 | 167.5822 | 0 | 0 | 12407.544 | 0.0087783 | 27.6017 | 59.414 | 14.0995 | 13.1891 | 0.013909 | 38.1409 | 0.0087783 | 27.6017 | 0.0088525 | 24.2047 | 74.982 | 61.99 | 23.8854 | 46109.7684 | 46358.5302 | 6412 | 0.47461 | 42210.6965 | 42459.4583 | 5.4663 | 0.26144 | -3.7163 | -15.568 | 53.9031 | 46109.7684 | 42148.0018 | 3961.7666 | 0 | 46109.7684 | 100%
2 | T2-RC7-105C1-105C2-90A-95-CE | 75T0193 | T2-RC7-105C1-105C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/8/2014 | 3:15:04 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.7 lbs/CK2: 6.5 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.7 | 6.5 | 6.4 | 6.2 | 460.3 | 0 | 14.9 | 0 | 57595 | 60 | 57753 | 377 | 11063 | 146 | 68668 | 149 | 8.2703 | 854 | 1310 |  | 6.9366 | [35 empty] | RC2, 105% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-MFB3-105C1-105C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.992 | 0.013 | 62 | 0.021 | 94.99 | 0.02 | 74.987 | 0.016 | 75.33 | 0.13 | 55.94 | 0.04 | 59.48 | 0.01 | 0.147 | 0.003 | 1.5019 | 0.0022 | 57595 | 60 | 11063 | 146 | 8.27 | 0.024 | [6 empty] | 460.3 | 2 | 461.4 | 2 | 459.7 | 2 | 14.9 | 0 | 12.7 | 0 | 12.8 | 0 | 6788.7 | 44.1 | 3162.6 | 50.9 | 1514.1 | 33.1 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.9 |  | 4.4 |  | 3200 |  | 0.83 | 460 | 460 | 460 | 5.1 | 4.7 | 4.2 | 3010 | 0.8 | 459.4 |  | 1.6 |  | 698.4 |  | 85 |  | 8303.4 | [14 empty] | 227.64 | 0.18 | 101.47 | 0.13 | 110.32 | 0.06 | 8.85 | 0.12 | 249.76 | 0.19 | 174.85 | 0.13 | 116.99 | 0.06 | 57.86 | 0.12 | 222.6 | 0.05 | 100.78 | 0.11 | 108.73 | 0.05 | 7.95 | 0.05 | 73.62 | 0.04 | 48.14 | 0.13 | 43.23 | 0.03 | 4.91 | 0.14 | 73.01 | 0.04 | 54.1 | 0.19 | 42.82 | 0.03 | 11.28 | 0.21 | [46 empty] | 252.16 | 0.21 | 172.42 | 0.19 | 117.69 | 0.06 | 54.73 | 0.19 | 235.16 | 0.29 | 112.63 | 0.09 | 12.93 | 0.12 | 225.6 | 0.05 | 94.97 | 0.06 | 109.67 | 0.05 | 14.7 | 0.05 | 77.13 | 0.09 | 45.51 | 0.05 | 2.4 | 0.4 | 76.73 | 0.08 | 55.88 | 0.5 | 45.25 | 0.05 | 10.62 | 0.54 | 99.87 | 0.1 | [28 empty] | 101.8 | 0.14 | 101.63 | 0.12 | 99.87 | 0.1 | 100.21 | 0.1 | 55.13 | 0.04 | 55.77 | 0.04 | 55.67 | 0.04 | 55.48 | 0.03 | 55.57 | 0.04 |  |  | 101.53 | 0.14 | 97.69 | 0.12 | 48.45 | 0.3 | 53.9 | 0.22 | 172.62 | 0.21 | 100.12 | 0.1 | 93.87 | 0.06 | 49.03 | 0.32 | 56.58 | 0.43 | 100.78 | 0.11 | 94.97 | 0.06 | 92.37 | 0.13 | 102.12 | 0.11 | 102.11 | 0.12 | 100.34 | 0.07 | 100.66 | 0.09 | 101.63 | 0.12 | 100.21 | 0.1 | [16 empty] | 101.47 | 0.13 | 99.7 | 0.1 | 101.8 | 0.14 | 99.87 | 0.1 | [16 empty] | 47.92 | 0.38 | [12 empty] | 175.74 | 0.15 | 94.06 | 0.2 | 95.89 | 0.1 | 75.54 | 0.06 | 77.18 | 0.06 | 75.34 | 0.06 | 77.33 | 0.07 | 75.82 | 0.06 | 75.93 | 0.08 | 75.85 | 0.07 | 79.88 | 0.13 | 77.93 | 0.06 | 77.59 | 0.05 | 76.2 | 0.08 | 77.45 | 0.07 | 77.34 | 0.07 | 77.44 | 0.06 | 77.05 | 0.06 | 75.93 | 0.07 | 76.49 | 0.07 | 75.58 | 0.07 | 75.34 | 0.07 | 75.33 | 0.07 | 75.35 | 0.07 | 75.71 | 0.07 | 75.42 | 0.06 | 75.37 | 0.05 | 80.83 | 0.06 | 79.74 | 0.08 |  |  | 76.53 | 0.08 | 75.35 | 0.06 | 75.69 | 0.07 | 75.84 | 0.07 | 76.74 |  | 75.22 | 0.07 | 80.22 | 0.07 | 80.37 | 0.08 | 77.54 | 0.07 | 75.83 | 0.07 | 75.36 | 0.07 | [12 empty] | 75.45 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.992 | 0.013 | 62 | 0.021 | 55.657 | 0.014 | 53.302 | 0.016 | 94.99 | 0.02 | 74.987 | 0.016 | 2694.7 | 2 | 2658.7 | 1.9 | 0.539 | 0.002 | -0.248 | 0.002 | 0.147 | 0.003 | 1.5019 | 0.0022 | 29.354 | 0.001 | 8303 | 18 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3105 | 12384.9957 | 168.3539 | 0 | 0 | 12384.9957 | 0.0087825 | 27.6088 | 54.3465 | 14.0996 | 13.0547 | 0.013912 | 38.1447 | 0.0087825 | 27.6088 | 0.0080784 | 22.1285 | 74.992 | 62 | 21.8092 | 71826.9991 | 61366.6307 | 6993 | 0.33229 | 67930.5609 | 57470.1926 | 8.1814 | 0.13876 | -5.7995 | -20.6455 | 51.0203 | 71826.9991 | 67873.4875 | 3953.5116 | 0 | 71826.9991 | 100%
2 | T2-RC8-110C1-110C2-90A-95-CE | 75T0194 | T2-RC8-110C1-110C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/8/2014 | 4:14:48 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.0 lbs/CK2: 6.8 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7 | 6.8 | 6.4 | 6.2 | 460.3 | 0 | 15 | 0 | 57793 | 65 | 57993 | 408 | 11245 | 115 | 69048 | 132 | 8.2841 | 854 | 1310 |  | 6.9338 | [35 empty] | RC3, 110% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC3-90C1-90C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.99 | 0.015 | 62.002 | 0.016 | 94.999 | 0.01 | 75.001 | 0.016 | 75.36 | 0.14 | 55.89 | 0.03 | 59.47 | 0.01 | 0.152 | 0.004 | 1.5017 | 0.0024 | 57793 | 65 | 11245 | 115 | 8.284 | 0.023 | [6 empty] | 460.3 | 2 | 461.5 | 2 | 459.7 | 2 | 15 | 0.1 | 12.7 | 0 | 12.8 | 0 | 6813.8 | 43.8 | 3157.8 | 50 | 1520.8 | 33.1 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 49 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.9 |  | 4.4 |  | 3220 |  | 0.83 | 460 | 460 | 460 | 5.1 | 4.7 | 4.2 | 3010 | 0.81 | 459.4 |  | 1.6 |  | 698 |  | 85 |  | 8323 | [14 empty] | 229.14 | 0.21 | 100.29 | 0.09 | 110.78 | 0.06 | 10.5 | 0.12 | 250.05 | 0.24 | 174.88 | 0.25 | 117.07 | 0.07 | 57.81 | 0.26 | 223.9 | 0.05 | 99.63 | 0.07 | 109.14 | 0.05 | 9.51 | 0.05 | 73.65 | 0.11 | 48.3 | 0.44 | 43.25 | 0.07 | 5.06 | 0.5 | 73.04 | 0.11 | 54.04 | 0.58 | 42.84 | 0.08 | 11.2 | 0.62 | [46 empty] | 254.92 | 0.23 | 173.56 | 0.34 | 118.49 | 0.07 | 55.08 | 0.38 | 238.47 | 0.32 | 113.64 | 0.1 | 15.15 | 0.12 | 228.4 | 0.05 | 93.91 | 0.04 | 110.55 | 0.05 | 16.64 | 0.05 | 76.94 | 0.15 | 45.38 | 0.09 | 2.45 | 0.67 | 76.56 | 0.13 | 55.41 | 0.97 | 45.14 | 0.08 | 10.26 | 1.03 | 98.71 | 0.07 | [28 empty] | 100.59 | 0.1 | 100.43 | 0.08 | 98.71 | 0.07 | 99.05 | 0.07 | 55.07 | 0.04 | 55.71 | 0.04 | 55.62 | 0.03 | 55.46 | 0.03 | 55.54 | 0.03 |  |  | 100.34 | 0.09 | 96.67 | 0.08 | 48.8 | 0.81 | 53.89 | 0.66 | 173.72 | 0.36 | 98.98 | 0.07 | 92.85 | 0.03 | 48.92 | 0.53 | 56.27 | 0.82 | 99.63 | 0.07 | 93.91 | 0.04 | 92.36 | 0.1 | 101.02 | 0.07 | 100.92 | 0.08 | 99.22 | 0.05 | 99.51 | 0.1 | 100.43 | 0.08 | 99.05 | 0.07 | [16 empty] | 100.29 | 0.09 | 98.49 | 0.09 | 100.59 | 0.1 | 98.71 | 0.07 | [16 empty] | 47.83 | 0.59 | [12 empty] | 175.79 | 0.3 | 94.02 | 0.19 | 95.87 | 0.08 | 75.53 | 0.06 | 77.17 | 0.06 | 75.33 | 0.06 | 77.32 | 0.07 | 75.81 | 0.06 | 75.92 | 0.07 | 75.85 | 0.07 | 79.86 | 0.11 | 77.94 | 0.06 | 77.59 | 0.05 | 76.17 | 0.08 | 77.43 | 0.06 | 77.33 | 0.06 | 77.44 | 0.06 | 77.02 | 0.06 | 75.94 | 0.07 | 76.49 | 0.07 | 75.6 | 0.07 | 75.31 | 0.07 | 75.31 | 0.07 | 75.33 | 0.07 | 75.68 | 0.07 | 75.39 | 0.06 | 75.33 | 0.05 | 80.78 | 0.06 | 79.72 | 0.08 |  |  | 76.52 | 0.06 | 75.36 | 0.05 | 75.7 | 0.06 | 75.85 | 0.07 | 76.74 |  | 75.22 | 0.07 | 80.22 | 0.08 | 80.35 | 0.07 | 77.51 | 0.06 | 75.82 | 0.07 | 75.34 | 0.07 | [12 empty] | 75.43 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.99 | 0.015 | 62.002 | 0.016 | 55.587 | 0.005 | 53.252 | 0.014 | 94.999 | 0.01 | 75.001 | 0.016 | 2695 | 2.2 | 2658.1 | 2.1 | 0.536 | 0.002 | -0.247 | 0.002 | 0.152 | 0.004 | 1.5017 | 0.0024 | 29.344 | 0 | 8335 | 18 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3113 | 12388.1406 | 167.3791 | 0 | 0 | 12388.1406 | 0.0087843 | 27.6102 | 54.2757 | 14.0999 | 13.0528 | 0.013922 | 38.1581 | 0.0087843 | 27.6102 | 0.0080671 | 22.0991 | 74.99 | 62.002 | 21.7797 | 72228.898 | 61586.7245 | 7025 | 0.33195 | 68329.1328 | 57686.9594 | 8.1979 | 0.13724 | -5.8305 | -20.7143 | 50.9808 | 72228.898 | 68272.0921 | 3956.8059 | 0 | 72228.898 | 100%
2 | T2-RC9-120C1-120C2-90A-95-CE | 75T0195 | T2-RC9-120C1-120C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/8/2014 | 5:35:43 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.7 lbs/CK2: 7.4 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.7 | 7.4 | 6.4 | 6.2 | 460.3 | 0 | 15 | 0 | 58201 | 60 | 58377 | 422 | 11555 | 139 | 69766 | 173 | 8.2857 | 854 | 1310 |  | 6.9122 | [35 empty] | RC4, 120% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-RC4-80C1-80C2-90A-95-CE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.996 | 0.01 | 61.999 | 0.019 | 95.016 | 0.022 | 75 | 0.016 | 75.26 | 0.14 | 55.66 | 0.03 | 59.42 | 0.03 | 0.153 | 0.004 | 1.5006 | 0.0021 | 58201 | 60 | 11555 | 139 | 8.286 | 0.027 | [6 empty] | 460.3 | 2 | 461.4 | 2 | 459.8 | 2 | 15 | 0 | 12.8 | 0 | 12.9 | 0 | 6841.1 | 43.8 | 3181.4 | 48.5 | 1578.8 | 32.9 | 460 |  | 460 |  | 460 |  | 3 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.9 |  | 4.4 |  | 3230 |  | 0.83 | 460 | 460 | 460 | 5.2 | 4.9 | 4.3 | 3080 | 0.81 | 459.4 |  | 1.6 |  | 698.1 |  | 85 |  | 8413.1 | [14 empty] | 232.25 | 0.24 | 98.18 | 0.12 | 111.74 | 0.08 | 13.56 | 0.12 | 251.58 | 0.28 | 175.11 | 0.2 | 117.52 | 0.08 | 57.59 | 0.22 | 227 | 0.05 | 97.62 | 0.11 | 110.11 | 0.05 | 12.49 | 0.05 | 73.52 | 0.1 | 48.05 | 0.32 | 43.16 | 0.07 | 4.89 | 0.36 | 72.9 | 0.1 | 53.54 | 0.51 | 42.76 | 0.07 | 10.78 | 0.55 | [46 empty] | 260.95 | 0.29 | 175.96 | 0.19 | 120.21 | 0.09 | 55.75 | 0.21 | 245.1 | 0.33 | 115.62 | 0.1 | 19.03 | 0.14 | 235.1 | 0.05 | 92.28 | 0.08 | 112.61 | 0.05 | 20.33 | 0.05 | 76.83 | 0.08 | 45.32 | 0.05 | 2.12 | 0.31 | 76.45 | 0.07 | 55.12 | 0.58 | 45.07 | 0.05 | 10.05 | 0.61 | 96.86 | 0.11 | [28 empty] | 98.45 | 0.13 | 98.35 | 0.11 | 96.86 | 0.11 | 97.12 | 0.12 | 54.89 | 0.04 | 55.6 | 0.04 | 55.54 | 0.04 | 55.27 | 0.03 | 55.35 | 0.03 |  |  | 98.26 | 0.12 | 94.74 | 0.11 | 48.59 | 0.69 | 53.44 | 0.61 | 176.12 | 0.2 | 97.12 | 0.12 | 91.33 | 0.07 | 48.69 | 0.23 | 56.06 | 0.47 | 97.62 | 0.11 | 92.28 | 0.08 | 92.34 | 0.12 | 99.09 | 0.1 | 98.87 | 0.12 | 97.53 | 0.08 | 97.81 | 0.09 | 98.35 | 0.11 | 97.12 | 0.12 | [16 empty] | 98.18 | 0.12 | 96.59 | 0.14 | 98.45 | 0.13 | 96.86 | 0.11 | [16 empty] | 47.44 | 0.28 | [12 empty] | 176.02 | 0.25 | 93.87 | 0.18 | 95.75 | 0.1 | 75.47 | 0.06 | 77.12 | 0.06 | 75.31 | 0.07 | 77.23 | 0.07 | 75.71 | 0.06 | 75.86 | 0.08 | 75.78 | 0.07 | 79.77 | 0.11 | 77.88 | 0.06 | 77.58 | 0.06 | 76.11 | 0.08 | 77.38 | 0.07 | 77.27 | 0.06 | 77.39 | 0.06 | 76.97 | 0.07 | 75.88 | 0.07 | 76.43 | 0.07 | 75.55 | 0.07 | 75.3 | 0.08 | 75.31 | 0.08 | 75.31 | 0.08 | 75.64 | 0.08 | 75.38 | 0.07 | 75.3 | 0.06 | 80.77 | 0.08 | 79.68 | 0.1 |  |  | 76.47 | 0.07 | 75.31 | 0.06 | 75.65 | 0.07 | 75.81 | 0.07 | 76.68 |  | 75.22 | 0.07 | 80.19 | 0.09 | 80.32 | 0.09 | 77.44 | 0.07 | 75.77 | 0.07 | 75.33 | 0.08 | [12 empty] | 75.41 | 0.08 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.996 | 0.01 | 61.999 | 0.019 | 55.458 | 0.011 | 53.148 | 0.017 | 95.016 | 0.022 | 75 | 0.016 | 2693.3 | 1.9 | 2657.9 | 1.8 | 0.537 | 0.003 | -0.247 | 0.002 | 0.153 | 0.004 | 1.5006 | 0.0021 | 29.354 | 0 | 8420 | 18 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.3229 | 12383.6279 | 167.6787 | 0 | 0 | 12383.6279 | 0.0087809 | 27.608 | 54.1351 | 14.1003 | 13.0493 | 0.013917 | 38.1568 | 0.0087809 | 27.608 | 0.0080397 | 22.0381 | 74.996 | 61.999 | 21.7158 | 72965.9788 | 62000.0373 | 7100 | 0.3321 | 69033.1064 | 58067.1649 | 8.1987 | 0.13478 | -5.8921 | -20.8609 | 50.8856 | 72965.9788 | 68975.7802 | 3990.1987 | 0 | 72965.9788 | 100%
2 | T2-RCB1-100C1-100C2-90A-95-CE-5 | 75T0196 | T2-RCB1-100C1-100C2-90A-95-CE-5 | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 11/7/2014 | 19:05:50 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 14.8 | 0 | 57018 | 63 | 57291 | 361 | 10020 | 140 | 67047 | 151 | 8.1112 | 854 | 1310 |  | 6.8979 | [35 empty] | RCB1, 100% charge CK1 and CK2, 90% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed to--match total static of run T2-RCB1-100C1-100C2-90A-95-CE-5-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.999 | 0.011 | 61.993 | 0.022 | 95.056 | 0.011 | 75.004 | 0.01 | 75.34 | 0.13 | 56.21 | 0.04 | 59.72 | 0.02 | 0.165 | 0.003 | 1.5188 | 0.0029 | 57018 | 63 | 10020 | 140 | 8.111 | 0.023 | [6 empty] | 460.2 | 2.1 | 461.1 | 2.1 | 459.9 | 2.1 | 14.8 | 0.1 | 12.7 | 0 | 12.7 | 0 | 6731.8 | 45.1 | 3192.7 | 52.3 | 1534.5 | 33.8 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.7 |  | 4.4 |  | 3160 |  | 0.83 | 460 | 460 | 460 | 5 | 4.7 | 4.2 | 2960 | 0.8 | 459.4 |  | 1.6 |  | 699.3 |  | 85 |  | 8214.3 | [14 empty] | 220.88 | 0.24 | 107.18 | 0.12 | 108.19 | 0.08 | 1.02 | 0.11 | 248.5 | 0.25 | 174.58 | 0.14 | 116.63 | 0.07 | 57.95 | 0.13 | 214 | 0.05 | 105.98 | 0.09 | 105.98 | 0.05 | 0 | 0.05 | 74.13 | 0.05 | 48.85 | 0.27 | 43.58 | 0.03 | 5.27 | 0.28 | 73.48 | 0.05 | 55.1 | 0.22 | 43.15 | 0.04 | 11.94 | 0.23 | [46 empty] | 250.15 | 0.24 | 171.87 | 0.25 | 117.11 | 0.07 | 54.76 | 0.26 | 231.96 | 0.33 | 111.66 | 0.1 | 10.28 | 0.13 | 221.8 | 0.05 | 96.5 | 0.06 | 108.48 | 0.05 | 11.98 | 0.05 | 77.03 | 0.08 | 45.46 | 0.05 | 2.35 | 0.44 | 76.75 | 0.09 | 56.18 | 0.65 | 45.29 | 0.06 | 10.9 | 0.69 | 101.64 | 0.1 | [28 empty] | 107.57 | 0.12 | 107.22 | 0.09 | 101.64 | 0.1 | 101.9 | 0.09 | 55.42 | 0.04 | 56.08 | 0.04 | 55.98 | 0.05 | 55.75 | 0.03 | 55.82 | 0.03 |  |  | 107.17 | 0.13 | 102.79 | 0.09 | 49.59 | 0.5 | 54.88 | 0.28 | 172.01 | 0.27 | 101.82 | 0.09 | 95.36 | 0.07 | 49.06 | 0.32 | 56.95 | 0.55 | 105.98 | 0.09 | 96.5 | 0.06 | 92.51 | 0.1 | 107.46 | 0.1 | 107.79 | 0.09 | 101.98 | 0.07 | 102.38 | 0.08 | 107.22 | 0.09 | 101.9 | 0.09 | [16 empty] | 107.18 | 0.12 | 101.37 | 0.11 | 107.57 | 0.12 | 101.64 | 0.1 | [16 empty] | 47.82 | 0.4 | [12 empty] | 175.41 | 0.17 | 94.19 | 0.19 | 95.91 | 0.1 | 75.5 | 0.06 | 77.24 | 0.06 | 75.29 | 0.07 | 77.31 | 0.07 | 75.77 | 0.06 | 75.91 | 0.07 | 75.83 | 0.07 | 79.85 | 0.12 | 77.9 | 0.06 | 77.59 | 0.05 | 76.15 | 0.08 | 77.44 | 0.07 | 77.33 | 0.07 | 77.39 | 0.06 | 77 | 0.07 | 75.93 | 0.07 | 76.47 | 0.07 | 75.54 | 0.07 | 75.29 | 0.07 | 75.29 | 0.07 | 75.3 | 0.07 | 75.62 | 0.06 | 75.35 | 0.07 | 75.3 | 0.05 | 80.34 | 0.06 | 79.27 | 0.09 |  |  | 76.5 | 0.07 | 75.32 | 0.06 | 75.66 | 0.07 | 75.81 | 0.07 | 76.73 |  | 75.23 | 0.07 | 80.26 | 0.08 | 80.35 | 0.09 | 77.5 | 0.07 | 75.8 | 0.07 | 75.31 | 0.07 | [12 empty] | 75.39 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.999 | 0.011 | 61.993 | 0.022 | 55.964 | 0.008 | 53.561 | 0.016 | 95.056 | 0.011 | 75.004 | 0.01 | 2708.3 | 2.6 | 2675.2 | 2.5 | 0.533 | 0.003 | -0.249 | 0.002 | 0.165 | 0.003 | 1.5188 | 0.0029 | 29.404 | 0 | 8266 | 18 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3057 | 12439.5577 | 167.513 | 0 | 0 | 12439.5577 | 0.0087762 | 27.6036 | 54.6583 | 14.1013 | 13.063 | 0.013911 | 38.16 | 0.0087762 | 27.6036 | 0.0081504 | 22.2815 | 74.999 | 61.993 | 21.9634 | 70161.9586 | 60727.0411 | 6956 | 0.33837 | 66262.6506 | 56827.7331 | 8.0163 | 0.14207 | -5.6402 | -20.3407 | 51.29 | 70161.9586 | 66205.0155 | 3956.9431 | 0 | 70161.9586 | 100%
2 | T2-MF45-100C1-100C2-90A-CB05-CCE | 75T0197 | T2-MF45-100C1-100C2-90A-CB05-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 5 | 0 | CUST 5 | 10/31/2014 | 20:54:46 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 15 | 0 | 57256 | 74 | 56841 | 515 | 9336 | 115 | 66601 | 148 | 7.9809 | 853 | 1310 |  | 6.8611 | [35 empty] | 5% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton), 4.5 turns,--5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester speed to--match total static of run T2-MF45-100C1-100C2-90A-CB05-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condesner Coil is blocked off 8`. | 74.972 | 0.019 | 61.997 | 0.025 | 95.011 | 0.014 | 75.006 | 0.018 | 75.16 | 0.18 | 56.37 | 0.03 | 59.97 | 0.03 | 0.163 | 0.003 | 1.5352 | 0.0024 | 57256 | 74 | 9336 | 115 | 7.981 | 0.024 | [6 empty] | 460 | 2.2 | 461.1 | 2.2 | 459.9 | 2.2 | 15 | 0 | 12.8 | 0 | 12.9 | 0 | 6786.7 | 44.2 | 3211.5 | 55.4 | 1558.2 | 34 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.9 |  | 4.4 |  | 3210 |  | 0.83 | 460 | 460 | 460 | 5 | 4.7 | 4.3 | 3030 | 0.81 | 459.1 |  | 1.6 |  | 697.8 |  | 85 |  | 8332.8 | [14 empty] | 223.95 | 0.13 | 108.26 | 0.1 | 109.21 | 0.04 | 0.95 | 0.09 | 251.88 | 0.17 | 175.28 | 0.14 | 117.65 | 0.05 | 57.62 | 0.16 | 218.7 | 0.05 | 106.94 | 0.05 | 107.54 | 0.05 | 0.6 | 0.05 | 74.59 | 0.06 | 48.53 | 0.3 | 43.97 | 0.04 | 4.57 | 0.31 | 73.96 | 0.06 | 55.72 | 0.26 | 43.55 | 0.04 | 12.17 | 0.27 | [46 empty] | 254 | 0.14 | 173.02 | 0.21 | 118.27 | 0.04 | 54.75 | 0.21 | 236.75 | 0.21 | 113.16 | 0.07 | 12.25 | 0.07 | 226.7 | 0.05 | 96.57 | 0.04 | 110.07 | 0.05 | 13.5 | 0.05 | 77.38 | 0.09 | 45.78 | 0.06 | 2.15 | 0.28 | 76.98 | 0.08 | 55.97 | 0.56 | 45.52 | 0.05 | 10.46 | 0.58 | 101.58 | 0.06 | [28 empty] | 108.44 | 0.1 | 108.29 | 0.05 | 101.58 | 0.06 | 102.17 | 0.06 | 55.62 | 0.05 | 56.21 | 0.05 | 56.04 | 0.05 | 55.87 | 0.03 | 55.97 | 0.03 |  |  | 108.13 | 0.11 | 102.95 | 0.08 | 49.95 | 0.55 | 55.83 | 0.3 | 173.38 | 0.23 | 101.46 | 0.06 | 95.4 | 0.03 | 49.08 | 0.19 | 57.57 | 0.45 | 106.94 | 0.05 | 96.57 | 0.04 | 93.26 | 0.18 | 107.78 | 0.08 | 108.8 | 0.06 | 101.78 | 0.04 | 102.18 | 0.04 | 108.29 | 0.05 | 102.17 | 0.06 | [16 empty] | 108.26 | 0.1 | 100.91 | 0.06 | 108.44 | 0.1 | 101.58 | 0.06 | [16 empty] | 47.94 | 0.24 | [12 empty] | 176.2 | 0.16 | 94.84 | 0.13 | 95.87 | 0.07 | 75.66 | 0.07 | 77.49 | 0.07 | 75.42 | 0.08 | 77.62 | 0.07 | 75.99 | 0.07 | 76.08 | 0.08 | 76 | 0.08 | 80.31 | 0.12 | 78.25 | 0.07 | 77.88 | 0.07 | 76.41 | 0.1 | 77.79 | 0.08 | 77.65 | 0.07 | 77.72 | 0.07 | 77.37 | 0.08 | 76.11 | 0.09 | 76.74 | 0.09 | 75.75 | 0.09 | 75.43 | 0.09 | 75.41 | 0.09 | 75.45 | 0.09 | 75.89 | 0.09 | 75.47 | 0.08 | 75.42 | 0.07 | 81.47 | 0.07 | 80.76 | 0.1 |  |  | 76.76 | 0.08 | 75.6 | 0.07 | 75.88 | 0.08 | 76.03 | 0.09 | 77.01 |  | 75.33 | 0.09 | 80.82 | 0.09 | 80.71 | 0.08 | 77.86 | 0.08 | 76.06 | 0.09 | 75.44 | 0.09 | [12 empty] | 75.54 | 0.09 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.972 | 0.019 | 61.997 | 0.025 | 56.039 | 0.011 | 53.662 | 0.021 | 95.011 | 0.014 | 75.006 | 0.018 | 2711 | 2.2 | 2701.5 | 2.2 | 0.536 | 0.002 | -0.248 | 0.002 | 0.163 | 0.003 | 1.5352 | 0.0024 | 29.675 | 0.001 | 8345 | 17 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3017 | 12449.8605 | 170.112 | 0 | 0 | 12449.8605 | 0.0087853 | 27.6069 | 54.7373 | 14.1002 | 13.0652 | 0.013923 | 38.1627 | 0.0087853 | 27.6069 | 0.0081893 | 22.3419 | 74.972 | 61.997 | 22.0248 | 69496.3249 | 60460.4682 | 7035 | 0.34549 | 65605.887 | 56570.0303 | 7.8617 | 0.14019 | -5.5821 | -20.2347 | 51.4383 | 69496.3249 | 65548.1036 | 3948.2213 | 0 | 69496.3249 | 100%
2 | T2-MF46-100C1-100C2-90A-CB10-CCE | 75T0198 | T2-MF46-100C1-100C2-90A-CB10-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 10 | 0 | CUST 5 | 10/31/2014 | 22:26:01 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.1 | 0 | 15.1 | 0 | 56928 | 70 | 56488 | 499 | 8970 | 218 | 65907 | 203 | 7.784 | 853 | 1310 |  | 6.7235 | [35 empty] | 10% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton), 4.5 turns,--5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester speed to--match total static of run T2-MF46-100C1-100C2-90A-CB10-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condesner Coil is blocked off 12" | 74.986 | 0.02 | 62.011 | 0.028 | 94.998 | 0.018 | 75.002 | 0.022 | 75.17 | 0.17 | 56.52 | 0.03 | 60.02 | 0.02 | 0.154 | 0.003 | 1.5391 | 0.0025 | 56928 | 70 | 8970 | 218 | 7.784 | 0.03 | [6 empty] | 460.1 | 2.1 | 461.4 | 2.2 | 459.9 | 2.1 | 15.1 | 0.1 | 12.9 | 0 | 13 | 0 | 6872.7 | 45.7 | 3203.1 | 53.7 | 1594.2 | 34.7 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.2 |  | 5 |  | 4.8 |  | 3270 |  | 0.84 | 460 | 460 | 460 | 5.1 | 4.8 | 4.4 | 3090 | 0.81 | 459.2 |  | 1.6 |  | 688.6 |  | 85 |  | 8443.6 | [14 empty] | 229.54 | 0.17 | 109.95 | 0.12 | 110.96 | 0.05 | 1.01 | 0.11 | 257.5 | 0.2 | 177.73 | 0.08 | 119.27 | 0.06 | 58.46 | 0.1 | 224.2 | 0.05 | 108.69 | 0.06 | 109.29 | 0.05 | 0.6 | 0.05 | 74.9 | 0.06 | 48.7 | 0.3 | 44.18 | 0.04 | 4.53 | 0.3 | 74.26 | 0.06 | 55.95 | 0.22 | 43.76 | 0.04 | 12.19 | 0.22 | [46 empty] | 260.09 | 0.2 | 175.77 | 0.15 | 120.01 | 0.06 | 55.76 | 0.14 | 242.93 | 0.27 | 115.02 | 0.08 | 13.07 | 0.08 | 233.8 | 0.05 | 97.51 | 0.03 | 112.77 | 0.05 | 15.26 | 0.05 | 77.55 | 0.06 | 45.88 | 0.04 | 2.09 | 0.19 | 77.15 | 0.05 | 55.91 | 0.37 | 45.63 | 0.03 | 10.28 | 0.37 | 102.71 | 0.06 | [28 empty] | 110.12 | 0.12 | 110.05 | 0.08 | 102.71 | 0.06 | 103.21 | 0.06 | 55.72 | 0.05 | 56.34 | 0.05 | 56.22 | 0.04 | 56.01 | 0.04 | 56.11 | 0.04 |  |  | 109.75 | 0.13 | 104.66 | 0.08 | 50.03 | 0.54 | 56.17 | 0.26 | 176.13 | 0.16 | 102.4 | 0.06 | 96.26 | 0.03 | 49.08 | 0.14 | 57.75 | 0.3 | 108.69 | 0.06 | 97.51 | 0.03 | 92.95 | 0.15 | 109.23 | 0.1 | 110.54 | 0.1 | 102.91 | 0.04 | 103.22 | 0.04 | 110.05 | 0.08 | 103.21 | 0.06 | [16 empty] | 109.95 | 0.12 | 101.95 | 0.07 | 110.12 | 0.12 | 102.71 | 0.06 | [16 empty] | 47.98 | 0.17 | [12 empty] | 178.62 | 0.11 | 95.32 | 0.14 | 96.18 | 0.08 | 75.62 | 0.07 | 77.49 | 0.07 | 75.42 | 0.08 | 77.55 | 0.08 | 75.93 | 0.07 | 76.04 | 0.09 | 75.95 | 0.09 | 80.2 | 0.1 | 78.22 | 0.07 | 77.88 | 0.07 | 76.36 | 0.09 | 77.74 | 0.08 | 77.65 | 0.08 | 77.7 | 0.07 | 77.32 | 0.08 | 76.13 | 0.09 | 76.74 | 0.09 | 75.72 | 0.09 | 75.39 | 0.09 | 75.38 | 0.09 | 75.43 | 0.09 | 75.88 | 0.09 | 75.43 | 0.08 | 75.41 | 0.07 | 81.42 | 0.09 | 80.69 | 0.1 |  |  | 76.74 | 0.09 | 75.56 | 0.08 | 75.84 | 0.09 | 76 | 0.09 | 76.99 |  | 75.33 | 0.09 | 80.78 | 0.09 | 80.68 | 0.08 | 77.82 | 0.09 | 76.01 | 0.09 | 75.4 | 0.09 | [12 empty] | 75.49 | 0.09 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.986 | 0.02 | 62.011 | 0.028 | 56.184 | 0.016 | 53.78 | 0.022 | 94.998 | 0.018 | 75.002 | 0.022 | 2713.6 | 2.3 | 2705.6 | 2.2 | 0.536 | 0.002 | -0.248 | 0.002 | 0.154 | 0.003 | 1.5391 | 0.0025 | 29.696 | 0.001 | 8467 | 18 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3005 | 12458.0607 | 170.3701 | 0 | 0 | 12458.0607 | 0.0087912 | 27.6168 | 54.8835 | 14.0999 | 13.0691 | 0.013923 | 38.1591 | 0.0087912 | 27.6168 | 0.0082212 | 22.412 | 74.986 | 62.011 | 22.0951 | 68789.4098 | 60105.167 | 7157 | 0.3551 | 64899.8531 | 56215.6103 | 7.665 | 0.1422 | -5.5217 | -20.1025 | 51.5511 | 68789.4098 | 64841.8527 | 3947.5571 | 0 | 68789.4098 | 100%
2 | T2-MF47-100C1-100C2-90A-CB20-CCE | 75T0199 | T2-MF47-100C1-100C2-90A-CB20-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 20 | 0 | CUST 5 | 11/3/2014 | 7:40:16 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 15.3 | 0 | 55289 | 76 | 54912 | 464 | 8315 | 133 | 63612 | 141 | 7.332 | 853 | 1300 |  | 6.3726 | [35 empty] | 20% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton), 4.5 turns,--5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester speed to--match total static of run T2-MF47-100C1-100C2-90A-CB20-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condesner Coil is blocked off 17 inches | 75.002 | 0.008 | 62.005 | 0.021 | 95.029 | 0.017 | 75.008 | 0.016 | 75.16 | 0.15 | 56.87 | 0.02 | 60.25 | 0.01 | 0.157 | 0.004 | 1.524 | 0.0028 | 55289 | 76 | 8315 | 133 | 7.332 | 0.021 | [6 empty] | 460.2 | 2 | 461.4 | 2 | 459.9 | 2 | 15.3 | 0 | 13.1 | 0 | 13.3 | 0 | 6969.6 | 41.9 | 3227.8 | 50.9 | 1706.6 | 32.6 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.3 |  | 5.1 |  | 4.7 |  | 3390 |  | 0.84 | 460 | 460 | 460 | 5.3 | 4.9 | 4.5 | 3230 | 0.82 | 459.3 |  | 1.5 |  | 648.2 |  | 85 |  | 8653.2 | [14 empty] | 237.56 | 0.29 | 113.35 | 0.1 | 113.38 | 0.09 | 0.03 | 0.05 | 267.61 | 0.33 | 184.04 | 0.07 | 122.1 | 0.09 | 61.94 | 0.09 | 229.4 | 0.06 | 110.54 | 0.09 | 110.88 | 0.03 | 0.34 | 0.05 | 75.18 | 0.05 | 49.9 | 0.19 | 44.3 | 0.03 | 5.6 | 0.19 | 74.53 | 0.05 | 57.62 | 0.13 | 43.88 | 0.03 | 13.75 | 0.14 | [46 empty] | 272.06 | 0.33 | 182.36 | 0.27 | 123.33 | 0.09 | 59.03 | 0.27 | 255.75 | 0.41 | 118.75 | 0.12 | 14.69 | 0.11 | 245.7 | 0.06 | 99.38 | 0.06 | 115.81 | 0.02 | 16.43 | 0.1 | 77.66 | 0.17 | 45.9 | 0.11 | 2.64 | 0.8 | 77.27 | 0.14 | 57.13 | 0.7 | 45.65 | 0.09 | 11.48 | 0.75 | 104.73 | 0.1 | [28 empty] | 112.38 | 0.1 | 112.1 | 0.09 | 104.73 | 0.1 | 105.32 | 0.1 | 56.14 | 0.05 | 56.75 | 0.04 | 56.57 | 0.05 | 56.47 | 0.05 | 56.54 | 0.04 |  |  | 112.57 | 0.1 | 106.5 | 0.1 | 51.4 | 0.37 | 57.84 | 0.14 | 182.72 | 0.31 | 104.45 | 0.1 | 98.15 | 0.05 | 49.77 | 0.6 | 59.13 | 0.61 | 110.54 | 0.09 | 99.38 | 0.06 | 93.43 | 0.11 | 111.77 | 0.08 | 112.54 | 0.1 | 105.01 | 0.06 | 105.32 | 0.06 | 112.1 | 0.09 | 105.32 | 0.1 | [16 empty] | 113.35 | 0.1 | 104.06 | 0.1 | 112.38 | 0.1 | 104.73 | 0.1 | [16 empty] | 48.55 | 0.72 | [12 empty] | 185.03 | 0.09 | 95.48 | 0.1 | 95.96 | 0.07 | 75.6 | 0.06 | 77.56 | 0.05 | 75.36 | 0.07 | 77.55 | 0.07 | 75.88 | 0.06 | 75.97 | 0.08 | 75.89 | 0.08 | 80 | 0.11 | 78.06 | 0.07 | 77.74 | 0.07 | 76.17 | 0.09 | 77.59 | 0.08 | 77.49 | 0.06 | 77.56 | 0.07 | 77.12 | 0.08 | 75.96 | 0.08 | 76.59 | 0.08 | 75.62 | 0.08 | 75.36 | 0.09 | 75.32 | 0.08 | 75.32 | 0.08 | 75.74 | 0.08 | 75.47 | 0.08 | 75.38 | 0.07 | 81.15 | 0.08 | 80.44 | 0.09 |  |  | 76.72 | 0.07 | 75.44 | 0.06 | 75.71 | 0.08 | 75.9 | 0.08 | 76.95 | 0.05 | 75.21 | 0.08 | 80.59 | 0.1 | 80.58 | 0.08 | 77.65 | 0.08 | 75.82 | 0.09 | 75.36 | 0.09 | [12 empty] | 75.48 | 0.09 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 75.002 | 0.008 | 62.005 | 0.021 | 56.584 | 0.018 | 54.044 | 0.019 | 95.029 | 0.017 | 75.008 | 0.016 | 2709.1 | 2.5 | 2683.3 | 2.5 | 0.532 | 0.003 | -0.245 | 0.002 | 0.157 | 0.004 | 1.524 | 0.0028 | 29.519 | 0.001 | 8676 | 19 | 1300 |  | 0 | 0 | 13.029 | 0.231 | 1.2953 | 12427.3637 | 167.705 | 0 | 0 | 12427.3637 | 0.0087834 | 27.6122 | 55.2887 | 14.1007 | 13.0797 | 0.013921 | 38.1643 | 0.0087834 | 27.6122 | 0.0082755 | 22.5683 | 75.002 | 62.005 | 22.2527 | 66604.6417 | 58796.315 | 7376 | 0.37797 | 62740.1188 | 54931.7921 | 7.2315 | 0.15269 | -5.3595 | -19.7133 | 51.7363 | 66604.6417 | 62682.1041 | 3922.5376 | 0 | 66604.6417 | 100%
2 | T2-MF48-100C1-100C2-90A-CB30-CCE | 75T0200 | T2-MF48-100C1-100C2-90A-CB30-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 30 | 0 | CUST 5 | 11/3/2014 | 11:04:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 15.5 | 0 | 54875 | 58 | 54533 | 421 | 8070 | 85 | 62953 | 104 | 7.0631 | 854 | 1310 |  | 6.1567 | [35 empty] | 30% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton),--4.5 turns, 5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester speed--to match total static of run T2-MF48-100C1-100C2-90A-CB30-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condenser Coil is blocked off 24 inches | 74.935 | 0.012 | 61.997 | 0.013 | 95.022 | 0.049 | 75.004 | 0.022 | 75.17 | 0.14 | 57 | 0.02 | 60.61 | 0.04 | 0.159 | 0.003 | 1.5221 | 0.0025 | 54875 | 58 | 8070 | 85 | 7.063 | 0.019 | [6 empty] | 460 | 2 | 461.1 | 2 | 460.1 | 2 | 15.5 | 0 | 13.4 | 0 | 13.5 | 0 | 7068.6 | 41.2 | 3269.2 | 49.1 | 1844.3 | 32.5 | 460 |  | 459 |  | 459 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 459 |  | 5.4 |  | 5.2 |  | 4.8 |  | 3500 |  | 0.85 | 460 | 459 | 459 | 5.4 | 5.1 | 4.6 | 3340 | 0.83 | 459.1 |  | 1.6 |  | 665.5 |  | 85 |  | 8900.5 | [14 empty] | 247.64 | 0.29 | 116.24 | 0.09 | 116.39 | 0.09 | 0.15 | 0.05 | 277.19 | 0.32 | 187.9 | 0.08 | 124.73 | 0.09 | 63.17 | 0.08 | 239.8 | 0.09 | 113.72 | 0.09 | 114.05 |  | 0.33 |  | 75.67 | 0.05 | 50.12 | 0.22 | 44.62 | 0.03 | 5.5 | 0.23 | 75.04 | 0.05 | 57.79 | 0.14 | 44.21 | 0.03 | 13.58 | 0.15 | [46 empty] | 281.52 | 0.36 | 186.7 | 0.29 | 125.9 | 0.1 | 60.8 | 0.3 | 265.57 | 0.47 | 121.54 | 0.13 | 16.58 | 0.17 | 256 |  | 100.51 | 0.08 | 118.81 |  | 18.3 |  | 77.76 | 0.17 | 45.96 | 0.11 | 2.68 | 0.91 | 77.36 | 0.15 | 58.27 | 0.8 | 45.71 | 0.09 | 12.56 | 0.86 | 106.01 | 0.13 | [28 empty] | 115.48 | 0.09 | 115.32 | 0.08 | 106.01 | 0.13 | 106.62 | 0.12 | 56.25 | 0.04 | 56.86 | 0.04 | 56.72 | 0.06 | 56.55 | 0.03 | 56.64 | 0.03 |  |  | 115.56 | 0.09 | 109.45 | 0.11 | 51.39 | 0.42 | 58.47 | 0.18 | 187.01 | 0.33 | 105.55 | 0.12 | 99.23 | 0.08 | 49.92 | 0.73 | 60.26 | 0.68 | 113.72 | 0.09 | 100.51 | 0.08 | 93.21 | 0.19 | 114.53 | 0.08 | 115.75 | 0.1 | 105.8 | 0.09 | 106.4 | 0.1 | 115.32 | 0.08 | 106.62 | 0.12 | [16 empty] | 116.24 | 0.09 | 104.96 | 0.14 | 115.48 | 0.09 | 106.01 | 0.13 | [16 empty] | 48.66 | 0.83 | [12 empty] | 188.86 | 0.1 | 94.4 | 0.16 | 94.53 | 0.09 | 75.58 | 0.05 | 77.48 | 0.05 | 75.37 | 0.07 | 77.51 | 0.07 | 75.87 | 0.05 | 75.96 | 0.07 | 75.88 | 0.07 | 79.82 | 0.11 | 77.92 | 0.06 | 77.61 | 0.06 | 76.21 | 0.07 | 77.54 | 0.07 | 77.4 | 0.07 | 77.46 | 0.06 | 77.07 | 0.07 | 75.94 | 0.08 | 76.54 | 0.08 | 75.62 | 0.08 | 75.4 | 0.08 | 75.36 | 0.08 | 75.33 | 0.08 | 75.7 | 0.08 | 75.52 | 0.07 | 75.39 | 0.06 | 80.67 | 0.08 | 80.04 | 0.12 |  |  | 76.69 | 0.06 | 75.43 | 0.05 | 75.69 | 0.07 | 75.86 | 0.08 | 76.89 |  | 75.21 | 0.08 | 80.37 | 0.08 | 80.35 | 0.08 | 77.62 | 0.07 | 75.84 | 0.08 | 75.41 | 0.08 | [12 empty] | 75.51 | 0.08 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.935 | 0.012 | 61.997 | 0.013 | 56.644 | 0.006 | 54.119 | 0.012 | 95.022 | 0.049 | 75.004 | 0.022 | 2708.6 | 2.3 | 2680.2 | 2.2 | 0.534 | 0.002 | -0.244 | 0.002 | 0.159 | 0.003 | 1.5221 | 0.0025 | 29.512 | 0.001 | 8913 | 19 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3067 | 12423.4177 | 168.141 | 0 | 0 | 12423.4177 | 0.008794 | 27.6074 | 55.3373 | 14.1005 | 13.0814 | 0.013919 | 38.1606 | 0.008794 | 27.6074 | 0.0083037 | 22.6136 | 74.935 | 61.997 | 22.2952 | 65996.2755 | 58432.8391 | 7603 | 0.39319 | 62099.1106 | 54535.6742 | 6.9673 | 0.15142 | -5.3122 | -19.5977 | 51.8404 | 65996.2755 | 62040.4025 | 3955.8729 | 0 | 65996.2755 | 100%
2 | T2-MF49-100C1-100C2-90A-CB40-CCE | 75T0201 | T2-MF49-100C1-100C2-90A-CB40-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 40 | 0 | CUST 5 | 11/3/2014 | 13:33:36 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 15.7 | 0 | 54641 | 53 | 54358 | 510 | 7631 | 154 | 62279 | 155 | 6.7658 | 854 | 1310 |  | 5.936 | [35 empty] | 40% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton),--4.5 turns, 5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester speed to--match total static of run T2-MF49-100C1-100C2-90A-CB40-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condesner Coil is blocked off 30 inches | 74.984 | 0.012 | 62.009 | 0.023 | 94.994 | 0.015 | 75 | 0.014 | 75.16 | 0.17 | 56.97 | 0.03 | 60.52 | 0.03 | 0.163 | 0.003 | 1.5166 | 0.0021 | 54641 | 53 | 7631 | 154 | 6.767 | 0.022 | [6 empty] | 459.7 | 2.1 | 460.8 | 2.1 | 460.4 | 2.1 | 15.7 | 0 | 13.7 | 0 | 13.9 | 0 | 7181.1 | 42.1 | 3327.9 | 51.7 | 2023.6 | 32.7 | 460 |  | 460 |  | 459 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 459 |  | 459 |  | 5.6 |  | 5.5 |  | 4.9 |  | 3650 |  | 0.86 | 460 | 459 | 459 | 5.5 | 5.3 | 4.8 | 3470 | 0.89 | 458.7 |  | 1.6 |  | 693.5 |  | 85 |  | 9208.5 | [14 empty] | 259.08 | 0.22 | 119.4 | 0.08 | 119.68 | 0.06 | 0.28 | 0.05 | 288.2 | 0.24 | 192.91 | 0.09 | 127.67 | 0.06 | 65.24 | 0.12 | 251.5 | 0.07 | 116.85 | 0.07 | 117.51 | 0.06 | 0.66 | 0.05 | 76.22 | 0.04 | 50.2 | 0.23 | 44.94 | 0.03 | 5.26 | 0.23 | 75.59 | 0.04 | 57.86 | 0.17 | 44.54 | 0.03 | 13.33 | 0.18 | [46 empty] | 292.83 | 0.27 | 191.45 | 0.27 | 128.88 | 0.07 | 62.56 | 0.29 | 277.04 | 0.4 | 124.68 | 0.11 | 17.27 | 0.12 | 266 | 0.05 | 102.59 | 0.06 | 121.65 | 0.05 | 19.06 | 0.06 | 78.15 | 0.16 | 46.18 | 0.1 | 2.5 | 0.73 | 77.76 | 0.14 | 58.71 | 0.83 | 45.93 | 0.09 | 12.77 | 0.88 | 108.39 | 0.1 | [28 empty] | 118.74 | 0.07 | 118.37 | 0.07 | 108.39 | 0.1 | 109.04 | 0.09 | 56.28 | 0.06 | 56.86 | 0.05 | 56.73 | 0.05 | 56.6 | 0.04 | 56.67 | 0.03 |  |  | 118.82 | 0.07 | 112.25 | 0.08 | 51.27 | 0.4 | 58.05 | 0.18 | 191.73 | 0.32 | 108.19 | 0.09 | 101.23 | 0.06 | 49.79 | 0.52 | 60.25 | 0.67 | 116.85 | 0.07 | 102.59 | 0.06 | 93.46 | 0.16 | 117.84 | 0.06 | 118.9 | 0.07 | 109.06 | 0.07 | 109.71 | 0.08 | 118.37 | 0.07 | 109.04 | 0.09 | [16 empty] | 119.4 | 0.08 | 107.41 | 0.1 | 118.74 | 0.07 | 108.39 | 0.1 | [16 empty] | 48.68 | 0.64 | [12 empty] | 193.76 | 0.1 | 95 | 0.15 | 95.36 | 0.08 | 75.6 | 0.07 | 77.53 | 0.06 | 75.38 | 0.07 | 77.52 | 0.07 | 75.85 | 0.06 | 75.94 | 0.08 | 75.86 | 0.07 | 79.93 | 0.11 | 77.99 | 0.07 | 77.7 | 0.07 | 76.11 | 0.08 | 77.5 | 0.07 | 77.41 | 0.07 | 77.49 | 0.06 | 77.02 | 0.07 | 75.92 | 0.07 | 76.54 | 0.08 | 75.6 | 0.08 | 75.35 | 0.09 | 75.33 | 0.08 | 75.32 | 0.08 | 75.71 | 0.09 | 75.45 | 0.08 | 75.36 | 0.07 | 80.85 | 0.07 | 80.21 | 0.09 |  |  | 76.71 | 0.07 | 75.4 | 0.06 | 75.67 | 0.08 | 75.86 | 0.08 | 76.93 |  | 75.23 | 0.08 | 80.48 | 0.1 | 80.48 | 0.1 | 77.55 | 0.07 | 75.75 | 0.08 | 75.36 | 0.08 | [12 empty] | 75.45 | 0.08 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.984 | 0.012 | 62.009 | 0.023 | 56.703 | 0.008 | 54.212 | 0.012 | 94.994 | 0.015 | 75 | 0.014 | 2707.7 | 1.9 | 2671.2 | 1.9 | 0.532 | 0.002 | -0.244 | 0.002 | 0.163 | 0.003 | 1.5166 | 0.0021 | 29.42 | 0.001 | 9205 | 20 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3087 | 12417.5849 | 166.9487 | 0 | 0 | 12417.5849 | 0.0087903 | 27.6154 | 55.3943 | 14.0998 | 13.0832 | 0.013922 | 38.1572 | 0.0087903 | 27.6154 | 0.0083424 | 22.67 | 74.984 | 62.009 | 22.3511 | 65369.6407 | 58381.4995 | 7895 | 0.4122 | 61468.4068 | 54480.2656 | 6.6777 | 0.14783 | -5.2643 | -19.5897 | 51.9962 | 65369.6407 | 61409.3581 | 3960.2826 | 0 | 65369.6407 | 100%
2 | T2-MF50-100C1-100C2-90A-CB50-CCE | 75T0202 | T2-MF50-100C1-100C2-90A-CB50-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 50 | 0 | CUST 5 | 11/3/2014 | 17:32:59 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.6 | 0 | 16.1 | 0 | 54569 | 98 | 54167 | 441 | 7436 | 112 | 62012 | 146 | 6.5607 | 854 | 1310 |  | 5.7733 | [35 empty] | 50% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton),--4.5 turns, 5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester speed--to match total static of run T2-MF50-100C1-100C2-90A-CB50-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condenser Coil is blocked off 36.5 inches | 74.993 | 0.014 | 62.008 | 0.023 | 94.908 | 0.115 | 75.007 | 0.027 | 75.07 | 0.16 | 56.9 | 0.08 | 60.48 | 0.02 | 0.148 | 0.004 | 1.5076 | 0.0038 | 54569 | 98 | 7436 | 112 | 6.561 | 0.028 | [6 empty] | 459.6 | 2.1 | 460.8 | 2.1 | 460.5 | 2.1 | 16.1 | 0.1 | 14 | 0.1 | 14.2 | 0 | 7336.4 | 45.9 | 3328.1 | 51.1 | 2115.7 | 36.7 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.7 |  | 5.6 |  | 5 |  | 3710 |  | 0.86 | 460 | 460 | 460 | 5.6 | 5.4 | 4.9 | 3570 | 0.85 | 458.6 |  | 1.7 |  | 740.7 |  | 85 |  | 9415.7 | [14 empty] | 266.88 | 1.19 | 121.4 | 0.33 | 121.89 | 0.33 | 0.49 | 0.09 | 296.31 | 1.2 | 195.55 | 0.28 | 129.79 | 0.31 | 65.76 | 0.29 | 258 | 0.05 | 119 | 0.33 | 119.37 | 0.05 | 0.37 | 0.05 | 76.49 | 0.08 | 50.31 | 0.34 | 45.12 | 0.05 | 5.19 | 0.36 | 75.86 | 0.08 | 57.6 | 0.31 | 44.71 | 0.05 | 12.88 | 0.34 | [46 empty] | 301.57 | 1.3 | 194.76 | 0.44 | 131.15 | 0.33 | 63.62 | 0.35 | 285.86 | 1.41 | 127.04 | 0.37 | 19.01 | 0.28 | 272.5 | 0.05 | 103.55 | 0.14 | 123.44 | 0.05 | 19.89 | 0.05 | 78.24 | 0.19 | 46.23 | 0.12 | 2.37 | 0.71 | 77.83 | 0.16 | 58.48 | 1.03 | 45.98 | 0.1 | 12.5 | 1.09 | 109.45 | 0.21 | [28 empty] | 120.79 | 0.35 | 120.54 | 0.33 | 109.45 | 0.21 | 110.11 | 0.21 | 56.24 | 0.09 | 56.83 | 0.07 | 56.71 | 0.07 | 56.53 | 0.05 | 56.6 | 0.04 |  |  | 120.67 | 0.32 | 114.15 | 0.32 | 51.36 | 0.66 | 57.65 | 0.35 | 194.96 | 0.48 | 108.81 | 0.19 | 102.18 | 0.13 | 49.74 | 0.48 | 60.21 | 0.84 | 119 | 0.33 | 103.55 | 0.14 | 91.89 | 0.17 | 119 | 0.27 | 121.07 | 0.34 | 108.59 | 0.14 | 109.02 | 0.16 | 120.54 | 0.33 | 110.11 | 0.21 | [16 empty] | 121.4 | 0.33 | 108.03 | 0.2 | 120.79 | 0.35 | 109.45 | 0.21 | [16 empty] | 48.58 | 0.61 | [12 empty] | 196.56 | 0.32 | 94.49 | 0.3 | 94.82 | 0.11 | 75.55 | 0.06 | 77.28 | 0.06 | 75.31 | 0.06 | 77.32 | 0.06 | 75.81 | 0.06 | 75.9 | 0.07 | 75.82 | 0.07 | 79.62 | 0.1 | 77.82 | 0.06 | 77.5 | 0.05 | 76.06 | 0.08 | 77.31 | 0.07 | 77.22 | 0.06 | 77.29 | 0.05 | 76.88 | 0.06 | 75.84 | 0.07 | 76.4 | 0.07 | 75.5 | 0.07 | 75.25 | 0.08 | 75.24 | 0.07 | 75.24 | 0.07 | 75.64 | 0.07 | 75.37 | 0.07 | 75.29 | 0.05 | 80.65 | 0.07 | 80.1 | 0.1 |  |  | 76.51 | 0.07 | 75.41 | 0.06 | 75.66 | 0.07 | 75.82 | 0.07 | 76.76 |  | 75.19 | 0.07 | 80.08 | 0.08 | 80.08 | 0.07 | 77.36 | 0.07 | 75.7 | 0.07 | 75.27 | 0.07 | [12 empty] | 75.37 | 0.07 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.993 | 0.014 | 62.008 | 0.023 | 56.681 | 0.019 | 54.22 | 0.021 | 94.908 | 0.115 | 75.007 | 0.027 | 2699.3 | 3.4 | 2663.5 | 3.4 | 0.533 | 0.003 | -0.242 | 0.002 | 0.148 | 0.004 | 1.5076 | 0.0038 | 29.426 | 0.001 | 9452 | 38 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3129 | 12379.5181 | 166.7804 | 0 | 0 | 12379.5181 | 0.0087876 | 27.6145 | 55.3681 | 14.0978 | 13.0827 | 0.013949 | 38.1655 | 0.0087876 | 27.6145 | 0.0083521 | 22.6752 | 74.993 | 62.008 | 22.3553 | 65107.0435 | 58307.1616 | 8142 | 0.42681 | 61205.235 | 54405.3531 | 6.4754 | 0.14501 | -5.2593 | -19.6249 | 52.0397 | 65107.0435 | 61146.1075 | 3960.936 | 0 | 65107.0435 | 100%
2 | T2-MF51-100C1-100C2-90A-CB60-CCE | 75T0203 | T2-MF51-100C1-100C2-90A-CB60-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 60 | 0 | CUST 5 | 11/3/2014 | 19:05:59 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 16.4 | 0 | 54029 | 90 | 53601 | 423 | 6893 | 106 | 60929 | 143 | 6.2665 | 854 | 1310 |  | 5.5568 | [35 empty] | 60% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton),--4.5 turns, 5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester speed--to match total static of run T2-MF51-100C1-100C2-90A-CB60-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condenser Coil is blocked off 39.5 inches | 74.966 | 0.008 | 62.01 | 0.015 | 94.975 | 0.07 | 75.002 | 0.025 | 74.98 | 0.15 | 57.01 | 0.08 | 60.57 | 0.01 | 0.152 | 0.004 | 1.512 | 0.0043 | 54029 | 90 | 6893 | 106 | 6.266 | 0.023 | [6 empty] | 459.7 | 2 | 460.8 | 2 | 460.5 | 2 | 16.4 | 0 | 14.3 | 0 | 14.4 | 0 | 7481.4 | 41.6 | 3351.9 | 48.8 | 2241.9 | 33 | 460 |  | 460 |  | 460 |  | 2.8 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.9 |  | 5.8 |  | 5.2 |  | 3880 |  | 0.87 | 460 | 460 | 460 | 5.8 | 5.5 | 5.1 | 3700 | 0.86 | 458.6 |  | 1.7 |  | 749.2 |  | 85 |  | 9724.2 | [14 empty] | 277.63 | 0.52 | 124.2 | 0.17 | 124.84 | 0.14 | 0.65 | 0.1 | 306.78 | 0.57 | 200.1 | 0.13 | 132.47 | 0.14 | 67.63 | 0.16 | 270.6 | 0.05 | 121.9 | 0.15 | 122.91 | 0.05 | 1.01 | 0.05 | 76.96 | 0.05 | 50.36 | 0.23 | 45.42 | 0.03 | 4.94 | 0.25 | 76.33 | 0.05 | 57.78 | 0.21 | 45.02 | 0.03 | 12.77 | 0.22 | [46 empty] | 312.74 | 0.61 | 199.87 | 0.26 | 133.97 | 0.15 | 65.9 | 0.26 | 297.22 | 0.73 | 130.03 | 0.19 | 19.52 | 0.19 | 286.9 | 0.05 | 105.76 | 0.09 | 127.32 | 0.05 | 21.56 | 0.05 | 78.57 | 0.16 | 46.45 | 0.1 | 2.22 | 0.66 | 78.18 | 0.13 | 59.18 | 0.76 | 46.2 | 0.08 | 12.98 | 0.81 | 111.85 | 0.16 | [28 empty] | 123.71 | 0.17 | 123.46 | 0.16 | 111.85 | 0.16 | 112.52 | 0.17 | 56.39 | 0.09 | 57 | 0.07 | 56.88 | 0.06 | 56.68 | 0.04 | 56.74 | 0.03 |  |  | 123.64 | 0.14 | 116.83 | 0.16 | 51.3 | 0.54 | 57.9 | 0.27 | 200.04 | 0.32 | 111.38 | 0.13 | 104.37 | 0.07 | 49.93 | 0.48 | 60.97 | 0.61 | 121.9 | 0.15 | 105.76 | 0.09 | 92.04 | 0.18 | 121.95 | 0.12 | 124.05 | 0.15 | 111.67 | 0.09 | 112.08 | 0.1 | 123.46 | 0.16 | 112.52 | 0.17 | [16 empty] | 124.2 | 0.17 | 110.51 | 0.17 | 123.71 | 0.17 | 111.85 | 0.16 | [16 empty] | 48.65 | 0.58 | [12 empty] | 201.06 | 0.16 | 94.67 | 0.29 | 94.72 | 0.09 | 75.53 | 0.06 | 77.25 | 0.06 | 75.3 | 0.06 | 77.33 | 0.07 | 75.79 | 0.06 | 75.85 | 0.07 | 75.76 | 0.07 | 79.61 | 0.11 | 77.81 | 0.06 | 77.5 | 0.06 | 76.04 | 0.09 | 77.3 | 0.08 | 77.17 | 0.07 | 77.27 | 0.06 | 76.86 | 0.08 | 75.79 | 0.07 | 76.35 | 0.07 | 75.5 | 0.08 | 75.26 | 0.09 | 75.24 | 0.09 | 75.24 | 0.08 | 75.61 | 0.08 | 75.37 | 0.09 | 75.29 | 0.07 | 80.52 | 0.06 | 79.88 | 0.08 |  |  | 76.51 | 0.07 | 75.39 | 0.06 | 75.66 | 0.08 | 75.83 | 0.08 | 76.79 |  | 75.19 | 0.08 | 80.1 | 0.08 | 80.1 | 0.08 | 77.35 | 0.08 | 75.68 | 0.09 | 75.27 | 0.09 | [12 empty] | 75.38 | 0.09 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.966 | 0.008 | 62.01 | 0.015 | 56.853 | 0.012 | 54.379 | 0.015 | 94.975 | 0.07 | 75.002 | 0.025 | 2703.3 | 3.9 | 2667.1 | 3.8 | 0.532 | 0.002 | -0.242 | 0.002 | 0.152 | 0.004 | 1.512 | 0.0043 | 29.43 | 0 | 9723 | 25 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3115 | 12393.3688 | 166.6925 | 0 | 0 | 12393.3688 | 0.0087953 | 27.6164 | 55.5415 | 14.0993 | 13.0875 | 0.013929 | 38.1595 | 0.0087953 | 27.6164 | 0.0084017 | 22.771 | 74.966 | 62.01 | 22.4514 | 64011.5943 | 57776.4265 | 8413 | 0.44857 | 60109.4857 | 53874.318 | 6.1822 | 0.14608 | -5.165 | -19.4245 | 52.2187 | 64011.5943 | 60049.9957 | 3961.5986 | 0 | 64011.5943 | 100%
2 | T2-MF52-100C1-100C2-90A-CB70-CCE | 75T0204 | T2-MF52-100C1-100C2-90A-CB70-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 70 | 0 | CUST 5 | 11/3/2014 | 20:33:07 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 16.8 | 0 | 53614 | 53 | 53201 | 430 | 6121 | 155 | 59741 | 143 | 5.9586 | 1310 | 854 |  | 5.3475 | [35 empty] | 70% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton),--4.5 turns, 5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester--speed to match total static of run T2-MF52-100C1-100C2-90A-CB70-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condenser Coil is blocked off 39.5 inches on face 1 and 4 insches on face 2. | 74.937 | 0.021 | 61.988 | 0.024 | 94.969 | 0.042 | 75 | 0.017 | 75.15 | 0.14 | 57.35 | 0.03 | 60.77 | 0.04 | 0.156 | 0.003 | 1.5192 | 0.002 | 53614 | 53 | 6121 | 155 | 5.959 | 0.022 | [6 empty] | 459.7 | 2.1 | 460.8 | 2.1 | 460.3 | 2.1 | 16.8 | 0 | 14.7 | 0 | 14.7 | 0 | 7667.4 | 41.6 | 3355.3 | 48.3 | 2358.3 | 32.6 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 6 |  | 5.9 |  | 5.4 |  | 4020 |  | 0.87 | 460 | 460 | 460 | 5.9 | 5.7 | 5.2 | 3850 | 0.86 | 458.5 |  | 1.8 |  | 764.7 |  | 85 |  | 10029.7 | [14 empty] | 289.59 | 0.47 | 127.45 | 0.11 | 128.04 | 0.12 | 0.59 | 0.05 | 318.48 | 0.48 | 205.12 | 0.17 | 135.39 | 0.12 | 69.73 | 0.16 | 281 | 0.05 | 125.1 | 0.12 | 125.75 | 0.05 | 0.65 | 0.05 | 77.38 | 0.05 | 50.5 | 0.2 | 45.69 | 0.03 | 4.8 | 0.2 | 76.76 | 0.05 | 58.05 | 0.22 | 45.29 | 0.03 | 12.76 | 0.22 | [46 empty] | 325.05 | 0.6 | 205.01 | 0.28 | 137 | 0.15 | 68.02 | 0.26 | 309.68 | 0.71 | 133.21 | 0.18 | 20.16 | 0.13 | 298 | 0.05 | 108.1 | 0.12 | 130.23 | 0.05 | 22.13 | 0.05 | 78.9 | 0.13 | 46.66 | 0.08 | 2.08 | 0.33 | 78.5 | 0.12 | 59.53 | 0.7 | 46.41 | 0.08 | 13.13 | 0.74 | 114.47 | 0.2 | [28 empty] | 126.99 | 0.12 | 126.69 | 0.12 | 114.47 | 0.2 | 115.17 | 0.17 | 56.72 | 0.05 | 57.22 | 0.05 | 57.05 | 0.05 | 56.96 | 0.03 | 57.01 | 0.03 |  |  | 126.71 | 0.11 | 119.73 | 0.14 | 51.58 | 0.43 | 58.21 | 0.24 | 205.24 | 0.3 | 113.88 | 0.18 | 106.55 | 0.11 | 49.91 | 0.19 | 61.29 | 0.54 | 125.1 | 0.12 | 108.1 | 0.12 | 91.79 | 0.22 | 124.7 | 0.09 | 127.25 | 0.13 | 113.76 | 0.12 | 114.08 | 0.13 | 126.69 | 0.12 | 115.17 | 0.17 | [16 empty] | 127.45 | 0.11 | 113.04 | 0.17 | 126.99 | 0.12 | 114.47 | 0.2 | [16 empty] | 48.73 | 0.27 | [12 empty] | 206.15 | 0.19 | 94.18 | 0.43 | 94.18 | 0.11 | 75.54 | 0.07 | 77.3 | 0.06 | 75.34 | 0.07 | 77.34 | 0.07 | 75.83 | 0.06 | 75.92 | 0.08 | 75.83 | 0.07 | 79.52 | 0.11 | 77.76 | 0.06 | 77.44 | 0.06 | 76.01 | 0.08 | 77.27 | 0.07 | 77.18 | 0.07 | 77.25 | 0.06 | 76.84 | 0.07 | 75.81 | 0.08 | 76.36 | 0.07 | 75.51 | 0.08 | 75.29 | 0.08 | 75.27 | 0.08 | 75.25 | 0.08 | 75.63 | 0.08 | 75.4 | 0.07 | 75.29 | 0.06 | 80.28 | 0.07 | 79.71 | 0.1 |  |  | 76.55 | 0.08 | 75.44 | 0.07 | 75.68 | 0.08 | 75.83 | 0.08 | 76.79 |  | 75.2 | 0.08 | 80.08 | 0.08 | 80.05 | 0.08 | 77.34 | 0.07 | 75.68 | 0.08 | 75.31 | 0.08 | [12 empty] | 75.41 | 0.08 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.937 | 0.021 | 61.988 | 0.024 | 56.999 | 0.013 | 54.53 | 0.02 | 94.969 | 0.042 | 75 | 0.017 | 2710.3 | 1.9 | 2672.9 | 1.8 | 0.53 | 0.003 | -0.243 | 0.002 | 0.156 | 0.003 | 1.5192 | 0.002 | 29.432 | 0.001 | 10026 | 23 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3088 | 12421.5692 | 166.427 | 0 | 0 | 12421.5692 | 0.0087876 | 27.6009 | 55.6902 | 14.0992 | 13.0916 | 0.013928 | 38.1577 | 0.0087876 | 27.6009 | 0.0084532 | 22.8625 | 74.937 | 61.988 | 22.5435 | 62821.1422 | 57378.2172 | 8716 | 0.47353 | 58918.1274 | 53475.2024 | 5.8765 | 0.14543 | -5.0574 | -19.2468 | 52.4148 | 62821.1422 | 58858.252 | 3962.8902 | 0 | 62821.1422 | 100%
2 | T2-MF53-100C1-100C2-90A-CB80-CCE | 75T0205 | T2-MF53-100C1-100C2-90A-CB80-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 80 | 0 | CUST 5 | 11/3/2014 | 21:37:41 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 17 | 0 | 53134 | 129 | 52649 | 434 | 5625 | 125 | 58765 | 108 | 5.727 | 854 | 1310 |  | 5.1782 | [35 empty] | 80% condenser coil blockage, factory charge, 2 HP fan motor, 90% airflow (350 cfm/ton),--4.5 turns, 5.75" AK59 pulley (866 rpm), Econo Closed damper, adjust code tester--speed to match total static of run T2-MF53-100C1-100C2-90A-CB80-CCE-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: Condenser Coil is blocked off 39.5 inches on face 1 and 5 inches on face 2. | 74.919 | 0.025 | 61.965 | 0.023 | 95.028 | 0.019 | 74.982 | 0.016 | 74.99 | 0.15 | 57.36 | 0.08 | 61.25 | 0.08 | 0.156 | 0.004 | 1.5176 | 0.0025 | 53134 | 129 | 5625 | 125 | 5.727 | 0.017 | [6 empty] | 459.7 | 2.1 | 460.8 | 2.1 | 460.3 | 2.1 | 17 | 0 | 14.9 | 0 | 15 | 0 | 7801.7 | 39.9 | 3370.2 | 49.3 | 2459.1 | 32.9 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 6.1 |  | 6 |  | 5.5 |  | 4140 |  | 0.88 | 460 | 460 | 460 | 6.1 | 5.8 | 5.4 | 3950 | 0.86 | 458.6 |  | 1.8 |  | 772.7 |  | 85 |  | 10257.7 | [14 empty] | 298.37 | 0.47 | 129.53 | 0.14 | 130.33 | 0.12 | 0.79 | 0.09 | 327.06 | 0.49 | 208.58 | 0.14 | 137.48 | 0.12 | 71.1 | 0.13 | 290.2 | 0.05 | 127.38 | 0.12 | 128.19 | 0.05 | 0.81 | 0.05 | 77.68 | 0.06 | 50.58 | 0.16 | 45.88 | 0.04 | 4.7 | 0.17 | 77.07 | 0.06 | 58.05 | 0.17 | 45.49 | 0.04 | 12.56 | 0.18 | [46 empty] | 334.3 | 0.56 | 208.88 | 0.27 | 139.22 | 0.13 | 69.67 | 0.26 | 319.09 | 0.65 | 135.54 | 0.16 | 21 | 0.14 | 306.8 | 0.05 | 109.68 | 0.09 | 132.47 | 0.05 | 22.79 | 0.05 | 79.09 | 0.14 | 46.78 | 0.09 | 1.97 | 0.4 | 78.69 | 0.13 | 59.57 | 0.74 | 46.53 | 0.08 | 13.05 | 0.78 | 116.13 | 0.16 | [28 empty] | 129.13 | 0.13 | 128.85 | 0.13 | 116.13 | 0.16 | 116.8 | 0.16 | 56.76 | 0.08 | 57.3 | 0.06 | 57.18 | 0.06 | 57.06 | 0.04 | 57.1 | 0.03 |  |  | 128.88 | 0.12 | 121.77 | 0.15 | 51.48 | 0.43 | 58.21 | 0.2 | 209.06 | 0.3 | 115.49 | 0.15 | 108.19 | 0.08 | 50.07 | 0.23 | 61.34 | 0.58 | 127.38 | 0.12 | 109.68 | 0.09 | 91.81 | 0.19 | 126.47 | 0.08 | 129.58 | 0.12 | 114.85 | 0.09 | 115.27 | 0.1 | 128.85 | 0.13 | 116.8 | 0.16 | [16 empty] | 129.53 | 0.14 | 114.55 | 0.15 | 129.13 | 0.13 | 116.13 | 0.16 | [16 empty] | 48.75 | 0.33 | [12 empty] | 209.7 | 0.15 | 94.78 | 0.36 | 94.04 | 0.11 | 75.49 | 0.07 | 77.27 | 0.06 | 75.25 | 0.07 | 77.3 | 0.07 | 75.78 | 0.07 | 75.87 | 0.08 | 75.78 | 0.08 | 79.43 | 0.09 | 77.7 | 0.07 | 77.43 | 0.06 | 75.96 | 0.08 | 77.21 | 0.08 | 77.11 | 0.08 | 77.18 | 0.06 | 76.77 | 0.08 | 75.75 | 0.08 | 76.3 | 0.08 | 75.44 | 0.08 | 75.24 | 0.08 | 75.22 | 0.08 | 75.18 | 0.07 | 75.55 | 0.09 | 75.35 | 0.07 | 75.22 | 0.05 | 80.2 | 0.06 | 79.92 | 0.08 |  |  | 76.47 | 0.07 | 75.42 | 0.06 | 75.65 | 0.07 | 75.81 | 0.08 | 76.74 |  | 75.18 | 0.08 | 80.05 | 0.09 | 80.02 | 0.08 | 77.27 | 0.08 | 75.61 | 0.08 | 75.25 | 0.08 | [12 empty] | 75.36 | 0.08 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 74.919 | 0.025 | 61.965 | 0.023 | 57.126 | 0.019 | 54.632 | 0.024 | 95.028 | 0.019 | 74.982 | 0.016 | 2710.6 | 2.2 | 2669.6 | 2.3 | 0.53 | 0.002 | -0.244 | 0.002 | 0.156 | 0.004 | 1.5176 | 0.0025 | 29.42 | 0.001 | 10261 | 25 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.3093 | 12419.683 | 166.2215 | 0 | 0 | 12419.683 | 0.0087767 | 27.5846 | 55.8167 | 14.1004 | 13.095 | 0.013898 | 38.1392 | 0.0087767 | 27.5846 | 0.0084814 | 22.9241 | 74.919 | 61.965 | 22.605 | 61845.3796 | 56938.5929 | 8951 | 0.49397 | 57941.6636 | 53034.8768 | 5.6468 | 0.14708 | -4.9796 | -19.1023 | 52.5227 | 61845.3796 | 57881.5738 | 3963.8058 | 0 | 61845.3796 | 100%
2 | T2-MFB3-100C1-100C2-90A-95-CE-2 | 75T0206 | T2-MFB3-100C1-100C2-90A-95-CE-2 | closed | on | on | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/31/2014 | 15:53:25 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.8 | 0 | 14.8 | 0 | 57429 | 60 | 57166 | 531 | 9595 | 174 | 67034 | 186 | 8.1283 | 853 | 1310 |  | 6.9636 | [35 empty] | Econo closed (2.0V), factory charge NC baseline, 90% airflow (350 cfm/ton), 4.5 turns,--5.75" AK59 pulley (866 rpm), unsealed cab, adjust code tester speed to match total--match total static of run T2-MFB3-100C1-100C2-90A-95-CE-2-SPWCT-SS | W/ECO: 2.0 V With comps: 95/75 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75 | 0.009 | 62.001 | 0.031 | 94.996 | 0.012 | 75 | 0.017 | 75.24 | 0.17 | 56.37 | 0.03 | 59.97 | 0.03 | 0.191 | 0.004 | 1.5435 | 0.0025 | 57429 | 60 | 9595 | 174 | 8.128 | 0.028 | [6 empty] | 459.8 | 2.1 | 460.6 | 2.1 | 460.1 | 2.1 | 14.8 | 0 | 12.7 | 0 | 12.8 | 0 | 6690.2 | 43.4 | 3244.3 | 50.9 | 1556.7 | 33.7 | 460 |  | 460 |  | 459 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 459 |  | 460 |  | 5 |  | 4.9 |  | 4.4 |  | 3150 |  | 0.83 | 460 | 459 | 460 | 4.9 | 4.7 | 4.3 | 2990 | 0.81 | 458.9 |  | 1.6 |  | 701.5 |  | 85 |  | 8236.5 | [14 empty] | 219.55 | 0.17 | 107.05 | 0.1 | 107.8 | 0.05 | 0.75 | 0.09 | 247.37 | 0.17 | 173.78 | 0.09 | 116.32 | 0.05 | 57.46 | 0.09 | 214 | 0.05 | 105.51 | 0.06 | 106.01 | 0.06 | 0.5 | 0.06 | 74.47 | 0.05 | 48.38 | 0.23 | 43.87 | 0.03 | 4.51 | 0.23 | 73.83 | 0.05 | 55.31 | 0.16 | 43.45 | 0.03 | 11.85 | 0.15 | [46 empty] | 249.21 | 0.17 | 171.17 | 0.15 | 116.86 | 0.05 | 54.3 | 0.16 | 231.77 | 0.24 | 111.63 | 0.07 | 11.21 | 0.09 | 222 | 0.05 | 95.94 | 0.05 | 108.58 | 0.05 | 12.64 | 0.05 | 77.34 | 0.08 | 45.73 | 0.05 | 2.28 | 0.23 | 76.93 | 0.07 | 56.12 | 0.42 | 45.47 | 0.04 | 10.65 | 0.44 | 100.89 | 0.07 | [28 empty] | 107.2 | 0.09 | 106.75 | 0.06 | 100.89 | 0.07 | 101.29 | 0.08 | 55.59 | 0.05 | 56.19 | 0.05 | 56 | 0.05 | 55.82 | 0.04 | 55.91 | 0.04 |  |  | 106.87 | 0.11 | 101.58 | 0.09 | 49.82 | 0.46 | 55.07 | 0.2 | 171.52 | 0.17 | 101.16 | 0.07 | 94.74 | 0.04 | 49.1 | 0.17 | 56.74 | 0.35 | 105.51 | 0.06 | 95.94 | 0.05 | 93.5 | 0.15 | 107.06 | 0.11 | 107.34 | 0.07 | 101.32 | 0.06 | 101.79 | 0.06 | 106.75 | 0.06 | 101.29 | 0.08 | [16 empty] | 107.05 | 0.1 | 100.43 | 0.11 | 107.2 | 0.09 | 100.89 | 0.07 | [16 empty] | 48.01 | 0.2 | [12 empty] | 174.62 | 0.11 | 94.84 | 0.11 | 95.55 | 0.08 | 75.69 | 0.06 | 77.56 | 0.07 | 75.47 | 0.07 | 77.66 | 0.06 | 76 | 0.06 | 76.09 | 0.08 | 76.01 | 0.08 | 80.35 | 0.13 | 78.25 | 0.06 | 77.9 | 0.07 | 76.37 | 0.09 | 77.79 | 0.08 | 77.64 | 0.08 | 77.71 | 0.07 | 77.34 | 0.07 | 76.11 | 0.08 | 76.71 | 0.08 | 75.72 | 0.08 | 75.4 | 0.09 | 75.39 | 0.08 | 75.43 | 0.08 | 75.85 | 0.08 | 75.44 | 0.08 | 75.4 | 0.06 | 81.36 | 0.07 | 80.62 | 0.1 |  |  | 76.82 | 0.08 | 75.6 | 0.06 | 75.88 | 0.08 | 76.05 | 0.08 | 77.06 |  | 75.35 | 0.08 | 80.91 | 0.1 | 80.77 | 0.08 | 77.87 | 0.08 | 76.01 | 0.09 | 75.41 | 0.08 | [12 empty] | 75.49 | 0.08 | [48 empty] | T2-TRN-88A-55-CE-DM-2 | 75 | 0.009 | 62.001 | 0.031 | 56.045 | 0.012 | 53.635 | 0.021 | 94.996 | 0.012 | 75 | 0.017 | 2720.6 | 2.2 | 2706.6 | 2.2 | 0.533 | 0.002 | -0.249 | 0.002 | 0.191 | 0.004 | 1.5435 | 0.0025 | 29.624 | 0 | 8247 | 17 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.2978 | 12493.9247 | 169.4792 | 0 | 0 | 12493.9247 | 0.0087813 | 27.6094 | 54.7472 | 14.0998 | 13.0652 | 0.013922 | 38.1572 | 0.0087813 | 27.6094 | 0.0081727 | 22.3254 | 75 | 62.001 | 22.0092 | 69967.5029 | 60728.8192 | 6937 | 0.33839 | 66074.9054 | 56836.2217 | 8.012 | 0.14292 | -5.6001 | -20.2528 | 51.3701 | 69967.5029 | 66017.209 | 3950.2939 | 0 | 69967.5029 | 100%
2 | T2-E-3000-95-CE-B30% | 75T0207 | T2-E-3000-95-CE-B30% | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  |  | 30 | CUST 6 | 8/15/2014 | 20:29:45 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.4 | 1.4 | 15.1 | 0 | 54027 | 113 | 54361 | 492 | 10680 | 100 | 64717 | 139 | 7.638 | 950 | [38 empty] | 30% evaporator coil blockage, factory charge, 2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm),--Econo Closed damper, adjust code tester speed to match total static of run--T2-E-3000-95-CE-SPWCT-SS. Both stages. | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .; | 74.828 | 0.021 | 62.204 | 0.014 | 95.027 | 0.015 | 74.98 | 0.033 | 75.11 | 0.16 | 57.29 | 0.04 | 59.92 | 0.02 | 0.075 | 0.003 | 1.0778 | 0.0021 | 54027 | 113 | 10680 | 100 | 7.638 | 0.025 | [6 empty] | 460.4 | 2.8 | 460.4 | 2.8 | 459.3 | 2.7 | 15.1 | 0.1 | 13.1 | 0 | 12.8 | 0.1 | 6857.5 | 71 | 3241.6 | 73 | 1615.9 | 60.3 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.1 |  | 3.1 |  | 0.55 | 460 |  | 460 |  | 460 |  | 4.8 |  | 4.8 |  | 4.4 |  | 3140 |  | 0.85 | 460 | 460 | 460 | 4.9 | 4.6 | 4.4 | 2970 | 0.81 | 459.5 |  | 1.6 |  | 696 |  | 85 |  | 8471 | [14 empty] | 215.67 | 0.2 | 106.68 | 0.09 | 106.49 | 0.06 | -0.19 | 0.06 | 244.64 | 0.23 | 174.46 | 0.14 | 115.46 | 0.07 | 59.01 | 0.12 | 209.2 | 0.05 | 99.78 | 0.07 | 104.37 | 0.05 | 4.47 | 0.05 | 74.48 | 0.04 | 51.18 | 0.39 | 43.74 | 0.03 | 7.44 | 0.39 | 73.92 | 0.05 | 56.8 | 0.13 | 43.38 | 0.03 | 13.42 | 0.12 | [46 empty] | 246.65 | 0.23 | 170.8 | 0.1 | 116.05 | 0.07 | 54.75 | 0.1 | 230.19 | 0.35 | 111.09 | 0.11 | 10.87 | 0.14 | 221.3 | 0.05 | 99.67 | 0.08 | 108.29 | 0.05 | 8.62 | 0.05 | 75.89 | 0.06 | 44.66 | 0.04 | 2.54 | 0.15 | 75.04 | 0.06 | 55.84 | 0.14 | 44.11 | 0.04 | 11.73 | 0.15 | 105.1 | 0.09 | [28 empty] | 105.53 | 0.09 | 105.1 | 0.09 | 100.82 | 0.09 | 101.13 | 0.08 | 57.19 | 0.04 | 56.95 | 0.05 |  |  | 57.27 | 0.03 | 57.33 | 0.03 | 56.97 | 0.04 | 105.67 | 0.07 | 101.28 | 0.09 | 52.23 | 0.43 | 57.09 | 0.15 | 170.19 | 0.11 | 101.1 | 0.08 | 99.91 | 0.08 | 47.79 | 0.08 | 57.43 | 0.24 | 99.78 | 0.07 | 99.67 | 0.08 | 94.06 | 0.06 | 106.18 | 0.1 | 106.04 | 0.08 | 101.07 | 0.06 | 101.18 | 0.12 | 100.82 | 0.09 | 101.13 | 0.08 | [12 empty] | 106.68 | 0.09 | 56.97 | 0.04 |  |  | 100.22 | 0.13 | 105.53 | 0.09 | 105.1 | 0.09 | [16 empty] | 47.2 | 0.13 | [12 empty] | 174.83 | 0.1 | 95.02 | 0.1 | 95.57 | 0.19 | 75.65 | 0.11 | 75.45 | 0.11 | 75.24 | 0.1 | 75.94 | 0.07 | 75.99 | 0.1 | 75.92 | 0.11 | 75.7 | 0.11 | 81.55 | 0.14 | 80.88 | 0.15 | 78.41 | 0.11 | 77.2 | 0.1 | 77.96 | 0.08 | 77.55 | 0.08 | 76.99 | 0.09 | 77.4 | 0.08 | 77.24 | 0.09 | 77.41 | 0.08 | 75.9 | 0.12 | 75.33 | 0.11 | 75.54 | 0.11 | 76.01 | 0.1 | 76.01 | 0.1 | 75.46 | 0.1 | 75.39 | 0.07 |  |  | 79.14 | 0.16 |  |  | 75.3 | 0.1 | 75.88 | 0.09 | 75.66 | 0.12 | 75.43 | 0.12 | 75.29 |  | 75.24 | 0.11 |  |  | 81.58 | 0.08 | 77.98 | 0.09 | 75.65 | 0.12 | 75.31 | 0.11 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 74.828 | 0.021 | 62.204 | 0.014 | 57.12 | 0.017 | 54.324 | 0.014 | 95.027 | 0.015 | 74.98 | 0.033 | 2780.4 | 2.7 | 2725.9 | 2.7 | 0.651 | 0.002 | -0.244 | 0.002 | 0.075 | 0.003 | 1.0778 | 0.0021 | 29.213 | 0.001 | 8473 | 22 | 1580 |  | 0 | 0 | 13.029 | 0.231 | 1.5304 | 12740.9651 | 208.476 | 0 | 0 | 12740.9651 | 0.0089561 | 27.7587 | 55.5896 | 14.1004 | 13.0935 | 0.013897 | 38.1373 | 0.0089561 | 27.7587 | 0.0083074 | 22.7337 | 74.828 | 62.204 | 22.3607 | 68775.4487 | 58827.7226 | 6893 | 0.34207 | 64094.4372 | 54146.7111 | 7.5646 | 0.16776 | -5.398 | -19.2384 | 51.7117 | 68775.4487 | 64023.8886 | 4751.5601 | 0 | 68775.4487 | 100%
2 | T2-HS-1875-95-CF-C | 75T0148 | T2-HS-1875-95-CF-C | closed | on | on | 4.5 turns | unsealed | unsealed |  | 8 |  | 0 | 0 | CUST 6 | 7/31/2014 | 5:19:46 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.8 | 1 | 14 | 0 | 48347 | 86 | 47710 | 229 | 16947 | 340 | 65309 | 390 | 8.3966 | 738 |  |  |  | 108.77 | 0.02 | 16.19 | [32 empty] | . | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: 8` BP no name: ID Blw M: MQC 56T17D5563B: Mtr Pulley 4.5 T/O: With econo: Supply Meriam @85% Return Meriam @75%: Horiz Air Disch: Max Mtr Amp 4.7 | 75.009 | 0.014 | 61.963 | 0.081 | 94.881 | 0.02 | 75.005 | 0.012 | 74.7 | 0.11 | 52.21 | 0.06 | 57.14 | 0.03 | 0.053 | 0.003 | 0.6685 | 0.0016 | 48347 | 86 | 16947 | 340 | 8.396 | 0.05 | 77924 | 210 | 10.018 | 0.03 | 16.19 | 0.42 | 459.8 | 2.4 | 459.9 | 2.4 | 460.2 | 2.4 | 14 | 0.1 | 12.3 | 0 | 12.1 | 0.1 | 6330.1 | 60.3 | 3228.9 | 66 | 1448.4 | 52.3 | 460 |  | 460 |  | 460 |  | 2.3 |  | 2.4 |  | 2.4 |  | 0.4 | 460 |  | 460 |  | 460 |  | 5 |  | 5 |  | 4.5 |  | 3140 |  | 0.82 | 460 | 460 | 460 | 4.9 | 4.7 | 4.5 | 3010 | 0.82 | 459 |  | 1.6 |  | 701.7 |  | 105 |  | 7806.7 | [14 empty] | 219.6 | 0.18 | 106.24 | 0.1 | 107.76 | 0.06 | 1.67 |  | 243.02 | 0.2 | 178.89 | 0.13 | 114.99 | 0.06 | 63.9 | 0.12 | 211.43 | 0.05 | 99.77 | 0.27 | 105.12 | 0.05 | 5.23 | 0.28 | 68.35 | 0.11 | 42.7 | 0.12 | 39.64 | 0.08 | 3.05 | 0.11 | 67.89 | 0.11 | 52.52 | 0.28 | 39.33 | 0.07 | 13.2 | 0.25 | 590.87 | 1.32 |  | 0.08 | 77924 | 210 | 40982 | 114 | [38 empty] | 245.37 | 0.21 | 173.97 | 0.22 | 115.69 | 0.06 | 58.28 | 0.24 | 230.28 | 0.23 | 111.13 | 0.05 | 10.28 | 0.05 | 220.87 |  | 98.69 | 0.08 | 108.17 | 0.07 | 9.51 | 0.09 | 70.83 | 0.16 | 41.34 | 0.11 | 2.29 | 0.23 | 70.47 | 0.15 | 52.29 | 0.44 | 41.1 | 0.1 | 11.2 | 0.46 | 105.57 | 0.06 | 582.83 | 1.98 | 39.07 | 0.03 | 108.77 | 0.04 | 77924 | 210 | 40626 | 127 | [18 empty] | 105.79 | 0.09 | 105.57 | 0.06 | 100.47 | 0.07 | 100.72 | 0.07 | 52.16 | 0.08 | 51.92 | 0.08 | 51.5 | 0.08 | 52.24 | 0.08 | 52.32 | 0.08 | 51.96 | 0.08 | 105.88 | 0.11 | 101.69 | 0.06 | 43.73 | 0.24 | 51.33 | 0.4 | 172.63 | 0.2 | 100.53 | 0.07 | 100.05 | 0.08 | 44.18 | 0.12 | 51.49 | 0.64 |  |  |  |  | 92.73 | 0.11 | [8 empty] | 100.47 | 0.07 | 100.72 | 0.07 | [14 empty] | 51.96 | 0.08 | 106.24 | 0.1 | 100.9 | 0.08 | 105.79 | 0.09 | 105.57 | 0.06 | [16 empty] | 43.63 | 0.21 | [12 empty] | 177.69 | 0.17 | 94.44 | 0.16 | 94.57 | 0.15 | 75.28 | 0.11 | 75.1 | 0.1 | 74.85 | 0.1 | 75.63 | 0.07 | 75.65 | 0.09 | 75.56 | 0.09 | 75.37 | 0.09 | 80.22 | 0.09 | 79.57 | 0.11 | 77.01 | 0.08 | 77.15 | 0.23 | 78.01 | 0.14 | 77.79 | 0.15 | 77.32 | 0.13 | 75.73 | 0.1 | 75.38 | 0.09 | 75.49 | 0.1 | 74.96 | 0.08 | 74.71 | 0.12 | 74.69 | 0.13 | 75.29 | 0.19 | 74.81 | 0.12 | 74.85 | 0.1 | 74.87 | 0.08 | 75.56 | 0.08 | 76.27 | 0.09 |  |  | 74.98 | 0.07 | 75.67 | 0.11 | 75.4 | 0.11 | 75.14 | 0.11 | 75 |  | 74.87 | 0.1 | 80.41 | 0.12 | 81.16 | 0.12 | 77.9 | 0.14 | 75.29 | 0.1 | 74.7 | 0.12 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 75.009 | 0.014 | 61.963 | 0.081 | 52.217 | 0.026 | 49.941 | 0.055 | 94.881 | 0.02 | 75.005 | 0.012 | 1896.9 | 2.2 | 1877.6 | 2.2 | 0.469 | 0.002 | -0.193 | 0.002 | 0.053 | 0.003 | 0.6685 | 0.0016 | 29.277 | 0 | 7778 | 17 | 850 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.2085 | 8782.0835 | 103.4525 | 65.9045 | 280.501 | 8501.5825 | 0.0089202 | 27.9198 | 51.0085 | 14.0972 | 12.9598 | 0.013954 | 38.1641 | 0.0087541 | 27.5818 | 0.0070781 | 20.206 | 75.6495 | 62.4424 | 19.9122 | 70323.9538 | 51935.9627 | 6928 | 0.33623 | 67775.9872 | 49387.9961 | 8.7138 | 0.14919 | -8.0077 | -24.6411 | 46.6876 | 70323.9538 | 64775.0399 | 2580.5744 | 2968.3395 | 70323.9538 | 100%
2 | T2-HS-2625-95-CF | 75T0151 | T2-HS-2625-95-CF | closed | on | on | 2 turns | unsealed | unsealed | 1002 | 6.25 |  | 0 | 0 | CUST 6 | 7/31/2014 | 12:52:13 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.4 | 1.4 | 15 | 0 | 52764 | 109 | 53441 | 361 | 9104 | 450 | 61876 | 470 | 6.9964 | 1036 |  |  |  | 109.37 | 0.11 | 25.57 | [32 empty] | 87.5% airflow (350 cfm/ton), 3 HP fan motor, 2 turns, 6.25" pulley (1002 rpm),--both stages, closed damper match adjust code tester speed to match--static of run 'T2-2625-95-CF-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: 6.25` BP no name: ID Blw M: MQC 56T17D5563B: Mtr Pulley 2 T/O: With econo: Supply Meriam @85% Return Meriam @75%: Horiz Air Disch: Max Mtr Amp 4.7 | 74.997 | 0.016 | 61.975 | 0.091 | 94.854 | 0.011 | 75.015 | 0.021 | 74.81 | 0.08 | 56.73 | 0.1 | 60.03 | 0.03 | 0.101 | 0.003 | 1.3256 | 0.0025 | 52764 | 109 | 9104 | 450 | 6.996 | 0.054 | 83135 | 370 | 9.4 | 0.046 | 25.57 | 0.43 | 459.4 | 2.6 | 459.6 | 2.6 | 460.8 | 2.6 | 15 | 0.1 | 13.4 | 0 | 13.3 | 0.1 | 6816 | 59 | 3307.6 | 69.8 | 2028.3 | 51.4 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.64 | 460 |  | 460 |  | 460 |  | 5.2 |  | 4.9 |  | 4.5 |  | 3170 |  | 0.82 | 460 | 460 | 460 | 5 | 4.7 | 4.5 | 3030 | 0.81 | 458.5 |  | 1.6 |  | 700.8 |  | 115 |  | 8855.8 | [14 empty] | 220.28 | 0.15 | 106.95 | 0.06 |  |  |  |  | 247.37 | 0.16 | 177 | 0.21 | 116.28 | 0.05 | -60.71 | 0.2 | 210 |  | 101.08 | 0.28 | 107.99 | 0.05 | 6.91 | 0.28 | 74.29 | 0.11 | 48.11 | 0.64 | 43.65 | 0.07 | 4.46 | 0.6 | 73.75 | 0.1 | 56.54 | 0.46 | 43.3 | 0.06 | 13.24 | 0.4 | 619.74 | 1.79 |  | 0.09 | 83135 | 370 | 43101 | 184 | [38 empty] | 249.69 | 0.2 | 173.02 | 0.36 | 116.96 | 0.06 | 56.06 | 0.38 | 232.58 | 0.31 |  |  |  |  | 221 |  | 99.31 | 0.1 | 111.84 | 0.1 | 12.53 | 0.1 | 76.84 | 0.26 | 45.31 | 0.17 | 3.53 | 1.65 | 76.42 | 0.24 | 56.36 | 0.79 | 45.04 | 0.15 | 11.32 | 0.81 | 105.21 | 0.05 | 623.95 | 4.24 | 39.26 | 0.03 | 109.33 | 0.29 | 83135 | 370 | 43717 | 251 | [18 empty] | 105.78 | 0.05 | 105.21 | 0.05 | 100.97 | 0.1 | 101.16 | 0.1 | 57.24 | 0.08 | 56.98 | 0.09 | 56.49 | 0.09 | 57.3 | 0.1 | 57.29 | 0.1 | 56.99 | 0.1 | 107.6 | 0.07 | 101.21 | 0.07 | 49.49 | 0.74 | 55.83 | 0.52 | 171.76 | 0.34 | 101.04 | 0.08 | 100.74 | 0.11 | 48.49 | 0.51 | 57.14 | 1.29 |  |  |  |  | 93.34 | 0.04 | [8 empty] | 100.97 | 0.1 | 101.16 | 0.1 | [12 empty] | 101.08 | 0.28 | 56.99 | 0.1 | 106.95 | 0.06 | 101.49 | 0.12 | 105.78 | 0.05 | 105.21 | 0.05 | [16 empty] | 48.81 | 1.5 | [12 empty] | 175.8 | 0.21 | 94.15 | 0.11 | 94.28 | 0.11 | 75.39 | 0.07 | 75.09 | 0.07 | 74.93 | 0.07 | 75.66 | 0.06 | 75.69 | 0.07 | 75.58 | 0.08 | 75.39 | 0.08 | 80.28 | 0.09 | 79.72 | 0.08 | 77.1 | 0.08 | 77.22 | 0.15 | 78.63 | 0.15 | 78.38 | 0.11 | 77.59 | 0.12 | 75.73 | 0.09 | 75.35 | 0.09 | 75.49 | 0.09 | 74.9 | 0.08 | 74.8 | 0.1 | 74.77 | 0.11 | 74.92 | 0.12 | 74.85 | 0.11 | 75 | 0.09 | 74.98 | 0.08 | 75.35 | 0.07 | 75.42 | 0.08 |  |  | 74.99 | 0.06 | 75.62 | 0.07 | 75.39 | 0.07 | 75.13 | 0.07 | 74.98 |  | 74.79 | 0.09 | 80.89 | 0.11 | 78.53 | 0.63 | 78.14 | 0.14 | 75.25 | 0.1 | 74.8 | 0.1 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 74.997 | 0.016 | 61.975 | 0.091 | 57.145 | 0.035 | 54.162 | 0.062 | 94.854 | 0.011 | 75.015 | 0.021 | 2684.2 | 2.5 | 2641 | 2.5 | 0.907 | 0.002 | -0.371 | 0.002 | 0.101 | 0.003 | 1.3256 | 0.0025 | 29.314 | 0.001 | 8844 | 18 | 1840 |  | 0 | 0 | 13.029 | 0.231 | 1.8014 | 12300.2561 | 281.4108 | 0 | 0 | 12300.2561 | 0.0087649 | 27.5906 | 55.3436 | 14.0966 | 13.0934 | 0.013969 | 38.1743 | 0.0087649 | 27.5906 | 0.0082097 | 22.6336 | 74.997 | 61.975 | 22.1947 | 66371.4881 | 58018.1074 | 7004 | 0.36016 | 61052.0232 | 52698.6425 | 6.9032 | 0.16485 | -5.3959 | -19.6534 | 51.4641 | 66371.4881 | 60972.8135 | 5398.6745 | 0 | 66371.4881 | 100%
2 | T2-1875-95-CF-C | 75T0154 | T2-1875-95-CF-C | closed | on | on | 3 turns | unsealed | unsealed | 640 | 9.25 |  | 0 | 0 | CUST 6 | 7/31/2014 | 18:51:50 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.6 | 0.9 | 14 | 0 | 49035 | 96 | 48850 | 318 | 17551 | 278 | 66602 | 329 | 8.6721 | 636 |  |  |  | 108.88 | 0.04 | 14.63 | [32 empty] | 62.5% airflow (250 cfm/ton), factory charge, closed damper, 2 HP fan motor, 3 turns, 9.25" AK94 pulley--(640 rpm), 95F Test, adjust code tester speed to match total static of run 'T2-1875-95-CF-C-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 9.25` BP no name: ID Blw 2 HP GE: Mtr Pulley 3.0 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.986 | 0.018 | 62.009 | 0.06 | 94.85 | 0.016 | 75.017 | 0.015 | 74.64 | 0.11 | 51.77 | 0.09 | 56.96 | 0.02 | 0.075 | 0.002 | 0.6764 | 0.0016 | 49035 | 96 | 17551 | 278 | 8.672 | 0.047 | 78018 | 267 | 10.158 | 0.042 | 14.63 | 0.4 | 459.6 | 2.3 | 459.2 | 2.3 | 460.5 | 2.3 | 14 | 0.1 | 12.4 | 0.1 | 12.3 | 0.1 | 6290.8 | 62.8 | 3432.6 | 70.2 | 1389.3 | 54.7 | 460 |  | 460 |  | 460 |  | 2.5 |  | 2.7 |  | 2.6 |  | 0.32 | 460 |  | 460 |  | 460 |  | 5 |  | 4.9 |  | 4.5 |  | 3140 |  | 0.82 | 460 | 460 | 460 | 4.7 | 4.6 | 4.5 | 3000 | 0.81 | 458.8 |  | 1.6 |  | 701.7 |  | 105 |  | 7696.7 | [14 empty] | 219.39 | 0.15 | 106.33 | 0.12 | 107.71 | 0.05 | 1.41 | 0.05 | 243.15 | 0.17 | 178.19 | 0.21 | 115.04 | 0.05 | 63.15 | 0.21 | 211.23 | 0.05 | 100.53 | 0.32 | 105.06 | 0.05 | 4.51 | 0.33 | 69.08 | 0.11 | 43.6 | 0.25 | 40.16 | 0.08 | 3.44 | 0.25 | 68.59 | 0.09 | 52.81 | 0.39 | 39.83 | 0.06 | 12.99 | 0.36 | 597.29 | 1.33 |  | 0.1 | 78018 | 267 | 41353 | 117 | [38 empty] | 244.61 | 0.21 | 174.59 | 0.27 | 115.47 | 0.06 | 59.12 | 0.29 | 229.65 | 0.32 | 110.96 | 0.05 | 10.09 | 0.05 | 220.03 | 0.05 | 98.78 | 0.09 | 110.94 | 0.1 | 12.15 | 0.09 | 70.34 | 0.19 | 41.03 | 0.13 | 2.87 | 1 | 69.92 | 0.2 | 52.41 | 0.61 | 40.74 | 0.14 | 11.67 | 0.63 | 105.36 | 0.06 | 578.46 | 3.41 | 39.1 | 0.03 | 108.86 | 0.17 | 78018 | 267 | 40356 | 201 | [18 empty] | 105.84 | 0.09 | 105.36 | 0.06 | 100.45 | 0.09 | 100.64 | 0.09 | 51.98 | 0.08 | 51.71 | 0.08 | 51.29 | 0.07 | 52.15 | 0.08 | 52.16 | 0.18 | 51.86 | 0.08 | 105.97 | 0.13 | 101.43 | 0.06 | 44.32 | 0.42 | 51.64 | 0.51 | 173.16 | 0.26 | 100.56 | 0.08 | 100.09 | 0.1 | 43.95 | 0.28 | 53.05 | 0.97 |  |  |  |  | 93.36 | 0.05 | [8 empty] | 100.45 | 0.09 | 100.64 | 0.09 | [14 empty] | 51.86 | 0.08 | 106.33 | 0.12 | 100.94 | 0.11 | 105.84 | 0.09 | 105.36 | 0.06 | [16 empty] | 43.92 | 0.9 | [12 empty] | 176.96 | 0.22 | 94.37 | 0.1 | 94.48 | 0.1 | 75.26 | 0.11 | 75.06 | 0.11 | 74.86 | 0.1 | 75.59 | 0.08 | 75.62 | 0.11 | 75.54 | 0.11 | 75.33 | 0.1 | 79.1 | 0.1 | 78.31 | 0.08 | 77.16 | 0.09 | 75.35 | 0.12 | 75.95 | 0.15 | 76.06 | 0.13 | 76.1 | 0.11 | 75.35 | 0.09 | 75.13 | 0.1 | 74.94 | 0.09 | 74.87 | 0.09 | 74.82 | 0.11 | 74.77 | 0.11 | 75.6 | 0.11 | 74.99 | 0.1 | 74.99 | 0.1 | 74.96 | 0.08 | 75.8 | 0.08 | 76.02 | 0.08 |  |  | 74.92 | 0.08 | 75.66 | 0.1 | 75.42 | 0.1 | 75.13 | 0.11 | 74.95 |  | 74.81 | 0.11 | 81.33 | 0.09 | 79.38 | 0.15 | 75.79 | 0.14 | 75.25 | 0.1 | 74.81 | 0.11 | [62 empty] | T2-TRN-63A-55-CE-DM-2 | 74.986 | 0.018 | 62.009 | 0.06 | 52.023 | 0.024 | 49.798 | 0.043 | 94.85 | 0.016 | 75.017 | 0.015 | 1906.2 | 2.3 | 1890.9 | 2.3 | 0.274 | 0.002 | -0.128 | 0.002 | 0.075 | 0.002 | 0.6764 | 0.0016 | 29.326 | 0.001 | 7680 | 21 | 750 |  | 0.027204 | 52.3978 | 13.029 | 0.132 | 1.1097 | 8828.6377 | 60.8673 | 53.67 | 228.4392 | 8600.1985 | 0.0089239 | 27.8886 | 50.9133 | 14.0965 | 12.9547 | 0.013972 | 38.1763 | 0.0087899 | 27.6153 | 0.0070492 | 20.1275 | 75.5047 | 62.3966 | 19.8577 | 70901.556 | 52106.0593 | 6930 | 0.33359 | 68549.5462 | 49754.0495 | 8.9257 | 0.15124 | -8.0309 | -24.5914 | 46.5315 | 70901.556 | 66107.0434 | 2381.9843 | 2412.5283 | 70901.556 | 100%
2 | T2-2625-95-CF | 75T0156 | T2-2625-95-CF | closed | on | on |  | unsealed | unsealed |  |  |  | 0 | 0 | CUST 6 | 7/31/2014 | 20:37:56 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.5 | 1.2 | 14.6 | 0 | 55581 | 75 | 54718 | 306 | 10742 | 380 | 66333 | 398 | 7.9939 | 862 |  |  |  | 109.5 | 0.12 | 19.6 | [32 empty] | Average Data--75.01 | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX38 belt: 6.25` AK64 BP: ID Blw 2 HP GE: Mtr Pulley 3.5 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.01 | 0.011 | 62.001 | 0.068 | 94.875 | 0.021 | 75.008 | 0.02 | 74.92 | 0.1 | 56.25 | 0.06 | 59.21 | 0.03 | 0.178 | 0.003 | 1.3004 | 0.0025 | 55581 | 75 | 10742 | 380 | 7.993 | 0.052 | 82499 | 350 | 9.941 | 0.048 | 19.6 | 0.38 | 459.5 | 2.5 | 459.1 | 2.5 | 460.3 | 2.5 | 14.6 | 0.1 | 13 | 0 | 12.9 | 0.1 | 6604.1 | 64.1 | 3407.9 | 72.5 | 1694.4 | 54.1 | 460 |  | 460 |  | 460 |  | 2.8 |  | 3 |  | 3 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.1 |  | 5 |  | 4.5 |  | 3190 |  | 0.83 | 460 | 460 | 460 | 4.8 | 4.7 | 4.5 | 3030 | 0.81 | 458.6 |  | 1.6 |  | 701 |  | 105 |  | 8316 | [14 empty] | 220.22 | 0.14 | 107.01 | 0.05 | 107.97 | 0.05 | 0.96 | 0.05 | 247.32 | 0.16 | 177.59 | 0.15 | 116.27 | 0.04 | 61.32 | 0.16 | 209.8 | 0.05 | 101.78 | 0.23 | 104.6 | 0.05 | 2.77 | 0.23 | 74.36 | 0.07 | 48.86 | 0.67 | 43.71 | 0.05 | 5.16 | 0.65 | 73.81 | 0.06 | 56.99 | 0.33 | 43.34 | 0.04 | 13.64 | 0.3 | 617.22 | 1.48 |  | 0.07 | 82499 | 350 | 42870 | 179 | [38 empty] | 249.03 | 0.19 | 172.89 | 0.31 | 116.77 | 0.05 | 56.11 | 0.35 | 232.04 | 0.33 | 111.59 | 0.05 | 9.8 | 0.05 | 220.6 | 0.05 | 99.59 | 0.11 | 111.67 | 0.1 | 12.08 | 0.1 | 76.01 | 0.22 | 44.78 | 0.14 | 3.68 | 1.59 | 75.61 | 0.21 | 55.83 | 0.7 | 44.52 | 0.13 | 11.31 | 0.73 | 105.24 | 0.05 | 619.05 | 4.01 | 39.35 | 0.03 | 109.31 | 0.28 | 82499 | 350 | 43309 | 232 | [18 empty] | 105.82 | 0.06 | 105.24 | 0.05 | 101.27 | 0.1 | 101.49 | 0.1 | 56.2 | 0.07 | 55.88 | 0.06 | 55.41 | 0.07 | 56.54 | 0.06 | 56.45 | 0.06 | 56.27 | 0.06 | 107.86 | 0.07 | 101.39 | 0.05 | 50.36 | 0.69 | 56.44 | 0.36 | 171.71 | 0.29 | 101.37 | 0.08 | 100.98 | 0.1 | 48.07 | 0.5 | 56.8 | 1.07 |  |  |  |  | 93.47 | 0.05 | [8 empty] | 101.27 | 0.1 | 101.49 | 0.1 | [14 empty] | 56.27 | 0.06 | 107.01 | 0.05 | 101.79 | 0.11 | 105.82 | 0.06 | 105.24 | 0.05 | [16 empty] | 48.44 | 1.47 | [12 empty] | 176.63 | 0.14 | 94.45 | 0.13 | 94.56 | 0.12 | 75.54 | 0.08 | 75.23 | 0.08 | 75.06 | 0.07 | 75.86 | 0.06 | 75.93 | 0.08 | 75.81 | 0.08 | 75.57 | 0.08 | 79.27 | 0.07 | 78.52 | 0.05 | 77.34 | 0.06 | 75.22 | 0.1 | 76.06 | 0.13 | 76.35 | 0.13 | 76.29 | 0.1 | 75.38 | 0.08 | 75.13 | 0.09 | 74.98 | 0.08 | 74.88 | 0.08 | 74.9 | 0.1 | 74.87 | 0.11 | 75.75 | 0.12 | 75.15 | 0.11 | 75.08 | 0.09 | 75.06 | 0.07 | 75.84 | 0.07 | 76.03 | 0.07 |  |  | 75.08 | 0.06 | 75.85 | 0.07 | 75.59 | 0.08 | 75.27 | 0.08 | 75.07 |  | 74.86 | 0.08 | 81.83 | 0.09 | 78.3 | 0.79 | 75.7 | 0.1 | 75.24 | 0.09 | 74.89 | 0.1 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 75.01 | 0.011 | 62.001 | 0.068 | 56.045 | 0.02 | 53.479 | 0.042 | 94.875 | 0.021 | 75.008 | 0.02 | 2655.2 | 2.6 | 2619.1 | 2.5 | 0.507 | 0.002 | -0.234 | 0.002 | 0.178 | 0.003 | 1.3004 | 0.0025 | 29.331 | 0.001 | 8298 | 19 | 1290 |  | 0 | 0 | 13.029 | 0.231 | 1.3221 | 12194.2186 | 156.0002 | 0 | 0 | 12194.2186 | 0.0087789 | 27.6092 | 54.7229 | 14.097 | 13.0646 | 0.013958 | 38.1671 | 0.0087789 | 27.6092 | 0.0080855 | 22.2307 | 75.01 | 62.001 | 21.9086 | 69513.9928 | 59372.4126 | 7008 | 0.34408 | 65643.6514 | 55502.0712 | 7.9108 | 0.15515 | -5.7006 | -20.2871 | 50.9974 | 69513.9928 | 65586.9093 | 3927.0834 | 0 | 69513.9928 | 100%
2 | T2-MF17-115C1-115C2-90A-95-CCE | 75T0002 | T2-MF17-115C1-115C2-90A-95-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 30 | 0 | CUST 5 | 10/10/2014 | 2:58:33 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.36 lbs/CK2: 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 460.9 | 1.1 | 16.2 | 0 | 57718 | 64 | 57268 | 446 | 10900 | 199 | 68629 | 208 | 7.3787 | 865 | [38 empty] | MF17, 115% charge CK1 and CK2, 87.5% airflow (360 cfm/ton), closed damper, 30% condenser coil blockage,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed to--to match total static of run T2-MFB2-100C1-100C2-90A-95-CCE-SPWC | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 4.5 turns open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 31.5` of 62` coil | 75 | 0.013 | 62.002 | 0.027 | 94.984 | 0.034 | 74.995 | 0.027 | 74.75 | 0.16 | 55.77 | 0.07 | 59.91 | 0.01 | 0.144 | 0.003 | 1.5473 | 0.0025 | 57718 | 64 | 10900 | 199 | 7.379 | 0.03 | [6 empty] | 460.9 | 2.5 | 462 | 2.5 | 459.4 | 2.5 | 16.2 | 0.1 | 13.8 | 0 | 13.7 | 0.1 | 7385.6 | 52.8 | 3203.2 | 62.4 | 1915.8 | 41.8 | 460 |  | 460 |  | 460 |  | 3 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 460 |  | 460 |  | 5.6 |  | 5.4 |  | 4.9 |  | 3600 |  | 0.86 | 460 | 460 | 460 | 5.7 | 5.3 | 4.9 | 3560 | 0.85 | 459.8 |  | 1.6 |  | 703.6 |  | 85 |  | 9298.6 | [14 empty] | 263.96 | 0.16 | 106.93 | 0.09 | 121.04 | 0.05 | 14.11 | 0.09 | 283.8 | 0.19 | 189.09 | 0.19 | 126.48 | 0.05 | 62.61 | 0.21 | 258.3 | 0.05 | 105.72 | 0.09 | 119.43 | 0.05 | 13.7767 | 0.05 | 75.38 | 0.1 | 47.75 | 0.29 | 44.34 | 0.07 | 3.41 | 0.33 | 74.78 | 0.1 | 54.69 | 0.47 | 43.95 | 0.07 | 10.74 | 0.51 | [46 empty] | 298.38 | 0.18 | 193.99 | 0.16 | 130.3 | 0.05 | 63.69 | 0.17 | 283.96 | 0.29 | 126.52 | 0.08 | 29.43 | 0.08 | 272.4 | 0.05 | 103.24 | 0.06 | 123.38 | 0.05 | 20.2033 | 0.05 | 77.53 | 0.13 | 45.73 | 0.08 | 2.62 | 0.43 | 77.21 | 0.1 | 56.47 | 0.38 | 45.52 | 0.06 | 10.94 | 0.37 | 103.16 | 0.06 | [28 empty] | 107.59 | 0.1 | 107.87 | 0.09 | 103.16 | 0.06 | 103.81 | 0.07 | 55.29 | 0.07 | 55.87 | 0.07 | 55.68 | 0.06 | 55.34 | 0.05 | 55.42 | 0.04 |  |  | 107.04 | 0.1 | 103.28 | 0.09 | 48.43 | 0.68 | 54.76 | 0.5 | 193.95 | 0.19 | 100.83 | 0.08 | 96.55 | 0.04 | 48.7 | 0.34 | 58.85 | 0.36 | 105.72 | 0.09 | 103.24 | 0.06 | 92.84 | 0.23 | 107.12 | 0.09 | 108.22 | 0.1 | 104.63 | 0.06 | 105.25 | 0.06 | 107.87 | 0.09 | 103.81 | 0.07 | [16 empty] | 106.93 | 0.09 | 97.09 | 0.05 | 107.59 | 0.1 | 103.16 | 0.06 | [16 empty] | 48.34 | 0.37 | [12 empty] | 190.15 | 0.23 | 93.65 | 0.1 | 93.22 | 0.11 | 74.95 | 0.08 | 75.37 | 0.07 | 74.96 | 0.08 | 75.35 | 0.09 | 75.24 | 0.09 | 75.36 | 0.1 | 75.21 | 0.09 | 79.06 | 0.1 | 76.78 | 0.07 | 76.76 | 0.07 | 78.04 | 0.11 | 78.03 | 0.09 | 77.31 | 0.08 | 76.63 | 0.09 | 75.54 | 0.09 | 75.19 | 0.09 | 75.49 | 0.1 | 75.02 | 0.09 | 75.35 | 0.08 | 75.22 | 0.08 | 75.27 | 0.08 | 75.64 | 0.07 | 75.42 | 0.08 | 75.19 | 0.05 | 76.31 | 0.08 | 76.37 | 0.09 |  |  | 74.97 | 0.08 | 75.31 | 0.07 | 75.53 | 0.09 | 75.34 | 0.09 | 75.51 |  | 75.07 | 0.08 | 80.97 | 0.07 | 81.31 | 0.08 | 78.61 | 0.1 | 75.33 | 0.1 | 75.3 | 0.08 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 75 | 0.013 | 62.002 | 0.027 | 55.867 | 0.013 | 53.456 | 0.025 | 94.984 | 0.034 | 74.995 | 0.027 | 2742.6 | 2.2 | 2691.5 | 2.2 | 0.554 | 0.002 | -0.249 | 0.002 | 0.144 | 0.003 | 1.5473 | 0.0025 | 29.226 | 0 | 9301 | 25 | 1350 |  | 0 | 0 | 13.029 | 0.231 | 1.3256 | 12599.7403 | 175.1738 | 0 | 0 | 12599.7403 | 0.0087819 | 27.6101 | 54.5414 | 14.0995 | 13.0603 | 0.01392 | 38.1526 | 0.0087819 | 27.6101 | 0.0081146 | 22.219 | 75 | 62.002 | 21.8961 | 71994.9964 | 61865.5063 | 7951 | 0.37693 | 67985.3147 | 57855.8246 | 7.3095 | 0.14222 | -5.714 | -20.4586 | 51.1493 | 71994.9964 | 67926.3135 | 4068.6829 | 0 | 71994.9964 | 100%
2 | T2-MF19-85C1-85C2-90A-95-CCE | 75T0003 | T2-MF19-85C1-85C2-90A-95-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 30 | 0 | CUST 5 | 10/10/2014 | 4:45:01 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.44 lbs/CK2: 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 460.3 | 1.4 | 15.5 | 0 | 54422 | 82 | 53746 | 365 | 7541 | 138 | 61969 | 122 | 7.0014 | 865 | [38 empty] | MF19, 85% charge CK1 and CK2, 87.5% airflow (360 cfm/ton), closed damper, 30% condenser coil blockage,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed--to match total static of run T2-MFB2-100C1-100C2-90A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 4.5 turns open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 31.5` of 62` coil | 75.015 | 0.012 | 62.003 | 0.023 | 94.982 | 0.017 | 75.005 | 0.021 | 74.82 | 0.14 | 56.96 | 0.07 | 60.71 | 0.02 | 0.143 | 0.003 | 1.5466 | 0.0026 | 54422 | 82 | 7541 | 138 | 7.001 | 0.024 | [6 empty] | 460.3 | 2.6 | 461.6 | 2.6 | 459.8 | 2.6 | 15.5 | 0.1 | 13.3 | 0 | 13.3 | 0 | 7067.1 | 52.7 | 3234.3 | 61.7 | 1784 | 40.6 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.51 | 460 |  | 460 |  | 460 |  | 5.4 |  | 5.2 |  | 4.7 |  | 3450 |  | 0.85 | 460 | 460 | 460 | 5.3 | 4.9 | 4.6 | 3260 | 0.82 | 459.3 |  | 1.7 |  | 705.5 |  | 85 |  | 8850.5 | [14 empty] | 238.21 | 0.13 | 112.81 | 0.08 | 113.54 | 0.04 | 0.72 | 0.07 | 271.64 | 0.13 | 200.72 | 0.21 | 123.18 | 0.04 | 77.53 | 0.19 | 226 | 0.05 | 108.65 | 0.05 | 109.78 | 0.05 | 1.0967 | 0.05 | 72.87 | 0.06 | 67.37 | 0.11 | 42.69 | 0.04 | 24.69 | 0.08 | 72.28 | 0.06 | 70.28 | 0.1 | 42.29 | 0.04 | 27.98 | 0.07 | [46 empty] | 273.14 | 0.15 | 183.24 | 0.19 | 123.59 | 0.04 | 59.65 | 0.21 | 251.03 | 0.26 | 117.34 | 0.08 | 10.17 | 0.11 | 240 | 0.05 | 114.29 | 0.18 | 114.07 | 0.05 | -0.26 | 0.05 | 78.18 | 0.15 | 46.14 | 0.09 | 3.35 | 0.75 | 77.85 | 0.12 | 71.47 | 0.12 | 45.93 | 0.08 | 25.54 | 0.14 | 114.06 | 0.18 | [28 empty] | 111.64 | 0.08 | 111.19 | 0.07 | 114.06 | 0.18 | 114.42 | 0.18 | 56.41 | 0.07 | 57.06 | 0.06 | 56.92 | 0.06 | 56.63 | 0.05 | 56.69 | 0.04 |  |  | 112.26 | 0.05 | 106.22 | 0.07 | 67.88 | 0.11 | 70.34 | 0.11 | 183.31 | 0.23 | 111.46 | 0.16 | 106.31 | 0.1 | 49.73 | 0.64 | 59.98 | 0.47 | 108.65 | 0.05 | 114.29 | 0.18 | 93.15 | 0.17 | 111.4 | 0.05 | 111.62 | 0.05 | 113.63 | 0.1 | 114.17 | 0.13 | 111.19 | 0.07 | 114.42 | 0.18 | [16 empty] | 112.81 | 0.08 | 107.17 | 0.11 | 111.64 | 0.08 | 114.06 | 0.18 | [16 empty] | 49.46 | 0.65 | [12 empty] | 202.03 | 0.2 | 94.09 | 0.1 | 93.63 | 0.08 | 75.19 | 0.06 | 75.57 | 0.06 | 75.08 | 0.06 | 75.7 | 0.07 | 75.56 | 0.07 | 75.65 | 0.07 | 75.45 | 0.07 | 79.13 | 0.1 | 76.81 | 0.07 | 76.82 | 0.06 | 78.08 | 0.11 | 78.14 | 0.09 | 77.41 | 0.06 | 76.73 | 0.06 | 75.54 | 0.08 | 75.31 | 0.08 | 75.59 | 0.09 | 75.04 | 0.07 | 75.3 | 0.07 | 75.21 | 0.07 | 75.23 | 0.07 | 75.63 | 0.06 | 75.4 | 0.07 | 75.29 | 0.04 | 76.33 | 0.06 | 76.37 | 0.08 |  |  | 75.09 | 0.06 | 75.35 | 0.06 | 75.56 | 0.07 | 75.36 | 0.07 | 75.52 |  | 75.08 | 0.07 | 81.04 | 0.06 | 81.49 | 0.07 | 78.71 | 0.08 | 75.36 | 0.08 | 75.27 | 0.07 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 75.015 | 0.012 | 62.003 | 0.023 | 56.924 | 0.014 | 54.336 | 0.019 | 94.982 | 0.017 | 75.005 | 0.021 | 2744 | 2.3 | 2688.3 | 2.3 | 0.556 | 0.002 | -0.249 | 0.002 | 0.143 | 0.003 | 1.5466 | 0.0026 | 29.233 | 0.001 | 8851 | 25 | 1350 |  | 0 | 0 | 13.029 | 0.231 | 1.3273 | 12578.5385 | 175.5972 | 0 | 0 | 12578.5385 | 0.0087791 | 27.6106 | 55.5967 | 14.0995 | 13.089 | 0.013929 | 38.1623 | 0.0087791 | 27.6106 | 0.0083605 | 22.7436 | 75.015 | 62.003 | 22.4201 | 65288.919 | 58621.0639 | 7501 | 0.39212 | 61280.6823 | 54612.8272 | 6.9236 | 0.15411 | -5.1905 | -19.4183 | 52.0588 | 65288.919 | 61219.8797 | 4069.0393 | 0 | 65288.919 | 100%
2 | T2-MF1-100C1-100C2-90A-95-CCE | 75T0006 | T2-MF1-100C1-100C2-90A-95-CCE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 30 | 0 | CUST 5 | 10/10/2014 | 1:42:05 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.3 | 1.3 | 16 | 0 | 56552 | 56 | 56167 | 343 | 9669 | 79 | 66230 | 101 | 7.2836 | 865 | [38 empty] | MF1, 100% charge CK1 and CK2, 87.5% airflow (360 cfm/ton), closed damper,--30% condenser coil blockage, 2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm),--closed damper, adjust code tester speed to match total static of run T2-MFB2-100C1-100C2-90A-9 | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 4.5 turns open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 31.5" of 62" coil | 75.003 | 0.009 | 61.995 | 0.014 | 94.999 | 0.026 | 75.007 | 0.026 | 74.71 | 0.12 | 56.08 | 0.04 | 60.19 | 0.02 | 0.143 | 0.003 | 1.5476 | 0.0023 | 56552 | 56 | 9669 | 79 | 7.284 | 0.023 | [6 empty] | 461.3 | 2.8 | 462.1 | 2.8 | 458.9 | 2.8 | 16 | 0.1 | 13.6 | 0 | 13.3 | 0 | 7316.2 | 57.6 | 3143.7 | 67.8 | 1776.3 | 43.8 | 460 |  | 460 |  | 460 |  | 3 |  | 2.9 |  | 2.8 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.6 |  | 5.2 |  | 4.8 |  | 3560 |  | 0.85 | 460 | 460 | 460 | 5.6 | 5 | 4.7 | 3420 | 0.84 | 460.3 |  | 1.6 |  | 702.9 |  | 85 |  | 9087.9 | [14 empty] | 250.67 | 0.14 | 116.24 | 0.07 | 117.24 | 0.04 | 1 | 0.05 | 279.59 | 0.15 | 188.75 | 0.07 | 125.34 | 0.04 | 63.41 | 0.07 | 243.5 | 0.05 | 113.39 | 0.05 | 115.12 | 0.05 | 1.7033 | 0.05 | 76.21 | 0.03 | 49.89 | 0.22 | 44.88 | 0.02 | 5.01 | 0.23 | 75.59 | 0.03 | 57.35 | 0.1 | 44.48 | 0.02 | 12.87 | 0.11 | [46 empty] | 285.34 | 0.16 | 188.57 | 0.16 | 126.89 | 0.04 | 61.69 | 0.17 | 270.01 | 0.28 | 122.73 | 0.08 | 22.43 | 0.06 | 258.6 | 0.05 | 106.73 | 0.06 | 119.52 | 0.05 | 12.77 | 0.05 | 77.72 | 0.14 | 45.84 | 0.09 | 2.88 | 0.54 | 77.38 | 0.1 | 58.94 | 0.09 | 45.63 | 0.06 | 13.31 | 0.12 | 106.55 | 0.06 | [28 empty] | 115.97 | 0.07 | 115.6 | 0.07 | 106.55 | 0.06 | 107.1 | 0.07 | 55.64 | 0.06 | 56.19 | 0.05 | 56.01 | 0.04 | 55.7 | 0.04 | 55.77 | 0.04 |  |  | 116.13 | 0.06 | 110.6 | 0.1 | 51.02 | 0.33 | 57.3 | 0.12 | 188.41 | 0.2 | 104.18 | 0.06 | 99.64 | 0.05 | 48.99 | 0.43 | 59.25 | 0.4 | 113.39 | 0.05 | 106.73 | 0.06 | 92.94 | 0.2 | 115.06 | 0.07 | 116.26 | 0.05 | 107.75 | 0.06 | 108.44 | 0.08 | 115.6 | 0.07 | 107.1 | 0.07 | [16 empty] | 116.24 | 0.07 | 100.3 | 0.04 | 115.97 | 0.07 | 106.55 | 0.06 | [16 empty] | 48.72 | 0.46 | [12 empty] | 189.72 | 0.09 | 93.64 | 0.1 | 93.18 | 0.1 | 75.01 | 0.07 | 75.41 | 0.05 | 75.01 | 0.06 | 75.41 | 0.08 | 75.31 | 0.07 | 75.4 | 0.08 | 75.24 | 0.07 | 79.18 | 0.08 | 76.84 | 0.06 | 76.83 | 0.06 | 78.1 | 0.11 | 78.06 | 0.1 | 77.33 | 0.07 | 76.7 | 0.07 | 75.57 | 0.07 | 75.2 | 0.09 | 75.53 | 0.08 | 75.05 | 0.08 | 75.43 | 0.06 | 75.29 | 0.06 | 75.32 | 0.06 | 75.68 | 0.05 | 75.53 | 0.06 | 75.3 | 0.03 | 76.35 | 0.06 | 76.39 | 0.07 |  |  | 75.01 | 0.07 | 75.41 | 0.06 | 75.61 | 0.07 | 75.41 | 0.07 | 75.58 |  | 75.13 | 0.06 | 81.01 | 0.06 | 81.44 | 0.08 | 78.63 | 0.1 | 75.36 | 0.08 | 75.39 | 0.06 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 75.003 | 0.009 | 61.995 | 0.014 | 56.241 | 0.011 | 53.767 | 0.013 | 94.999 | 0.026 | 75.007 | 0.026 | 2743.8 | 2.1 | 2690.7 | 2.1 | 0.555 | 0.003 | -0.249 | 0.002 | 0.143 | 0.003 | 1.5476 | 0.0023 | 29.225 | 0.001 | 9093 | 26 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.2919 | 12595.4719 | 175.4379 | 0 | 0 | 12595.4719 | 0.0087766 | 27.605 | 54.9491 | 14.0999 | 13.0704 | 0.013927 | 38.1639 | 0.0087766 | 27.605 | 0.0082005 | 22.4033 | 75.003 | 61.995 | 22.0886 | 69481.9578 | 60621.1444 | 7773 | 0.38181 | 65575.5673 | 56714.7539 | 7.2117 | 0.14801 | -5.5164 | -20.0539 | 51.4652 | 69481.9578 | 65517.4658 | 3964.492 | 0 | 69481.9578 | 100%
2 | T2-MF35-115C1-115C2-90A-95-CE | 75T0007 | T2-MF35-115C1-115C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 848 | 5.75 |  | 0 | 0 | CUST 5 | 10/9/2014 | 1:55:01 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.36 lbs/CK2: 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 461.1 | 1.2 | 15.3 | 0 | 58963 | 71 | 58196 | 371 | 11529 | 182 | 70504 | 175 | 8.3102 | 865 | [38 empty] | MF35, 115% charge CK1 and CK2, 87.5% airflow (360 cfm/ton), closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (848 rpm), adjust code tester speed--to match total static of run T2-MFB2-2700-95-C-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 4.5 turns open: AX 35 belt: 100% inlet-outlet Meriam | 74.99 | 0.012 | 62.002 | 0.025 | 95.005 | 0.011 | 75.005 | 0.031 | 74.72 | 0.12 | 55.61 | 0.05 | 59.78 | 0.01 | 0.2 | 0.004 | 1.0656 | 0.0027 | 58963 | 71 | 11529 | 182 | 8.311 | 0.031 | [6 empty] | 461.1 | 2.5 | 461.8 | 2.5 | 458.9 | 2.4 | 15.3 | 0.1 | 13 | 0 | 12.7 | 0.1 | 6961.3 | 52.4 | 3128.8 | 60.4 | 1522.3 | 40.7 | 460 |  | 460 |  | 460 |  | 3 |  | 3 |  | 2.9 |  | 0.81 | 460 |  | 460 |  | 460 |  | 5.2 |  | 4.8 |  | 4.5 |  | 3210 |  | 0.83 | 460 | 460 | 460 | 5.2 | 4.7 | 4.5 | 3140 | 0.82 | 460.2 |  | 1.6 |  | 701.5 |  | 85 |  | 8486.5 | [14 empty] | 228.6 | 0.13 | 100.47 | 0.06 | 110.61 | 0.04 | 10.14 | 0.07 | 250.3 | 0.13 | 174.58 | 0.17 | 117.14 | 0.04 | 57.44 | 0.17 | 222.6 | 0.05 | 99.32 | 0.05 | 108.72 | 0.05 | 9.4533 | 0.05 | 74.51 | 0.05 | 47.69 | 0.27 | 43.8 | 0.03 | 3.89 | 0.28 | 73.88 | 0.06 | 54.27 | 0.32 | 43.38 | 0.04 | 10.89 | 0.33 | [46 empty] | 261.75 | 0.15 | 177.21 | 0.32 | 120.43 | 0.04 | 56.78 | 0.35 | 246.22 | 0.33 | 115.94 | 0.1 | 23.2 | 0.09 | 236.6 | 0.05 | 98.77 | 0.05 | 113.06 | 0.05 | 14.33 | 0.05 | 77.03 | 0.2 | 45.43 | 0.12 | 3.51 | 1.24 | 76.46 | 0.19 | 55.62 | 0.28 | 45.06 | 0.12 | 10.56 | 0.29 | 100.49 | 0.06 | [28 empty] | 100.62 | 0.07 | 100.49 | 0.06 | 98.3 | 0.05 | 98.6 | 0.06 | 55.07 | 0.06 | 55.66 | 0.05 | 55.52 | 0.04 | 55.23 | 0.04 | 55.29 | 0.04 |  |  | 99.98 | 0.07 | 97.9 | 0.06 | 48.67 | 0.52 | 53.75 | 0.34 | 177.21 | 0.39 | 96.19 | 0.06 | 92.43 | 0.03 | 49.19 | 1.26 | 57.5 | 0.64 | 99.32 | 0.05 | 98.77 | 0.05 | 93.45 | 0.11 | 100.99 | 0.08 | 101.07 | 0.06 | 99.45 | 0.04 | 99.67 | 0.04 | 98.3 | 0.05 | 98.6 | 0.06 | [16 empty] | 100.47 | 0.06 | 92.74 | 0.04 | 100.62 | 0.07 | 100.49 | 0.06 | [16 empty] | 48.94 | 1.14 | [12 empty] | 175.56 | 0.19 | 95.6 | 0.06 | 95.34 | 0.07 | 75.11 | 0.05 | 75.45 | 0.05 | 75.01 | 0.05 | 75.61 | 0.06 | 75.47 | 0.05 | 75.54 | 0.07 | 75.34 | 0.06 | 78.79 | 0.08 | 76.9 | 0.06 | 76.9 | 0.06 | 78.05 | 0.12 | 78.08 | 0.08 | 77.5 | 0.06 | 76.68 | 0.07 | 75.51 | 0.07 | 75.97 | 0.14 | 75.53 | 0.08 | 75.01 | 0.07 | 75.23 | 0.07 | 75.13 | 0.06 | 75.28 | 0.1 | 76.71 | 0.09 | 75.33 | 0.07 | 75.73 | 0.06 | 80.16 | 0.14 | 80.08 | 0.18 |  |  | 75 | 0.06 | 75.28 | 0.05 | 75.49 | 0.06 | 75.28 | 0.06 | 75.47 |  | 75.04 | 0.06 | 80.79 | 0.04 | 80.41 | 0.19 | 78.63 | 0.08 | 75.34 | 0.08 | 75.2 | 0.06 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 74.99 | 0.012 | 62.002 | 0.025 | 55.627 | 0.011 | 53.273 | 0.017 | 95.005 | 0.011 | 75.005 | 0.031 | 2759 | 3.5 | 2716.6 | 3.5 | 0.555 | 0.003 | -0.249 | 0.002 | 0.2 | 0.004 | 1.0656 | 0.0027 | 29.308 | 0.001 | 8484 | 24 | 1350 |  | 0 | 0 | 13.029 | 0.231 | 1.3149 | 12681.3288 | 177.1266 | 0 | 0 | 12681.3288 | 0.0087843 | 27.6102 | 54.3121 | 14.1001 | 13.0538 | 0.013924 | 38.1619 | 0.0087843 | 27.6102 | 0.0080693 | 22.1113 | 74.99 | 62.002 | 21.791 | 73795.0728 | 62933.5008 | 7134 | 0.32995 | 69792.0559 | 58930.4839 | 8.2263 | 0.1386 | -5.8192 | -20.6779 | 50.985 | 73795.0728 | 69733.4883 | 4061.5845 | 0 | 73795.0728 | 100%
2 | T2-MF37-85C1-85C2-90A-95-CE | 75T0008 | T2-MF37-85C1-85C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 848 | 5.75 |  | 0 | 0 | CUST 5 | 10/9/2014 | 3:34:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.44 lbs/CK2: 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 461.2 | 1.5 | 15 | 0 | 55559 | 83 | 54761 | 271 | 8629 | 201 | 64196 | 181 | 7.8164 | 865 |  |  | 6.7648 | [35 empty] | MF37, 85% charge CK1 and CK2, 87.5% airflow (360 cfm/ton), 2 HP fan motor,--4.5 turns, 5.75" AK59 pulley (848 rpm), adjust code tester speed to match--total static of run T2-MF20-3000-95-C-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 4.5 turns open: AX 35 belt: 100% inlet-outlet Meriam | 74.998 | 0.012 | 62.006 | 0.031 | 94.999 | 0.011 | 74.994 | 0.026 | 74.69 | 0.11 | 56.66 | 0.08 | 60.62 | 0.01 | 0.197 | 0.003 | 1.0651 | 0.0024 | 55559 | 83 | 8629 | 201 | 7.817 | 0.03 | [6 empty] | 461.2 | 2.6 | 461.7 | 2.6 | 458.9 | 2.6 | 15 | 0.1 | 12.7 | 0 | 12.4 | 0.1 | 6802.1 | 55.6 | 3120.9 | 63.2 | 1410.6 | 43.1 | 460 |  | 460 |  | 460 |  | 3 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.7 |  | 4.4 |  | 3120 |  | 0.83 | 460 | 460 | 460 | 5 | 4.5 | 4.3 | 2970 | 0.8 | 460.3 |  | 1.6 |  | 702.5 |  | 85 |  | 8217.5 | [14 empty] | 211 | 0.16 | 104.6 | 0.09 | 104.98 | 0.05 | 0.38 | 0.09 | 242.8 | 0.14 | 191.34 | 0.05 | 114.93 | 0.04 | 76.42 | 0.05 | 199.8 | 0.05 | 100.67 | 0.04 | 101.23 | 0.05 | 0.57667 | 0.05 | 71.48 | 0.04 | 68.38 | 0.03 | 41.78 | 0.02 | 26.6 | 0.03 | 70.88 | 0.04 | 70.77 | 0.02 | 41.38 | 0.02 | 29.38 | 0.03 | [46 empty] | 245.91 | 0.15 | 171.62 | 0.12 | 115.85 | 0.05 | 55.77 | 0.13 | 223.25 | 0.19 | 108.93 | 0.06 | 0.85 | 0.08 | 211.8 | 0.05 | 100.31 | 0.05 | 105.25 | 0.05 | 4.94 | 0.05 | 77.43 | 0.05 | 45.68 | 0.03 | 3.54 | 0.43 | 76.83 | 0.06 | 71.74 | 0.02 | 45.3 | 0.04 | 26.44 | 0.04 | 106.82 | 0.07 | [28 empty] | 103.07 | 0.08 | 102.5 | 0.07 | 106.82 | 0.07 | 106.83 | 0.1 | 56.09 | 0.06 | 56.75 | 0.06 | 56.61 | 0.06 | 56.24 | 0.05 | 56.33 | 0.04 |  |  | 103.19 | 0.06 | 99.13 | 0.08 | 68.85 | 0.08 | 70.33 | 0.06 | 171.6 | 0.12 | 104.14 | 0.08 | 99.68 | 0.04 | 49.17 | 0.42 | 58.95 | 0.22 | 100.67 | 0.04 | 108.08 | 0.08 | 93.47 | 0.08 | 104.59 | 0.04 | 103 | 0.05 | 107.86 | 0.04 | 107.78 | 0.07 | 102.5 | 0.07 | 106.83 | 0.1 | [16 empty] | 104.6 | 0.09 | 108.08 | 0.08 | 103.07 | 0.08 | 106.82 | 0.07 | [16 empty] | 49.22 | 0.41 | [12 empty] | 192.44 | 0.06 | 95.46 | 0.08 | 95.26 | 0.07 | 75.03 | 0.07 | 75.41 | 0.05 | 74.99 | 0.05 | 75.46 | 0.09 | 75.33 | 0.09 | 75.44 | 0.08 | 75.27 | 0.07 | 78.83 | 0.07 | 76.9 | 0.06 | 76.89 | 0.05 | 78.02 | 0.1 | 78.06 | 0.11 | 77.47 | 0.1 | 76.73 | 0.07 | 75.44 | 0.08 | 75.6 | 0.84 | 75.48 | 0.1 | 74.95 | 0.07 | 75.24 | 0.05 | 75.12 | 0.05 | 75.25 | 0.07 | 76.8 | 0.07 | 75.32 | 0.06 | 75.78 | 0.06 | 80.37 | 0.13 | 80.19 | 0.17 |  |  | 74.99 | 0.06 | 75.32 | 0.04 | 75.5 | 0.05 | 75.3 | 0.05 | 75.44 |  | 75 | 0.04 | 80.86 | 0.04 | 80.76 | 0.13 | 78.61 | 0.1 | 75.25 | 0.09 | 75.2 | 0.05 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 74.998 | 0.012 | 62.006 | 0.031 | 56.702 | 0.014 | 54.106 | 0.021 | 94.999 | 0.011 | 74.994 | 0.026 | 2761.2 | 3.2 | 2712.6 | 3.1 | 0.557 | 0.002 | -0.249 | 0.002 | 0.197 | 0.003 | 1.0651 | 0.0024 | 29.299 | 0.001 | 8213 | 24 | 1340 |  | 0 | 0 | 13.029 | 0.231 | 1.3051 | 12663.4119 | 177.5031 | 0 | 0 | 12663.4119 | 0.0087851 | 27.613 | 55.3969 | 14.0998 | 13.0827 | 0.013916 | 38.1513 | 0.0087851 | 27.613 | 0.0082826 | 22.6049 | 74.998 | 62.006 | 22.2869 | 67447.1344 | 59571.9873 | 6873 | 0.34779 | 63479.5327 | 55604.3855 | 7.7292 | 0.15675 | -5.3261 | -19.6011 | 51.7534 | 67447.1344 | 63419.9179 | 4027.2165 | 0 | 67447.1344 | 100%
2 | T2-MFB2-100C1-100C2-90A-95-CE | 75T0009 | T2-MFB2-100C1-100C2-90A-95-CE | closed | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 0 | 0 | CUST 5 | 10/7/2014 | 22:38:52 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs CK2- 6.20 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 1.3 | 15.2 | 0 | 57713 | 68 | 56775 | 329 | 11019 | 98 | 68743 | 126 | 8.2495 | 866 |  |  | 6.9258 | [35 empty] | MFB2, 100% charge CK1 and CK2, 87.5% airflow, 360 cfm/ton, closed damper,--2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (865 rpm), adjust code tester speed to match--total static of run T2-MFB2-100C1-100C2-88A-95-CE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 4.5 turns open: 100% inlet-outlet Meriam | 75.003 | 0.013 | 62.002 | 0.017 | 94.997 | 0.017 | 74.996 | 0.027 | 74.76 | 0.13 | 55.98 | 0.06 | 59.74 | 0.02 | 0.193 | 0.003 | 1.0537 | 0.0022 | 57713 | 68 | 11019 | 98 | 8.25 | 0.028 | [6 empty] | 461 | 2.7 | 461.6 | 2.7 | 459 | 2.6 | 15.2 | 0.1 | 12.8 | 0 | 12.6 | 0.1 | 6891.2 | 56 | 3135.9 | 63.9 | 1441.8 | 43.6 | 460 |  | 460 |  | 460 |  | 3 |  | 0.29 |  | 0.29 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.24 |  | 4.8 |  | 4.4 |  | 3160 |  | 0.82 | 460 | 460 | 460 | 5.1 | 4.6 | 4.4 | 3060 | 0.81 | 460 |  | 1.6 |  | 703.5 |  | 85 |  | 8328.5 | [14 empty] | 220.6 | 0.15 | 107.57 | 0.08 | 108.08 | 0.05 | 0.51 | 0.06 | 249.12 | 0.16 | 175.05 | 0.06 | 116.79 | 0.05 | -58.26 | 0.08 | 213.5 | 0.05 | 104.68 | 0.06 | 105.79 | 0.05 | 1.07 | 0.05 | 74.97 | 0.04 | 49.41 | 0.28 | 44.08 | 0.02 | 5.33 | 0.28 | 74.34 | 0.04 | 55.88 | 0.12 | 43.67 | 0.02 | 12.21 | 0.11 | [46 empty] | 252.38 | 0.18 | 173.96 | 0.3 | 117.73 | 0.05 | 56.22 | 0.33 | 236.35 | 0.34 | 112.99 | 0.11 | 11.52 | 0.1 | 226.3 | 0.05 | 95.21 | 0.06 | 109.89 | 0.05 | 14.68 | 0.05 | 76.73 | 0.2 | 45.21 | 0.12 | 3.73 | 1.07 | 76.29 | 0.18 | 57.29 | 0.1 | 44.94 | 0.11 | 12.36 | 0.16 | 101.09 | 0.08 | [28 empty] | 106.9 | 0.08 | 106.35 | 0.07 | 101.09 | 0.08 | 101.37 | 0.08 | 55.37 | 0.06 | 55.94 | 0.05 | 55.81 | 0.04 | 55.61 | 0.04 | 55.67 | 0.04 |  |  | 106.1 | 0.06 | 103.82 | 0.08 | 50.73 | 0.36 | 55.67 | 0.14 | 173.99 | 0.37 | 98.71 | 0.07 | 94.68 | 0.05 | 48.96 | 1.02 | 57.89 | 0.62 | 104.68 | 0.06 | 101.47 | 0.09 | 92.9 | 0.2 | 107.28 | 0.07 | 106.99 | 0.06 | 102.06 | 0.05 | 102.17 | 0.05 | 106.35 | 0.07 | 101.37 | 0.08 | [16 empty] | 107.57 | 0.08 | 101.47 | 0.09 | 106.9 | 0.08 | 101.09 | 0.08 | [16 empty] | 48.91 | 0.97 | [12 empty] | 176.07 | 0.09 | 95.67 | 0.09 | 95.68 | 0.09 | 75.18 | 0.06 | 75.5 | 0.05 | 75.02 | 0.06 | 75.71 | 0.07 | 75.55 | 0.06 | 75.6 | 0.07 | 75.39 | 0.07 | 78.45 | 0.08 | 76.79 | 0.06 | 76.82 | 0.05 | 77.75 | 0.1 | 77.98 | 0.08 | 77.46 | 0.07 | 76.76 | 0.07 | 75.48 | 0.07 | 75.34 | 0.24 | 75.48 | 0.09 | 74.98 | 0.07 | 75.19 | 0.07 | 75.11 | 0.07 | 75.2 | 0.07 | 76.78 | 0.08 | 75.29 | 0.07 | 75.87 | 0.06 | 80.57 | 0.13 | 80.32 | 0.18 |  |  | 75.01 | 0.06 | 75.25 | 0.06 | 75.45 | 0.07 | 75.23 | 0.07 | 75.38 |  | 74.98 | 0.06 | 80.52 | 0.06 | 80.44 | 0.07 | 78.51 | 0.08 | 75.3 | 0.08 | 75.18 | 0.07 | [62 empty] | T2-TRN-88A-55-CE-DM-2 | 75.003 | 0.013 | 62.002 | 0.017 | 55.915 | 0.011 | 53.455 | 0.017 | 94.997 | 0.017 | 74.996 | 0.027 | 2745.9 | 2.9 | 2698.8 | 2.8 | 0.555 | 0.002 | -0.249 | 0.002 | 0.193 | 0.003 | 1.0537 | 0.0022 | 29.257 | 0.001 | 8333 | 23 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.2894 | 12613.8156 | 175.966 | 0 | 0 | 12613.8156 | 0.0087812 | 27.61 | 54.6256 | 14.0998 | 13.0614 | 0.013918 | 38.1533 | 0.0087812 | 27.61 | 0.0081028 | 22.2178 | 75.003 | 62.002 | 21.9037 | 71978.8782 | 61688.8468 | 7013 | 0.33253 | 68074.2902 | 57784.2587 | 8.1692 | 0.14799 | -5.7064 | -20.3774 | 51.0862 | 71978.8782 | 68016.9212 | 3961.957 | 0 | 71978.8782 | 100%
2 | T2-MFR10-85C1-85C2-90A-95-CC2F | 75T0010 | T2-MFR10-85C1-85C2-90A-95-CC2F | 2 finger | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 30 | 0 | CUST 5 | 10/15/2014 | 20:03:47 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.44 lbs/CK2: 5.3 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.3 | 6.4 | 6.2 | 459.4 | 0 | 14.9 | 0 | 42188 | 50 | 41543 | 332 | -6301 | 103 | 35881 | 92 | 4.1829 | 864 |  |  | 4.9182 | [35 empty] | MFR10, Restrict CK1 per MFR1, 85% charge C1, 85% charge C2, 6V open economizer damper,--90% airflow (360 cfm/ton), 4.5 turns, 5.75" AK59 pulley (865 rpm), 30% condenser coil blockage,--2 HP fan motor, adjust code tester speed to match total static of run | W/Econ: 2 stages:95/75 amb:2HP blwr mtr 5.75` mtr. pulley:4.5 turns open:AX 35 belt:100% inlet-outlet Meriam:adjusted CK1 liq ln sv.valve 8.5 turns.Rstrct CK1 to achieve 22 psig suction from T2-RBASE-100C1-100C2-100A-95-CE: cond coil blk 21. 6V Eco | 75.003 | 0.012 | 62.021 | 0.015 | 95.003 | 0.028 | 75.001 | 0.012 | 74.71 | 0.12 | 61.14 | 0.05 | 64.09 | 0.01 | 0.159 | 0.004 | 1.641 | 0.0025 | 42188 | 50 | -6301 | 103 | 4.183 | 0.016 | [6 empty] | 459.4 | 2.1 | 460.7 | 2.1 | 460.6 | 2.1 | 14.9 | 0 | 13 | 0 | 13.3 | 0 | 6790 | 41.2 | 3308 | 53.6 | 1788.3 | 32.5 | 460 |  | 460 |  | 460 |  | 2.8 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.1 |  | 5.1 |  | 4.6 |  | 3300 |  | 0.84 | 460 | 460 | 460 | 5.1 | 5 | 4.6 | 3210 | 0.83 | 458.6 |  | 1.6 |  | 660.7 |  | 85 |  | 8585.7 | [14 empty] | 239.36 | 0.39 | 108.71 | 0.16 | 113.9 | 0.12 | 5.19 | 0.1 | 253 | 0.45 | 235.54 | 0.11 | 117.92 | 0.13 | 117.61 | 0.1 | 146.1 | 0.05 | 81.67 | 0.1 | 80.92 | 0.05 | -0.75 | 0.05 | 50.84 | 0.07 | 71.53 | 0.02 | 26.45 | 0.06 | 45.09 | 0.06 | 50.48 | 0.07 | 75.35 | 0.02 | 26.15 | 0.06 | 49.2 | 0.05 | [46 empty] | 269.7 | 0.45 | 178.89 | 0.17 | 122.65 | 0.12 | 56.24 | 0.2 | 244.37 | 0.49 | 115.4 | 0.15 | 3.19 | 0.18 | 233.4 | 0.05 | 106.97 | 0.12 | 112.09 | 0.05 | 5.12 | 0.05 | 83.63 | 0.07 | 49.56 | 0.04 | 3.17 | 0.59 | 83.14 | 0.08 | 62.12 | 0.41 | 49.27 | 0.05 | 12.85 | 0.45 | 112.55 | 0.2 | [28 empty] | 83.62 | 0.12 | 84.7 | 0.1 | 112.55 | 0.2 | 112.92 | 0.19 | 60.97 | 0.05 | 61.31 | 0.04 | 61.05 | 0.05 | 60.97 | 0.05 | 60.91 | 0.05 |  |  | 108.87 | 0.16 | 79.9 | 0.1 | 72.63 | 0.08 | 75.91 | 0.06 | 179.02 | 0.18 | 112.5 | 0.2 | 105.56 | 0.11 | 53.18 | 0.54 | 63.12 | 0.36 | 81.67 | 0.1 | 106.97 | 0.12 | 93.07 | 0.15 | 107.77 | 0.12 | 84.02 | 0.11 | 111.94 | 0.11 | 112.56 | 0.14 | 84.7 | 0.1 | 112.92 | 0.19 | [16 empty] | 108.71 | 0.16 | 112.2 | 0.22 | 83.62 | 0.12 | 112.55 | 0.2 | [16 empty] | 52.74 | 0.55 | [12 empty] | 237.33 | 0.16 | 95.54 | 0.32 | 93.82 | 0.19 | 75.07 | 0.08 | 75.35 | 0.07 | 74.97 | 0.06 | 75.49 | 0.1 | 75.38 | 0.09 | 75.48 | 0.09 | 75.31 | 0.09 | 85.66 | 0.16 | 86.47 | 0.15 | 86.95 | 0.1 | 82.49 | 0.16 | 82.83 | 0.17 | 82.24 | 0.25 | 80.12 | 0.28 | 79.31 | 0.09 | 79.29 | 0.12 | 79.58 | 0.12 | 76.79 | 0.14 | 75.25 | 0.07 | 76.37 | 0.08 | 76.63 | 0.07 | 76.51 | 0.07 | 75.32 | 0.06 | 75.33 | 0.06 | 76.3 | 0.13 | 76.95 | 0.07 |  |  | 74.98 | 0.06 | 75.45 | 0.06 | 75.56 | 0.07 | 75.37 | 0.07 | 75.42 |  | 75.04 | 0.06 | 87.85 | 0.1 | 85.74 | 0.12 | 82.65 | 0.12 | 75.74 | 0.1 | 75.23 | 0.07 | [62 empty] | T2-TRN-88A-55-2F-DM-2 | 75.003 | 0.012 | 62.021 | 0.015 | 61.222 | 0.007 | 57.81 | 0.009 | 95.003 | 0.028 | 75.001 | 0.012 | 2832.3 | 2.2 | 2761.4 | 2.1 | 0.501 | 0.003 | -0.181 | 0.002 | 0.159 | 0.004 | 1.641 | 0.0025 | 29.328 | 0 | 8578 | 25 | 1330 |  | 0 | 0 | 13.029 | 0.231 | 1.2898 | 12868.3369 | 162.5295 | 0 | 0 | 12868.3369 | 0.0087938 | 27.6238 | 59.9322 | 14.1 | 13.2059 | 0.013921 | 38.158 | 0.0087938 | 27.6238 | 0.0093862 | 24.9072 | 75.003 | 62.021 | 24.5923 | 39010.2986 | 46544.6617 | 7248 | 0.63413 | 35025.7217 | 42560.0848 | 4.0832 | 0.21293 | -3.0315 | -15.0708 | 55.8551 | 39010.2986 | 34957.7194 | 4052.5792 | 0 | 39010.2986 | 100%
2 | T2-MFR12-115C1-115C2-90A-95-CC2F | 75T0011 | T2-MFR12-115C1-115C2-90A-95-CC2F | 2 finger | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 30 | 0 | CUST 5 | 10/15/2014 | 23:06:04 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.4 lbs/CK2: 7.1 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.4 | 7.1 | 6.4 | 6.2 | 460 | 0 | 15.7 | 0 | 48340 | 87 | 47810 | 466 | -2016 | 143 | 46323 | 137 | 5.1056 | 864 |  |  | 5.3279 | [35 empty] | MFR12, Restrict CK1 per MFR1, 115% charge C1, 115% charge C2, 6V open economizer damper,--90% airflow (360 cfm/ton), 4.5 turns, 5.75" AK59 pulley (865 rpm), 30% condenser coil blockage,--2 HP fan motor, adjust code tester speed to match total static of ru | W/Econ: 2 stages:95/75 amb:2HP blwr mtr 5.75` mtr. pulley:4.5 turns open:AX 35 belt:100% inlet-outlet Meriam:adjusted CK1 liq ln sv.valve 8.5 turns.Rstrct CK1 to achieve 22 psig suction from T2-RBASE-100C1-100C2-100A-95-CE: cond coil blk 21. 6V Eco | 74.97 | 0.022 | 61.997 | 0.023 | 94.992 | 0.032 | 75.004 | 0.02 | 74.95 | 0.15 | 59.43 | 0.06 | 62.67 | 0.03 | 0.164 | 0.004 | 1.6442 | 0.0024 | 48340 | 87 | -2016 | 143 | 5.106 | 0.022 | [6 empty] | 460 | 2 | 461.5 | 2 | 459.9 | 2 | 15.7 | 0 | 13.5 | 0 | 13.7 | 0 | 7169.6 | 41 | 3245 | 49.7 | 1903.5 | 31.8 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.5 | 460 |  | 460 |  | 460 |  | 5.4 |  | 5.3 |  | 4.8 |  | 3510 |  | 0.85 | 460 | 460 | 460 | 5.5 | 5.2 | 4.9 | 3510 | 0.84 | 459 |  | 1.6 |  | 658.8 |  | 85 |  | 9073.8 | [14 empty] | 260.09 | 0.36 | 100.26 | 0.13 | 119.96 | 0.1 | 19.7 | 0.12 | 272.8 | 0.37 | 219.18 | 0.08 | 123.51 | 0.1 | 95.67 | 0.1 | 155.9 | 0.05 | 85.58 | 0.08 | 84.97 | 0.05 | -0.49667 | 0.05 | 64.36 | 0.09 | 71 | 0.03 | 36.85 | 0.07 | 34.15 | 0.08 | 63.88 | 0.09 | 74.22 | 0.03 | 36.5 | 0.06 | 37.72 | 0.06 | [46 empty] | 294.92 | 0.4 | 188.85 | 0.3 | 129.42 | 0.11 | 59.43 | 0.32 | 278.68 | 0.56 | 125.11 | 0.15 | 25.32 | 0.17 | 268.6 | 0.05 | 95.42 | 0.08 | 122.34 | 0.05 | 26.9433 | 0.05 | 82.75 | 0.22 | 49.02 | 0.13 | 3.32 | 1.16 | 82.38 | 0.15 | 60.34 | 0.82 | 48.79 | 0.09 | 11.55 | 0.86 | 100.37 | 0.14 | [28 empty] | 87.64 | 0.11 | 88.72 | 0.09 | 100.37 | 0.14 | 101.31 | 0.12 | 58.78 | 0.06 | 59.57 | 0.05 | 59.38 | 0.05 | 59.05 | 0.03 | 59.08 | 0.03 |  |  | 100.3 | 0.11 | 83.9 | 0.08 | 72.29 | 0.05 | 75.02 | 0.05 | 189.1 | 0.38 | 100.1 | 0.12 | 94.24 | 0.09 | 52.92 | 1.09 | 61.82 | 0.76 | 85.58 | 0.08 | 95.42 | 0.08 | 92.73 | 0.18 | 100.36 | 0.11 | 88.01 | 0.09 | 101.5 | 0.11 | 102.08 | 0.13 | 88.72 | 0.09 | 101.31 | 0.12 | [16 empty] | 100.26 | 0.13 | 99.79 | 0.14 | 87.64 | 0.11 | 100.37 | 0.14 | [16 empty] | 52.35 | 1.04 | [12 empty] | 220.96 | 0.12 | 95.96 | 0.31 | 93.86 | 0.19 | 75.28 | 0.07 | 75.51 | 0.06 | 75.12 | 0.07 | 75.84 | 0.08 | 75.64 | 0.08 | 75.72 | 0.09 | 75.52 | 0.08 | 85.51 | 0.16 | 86.32 | 0.14 | 86.79 | 0.11 | 82.38 | 0.19 | 82.78 | 0.16 | 82.21 | 0.24 | 80.05 | 0.26 | 79.27 | 0.09 | 79.33 | 0.13 | 79.57 | 0.12 | 76.87 | 0.14 | 75.16 | 0.09 | 76.27 | 0.1 | 76.59 | 0.08 | 76.5 | 0.08 | 75.18 | 0.09 | 75.25 | 0.08 | 76.26 | 0.14 | 76.89 | 0.08 |  |  | 75.14 | 0.08 | 75.36 | 0.07 | 75.61 | 0.08 | 75.41 | 0.09 | 75.44 |  | 75.1 | 0.09 | 87.59 | 0.13 | 85.47 | 0.11 | 82.58 | 0.13 | 75.82 | 0.1 | 75.15 | 0.1 | [62 empty] | T2-TRN-88A-55-2F-DM-2 | 74.97 | 0.022 | 61.997 | 0.023 | 59.282 | 0.009 | 56.52 | 0.018 | 94.992 | 0.032 | 75.004 | 0.02 | 2831.3 | 2 | 2768.9 | 2 | 0.5 | 0.002 | -0.181 | 0.004 | 0.164 | 0.004 | 1.6442 | 0.0024 | 29.322 | 0.001 | 9073 | 25 | 1310 |  | 0 | 0 | 13.029 | 0.231 | 1.2631 | 12914.3012 | 162.6456 | 0 | 0 | 12914.3012 | 0.0087857 | 27.6069 | 58.0189 | 14.0998 | 13.1543 | 0.013926 | 38.1611 | 0.0087857 | 27.6069 | 0.0090705 | 24.0903 | 74.97 | 61.997 | 23.782 | 49395.5691 | 52538.6668 | 7763 | 0.53639 | 45479.6486 | 48622.7463 | 5.0126 | 0.1661 | -3.8249 | -16.9511 | 54.6426 | 49395.5691 | 45415.1042 | 3980.4649 | 0 | 49395.5691 | 100%
2 | T2-MFR8-100C1-100C2-90A-95-CC2F | 75T0012 | T2-MFR8-100C1-100C2-90A-95-CC2F | 2 finger | on | on | 4.5 turns | unsealed | unsealed | 865 | 5.75 |  | 30 | 0 | CUST 5 | 10/15/2014 | 16:34:39 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 15.4 | 0 | 46104 | 46 | 45456 | 353 | -3940 | 160 | 42159 | 158 | 4.7653 | 865 |  |  | 5.2113 | [35 empty] | MFR8, Restrict CK1 per MFR1, 100% charge C1, 100% charge C2, 6V open economizer damper,--90% airflow (360 cfm/ton), 4.5 turns, 5.75" AK59 pulley (865 rpm), 30% condenser coil blockage,--2 HP fan motor, adjust code tester speed to match total static of run | W/Econ: 2 stages:95/75 amb:2HP blwr mtr 5.75` mtr. pulley:4.5 turns open:AX 35 belt:100% inlet-outlet Meriam:adjusted CK1 liq ln sv.valve 8.5 turns.Rstrct CK1 to achieve 22 psig suction from T2-RBASE-100C1-100C2-100A-95-CE: cond coil blk 21. 6V Eco | 74.985 | 0.011 | 62.001 | 0.026 | 94.961 | 0.047 | 75.009 | 0.021 | 74.84 | 0.14 | 60.11 | 0.08 | 63.09 | 0.01 | 0.171 | 0.004 | 1.6569 | 0.0025 | 46104 | 46 | -3940 | 160 | 4.766 | 0.022 | [6 empty] | 460.2 | 2 | 460.9 | 2 | 459.8 | 2 | 15.4 | 0 | 13.4 | 0 | 13.4 | 0 | 7013.4 | 42.3 | 3251.9 | 49.1 | 1833.6 | 33.4 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.49 | 460 |  | 459 |  | 459 |  | 5.3 |  | 5.2 |  | 4.7 |  | 3410 |  | 0.85 | 460 | 459 | 459 | 5.3 | 5.1 | 4.7 | 3340 | 0.84 | 459.3 |  | 1.6 |  | 659.9 |  | 85 |  | 8814.9 | [14 empty] | 252.58 | 0.29 | 102.71 | 0.13 | 117.8 | 0.09 | 15.1 | 0.09 | 265.38 | 0.33 | 224.36 | 0.06 | 121.45 | 0.09 | 102.91 | 0.07 | 151.7 | 0.05 | 84.29 | 0.07 | 83.27 |  | -1.02 |  | 59.83 | 0.06 | 71.7 | 0.04 | 33.52 | 0.04 | 38.18 | 0.05 | 59.4 | 0.06 | 74.96 | 0.03 | 33.2 | 0.04 | 41.76 | 0.05 | [46 empty] | 281.19 | 0.34 | 183.03 | 0.31 | 125.79 | 0.09 | 57.24 | 0.34 | 263.34 | 0.51 | 120.88 | 0.14 | 17.28 | 0.15 | 250 | 0.07 | 99.35 | 0.07 | 117.06 | 0.07 | 17.71 |  | 83.34 | 0.18 | 49.38 | 0.11 | 3.78 | 1.41 | 82.93 | 0.17 | 61.16 | 0.82 | 49.14 | 0.1 | 12.03 | 0.88 | 104.09 | 0.14 | [28 empty] | 86.34 | 0.11 | 87.43 | 0.1 | 104.09 | 0.14 | 104.89 | 0.14 | 59.42 | 0.08 | 60.32 | 0.06 | 60.11 | 0.05 | 59.62 | 0.03 | 59.69 | 0.03 |  |  | 102.73 | 0.11 | 82.77 | 0.08 | 72.84 | 0.06 | 75.7 | 0.05 | 183.26 | 0.37 | 103.87 | 0.13 | 98.3 | 0.07 | 53.48 | 1.32 | 62.33 | 0.77 | 84.29 | 0.07 | 99.35 | 0.07 | 92.54 | 0.14 | 102.49 | 0.08 | 86.61 | 0.07 | 104.74 | 0.08 | 105.29 | 0.09 | 87.43 | 0.1 | 104.89 | 0.14 | [16 empty] | 102.71 | 0.13 | 103.6 | 0.15 | 86.34 | 0.11 | 104.09 | 0.14 | [16 empty] | 53.07 | 1.24 | [12 empty] | 226.1 | 0.09 | 96.05 | 0.3 | 93.94 | 0.19 | 75.14 | 0.06 | 75.4 | 0.05 | 74.99 | 0.06 | 75.66 | 0.06 | 75.48 | 0.06 | 75.59 | 0.07 | 75.4 | 0.07 | 85.65 | 0.16 | 86.09 | 0.12 | 86.7 | 0.1 | 82.33 | 0.2 | 83.19 | 0.18 | 82.81 | 0.24 | 80.9 | 0.37 | 79.54 | 0.1 | 79.43 | 0.15 | 79.94 | 0.12 | 76.71 | 0.14 | 75.09 | 0.07 | 76.38 | 0.07 | 76.68 | 0.07 | 76.56 | 0.07 | 75.12 | 0.06 | 75.2 | 0.05 | 76.16 | 0.12 | 76.91 | 0.07 |  |  | 75.02 | 0.06 | 75.16 | 0.06 | 75.44 | 0.07 | 75.27 | 0.07 | 75.34 |  | 74.96 | 0.07 | 88.06 | 0.13 | 86.28 | 0.13 | 83.03 | 0.14 | 75.65 | 0.1 | 75.09 | 0.07 | [62 empty] | T2-TRN-88A-55-2F-DM-2 | 74.985 | 0.011 | 62.001 | 0.026 | 60.045 | 0.012 | 57.051 | 0.018 | 94.961 | 0.047 | 75.009 | 0.021 | 2843 | 2.2 | 2778.3 | 2.1 | 0.495 | 0.003 | -0.173 | 0.002 | 0.171 | 0.004 | 1.6569 | 0.0025 | 29.331 | 0.001 | 8847 | 25 | 1320 |  | 0 | 0 | 13.029 | 0.231 | 1.272 | 12947.5848 | 161.5658 | 0 | 0 | 12947.5848 | 0.0087848 | 27.6096 | 58.773 | 14.0991 | 13.1747 | 0.013938 | 38.1665 | 0.0087848 | 27.6096 | 0.0092065 | 24.4244 | 74.985 | 62.001 | 24.1139 | 45260.6207 | 50377.4374 | 7527 | 0.56759 | 41306.8848 | 46423.7015 | 4.669 | 0.18267 | -3.4957 | -16.212 | 55.1497 | 45260.6207 | 41240.7226 | 4019.8981 | 0 | 45260.6207 | 100%
2 | T2-TRN-88A-55-T1ER-DM | 75T0094 | T2-TRN-88A-55-T1ER-DM | 10% open | off | off | 3.5 turns | unsealed | unsealed | 864 | 6.25 |  | 0 | 0 | CUST 5 | 10/20/2014 | 23:47:42 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.1 | 0 | 3.4 | 0 | 1389 | 19 | 1050 | 96 | 2722 | 68 | 4114 | 72 | 2.9344 | 862 | 1310 |  | 0.99073 | [35 empty] | Econo 10%-open (2,8V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor, 3.5 turns, 6.25" AK64 pulley (864 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester | W/ECO: Eco set at 2.8v: No Compr:55/51 amb:2HP blwr mtr 6.25` AK64 mtr. pulley:3.5 turns open: AX38 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.006 | 0.016 | 62.004 | 0.025 | 55.02 | 0.011 | 51.004 | 0.019 | 74.75 | 0.07 | 74.42 | 0.07 | 74.81 | 0.01 | 0.155 | 0.003 | 1.5284 | 0.0022 | 1389 | 19 | 2722 | 68 | 2.935 | 0.064 | [6 empty] | 460.1 | 2 | 461.2 | 2 | 460 | 2 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1424 | 16.7 | 1097.7 | 18.6 | -8.9 | 2.9 | 460 |  | 460 |  | 460 |  | 2.9 |  | 3 |  | 2.9 |  | 0.48 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 1395 | [14 empty] | 96.64 | 0.01 | 55.53 | 0.07 | 57.14 | 0.01 | 1.62 | 0.07 | 96.12 | 0.02 | 57.44 | 0.02 | 56.84 | 0.01 | 0.6 | 0.02 |  |  | 69.84 | 0.03 |  |  |  |  | 96.2 | 0.02 | 71.58 | 0.01 | 56.89 | 0.01 | 14.69 | 0.02 | 95.78 | 0.1 | 57.1 | 0.01 | 56.69 | 0.05 | 0.42 | 0.05 | [46 empty] | 96.29 | 0.03 | 56.56 | 0.02 | 56.94 | 0.01 | 0.38 | 0.03 | 96.93 | 0.02 | 57.29 | 0.01 | 1.06 | 0.03 |  |  | 72.95 | 0.02 |  |  |  |  | 96.11 | 0.01 | 56.84 | 0.01 | 14.47 | 0.04 | 96.22 | 0.01 | 58.87 | 0.02 | 56.9 | 0.01 | 1.97 | 0.02 | 58.09 | 0.05 | [28 empty] | 56.64 | 0.06 | 58.12 | 0.06 | 58.09 | 0.05 | 59.58 | 0.07 | 74.5 | 0.06 | 74.35 | 0.05 | 74.23 | 0.04 | 74.63 | 0.05 | 74.66 | 0.05 |  |  | 55.03 | 0.02 | 70.05 | 0.07 | 71.5 | 0.06 | 57.4 | 0.04 | 56.97 | 0.03 | 56.38 | 0.03 | 73.53 | 0.02 | 72.43 | 0.02 | 60.7 | 0.03 | 69.84 | 0.03 | 72.95 | 0.02 | 55.13 | 0.07 | 56.11 | 0.02 | 59.12 | 0.03 | 56.79 | 0.01 | 57.56 | 0.01 | 58.12 | 0.06 | 59.58 | 0.07 | [16 empty] | 55.53 | 0.07 | 56.24 | 0.03 | 56.64 | 0.06 | 58.09 | 0.05 | [16 empty] | 71.32 | 0.04 | [12 empty] | 57.33 | 0.03 | 56.63 | 0.12 | 56.4 | 0.14 | 75.12 | 0.04 | 74.83 | 0.02 | 74.73 | 0.03 | 75.42 | 0.04 | 75.42 | 0.05 | 75.4 | 0.03 | 75.23 | 0.03 | 73.18 | 0.05 | 73.83 | 0.03 | 73.5 | 0.03 | 74.79 | 0.05 | 73.44 | 0.06 | 73.22 | 0.06 | 73.71 | 0.05 | 74.35 | 0.05 | 74.53 | 0.05 | 74.2 | 0.06 | 74.6 | 0.04 | 74.78 | 0.03 | 74.76 | 0.03 | 74.19 | 0.07 | 72.42 | 0.08 | 74.82 | 0.03 | 71.95 | 0.28 | 67.29 | 0.12 | 68.87 | 0.17 |  |  | 74.86 | 0.03 | 75.54 | 0.03 | 75.39 | 0.02 | 75.25 | 0.02 | 74.8 |  | 74.9 | 0.02 | 72.07 | 0.04 | 72.59 | 0.05 | 73.85 | 0.06 | 74.72 | 0.05 | 74.81 | 0.02 | [62 empty] | Economizer test | 75.006 | 0.016 | 62.004 | 0.025 | 74.56 | 0.011 | 61.547 | 0.02 | 55.02 | 0.011 | 51.004 | 0.019 | 2756.7 | 2 | 2642.1 | 2 | 0.542 | 0.002 | -0.251 | 0.002 | 0.155 | 0.003 | 1.5284 | 0.0022 | 29.386 | 0 | 1402 | 19 | 1310 |  | 0 | 0 | 13.03 | 0.251 | 1.3285 | 12217.9435 | 168.2339 | 0 | 0 | 12217.9435 | 0.0087818 | 27.6114 | 73.2315 | 13.03 | 13.5376 | 0.0069788 | 20.7798 | 0.0087818 | 27.6114 | 0.0085873 | 27.2898 | 75.006 | 62.004 | 26.9659
2 | T2-TRN-88A-55-T2E-DM-2 | 75T0095 | T2-TRN-88A-55-T2E-DM-2 | 20% open | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 0:53:26 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.4 | 0 | 3.4 | 0 | 4097 | 20 | 3703 | 72 | 2989 | 76 | 7089 | 82 | 5.182 | 858 | 1280 |  | 2.9949 | [35 empty] | Econo 20%-open (3.6V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (866 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.007 | 0.006 | 62.004 | 0.017 | 55.007 | 0.012 | 51 | 0.016 | 75.12 | 0.03 | 73.91 | 0.02 | 73.99 | 0 | 0.171 | 0.003 | 1.5839 | 0.0026 | 4097 | 20 | 2989 | 76 | 5.181 | 0.072 | [6 empty] | 460.4 | 1.9 | 461.2 | 1.9 | 459.5 | 1.9 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1423.7 | 14.5 | 1090.8 | 17.3 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.9 |  | 2.9 |  | 2.9 |  | 0.48 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1365 | [14 empty] | 95.7 | 0.02 | 57.81 | 0.03 | 56.64 | 0.01 | -1.17 | 0.03 | 96 | 0.01 | 58.39 | 0.02 | 56.81 | 0.01 | -1.58 | 0.02 |  |  | 71.45 | 0.01 |  |  |  |  | 95.67 | 0.01 | 71.4 | 0.01 | 56.62 | 0.01 | 14.78 | 0.02 | 95.39 | 0.02 | 60.48 | 0.03 | 56.46 | 0.01 | 4.02 | 0.03 | [46 empty] | 96.39 | 0.03 | 60.39 | 0.04 | 57.02 | 0.02 | 3.38 | 0.05 | 96.66 | 0.04 | 57.17 | 0.02 | -0.06 | 0.16 |  |  | 73.03 | 0.13 |  |  |  |  | 95.99 | 0.03 | 56.79 | 0.02 | 14.5 | 0.03 | 96.17 | 0.03 | 61.29 | 0.02 | 56.89 | 0.01 | 4.39 | 0.02 | 60.65 | 0.14 | [28 empty] | 59.69 | 0.02 | 60.68 | 0.02 | 60.65 | 0.14 | 62.08 | 0.04 | 73.94 | 0.02 | 73.6 | 0.02 | 73.4 | 0.02 | 74.21 | 0.01 | 74.21 | 0.01 |  |  | 56.97 | 0.02 | 71.8 | 0.01 | 72.22 | 0.02 | 60.71 | 0.01 | 61.13 | 0.03 | 57.53 | 0.1 | 73.61 | 0.11 | 72.58 | 0.02 | 63.39 | 0.03 | 71.45 | 0.01 | 73.03 | 0.13 | 55.7 | 0.04 | 58.81 | 0.01 | 61.61 | 0.01 | 58.55 | 0.07 | 59.52 | 0.11 | 60.68 | 0.02 | 62.08 | 0.04 | [16 empty] | 57.81 | 0.03 | 57.24 | 0.16 | 59.69 | 0.02 | 60.65 | 0.14 | [16 empty] | 71.29 | 0.03 | [12 empty] | 58.54 | 0.01 | 56.44 | 0.11 | 55.86 | 0.04 | 75.46 | 0.01 | 73.21 | 0.04 | 74.84 | 0.03 | 74.19 | 0.04 | 75.85 | 3.36 | 75.91 | 0.02 | 75.52 | 0.02 | 70.54 | 0.07 | 71.8 | 0.05 | 71.75 | 0.03 | 70.78 | 0.08 | 72.06 | 0.07 | 71.67 | 0.05 | 71.86 | 0.04 | 72.8 | 0.03 | 73.03 | 0.05 | 72.21 | 0.06 | 72.73 | 0.06 | 74.9 | 0.02 | 74.88 | 0.02 | 74.82 | 0.02 | 74.22 | 0.1 | 75.08 | 0.02 | 74.83 | 0.02 | 70.48 | 0.09 | 69.11 | 0.07 |  |  | 73.58 | 0.05 | 75.88 | 0.01 | 75.71 | 0.02 | 75.04 | 0.02 | 73.5 |  | 75.12 | 0.02 | 67.8 | 0.09 |  |  | 71.18 | 0.07 | 73.55 | 0.06 | 74.96 | 0.02 | [62 empty] | Economizer test | 75.007 | 0.006 | 62.004 | 0.017 | 73.666 | 0.001 | 61.206 | 0.012 | 55.007 | 0.012 | 51 | 0.016 | 2800.3 | 2.3 | 2696.1 | 2.2 | 0.555 | 0.003 | -0.234 | 0.002 | 0.171 | 0.003 | 1.5839 | 0.0026 | 29.471 | 0 | 1368 | 10 | 1280 |  | 0.00405 | 10.9192 | 13.03 | 0.234 | 1.2627 | 12432.0669 | 175.79 | 10.9191 | 50.2809 | 12381.786 | 0.0087743 | 27.5838 | 72.4033 | 13.0297 | 13.5149 | 0.0069797 | 20.7776 | 0.0087816 | 27.6114 | 0.0085764 | 27.06 | 74.9264 | 61.9641 | 26.7521
2 | T2-TRN-88A-55-T3E-DM-2 | 75T0096 | T2-TRN-88A-55-T3E-DM-2 | 30% open | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/29/2014 | 1:48:28 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.4 | 0 | 6863 | 15 | 6426 | 75 | 4214 | 82 | 11080 | 80 | 8.0523 | 858 | 1280 |  | 4.9876 | [35 empty] | Econo 30%-open (4.4V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 87.5% airflow (350 cfm/ton), 2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (866 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.978 | 0.007 | 62.001 | 0.021 | 54.997 | 0.008 | 50.997 | 0.015 | 75.05 | 0.03 | 72.96 | 0.02 | 73.27 | 0.01 | 0.174 | 0.003 | 1.6085 | 0.0025 | 6863 | 15 | 4214 | 82 | 8.05 | 0.086 | [6 empty] | 460.5 | 2 | 461.4 | 2 | 459.4 | 2 | 3.4 | 0 | 2.9 | 0 | 3.2 | 0 | 1432.2 | 15.5 | 1087.1 | 18.5 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.9 |  | 2.9 |  | 2.8 |  | 0.48 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1365 | [14 empty] | 95.71 | 0.05 | 58.36 | 0.04 | 56.64 | 0.03 | -1.72 | 0.04 | 96.49 | 0.04 | 58.72 | 0.02 | 57.08 | 0.02 | -1.65 | 0.02 |  |  | 71.8 | 0.03 |  |  |  |  | 96.06 | 0.02 | 71.32 | 0.02 | 56.84 | 0.01 | 14.48 | 0.02 | 95.83 | 0.03 | 61.56 | 0.02 | 56.71 | 0.02 | 4.85 | 0.02 | [46 empty] | 96.88 | 0.04 | 60.62 | 0.07 | 57.29 | 0.03 | 3.35 | 0.1 | 97.04 | 0.05 | 57.38 | 0.02 | -0.58 | 0.14 |  |  | 72.69 | 0.13 |  |  |  |  | 96.38 | 0.05 | 57.02 | 0.03 | 14.4 | 0.04 | 96.51 | 0.04 | 61.74 | 0.02 | 57.09 | 0.03 | 4.65 | 0.04 | 61.26 | 0.05 | [28 empty] | 60.07 | 0.02 | 60.97 | 0.01 | 61.26 | 0.05 | 62.36 | 0.03 | 73.21 | 0.02 | 72.56 | 0.02 | 72.31 | 0.02 | 73.49 | 0.03 | 73.44 | 0.02 |  |  | 57.47 | 0.03 | 72.14 | 0.03 | 72.19 | 0.02 | 61.59 | 0.02 | 61.34 | 0.05 | 58.12 | 0.11 | 73.27 | 0.13 | 72.73 | 0.02 | 63.87 | 0.03 | 71.8 | 0.03 | 72.69 | 0.13 | 55.7 | 0.02 | 59.55 | 0.01 | 61.96 | 0.03 | 58.94 | 0.07 | 59.96 | 0.1 | 60.97 | 0.01 | 62.36 | 0.03 | [16 empty] | 58.36 | 0.04 | 57.97 | 0.15 | 60.07 | 0.02 | 61.26 | 0.05 | [16 empty] | 71.42 | 0.04 | [12 empty] | 58.85 | 0.02 | 56.73 | 0.14 | 55.91 | 0.05 | 75.43 | 0.02 | 73.18 | 0.04 | 74.86 | 0.02 | 74.19 | 0.05 | 76.61 | 4.44 | 75.88 | 0.02 | 75.49 | 0.02 | 67.76 | 0.1 | 70.34 | 0.17 | 71.56 | 0.06 | 69.46 | 0.13 | 67.71 | 0.1 | 70.66 | 0.07 | 71.3 | 0.03 | 71.02 | 0.05 | 68.72 | 0.11 | 70.08 | 0.07 | 68.14 | 0.15 | 74.6 | 0.03 | 74.56 | 0.03 | 74.68 | 0.03 | 74.59 | 0.03 | 75.04 | 0.01 | 74.86 | 0.02 | 71.89 | 0.16 | 69.98 | 0.1 |  |  | 73.52 | 0.05 | 75.88 | 0.02 | 75.7 | 0.02 | 75.05 | 0.03 | 73.6 |  | 75.11 | 0.02 | 64.83 | 0.09 |  |  | 66.31 | 0.11 | 67.66 | 0.14 | 74.66 | 0.03 | [62 empty] | Economizer test | 74.978 | 0.007 | 62.001 | 0.021 | 72.743 | 0.006 | 60.744 | 0.017 | 54.997 | 0.008 | 50.997 | 0.015 | 2820.2 | 2.2 | 2719.2 | 2.1 | 0.541 | 0.003 | -0.214 | 0.001 | 0.174 | 0.003 | 1.6085 | 0.0025 | 29.47 | 0 | 1376 | 11 | 1280 |  | 0.049297 | 134.0479 | 13.029 | 0.214 | 1.2549 | 12542.7185 | 172.8238 | 134.0501 | 617.2958 | 11925.4227 | 0.0086976 | 27.2734 | 71.4881 | 13.0294 | 13.4909 | 0.0069805 | 20.776 | 0.0087865 | 27.6097 | 0.0084961 | 26.7471 | 73.9977 | 61.5126 | 26.4412
2 | T2-TRN-88A-55-TCE-DM-2 | 75T0097 | T2-TRN-88A-55-TCE-DM-2 | closed | off | off | 4.5 turns | unsealed | unsealed | 866 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 22:08:18 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.9 | 0 | 3.3 | 0 | 1674 | 10 | 1402 | 95 | 1887 | 68 | 3563 | 67 | 2.6295 | 858 | 1270 |  | 1.2354 | [35 empty] | Econo closed (2V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--87.5% airflow (350 cfm/ton), 2 HP fan motor, 4.5 turns, 5.75" AK59 pulley (866 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match tot | W/ECO: 2 V No comp: 55/51 amb:2HP blwr mtr 5.75`` AK59 mtr. pulley: 4.5 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.991 | 0.004 | 62 | 0.015 | 55.005 | 0.011 | 51.006 | 0.013 | 74.85 | 0.06 | 74.39 | 0.07 | 74.61 | 0.01 | 0.158 | 0.003 | 1.5429 | 0.002 | 1674 | 10 | 1887 | 68 | 2.629 | 0.054 | [6 empty] | 459.9 | 2.1 | 460.2 | 2.1 | 460.2 | 2.1 | 3.3 | 0 | 2.9 | 0 | 3.2 | 0 | 1385.3 | 15 | 1117.8 | 19.3 | -10 | 0.3 | 460 |  | 460 |  | 460 |  | 2.8 |  | 2.9 |  | 2.9 |  | 0.48 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1355 | [14 empty] | 94.9 | 0.03 | 57.08 | 0.08 | 56.17 | 0.01 | -0.9 | 0.08 | 95.6 | 0.01 | 57.72 | 0.01 | 56.56 | 0.01 | -1.15 | 0.01 |  |  | 70.99 | 0.03 |  |  |  |  | 95.22 | 0.01 | 71.71 | 0.02 | 56.35 | 0.01 | 15.35 | 0.02 | 95.04 | 0.01 | 59.52 | 0.02 | 56.25 | 0.01 | 3.26 | 0.02 | [46 empty] | 95.96 | 0.01 | 59.35 | 0.13 | 56.77 | 0.01 | 2.58 | 0.14 | 95.92 | 0.02 | 56.75 | 0.01 | 0.14 | 0.12 |  |  | 73.07 | 0.05 |  |  |  |  | 95.5 | 0.02 | 56.51 | 0.01 | 14.82 | 0.05 | 95.66 | 0.02 | 60.72 | 0.02 | 56.6 | 0.01 | 4.12 | 0.02 | 59.88 | 0.09 | [28 empty] | 59.02 | 0.06 | 60.14 | 0.05 | 59.88 | 0.09 | 61.39 | 0.07 | 74.46 | 0.07 | 74.28 | 0.04 | 74.21 | 0.03 | 74.77 | 0.02 | 74.77 | 0.02 |  |  | 56.61 | 0.03 | 71.18 | 0.04 | 72.11 | 0.04 | 59.71 | 0.03 | 59.93 | 0.13 | 57.07 | 0.08 | 73.73 | 0.05 | 72.78 | 0.03 | 62.84 | 0.04 | 70.99 | 0.03 | 73.07 | 0.05 | 55.85 | 0.03 | 58.25 | 0.02 | 61.17 | 0.02 | 58.03 | 0.03 | 58.85 | 0.05 | 60.14 | 0.05 | 61.39 | 0.07 | [16 empty] | 57.08 | 0.08 | 56.6 | 0.12 | 59.02 | 0.06 | 59.88 | 0.09 | [16 empty] | 71.33 | 0.05 | [12 empty] | 57.79 | 0.02 | 56.04 | 0.05 | 55.66 | 0.04 | 75.32 | 0.01 | 73.08 | 0.04 | 74.75 | 0.02 | 74.01 | 0.04 | 75.82 | 2.5 | 75.7 | 0.02 | 75.34 | 0.02 | 72.35 | 0.04 | 72.79 | 0.04 | 72.69 | 0.03 | 73.04 | 0.05 | 73.23 | 0.04 | 73.14 | 0.04 | 73.32 | 0.03 | 73.9 | 0.03 | 74.11 | 0.03 | 73.8 | 0.03 | 74.02 | 0.03 | 74.85 | 0.02 | 74.86 | 0.01 | 74.76 | 0.02 | 73.3 | 0.15 | 74.99 | 0.02 | 74.7 | 0.02 | 69.42 | 0.09 | 69.37 | 0.08 |  |  | 73.46 | 0.05 | 75.75 | 0.02 | 75.57 | 0.02 | 74.92 | 0.03 | 73.32 |  | 75.05 | 0.02 | 71.15 | 0.08 |  |  | 72.71 | 0.05 | 74.21 | 0.03 | 74.9 | 0.02 | [62 empty] | Economizer test | 74.991 | 0.004 | 62 | 0.015 | 74.443 | 0.002 | 61.609 | 0.015 | 55.005 | 0.011 | 51.006 | 0.013 | 2767.4 | 1.8 | 2656.9 | 1.7 | 0.567 | 0.003 | -0.248 | 0.002 | 0.158 | 0.003 | 1.5429 | 0.002 | 29.429 | 0.001 | 1355 | 11 | 1270 |  | 0 | 0 | 13.03 | 0.248 | 1.2667 | 12267.5568 | 176.9797 | 0 | 0 | 12267.5568 | 0.0087828 | 27.6088 | 73.1763 | 13.0296 | 13.5352 | 0.0069834 | 20.7811 | 0.0087828 | 27.6088 | 0.0086554 | 27.3358 | 74.991 | 62 | 27.0269
2 | T2-TRN-100A-55-T1E-DM | 75T0099 | T2-TRN-100A-55-T1E-DM | 10% open | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 9:04:25 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 3.6 | 0 | 840 | 12 | 468 | 112 | 2394 | 69 | 3236 | 73 | 1.9331 | 945 | 1550 |  | 0.50179 | [35 empty] | Econo 10%-open (2.8V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--100% airflow (400 cfm/ton), 2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match to | W/ECO: 2.8 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.985 | 0.007 | 61.997 | 0.027 | 54.994 | 0.012 | 50.998 | 0.016 | 75.06 | 0.03 | 74.94 | 0.01 | 74.8 | 0.01 | 0.198 | 0.004 | 1.8796 | 0.003 | 840 | 12 | 2394 | 69 | 1.933 | 0.045 | [6 empty] | 459.7 | 2 | 460.2 | 2 | 460.3 | 2 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1549.4 | 14.3 | 1114.4 | 18.3 | 124.9 | 10.2 | 460 |  | 459 |  | 459 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.55 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1635 | [14 empty] | 94.63 | 0.03 | 57.09 | 0.06 | 56 | 0.01 | -1.09 | 0.06 | 95.9 | 0.01 | 59.18 | 0.02 | 56.71 | 0.01 | -2.47 | 0.02 |  |  | 71.78 | 0.02 |  |  |  |  | 94.46 | 0.04 | 72.32 | 0.03 | 55.9 | 0.02 | 16.43 | 0.04 | 94.99 | 0.02 | 60.32 | 0.02 | 56.2 | 0.01 | 4.12 | 0.02 | [46 empty] | 95.71 | 0.02 | 60.18 | 0.02 | 56.6 | 0.01 | 3.58 | 0.03 | 96.17 | 0.02 | 56.86 | 0.01 | -0.1 | 0.17 |  |  | 73.83 | 0.04 |  |  |  |  | 95.83 | 0.03 | 56.67 | 0.01 | 15.53 | 0.03 | 95.55 | 0.02 | 60.84 | 0.02 | 56.51 | 0.01 | 4.33 | 0.03 | 60.65 | 0.08 | [28 empty] | 59.8 | 0.02 | 60.39 | 0.02 | 60.65 | 0.08 | 61.51 | 0.02 | 74.94 | 0.02 | 74.7 | 0.02 | 74.51 | 0.02 | 75.2 | 0.02 | 75.2 | 0.02 |  |  | 56.68 | 0.03 | 72.22 | 0.01 | 72.63 | 0.01 | 60.52 | 0.01 | 60.96 | 0.02 | 57.17 | 0.11 | 74.39 | 0.03 | 73.4 | 0.01 | 62.73 | 0.02 | 71.78 | 0.02 | 73.83 | 0.04 | 55.74 | 0.04 | 58.28 | 0.01 | 61.2 | 0.02 | 58.03 | 0.02 | 59.01 | 0.08 | 60.39 | 0.02 | 61.51 | 0.02 | [16 empty] | 57.09 | 0.06 | 56.95 | 0.19 | 59.8 | 0.02 | 60.65 | 0.08 | [16 empty] | 72.2 | 0.02 | [12 empty] | 59.46 | 0.01 | 56.15 | 0.07 | 55.73 | 0.03 | 75.42 | 0.02 | 73.19 | 0.04 | 74.83 | 0.03 | 74.21 | 0.04 | 75.9 | 0.94 | 75.82 | 0.03 | 75.47 | 0.03 | 72.32 | 0.05 | 72.75 | 0.04 | 72.69 | 0.04 | 73.12 | 0.06 | 73.16 | 0.04 | 73.18 | 0.04 | 73.36 | 0.02 | 73.85 | 0.03 | 74.09 | 0.03 | 73.8 | 0.03 | 74.05 | 0.03 | 74.81 | 0.02 | 74.81 | 0.02 | 74.7 | 0.02 | 73.82 | 0.14 | 74.9 | 0.02 | 74.66 | 0.02 | 69.69 | 0.14 | 69.67 | 0.1 |  |  | 73.58 | 0.04 | 75.8 | 0.02 | 75.61 | 0.03 | 74.98 | 0.03 | 73.45 |  | 75.06 | 0.02 | 70.76 | 0.1 |  |  | 72.68 | 0.08 | 74.2 | 0.03 | 74.85 | 0.02 | [62 empty] | Economizer test | 74.985 | 0.007 | 61.997 | 0.027 | 74.749 | 0.006 | 61.689 | 0.023 | 54.994 | 0.012 | 50.998 | 0.016 | 3062.2 | 2.4 | 2928.8 | 2.4 | 0.693 | 0.003 | -0.299 | 0.002 | 0.198 | 0.004 | 1.8796 | 0.003 | 29.325 | 0.001 | 1674 | 10 | 1550 |  | 0 | 0 | 13.029 | 0.299 | 1.3744 | 13566.7583 | 238.4449 | 0 | 0 | 13566.7583 | 0.0087822 | 27.6067 | 73.3746 | 13.0294 | 13.5428 | 0.0069817 | 20.7766 | 0.0087822 | 27.6067 | 0.0086355 | 27.3887 | 74.985 | 61.997 | 27.0535
2 | T2-TRN-100A-55-T2E-DM | 75T0100 | T2-TRN-100A-55-T2E-DM | 20% open | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 10:12:26 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 3.6 | 0 | 3097 | 14 | 2682 | 85 | 3343 | 71 | 6443 | 76 | 3.8237 | 945 | 1550 |  | 1.838 | [35 empty] | Econo 20%-open (3.6V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--100% airflow (400 cfm/ton), 2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet Meriam, adjust--code tester speed to match to | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.983 | 0.005 | 62.001 | 0.023 | 55.004 | 0.013 | 51.003 | 0.018 | 75.06 | 0.03 | 74.27 | 0.02 | 74.24 | 0.01 | 0.199 | 0.004 | 1.9067 | 0.003 | 3097 | 14 | 3343 | 71 | 3.826 | 0.05 | [6 empty] | 459.7 | 2 | 460.3 | 2 | 460.5 | 2 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1551.1 | 13.6 | 1120.2 | 18.1 | 133.4 | 9.8 | 460 |  | 459 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.55 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1635 | [14 empty] | 95.37 | 0.04 | 57.79 | 0.02 | 56.42 | 0.02 | -1.37 | 0.02 | 96.3 | 0.03 | 59.71 | 0.02 | 56.94 | 0.02 | -2.77 | 0.02 |  |  | 72.03 | 0.02 |  |  |  |  | 95.73 | 0.01 | 72.09 | 0.01 | 56.62 | 0.01 | 15.46 | 0.02 | 95.54 | 0.03 | 61.3 | 0.02 | 56.51 | 0.02 | 4.78 | 0.02 | [46 empty] | 96.32 | 0.03 | 60.64 | 0.07 | 56.95 | 0.02 | 3.69 | 0.07 | 96.71 | 0.03 | 57.16 | 0.02 | -0.05 | 0.23 |  |  | 73.63 | 0.13 |  |  |  |  | 96.29 | 0.03 | 56.93 | 0.01 | 15.03 | 0.03 | 96.07 | 0.02 | 61.33 | 0.01 | 56.81 | 0.01 | 4.52 | 0.02 | 61.02 | 0.1 | [28 empty] | 60.29 | 0.02 | 60.74 | 0.02 | 61.02 | 0.1 | 61.85 | 0.03 | 74.27 | 0.03 | 73.99 | 0.02 | 73.8 | 0.02 | 74.6 | 0.02 | 74.6 | 0.02 |  |  | 57.08 | 0.03 | 72.33 | 0.02 | 72.5 | 0.02 | 61.38 | 0.02 | 61.35 | 0.04 | 57.49 | 0.15 | 74.21 | 0.11 | 73.29 | 0.02 | 63.39 | 0.03 | 72.03 | 0.02 | 73.63 | 0.13 | 55.77 | 0.05 | 59.39 | 0.03 | 61.67 | 0.02 | 58.45 | 0.04 | 59.43 | 0.09 | 60.74 | 0.02 | 61.85 | 0.03 | [16 empty] | 57.79 | 0.02 | 57.22 | 0.23 | 60.29 | 0.02 | 61.02 | 0.1 | [16 empty] | 71.96 | 0.04 | [12 empty] | 60.07 | 0.02 | 56.48 | 0.11 | 55.89 | 0.05 | 75.51 | 0.02 | 73.29 | 0.04 | 74.91 | 0.02 | 74.35 | 0.04 | 76 | 2.37 | 75.96 | 0.03 | 75.58 | 0.03 | 70.9 | 0.08 | 71.96 | 0.06 | 71.84 | 0.04 | 71.34 | 0.08 | 72.27 | 0.05 | 71.84 | 0.05 | 72.24 | 0.07 | 72.91 | 0.04 | 73.18 | 0.05 | 72.38 | 0.05 | 73.08 | 0.06 | 74.89 | 0.02 | 74.87 | 0.02 | 74.8 | 0.02 | 73.96 | 0.15 | 75.05 | 0.02 | 74.81 | 0.03 | 70.56 | 0.09 | 69.14 | 0.07 |  |  | 73.66 | 0.05 | 75.94 | 0.03 | 75.75 | 0.03 | 75.11 | 0.03 | 73.6 |  | 75.16 | 0.02 | 68.22 | 0.1 |  |  | 71.34 | 0.07 | 73.94 | 0.05 | 74.93 | 0.03 | [62 empty] | Economizer test | 74.983 | 0.005 | 62.001 | 0.023 | 74.068 | 0.006 | 61.353 | 0.02 | 55.004 | 0.013 | 51.003 | 0.018 | 3081.3 | 2.4 | 2953.1 | 2.3 | 0.685 | 0.003 | -0.28 | 0.002 | 0.199 | 0.004 | 1.9067 | 0.003 | 29.351 | 0.001 | 1685 | 10 | 1550 |  | 0 | 0 | 13.03 | 0.28 | 1.3649 | 13669.2722 | 237.6478 | 0 | 0 | 13669.2722 | 0.0087853 | 27.6096 | 72.7031 | 13.0296 | 13.5251 | 0.006982 | 20.7794 | 0.0087853 | 27.6096 | 0.008577 | 27.1586 | 74.983 | 62.001 | 26.8258
2 | T2-TRN-100A-55-T3E-DM | 75T0101 | T2-TRN-100A-55-T3E-DM | 30% open | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 11:03:23 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.6 | 0 | 3.6 | 0 | 6401 | 17 | 5963 | 69 | 4772 | 75 | 11178 | 80 | 6.5869 | 944 | 1560 |  | 3.772 | [35 empty] | Econo 30%-open (4.4V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--100% airflow (400 cfm/ton), 2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match to | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.984 | 0.006 | 61.996 | 0.021 | 55.004 | 0.01 | 51.006 | 0.018 | 75.07 | 0.02 | 73.31 | 0.02 | 73.45 | 0 | 0.201 | 0.005 | 1.9399 | 0.0035 | 6401 | 17 | 4772 | 75 | 6.587 | 0.062 | [6 empty] | 459.6 | 2 | 460.2 | 2 | 460.4 | 2 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1558.7 | 14.6 | 1117.5 | 18.6 | 138.3 | 9.8 | 460 |  | 460 |  | 459 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.55 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1645 | [14 empty] | 96.14 | 0.06 | 58.6 | 0.03 | 56.85 | 0.03 | -1.75 | 0.04 | 96.7 | 0.02 | 60.3 | 0.01 | 57.16 | 0.01 | -3.13 | 0.02 |  |  | 72.39 | 0.01 |  |  |  |  | 96.14 | 0.02 | 71.88 | 0.01 | 56.85 | 0.01 | 15.03 | 0.02 | 96.05 | 0.02 | 62.6 | 0.02 | 56.8 | 0.01 | 5.79 | 0.02 | [46 empty] | 96.95 | 0.02 | 61.06 | 0.06 | 57.3 | 0.02 | 3.75 | 0.06 | 97.31 | 0.05 | 57.51 | 0.03 | -0.28 | 0.22 |  |  | 73.2 | 0.14 |  |  |  |  | 96.83 | 0.04 | 57.24 | 0.02 | 14.71 | 0.03 | 96.57 | 0.02 | 61.98 | 0.01 | 57.1 | 0.01 | 4.88 | 0.02 | 61.83 | 0.07 | [28 empty] | 60.81 | 0.02 | 61.12 | 0.02 | 61.83 | 0.07 | 62.27 | 0.03 | 73.52 | 0.02 | 72.91 | 0.02 | 72.69 | 0.02 | 73.82 | 0.01 | 73.78 | 0.02 |  |  | 57.67 | 0.02 | 72.62 | 0.02 | 72.5 | 0.01 | 62.51 | 0.02 | 61.75 | 0.05 | 58.01 | 0.15 | 73.74 | 0.13 | 73.31 | 0.01 | 64.06 | 0.04 | 72.39 | 0.01 | 73.2 | 0.14 | 55.7 | 0.02 | 60.4 | 0.02 | 62.06 | 0.02 | 58.97 | 0.06 | 60 | 0.08 | 61.12 | 0.02 | 62.27 | 0.03 | [16 empty] | 58.6 | 0.03 | 57.79 | 0.22 | 60.81 | 0.02 | 61.83 | 0.07 | [16 empty] | 71.95 | 0.03 | [12 empty] | 60.7 | 0.01 | 56.84 | 0.14 | 55.97 | 0.06 | 75.51 | 0.02 | 73.26 | 0.03 | 74.92 | 0.02 | 74.35 | 0.04 | 75.94 | 1.36 | 75.92 | 0.02 | 75.54 | 0.02 | 67.58 | 0.1 | 70.39 | 0.25 | 71.58 | 0.07 | 69.5 | 0.12 | 67.51 | 0.1 | 70.51 | 0.09 | 71.31 | 0.04 | 70.99 | 0.04 | 68.77 | 0.11 | 69.99 | 0.09 | 68.56 | 0.12 | 74.77 | 0.02 | 74.62 | 0.03 | 74.64 | 0.02 | 74.55 | 0.02 | 75 | 0.03 | 74.79 | 0.02 | 71.55 | 0.14 | 69.04 | 0.1 |  |  | 73.57 | 0.05 | 75.9 | 0.03 | 75.72 | 0.02 | 75.11 | 0.03 | 73.72 |  | 75.15 | 0.02 | 65.01 | 0.08 |  |  | 66.19 | 0.1 | 68.26 | 0.12 | 74.75 | 0.03 | [62 empty] | Economizer test | 74.984 | 0.006 | 61.996 | 0.021 | 73.091 | 0.003 | 60.851 | 0.021 | 55.004 | 0.01 | 51.006 | 0.018 | 3104.6 | 2.8 | 2982.7 | 2.7 | 0.669 | 0.004 | -0.254 | 0.002 | 0.201 | 0.005 | 1.9399 | 0.0035 | 29.373 | 0.001 | 1697 | 11 | 1560 |  | 0.026176 | 78.0757 | 13.03 | 0.254 | 1.3657 | 13798.6655 | 234.4233 | 78.0745 | 359.5249 | 13439.1407 | 0.0087349 | 27.4282 | 71.7253 | 13.0296 | 13.4996 | 0.0069836 | 20.7811 | 0.0087818 | 27.606 | 0.0084828 | 26.8173 | 74.4651 | 61.7383 | 26.4844
2 | T2-TRN-100A-55-TCE-DM | 75T0102 | T2-TRN-100A-55-TCE-DM | closed | off | off | 3 turns | unsealed | unsealed | 950 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 7:10:47 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 3.6 | 0 | 1034 | 25 | 639 | 109 | 2384 | 74 | 3421 | 73 | 2.0412 | 945 | 1520 |  | 0.61695 | [35 empty] | Econo closed, tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--100% airflow (400 cfm/ton), 2 HP fan motor, 3 turns, 5.75" AK59 pulley (950 rpm), 100% inlet/outlet--Meriam, adjust code tester speed to match total stati | W/ECO: 2 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.989 | 0.01 | 61.993 | 0.019 | 54.993 | 0.009 | 51.001 | 0.015 | 74.96 | 0.04 | 74.79 | 0.04 | 74.77 | 0.01 | 0.196 | 0.004 | 1.877 | 0.0024 | 1034 | 25 | 2384 | 74 | 2.041 | 0.045 | [6 empty] | 460 | 2 | 461.4 | 2 | 460 | 2 | 3.6 | 0 | 3.1 | 0 | 3.4 | 0 | 1574.5 | 14 | 1096.4 | 17.8 | 101.2 | 10.3 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.56 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1605 | [14 empty] | 96.63 | 0.01 | 57.59 | 0.04 | 57.1 | 0 | 0.48 | 0.05 | 95.63 | 0 | 59.48 | 0.02 | 56.54 | 0 | -2.94 | 0.02 |  |  | 71.64 | 0.01 |  |  |  |  | 95.75 | 0.01 | 72.39 | 0.02 | 56.6 | 0.01 | 15.79 | 0.02 | 95.45 | 0.02 | 60.52 | 0.02 | 56.44 | 0.01 | 4.08 | 0.02 | [46 empty] | 96.28 | 0.02 | 60.26 | 0.02 | 56.91 | 0.01 | 3.36 | 0.02 | 96.42 | 0.03 | 56.98 | 0.02 | 3.11 | 0.03 |  |  | 73.86 | 0.01 |  |  |  |  | 96.11 | 0.01 | 56.81 | 0.01 | 15.31 | 0.02 | 96.05 | 0.01 | 60 | 0.02 | 56.77 | 0.01 | 3.23 | 0.02 | 61.3 | 0.02 | [28 empty] | 59.44 | 0.03 | 60.3 | 0.03 | 61.3 | 0.02 | 61.35 | 0.04 | 74.83 | 0.04 | 74.63 | 0.03 | 74.47 | 0.02 | 75.12 | 0.02 | 75.12 | 0.02 |  |  | 56.56 | 0.02 | 72.1 | 0.02 | 72.63 | 0.02 | 60.57 | 0.02 | 61 | 0.02 | 60.26 | 0.02 | 74.51 | 0.02 | 73.39 | 0.01 | 62.1 | 0.01 | 71.64 | 0.01 | 73.86 | 0.01 | 55.71 | 0.02 | 57.74 | 0.01 | 61.13 | 0.02 | 61.48 | 0.01 | 62.7 | 0.02 | 60.3 | 0.03 | 61.35 | 0.04 | [16 empty] | 57.59 | 0.04 | 60.09 | 0.03 | 59.44 | 0.03 | 61.3 | 0.02 | [16 empty] | 72.12 | 0.02 | [12 empty] | 59.62 | 0.03 | 56.16 | 0.07 | 55.74 | 0.04 | 75.42 | 0.02 | 73.14 | 0.04 | 74.82 | 0.02 | 74.17 | 0.03 | 75.96 | 1.21 | 75.76 | 0.03 | 75.41 | 0.03 | 72.15 | 0.06 | 72.65 | 0.04 | 72.64 | 0.04 | 73.19 | 0.05 | 73.14 | 0.05 | 73.18 | 0.04 | 73.37 | 0.02 | 73.87 | 0.03 | 74.14 | 0.03 | 73.82 | 0.04 | 74.1 | 0.03 | 74.85 | 0.02 | 74.83 | 0.02 | 74.73 | 0.02 | 73.98 | 0.09 | 74.92 | 0.03 | 74.67 | 0.02 | 69.67 | 0.15 | 69.98 | 0.11 |  |  | 73.53 | 0.04 | 75.74 | 0.03 | 75.57 | 0.02 | 74.96 | 0.03 | 73.43 |  | 75.07 | 0.02 | 70.46 | 0.09 |  |  | 72.66 | 0.07 | 74.26 | 0.03 | 74.88 | 0.03 | [62 empty] | Economizer test | 74.989 | 0.01 | 61.993 | 0.019 | 74.693 | 0.01 | 61.664 | 0.018 | 54.993 | 0.009 | 51.001 | 0.015 | 3063 | 2 | 2923.9 | 1.9 | 0.691 | 0.003 | -0.299 | 0.002 | 0.196 | 0.004 | 1.877 | 0.0024 | 29.267 | 0.001 | 1676 | 10 | 1520 |  | 0 | 0 | 13.029 | 0.299 | 1.3436 | 13571.7501 | 237.359 | 0 | 0 | 13571.7501 | 0.0087786 | 27.6037 | 73.3494 | 13.0293 | 13.5414 | 0.0069835 | 20.7784 | 0.0087786 | 27.6037 | 0.0086324 | 27.3716 | 74.989 | 61.993 | 27.0439
2 | T2-TRN-95-T1ER-DM | 75T0130 | T2-TRN-95-T1ER-DM | 10% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 0:27:36 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.1 | 15.4 | 0 | 58965 | 84 | 59674 | 576 | 8994 | 80 | 67967 | 120 | 7.8857 | 950 |  |  | 6.8413 | [35 empty] | Econo 10%-open, tape around damper perimeter inside/outside frame gaps, both stages,--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-95- | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.971 | 0.015 | 61.988 | 0.014 | 95.007 | 0.022 | 74.988 | 0.027 | 75.94 | 0.17 | 57.7 | 0.02 | 59.73 | 0.01 | 0.222 | 0.003 | 1.2368 | 0.0027 | 58965 | 84 | 8994 | 80 | 7.886 | 0.022 | [6 empty] | 461.1 | 2.4 | 461.3 | 2.4 | 459 | 2.4 | 15.4 | 0.1 | 13.2 | 0 | 12.8 | 0.1 | 7020 | 66.4 | 3161.6 | 69.1 | 1598.8 | 56.8 | 460 |  | 460 |  | 460 |  | 3.3 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.7 |  | 4.9 |  | 4.4 |  | 3140 |  | 0.86 | 460 | 460 | 460 | 5 | 4.5 | 4.4 | 3010 | 0.81 | 460.2 |  | 1.6 |  | 706.5 |  | 85 |  | 8571.5 | [14 empty] | 217.31 | 0.17 | 107.63 | 0.07 | 107.05 | 0.05 | -0.58 | 0.04 | 245.88 | 0.19 | 173.96 | 0.06 | 115.85 | 0.05 | 58.11 | 0.08 | 211 | 0.05 | 99.8 | 0.06 | 105 | 0.05 | 5.21 | 0.05 | 75.86 | 0.04 | 50.18 | 0.28 | 44.7 | 0.02 | 5.48 | 0.29 | 74.93 | 0.02 | 57.13 | 0.12 | 44.1 | 0.01 | 13.04 | 0.12 | [46 empty] | 247.81 | 0.19 | 169.23 | 0.12 | 116.42 | 0.05 | 52.81 | 0.12 | 230.51 | 0.23 | 111.21 | 0.07 | 9.88 | 0.16 | 220.1 | 0.05 | 100.46 | 0.07 | 107.94 | 0.05 | 7.51 | 0.05 | 77.86 | 0.03 | 45.98 | 0.02 | 2.9 | 0.1 | 77.03 | 0.04 | 56.04 | 0.22 | 45.45 | 0.03 | 10.58 | 0.22 | 105.8 | 0.07 | [28 empty] | 106.31 | 0.07 | 105.8 | 0.07 | 101.54 | 0.07 | 102.4 | 0.07 | 57.66 | 0.04 | 57.22 | 0.04 | 56.66 | 0.04 | 57.85 | 0.03 | 57.54 | 0.03 | 57.48 | 0.03 | 106.51 | 0.06 | 101.52 | 0.06 | 51.66 | 0.4 | 57.55 | 0.15 | 169.21 | 0.12 | 102.01 | 0.09 | 100.59 | 0.07 | 48.92 | 0.07 | 57.54 | 0.31 | 99.8 | 0.06 | 100.46 | 0.07 | 93.4 | 0.05 | 106.72 | 0.07 | 106.65 | 0.06 | 102.1 | 0.05 | 101.61 | 0.21 | 101.54 | 0.07 | 102.4 | 0.07 | [12 empty] | 107.63 | 0.07 | 57.48 | 0.03 |  |  | 101.33 | 0.17 | 106.31 | 0.07 | 105.8 | 0.07 | [16 empty] | 48.88 | 0.1 | [12 empty] | 174.76 | 0.07 | 95.69 | 0.1 | 95.4 | 0.11 | 76.34 | 0.08 | 76.09 | 0.08 | 75.82 | 0.07 | 76.72 | 0.05 | 76.75 | 0.08 | 76.64 | 0.08 | 76.35 | 0.08 | 80.11 | 0.18 | 80.56 | 0.1 | 77.25 | 0.08 | 75.77 | 0.11 | 76.92 | 0.09 | 77.65 | 0.08 | 77.32 | 0.07 | 77.49 | 0.07 | 75.88 | 0.09 | 76.97 | 0.08 | 75.61 | 0.1 | 75.56 | 0.08 | 75.24 | 0.1 | 76.25 | 0.08 | 75.87 | 0.08 | 75.65 | 0.08 | 75.56 | 0.08 | 75.53 | 0.09 | 75.74 | 0.08 |  |  | 75.87 | 0.08 | 76.49 | 0.07 | 76.2 | 0.08 | 75.93 | 0.09 | 75.81 |  | 75.74 | 0.1 |  |  | 80.2 | 0.07 | 76.13 | 0.1 | 75.84 | 0.09 | 75.53 | 0.09 | [62 empty] | T2-TRN-100A-55-T1E-DM | 74.971 | 0.015 | 61.988 | 0.014 | 56.955 | 0.007 | 54.226 | 0.016 | 95.007 | 0.022 | 74.988 | 0.027 | 2970 | 3.3 | 2931.4 | 3.3 | 0.649 | 0.002 | -0.287 | 0.002 | 0.222 | 0.003 | 1.2368 | 0.0027 | 29.383 | 0.001 | 8619 | 19 | 1630 |  | 0 | 0 | 13.029 | 0.299 | 1.4687 | 13614.2735 | 223.5038 | 0 | 0 | 13614.2735 | 0.0087796 | 27.6004 | 55.4863 | 14.1 | 13.0892 | 0.013909 | 38.1454 | 0.0087796 | 27.6004 | 0.0082908 | 22.6754 | 74.971 | 61.988 | 22.3175 | 71922.9163 | 63664.9056 | 6989 | 0.33165 | 67122.5448 | 58864.534 | 7.7877 | 0.15977 | -5.2829 | -19.4847 | 51.7812 | 71922.9163 | 67050.3448 | 4872.5716 | 0 | 71922.9163 | 100%
2 | T2-TRN-95-T2ER-DM | 75T0132 | T2-TRN-95-T2ER-DM | 20% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/11/2014 | 23:09:12 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 0.9 | 15.4 | 0 | 57762 | 75 | 58269 | 550 | 6967 | 123 | 64735 | 149 | 7.5029 | 950 |  |  | 6.6947 | [35 empty] | Econo 20%-open, tape around damper perimeter inside/outside frame gaps, both stages,--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-95- | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.002 | 0.023 | 61.997 | 0.027 | 94.986 | 0.021 | 74.988 | 0.019 | 75.8 | 0.18 | 58.07 | 0.03 | 60.14 | 0.03 | 0.225 | 0.003 | 1.2517 | 0.0025 | 57762 | 75 | 6967 | 123 | 7.503 | 0.024 | [6 empty] | 461 | 2.3 | 461.1 | 2.3 | 459 | 2.3 | 15.4 | 0.1 | 13.2 | 0 | 12.8 | 0.1 | 7007.9 | 66.8 | 3174.9 | 66 | 1620 | 56.7 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.5 |  | 3150 |  | 0.86 | 460 | 460 | 460 | 5 | 4.6 | 4.5 | 3030 | 0.81 | 460 |  | 1.6 |  | 706.3 |  | 85 |  | 8601.3 | [14 empty] | 217.38 | 0.18 | 107.53 | 0.08 | 107.07 | 0.06 | -0.46 | 0.05 | 246.07 | 0.2 | 173.79 | 0.13 | 115.91 | 0.06 | 57.88 | 0.14 | 210.1 | 0.05 | 99.7 | 0.06 | 104.7 | 0.05 | 4.96 | 0.05 | 75.96 | 0.06 | 50.05 | 0.45 | 44.76 | 0.04 | 5.29 | 0.44 | 75.01 | 0.03 | 56.98 | 0.26 | 44.15 | 0.02 | 12.84 | 0.24 | [46 empty] | 248.43 | 0.19 | 169.17 | 0.11 | 116.6 | 0.05 | 52.56 | 0.11 | 230.73 | 0.26 | 111.28 | 0.08 | 10.19 | 0.15 | 219.63 | 0.05 | 100.39 | 0.08 | 107.79 | 0.05 | 7.43 | 0.05 | 78.9 | 0.05 | 46.65 | 0.03 | 2.74 | 0.09 | 78.04 | 0.06 | 56.66 | 0.22 | 46.1 | 0.04 | 10.56 | 0.23 | 105.76 | 0.08 | [28 empty] | 106.24 | 0.07 | 105.76 | 0.08 | 101.47 | 0.08 | 102.26 | 0.08 | 58.03 | 0.04 | 57.59 | 0.05 | 57.04 | 0.05 | 58.25 | 0.04 | 57.93 | 0.04 | 57.88 | 0.04 | 106.47 | 0.06 | 101.45 | 0.07 | 51.46 | 0.57 | 57.34 | 0.29 | 169.16 | 0.14 | 102.01 | 0.08 | 100.55 | 0.08 | 49.46 | 0.08 | 58.21 | 0.33 | 99.7 | 0.06 | 100.39 | 0.08 | 93.37 | 0.06 | 106.68 | 0.08 | 106.62 | 0.06 | 102.09 | 0.05 | 101.79 | 0.06 | 101.47 | 0.08 | 102.26 | 0.08 | [12 empty] | 107.53 | 0.08 | 57.88 | 0.04 |  |  | 101.09 | 0.16 | 106.24 | 0.07 | 105.76 | 0.08 | [16 empty] | 49.38 | 0.1 | [12 empty] | 174.56 | 0.13 | 95.64 | 0.11 | 95.36 | 0.12 | 76.29 | 0.11 | 76 | 0.11 | 75.78 | 0.1 | 76.67 | 0.08 | 76.69 | 0.11 | 76.53 | 0.11 | 76.26 | 0.11 | 80.74 | 0.13 | 83.01 | 0.14 | 79.1 | 0.19 | 75.72 | 0.12 | 78.45 | 0.11 | 78.97 | 0.1 | 77.76 | 0.09 | 78.05 | 0.09 | 76.82 | 0.12 | 78.14 | 0.1 | 75.6 | 0.12 | 75.51 | 0.11 | 75.44 | 0.13 | 76.73 | 0.1 | 76.21 | 0.11 | 75.59 | 0.11 | 75.55 | 0.11 | 75.56 | 0.11 | 75.84 | 0.11 |  |  | 75.83 | 0.1 | 76.46 | 0.1 | 76.17 | 0.11 | 75.91 | 0.12 | 75.75 |  | 75.67 | 0.11 |  |  | 81.44 | 0.11 | 77.33 | 0.12 | 75.79 | 0.11 | 75.47 | 0.11 | [62 empty] | T2-TRN-100A-55-T2E-DM | 75.002 | 0.023 | 61.997 | 0.027 | 57.433 | 0.012 | 54.673 | 0.021 | 94.986 | 0.021 | 74.988 | 0.019 | 2989.2 | 3 | 2947.5 | 3 | 0.636 | 0.002 | -0.268 | 0.002 | 0.225 | 0.003 | 1.2517 | 0.0025 | 29.385 | 0 | 8628 | 20 | 1630 |  | 0 | 0 | 13.03 | 0.28 | 1.4642 | 13688.4671 | 220.2298 | 0 | 0 | 13688.4671 | 0.0087782 | 27.6064 | 55.9688 | 14.0995 | 13.1024 | 0.013914 | 38.1458 | 0.0087782 | 27.6064 | 0.0084323 | 22.9456 | 75.002 | 61.997 | 22.5887 | 68685.0332 | 62528.3787 | 6998 | 0.34773 | 63873.4874 | 57716.8329 | 7.403 | 0.16092 | -5.0177 | -19.0332 | 52.3187 | 68685.0332 | 63799.8604 | 4885.1728 | 0 | 68685.0332 | 100%
2 | T2-TRN-95-T3ER-DM | 75T0134 | T2-TRN-95-T3ER-DM | 30% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/11/2014 | 21:50:05 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.5 | 15.4 | 0 | 55976 | 95 | 55964 | 636 | 4283 | 141 | 60264 | 107 | 6.9782 | 949 |  |  | 6.4817 | [35 empty] | Econo 30%-open, tape around damper perimeter inside/outside frame gaps, both stages,--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-95- | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.998 | 0.037 | 61.985 | 0.01 | 94.992 | 0.014 | 75.03 | 0.018 | 75.2 | 0.19 | 58.17 | 0.04 | 60.68 | 0.03 | 0.222 | 0.003 | 1.2558 | 0.0027 | 55976 | 95 | 4283 | 141 | 6.978 | 0.02 | [6 empty] | 461.1 | 2.6 | 460.8 | 2.6 | 459.2 | 2.6 | 15.4 | 0.1 | 13.3 | 0 | 12.8 | 0.1 | 6984.1 | 66.9 | 3204 | 73.9 | 1651.5 | 57.3 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.5 |  | 3150 |  | 0.85 | 460 | 460 | 460 | 5 | 4.5 | 4.6 | 3030 | 0.81 | 460.1 |  | 1.6 |  | 706.1 |  | 85 |  | 8591.1 | [14 empty] | 217.52 | 0.18 | 107 | 0.08 | 107.11 | 0.06 | 0.11 | 0.05 | 246.24 | 0.2 | 173.78 | 0.08 | 115.96 | 0.06 | -57.83 | 0.09 | 210.03 | 0.05 | 99.6 | 0.06 | 104.67 | 0.05 | 5.04 | 0.05 | 76.05 | 0.05 | 49.75 | 0.24 | 44.82 | 0.03 | 4.93 | 0.25 | 75 | 0.02 | 57.04 | 0.14 | 44.13 | 0.01 | 12.91 | 0.14 | [46 empty] | 249.01 | 0.19 | 168.6 | 0.11 | 116.77 | 0.06 | 51.83 | 0.11 | 230.85 | 0.27 | 111.31 | 0.08 | 10.19 | 0.12 | 219.03 | 0.05 | 100.31 | 0.08 | 107.59 | 0.05 | 7.25 | 0.05 | 79.96 | 0.03 | 47.31 | 0.02 | 2.5 | 0.09 | 79.1 | 0.04 | 57.27 | 0.17 | 46.77 | 0.03 | 10.5 | 0.17 | 105.55 | 0.07 | [28 empty] | 105.94 | 0.08 | 105.55 | 0.07 | 101.33 | 0.08 | 101.63 | 0.08 | 58.04 | 0.04 | 57.71 | 0.05 | 57.36 | 0.05 | 58.36 | 0.04 | 58.11 | 0.03 | 58.13 | 0.04 | 106.31 | 0.06 | 101.08 | 0.07 | 50.97 | 0.39 | 57.16 | 0.18 | 168.35 | 0.12 | 101.84 | 0.08 | 100.71 | 0.08 | 50.27 | 0.06 | 59.03 | 0.27 | 99.6 | 0.06 | 100.31 | 0.08 | 93.47 | 0.06 | 106.82 | 0.08 | 106.66 | 0.06 | 102.04 | 0.05 | 101.77 | 0.1 | 101.33 | 0.08 | 101.63 | 0.08 | [12 empty] | 107 | 0.08 | 58.13 | 0.04 |  |  | 101.12 | 0.13 | 105.94 | 0.08 | 105.55 | 0.07 | [16 empty] | 49.8 | 0.09 | [12 empty] | 174.33 | 0.09 | 95.32 | 0.12 | 95.14 | 0.14 | 75.99 | 0.1 | 75.69 | 0.11 | 75.51 | 0.1 | 76.32 | 0.08 | 76.33 | 0.1 | 76.17 | 0.1 | 75.94 | 0.11 | 81.46 | 0.19 | 82.87 | 0.14 | 81.24 | 0.26 | 75.75 | 0.14 | 81.88 | 0.14 | 81.45 | 0.16 | 79.24 | 0.18 | 78.4 | 0.12 | 81.15 | 0.13 | 79.17 | 0.14 | 76.82 | 0.15 | 75.48 | 0.11 | 75.38 | 0.13 | 77.32 | 0.1 | 76.85 | 0.12 | 75.57 | 0.11 | 75.51 | 0.11 | 75.67 | 0.12 | 75.94 | 0.11 |  |  | 75.52 | 0.1 | 76.18 | 0.09 | 75.89 | 0.11 | 75.64 | 0.12 | 75.54 |  | 75.43 | 0.13 |  |  | 82.77 | 0.13 | 79.26 | 0.13 | 75.75 | 0.13 | 75.43 | 0.12 | [62 empty] | T2-TRN-100A-55-T3E-DM | 74.998 | 0.037 | 61.985 | 0.01 | 57.964 | 0.012 | 55.205 | 0.011 | 94.992 | 0.014 | 75.03 | 0.018 | 2996.7 | 3.3 | 2949.2 | 3.2 | 0.62 | 0.002 | -0.24 | 0.002 | 0.222 | 0.003 | 1.2558 | 0.0027 | 29.369 | 0 | 8636 | 20 | 1620 |  | 0.026176 | 78.0757 | 13.03 | 0.254 | 1.4574 | 13707.266 | 214.8132 | 78.948 | 335.9502 | 13371.3158 | 0.0088981 | 27.8574 | 56.5066 | 14.0999 | 13.1173 | 0.013949 | 38.1863 | 0.0087712 | 27.5978 | 0.0086125 | 23.2709 | 75.4925 | 62.3534 | 22.9155 | 67738.894 | 62458.8906 | 7016 | 0.3535 | 62942.9915 | 57662.9881 | 7.2884 | 0.15879 | -4.9418 | -18.9859 | 52.9228 | 67738.894 | 59310.8174 | 4870.8887 | 3557.1879 | 67738.894 | 100%
2 | T2-TRN-95-TCE-DM | 75T0136 | T2-TRN-95-TCE-DM | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/12/2014 | 1:45:20 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 1.1 | 15.4 | 0 | 59033 | 88 | 59713 | 628 | 9791 | 116 | 68833 | 135 | 8.002 | 950 | 1620 |  | 6.8627 | [35 empty] | Econo closed, tape around damper perimeter frame gaps, both stages, 95/75 ambient, 2 HP fan motor,--5.75" pulley, 3 turns (939 rpm), 100% inlet/outlet Meriam, adjust code tester speed to match total static--of run T2-TRN-95-TCE-DM-SPWCT-SS | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.971 | 0.024 | 61.989 | 0.015 | 94.999 | 0.02 | 74.98 | 0.015 | 75.83 | 0.21 | 57.43 | 0.04 | 59.64 | 0.02 | 0.186 | 0.004 | 1.2139 | 0.003 | 59033 | 88 | 9791 | 116 | 8.002 | 0.024 | [6 empty] | 461 | 2.4 | 461 | 2.4 | 459.2 | 2.4 | 15.4 | 0.1 | 13.2 | 0 | 12.8 | 0.1 | 6977.3 | 64.5 | 3193.4 | 71.8 | 1624.4 | 55.2 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.4 |  | 3150 |  | 0.85 | 460 | 460 | 460 | 5 | 4.6 | 4.4 | 3010 | 0.81 | 460 |  | 1.6 |  | 706.2 |  | 85 |  | 8571.2 | [14 empty] | 217.2 | 0.16 | 107.5 | 0.07 | 107.01 | 0.05 | -0.48 | 0.06 | 245.69 | 0.18 | 173.82 | 0.13 | 115.79 | 0.05 | 58.03 | 0.12 | 209.97 | 0.05 | 99.72 | 0.06 | 104.65 | 0.05 | 4.9 | 0.05 | 75.76 | 0.04 | 50.01 | 0.33 | 44.63 | 0.03 | 5.38 | 0.33 | 74.88 | 0.02 | 57.01 | 0.17 | 44.06 | 0.01 | 12.95 | 0.16 | [46 empty] | 247.48 | 0.18 | 169.38 | 0.1 | 116.32 | 0.05 | 53.06 | 0.08 | 230.3 | 0.22 | 111.14 | 0.07 | 9.96 | 0.09 | 219.73 | 0.05 | 100.52 | 0.07 | 107.82 | 0.05 | 7.26 | 0.05 | 77.54 | 0.04 | 45.78 | 0.02 | 2.73 | 0.08 | 76.69 | 0.04 | 55.73 | 0.2 | 45.24 | 0.03 | 10.49 | 0.19 | 105.72 | 0.07 | [28 empty] | 106.21 | 0.06 | 105.72 | 0.07 | 101.49 | 0.07 | 102.27 | 0.08 | 57.38 | 0.06 | 56.97 | 0.06 | 56.44 | 0.05 | 57.6 | 0.05 | 57.31 | 0.05 | 57.25 | 0.05 | 106.45 | 0.06 | 101.44 | 0.06 | 51.49 | 0.47 | 57.42 | 0.2 | 169.3 | 0.12 | 101.99 | 0.07 | 100.65 | 0.06 | 48.7 | 0.07 | 57.27 | 0.28 | 99.72 | 0.06 | 100.52 | 0.07 | 93.34 | 0.06 | 106.74 | 0.07 | 106.63 | 0.07 | 102.17 | 0.04 | 101.72 | 0.19 | 101.49 | 0.07 | 102.27 | 0.08 | [12 empty] | 107.5 | 0.07 | 57.25 | 0.05 |  |  | 101.19 | 0.1 | 106.21 | 0.06 | 105.72 | 0.07 | [16 empty] | 48.51 | 0.08 | [12 empty] | 174.69 | 0.07 | 95.65 | 0.1 | 95.36 | 0.12 | 76.31 | 0.1 | 76.07 | 0.11 | 75.79 | 0.1 | 76.71 | 0.08 | 76.73 | 0.09 | 76.62 | 0.11 | 76.34 | 0.11 | 80.48 | 0.18 | 79.74 | 0.12 | 77 | 0.09 | 75.78 | 0.13 | 76.9 | 0.11 | 77.58 | 0.09 | 77.28 | 0.08 | 77.35 | 0.09 | 75.8 | 0.11 | 76.69 | 0.11 | 75.6 | 0.13 | 75.56 | 0.1 | 75.21 | 0.11 | 76.19 | 0.1 | 75.83 | 0.1 | 75.66 | 0.1 | 75.61 | 0.1 | 75.6 | 0.1 | 75.79 | 0.1 |  |  | 75.85 | 0.1 | 76.53 | 0.09 | 76.23 | 0.11 | 75.96 | 0.12 | 75.8 |  | 75.73 | 0.12 |  |  | 79.88 | 0.09 | 76.16 | 0.12 | 75.85 | 0.12 | 75.52 | 0.11 | [62 empty] | T2-TRN-100A-55-TCE-DM | 74.971 | 0.024 | 61.989 | 0.015 | 56.775 | 0.013 | 54.045 | 0.017 | 94.999 | 0.02 | 74.98 | 0.015 | 2942.4 | 3.6 | 2903.9 | 3.5 | 0.657 | 0.002 | -0.289 | 0.002 | 0.186 | 0.004 | 1.2139 | 0.003 | 29.376 | 0 | 8602 | 20 | 1620 |  | 0 | 0 | 13.029 | 0.299 | 1.4707 | 13492.9385 | 224.1363 | 0 | 0 | 13492.9385 | 0.0087802 | 27.6011 | 55.3043 | 14.0997 | 13.0842 | 0.013903 | 38.1378 | 0.0087802 | 27.6011 | 0.0082309 | 22.5665 | 74.971 | 61.989 | 22.2082 | 72766.9096 | 63686.8893 | 6982 | 0.32748 | 68002.8266 | 58922.8064 | 7.9055 | 0.16035 | -5.393 | -19.6667 | 51.5485 | 72766.9096 | 67931.6999 | 4835.2097 | 0 | 72766.9096 | 100%
2 | T2-TRN-75A-55-1E-DM | 75T0072 | T2-TRN-75A-55-1E-DM | 10% open | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/22/2014 | 4:14:38 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.4 | 0 | 3.2 | 0 | 3754 | 15 | 3333 | 77 | 2673 | 59 | 6429 | 64 | 5.9308 | 755 | 980 |  | 3.4631 | [35 empty] | Econo 10%-open (2.8V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-75A-55-1E-DM-SPWCT | W/ECO: Eco set at 2.8v: No Compr:55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley:3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.997 | 0.006 | 61.997 | 0.022 | 54.997 | 0.011 | 51.001 | 0.012 | 74.57 | 0.04 | 73.31 | 0.05 | 74.11 | 0 | 0.112 | 0.003 | 1.1858 | 0.0016 | 3754 | 15 | 2673 | 59 | 5.931 | 0.075 | [6 empty] | 460.4 | 2 | 461.1 | 2 | 459.6 | 1.9 | 3.2 | 0 | 2.7 | 0 | 3.1 | 0 | 1272.2 | 14.6 | 1099 | 18.5 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.8 |  | 2.7 |  | 2.7 |  | 0.38 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 | [16 empty] | 97.1 | 0.03 | 55.33 | 0.05 | 57.39 | 0.01 | 2.06 | 0.05 | 96.4 | 0.02 | 57.36 | 0.01 | 57.01 | 0.01 | 0.35 | 0.01 |  |  | 68.58 | 0.02 |  |  |  |  | 96.45 | 0.02 | 71.02 | 0.01 | 57.03 | 0.01 | 13.99 | 0.01 | 95.95 | 0.02 | 56.97 | 0.02 | 56.76 | 0 | 0.22 | 0.02 | [46 empty] | 97.2 | 0.01 | 56.99 | 0.01 | 57.46 | 0.01 | 0.47 | 0.01 | 97.8 | 0.03 | 57.79 | 0.01 | 1.28 | 0.02 |  |  | 72.46 | 0.02 |  |  |  |  | 97.32 | 0.01 | 57.52 | 0.01 | 13.12 | 0.02 | 96.8 | 0.01 | 58.87 | 0.02 | 57.24 | 0.01 | 1.63 | 0.02 | 57.26 | 0.05 | [28 empty] | 56.45 | 0.05 | 57.92 | 0.04 | 57.26 | 0.05 | 59.23 | 0.06 | 73.44 | 0.04 | 73.3 | 0.04 | 73.17 | 0.03 | 73.42 | 0.04 | 73.48 | 0.04 |  |  | 54.82 | 0.03 | 68.57 | 0.06 | 70.74 | 0.06 | 57.06 | 0.05 | 57.32 | 0.04 | 56.77 | 0.03 | 73.01 | 0.03 | 71.63 | 0.02 | 60.63 | 0.02 | 68.58 | 0.02 | 72.46 | 0.02 | 55.06 | 0.06 | 55.8 | 0.02 | 59.02 | 0.02 | 57.19 | 0.01 | 57.97 | 0.02 | 57.92 | 0.04 | 59.23 | 0.06 | [16 empty] | 55.33 | 0.05 | 56.51 | 0.03 | 56.45 | 0.05 | 57.26 | 0.05 | [16 empty] | 70.64 | 0.02 | [12 empty] | 57.08 | 0.05 | 56.29 | 0.15 | 56.08 | 0.16 | 74.79 | 0.05 | 74.46 | 0.03 | 74.55 | 0.02 | 74.95 | 0.06 | 75.23 | 6.76 | 75.03 | 0.05 | 74.92 | 0.04 | 71.62 | 0.09 | 72.99 | 0.05 | 72.56 | 0.05 | 72.4 | 0.12 | 72.89 | 0.1 | 72.91 | 0.1 | 73.33 | 0.06 | 74.16 | 0.06 | 74.26 | 0.08 | 73.98 | 0.07 | 74.44 | 0.04 | 74.54 | 0.04 | 74.68 | 0.02 | 74.55 | 0.03 | 72.43 | 0.09 | 74.8 | 0.02 | 73.67 | 0.05 | 68.44 | 0.16 | 68.99 | 0.11 |  |  | 74.72 | 0.03 | 75.46 | 0.02 | 75.33 | 0.02 | 75.2 | 0.02 | 74.62 |  | 74.86 | 0.02 | 68.2 | 0.1 | 69.97 | 0.07 | 72.59 | 0.11 | 74.21 | 0.07 | 74.77 | 0.02 | [62 empty] | Economizer test | 74.997 | 0.006 | 61.997 | 0.022 | 73.575 | 0.004 | 61.152 | 0.02 | 54.997 | 0.011 | 51.001 | 0.012 | 2423.6 | 1.7 | 2327.6 | 1.6 | 0.401 | 0.002 | -0.182 | 0.002 | 0.112 | 0.003 | 1.1858 | 0.0016 | 29.409 | 0 | 1084 | 9 | 980 |  | 0.0136 | 31.6554 | 13.029 | 0.182 | 1.1498 | 10761.6117 | 109.6523 | 31.6559 | 145.774 | 10615.8377 | 0.008755 | 27.514 | 72.4252 | 13.0294 | 13.5125 | 0.0069826 | 20.7783 | 0.0087794 | 27.6065 | 0.0085629 | 27.023 | 74.727 | 61.8631 | 26.7427
2 | T2-TRN-75A-55-1F-DM-2 | 75T0073 | T2-TRN-75A-55-1F-DM-2 | 1 finger | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/29/2014 | 17:31:58 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 3.2 | 0 | 9822 | 23 | 9545 | 53 | 5152 | 120 | 14979 | 121 | 13.8823 | 749 | 990 |  | 9.1029 | [35 empty] | Econo 1F-open (5.1V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-75A-55-1F-DM-2-SPWC | W/ECO: 5.1 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.975 | 0.007 | 62.004 | 0.034 | 54.997 | 0.011 | 51.007 | 0.014 | 75.04 | 0.04 | 71.47 | 0.03 | 72.29 | 0.02 | 0.122 | 0.002 | 1.2186 | 0.0018 | 9822 | 23 | 5152 | 120 | 13.882 | 0.161 | [6 empty] | 460.6 | 2 | 460.3 | 2 | 459.5 | 2 | 3.2 | 0 | 2.8 | 0 | 3 | 0 | 1269.9 | 14.6 | 1111 | 18.7 | -10 | 0 | 460 |  | 459 |  | 460 |  | 2.7 |  | 2.7 |  | 2.7 |  | 0.39 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1075 | [14 empty] | 96.6 | 0.02 | 59.3 | 0.05 | 57.13 | 0.01 | -2.17 | 0.05 | 96.75 | 0.03 | 60.01 | 0.02 | 57.22 | 0.01 | -2.79 | 0.03 |  |  | 70.92 | 0.02 |  |  |  |  | 96.21 | 0.02 | 70.33 | 0.02 | 56.92 | 0.01 | 13.41 | 0.02 | 96.08 | 0.02 | 62.9 | 0.02 | 56.85 | 0.01 | 6.05 | 0.03 | [46 empty] | 97.21 | 0.03 | 61.23 | 0.04 | 57.47 | 0.01 | 3.76 | 0.04 | 97.38 | 0.05 | 57.57 | 0.03 | -0.65 | 0.19 |  |  | 71.16 | 0.06 |  |  |  |  | 96.97 | 0.03 | 57.34 | 0.02 | 13.13 | 0.04 | 96.93 | 0.03 | 62.48 | 0.04 | 57.32 | 0.02 | 5.16 | 0.04 | 61.42 | 0.04 | [28 empty] | 60.51 | 0.02 | 61.19 | 0.02 | 61.42 | 0.04 | 62.45 | 0.04 | 71.87 | 0.05 | 70.96 | 0.03 | 70.77 | 0.03 | 72.1 | 0.03 | 72 | 0.03 |  |  | 58.7 | 0.03 | 71.36 | 0.03 | 71.29 | 0.03 | 62.74 | 0.01 | 61.95 | 0.03 | 58.44 | 0.14 | 71.66 | 0.05 | 71.52 | 0.01 | 64.24 | 0.02 | 70.92 | 0.02 | 71.16 | 0.06 | 55.25 | 0.03 | 60.6 | 0.02 | 62.02 | 0.01 | 58.97 | 0.07 | 60.1 | 0.11 | 61.19 | 0.02 | 62.45 | 0.04 | [16 empty] | 59.3 | 0.05 | 58.23 | 0.18 | 60.51 | 0.02 | 61.42 | 0.04 | [16 empty] | 70.47 | 0.04 | [12 empty] | 60.16 | 0.02 | 56.87 | 0.14 | 55.96 | 0.05 | 75.37 | 0.02 | 72.95 | 0.05 | 74.85 | 0.03 | 73.85 | 0.05 | 76 | 1.48 | 75.74 | 0.03 | 75.35 | 0.03 | 63.53 | 0.14 | 67.55 | 0.13 | 68.89 | 0.34 | 65.81 | 0.18 | 64.57 | 0.21 | 68.19 | 0.12 | 69.8 | 0.04 | 69.73 | 0.04 | 66.95 | 0.17 | 68.93 | 0.07 | 66.09 | 0.16 | 71.13 | 0.16 | 73.15 | 0.12 | 73.07 | 0.13 | 73.47 | 0.05 | 69.77 | 0.11 | 73.84 | 0.04 | 73.11 | 0.07 | 70.43 | 0.05 |  |  | 73.31 | 0.06 | 75.73 | 0.02 | 75.59 | 0.02 | 74.95 | 0.03 | 73.4 |  | 75.04 | 0.02 | 63.4 | 0.1 |  |  | 64.28 | 0.11 | 63.15 | 0.15 | 73.36 | 0.09 | [62 empty] | Economizer test | 74.975 | 0.007 | 62.004 | 0.034 | 71.294 | 0.009 | 60.012 | 0.028 | 54.997 | 0.011 | 51.007 | 0.014 | 2450.6 | 1.9 | 2366.8 | 1.8 | 0.391 | 0.002 | -0.141 | 0.001 | 0.122 | 0.002 | 1.2186 | 0.0018 | 29.463 | 0 | 1079 | 9 | 990 |  | 0.12669 | 299.8484 | 13.029 | 0.141 | 1.1463 | 10929.493 | 108.7185 | 299.8537 | 1380.8109 | 9548.6822 | 0.0085613 | 26.749 | 70.1477 | 13.0295 | 13.4531 | 0.0069858 | 20.7818 | 0.0087892 | 27.6119 | 0.0083712 | 26.2574 | 72.4583 | 60.7409 | 25.9781
2 | T2-TRN-75A-55-2E-DM-2 | 75T0074 | T2-TRN-75A-55-2E-DM-2 | 20% open | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/29/2014 | 15:28:48 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 3.2 | 0 | 5170 | 14 | 4941 | 56 | 3153 | 64 | 8326 | 66 | 7.7523 | 749 | 990 |  | 4.8138 | [35 empty] | Econo 20%-open (3.6V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-75A-55-2E-DM-2-SPW | W/ECO: 3.6 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.977 | 0.007 | 61.994 | 0.023 | 55.005 | 0.012 | 50.993 | 0.014 | 75.09 | 0.04 | 73.22 | 0.04 | 73.6 | 0.01 | 0.125 | 0.002 | 1.1976 | 0.0022 | 5170 | 14 | 3153 | 64 | 7.756 | 0.084 | [6 empty] | 460.5 | 2 | 460.5 | 2 | 459.6 | 2 | 3.2 | 0 | 2.8 | 0 | 3.1 | 0 | 1268.8 | 14.7 | 1110.8 | 19.2 | -10 | 0 | 460 |  | 459 |  | 459 |  | 2.7 |  | 2.8 |  | 2.8 |  | 0.4 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1075 | [14 empty] | 96.05 | 0.01 | 58.39 | 0.04 | 56.83 | 0.01 | -1.56 | 0.04 | 96.32 | 0.01 | 59.5 | 0.02 | 56.97 | 0.01 | -2.53 | 0.02 |  |  | 70.84 | 0.01 |  |  |  |  | 95.66 | 0.01 | 71.08 | 0.02 | 56.61 | 0.01 | 14.47 | 0.02 | 95.46 | 0.02 | 61.1 | 0.02 | 56.5 | 0.01 | 4.6 | 0.03 | [46 empty] | 96.52 | 0.02 | 60.51 | 0.02 | 57.1 | 0.01 | 3.41 | 0.02 | 96.64 | 0.03 | 57.16 | 0.02 | -0.53 | 0.18 |  |  | 72.52 | 0.03 |  |  |  |  | 96.39 | 0.02 | 57.02 | 0.01 | 13.9 | 0.04 | 96.32 | 0.02 | 61.67 | 0.01 | 56.98 | 0.01 | 4.69 | 0.02 | 60.81 | 0.06 | [28 empty] | 59.86 | 0.02 | 60.69 | 0.01 | 60.81 | 0.06 | 62.07 | 0.04 | 73.22 | 0.03 | 72.88 | 0.02 | 72.71 | 0.02 | 73.48 | 0.02 | 73.49 | 0.02 |  |  | 57.47 | 0.02 | 71.3 | 0.02 | 71.85 | 0.02 | 61.19 | 0.01 | 61.25 | 0.02 | 57.87 | 0.13 | 73.06 | 0.03 | 71.96 | 0.01 | 63.51 | 0.03 | 70.84 | 0.01 | 72.52 | 0.03 | 55.45 | 0.02 | 59.27 | 0.02 | 61.49 | 0.02 | 58.44 | 0.04 | 59.43 | 0.08 | 60.69 | 0.01 | 62.07 | 0.04 | [16 empty] | 58.39 | 0.04 | 57.69 | 0.18 | 59.86 | 0.02 | 60.81 | 0.06 | [16 empty] | 70.92 | 0.04 | [12 empty] | 59.67 | 0.02 | 56.41 | 0.09 | 55.89 | 0.04 | 75.39 | 0.02 | 72.95 | 0.04 | 74.83 | 0.03 | 73.93 | 0.04 | 76.11 | 2.19 | 75.78 | 0.03 | 75.4 | 0.03 | 67.04 | 0.11 | 70.57 | 0.08 | 70.85 | 0.04 | 69.9 | 0.09 | 71.03 | 0.09 | 70.55 | 0.06 | 71.03 | 0.06 | 72.03 | 0.05 | 72.84 | 0.07 | 71.58 | 0.07 | 72.63 | 0.07 | 74.6 | 0.02 | 74.6 | 0.02 | 74.64 | 0.02 | 74.34 | 0.09 | 74.62 | 0.02 | 74.49 | 0.02 | 70.4 | 0.16 | 68.85 | 0.08 |  |  | 73.35 | 0.05 | 75.74 | 0.02 | 75.6 | 0.02 | 74.94 | 0.03 | 73.34 |  | 75.04 | 0.01 | 66.28 | 0.09 |  |  | 69.91 | 0.07 | 73.45 | 0.06 | 74.64 | 0.02 | [62 empty] | Economizer test | 74.977 | 0.007 | 61.994 | 0.023 | 73.024 | 0.005 | 60.896 | 0.021 | 55.005 | 0.012 | 50.993 | 0.014 | 2432 | 2.3 | 2343 | 2.2 | 0.411 | 0.002 | -0.172 | 0.001 | 0.125 | 0.002 | 1.1976 | 0.0022 | 29.47 | 0.001 | 1074 | 9 | 990 |  | 0.040206 | 94.2033 | 13.03 | 0.172 | 1.1532 | 10810.3077 | 113.1304 | 94.2019 | 433.7904 | 10376.5173 | 0.0087096 | 27.3305 | 71.8708 | 13.0296 | 13.4982 | 0.0069764 | 20.7736 | 0.0087821 | 27.6046 | 0.0085276 | 26.85 | 74.1781 | 61.5962 | 26.5689
2 | T2-TRN-75A-55-2F-DM-2 | 75T0075 | T2-TRN-75A-55-2F-DM-2 | 2 finger | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/29/2014 | 18:40:28 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 3.1 | 0 | 13701 | 22 | 13396 | 94 | 6799 | 90 | 20506 | 94 | 18.9695 | 748 | 990 |  | 12.6744 | [35 empty] | Econo 2F-open (6V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-75A-55-2F-DM-2-SPWCT- | W/ECO: 6 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.973 | 0.006 | 62.004 | 0.022 | 55.002 | 0.013 | 51.003 | 0.015 | 74.99 | 0.04 | 69.98 | 0.04 | 71.15 | 0.01 | 0.113 | 0.003 | 1.224 | 0.0017 | 13701 | 22 | 6799 | 90 | 18.963 | 0.169 | [6 empty] | 459.7 | 2 | 459.7 | 2 | 460.3 | 2 | 3.1 | 0 | 2.8 | 0 | 3.1 | 0 | 1245 | 14.2 | 1134.4 | 19.1 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.8 |  | 0.4 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1075 | [14 empty] | 97.2 | 0.02 | 59.93 | 0.04 | 57.46 | 0.01 | -2.46 | 0.05 | 97.37 | 0.01 | 60.4 | 0.03 | 57.55 | 0.01 | -2.85 | 0.02 |  |  | 70.26 | 0.02 |  |  |  |  | 96.97 | 0.02 | 68.47 | 0.03 | 57.34 | 0.01 | 11.13 | 0.03 | 96.64 | 0.02 | 64.12 | 0.02 | 57.16 | 0.01 | 6.97 | 0.02 | [46 empty] | 97.97 | 0.04 | 61.57 | 0.08 | 57.89 | 0.02 | 3.69 | 0.1 | 97.77 | 0.03 | 57.78 | 0.02 | -1.07 | 0.17 |  |  | 69.88 | 0.08 |  |  |  |  | 97.54 | 0.04 | 57.66 | 0.02 | 10.83 | 0.06 | 97.59 | 0.03 | 63.11 | 0.03 | 57.68 | 0.02 | 5.44 | 0.03 | 61.93 | 0.06 | [28 empty] | 60.91 | 0.03 | 61.47 | 0.02 | 61.93 | 0.06 | 62.62 | 0.05 | 70.54 | 0.04 | 69.36 | 0.04 | 69.23 | 0.04 | 70.79 | 0.03 | 70.67 | 0.02 |  |  | 59.53 | 0.03 | 70.6 | 0.02 | 69.47 | 0.02 | 63.81 | 0.02 | 62.23 | 0.07 | 59.1 | 0.16 | 70.42 | 0.07 | 69.59 | 0.03 | 64.91 | 0.03 | 70.26 | 0.02 | 69.88 | 0.08 | 55.17 | 0.04 | 61.59 | 0.02 | 62.34 | 0.02 | 59.34 | 0.09 | 60.55 | 0.09 | 61.47 | 0.02 | 62.62 | 0.05 | [16 empty] | 59.93 | 0.04 | 58.86 | 0.17 | 60.91 | 0.03 | 61.93 | 0.06 | [16 empty] | 68.48 | 0.06 | [12 empty] | 60.53 | 0.02 | 57.25 | 0.18 | 56.06 | 0.06 | 75.39 | 0.03 | 73.04 | 0.04 | 74.87 | 0.02 | 73.84 | 0.05 | 75.83 | 0.47 | 75.75 | 0.03 | 75.34 | 0.03 | 62.92 | 0.14 | 60.69 | 0.13 | 59.64 | 0.06 | 60.79 | 0.1 | 64.56 | 0.24 | 65.38 | 0.28 | 66.66 | 0.27 | 68.47 | 0.12 | 67.05 | 0.17 | 67.35 | 0.13 | 66.99 | 0.22 | 66.21 | 0.1 | 70.61 | 0.1 | 71.35 | 0.08 | 71.05 | 0.08 | 68.9 | 0.09 | 72.42 | 0.06 | 72.86 | 0.09 | 72.62 | 0.1 |  |  | 73.38 | 0.06 | 75.72 | 0.03 | 75.58 | 0.03 | 74.93 | 0.04 | 73.4 |  | 75.05 | 0.02 | 60.44 | 0.18 |  |  | 63.83 | 0.13 | 64.19 | 0.31 | 69.34 | 0.09 | [62 empty] | Economizer test | 74.973 | 0.006 | 62.004 | 0.022 | 69.854 | 0.003 | 59.254 | 0.022 | 55.002 | 0.013 | 51.003 | 0.015 | 2453.5 | 1.7 | 2375 | 1.7 | 0.373 | 0.002 | -0.116 | 0.002 | 0.113 | 0.003 | 1.224 | 0.0017 | 29.46 | 0 | 1081 | 8 | 990 |  | 0.19874 | 472.0032 | 13.03 | 0.116 | 1.1478 | 10973.0746 | 104.0729 | 471.9952 | 2173.497 | 8799.5775 | 0.0084317 | 26.2586 | 68.7062 | 13.0296 | 13.4156 | 0.0069825 | 20.7794 | 0.0087896 | 27.6119 | 0.0082348 | 25.7575 | 71.0277 | 60.0082 | 25.4778
2 | T2-TRN-75A-55-3E-DM-2 | 75T0076 | T2-TRN-75A-55-3E-DM-2 | 30% open | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/29/2014 | 16:30:19 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 3.2 | 0 | 7561 | 20 | 7263 | 56 | 4195 | 59 | 11761 | 60 | 10.9201 | 749 | 990 |  | 7.0204 | [35 empty] | Econo 30%-open (4.4V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-TRN-75A-55-3E-DM-2-SPW | W/ECO: 4.4 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.984 | 0.003 | 61.996 | 0.011 | 55.001 | 0.017 | 51.006 | 0.018 | 75.09 | 0.02 | 72.37 | 0.02 | 72.94 | 0.02 | 0.128 | 0.003 | 1.2157 | 0.0018 | 7561 | 20 | 4195 | 59 | 10.92 | 0.108 | [6 empty] | 460.6 | 2.1 | 460 | 2.1 | 459.3 | 2.1 | 3.2 | 0 | 2.8 | 0 | 3 | 0 | 1268 | 15.3 | 1110.1 | 20 | -10 | 0 | 460 |  | 459 |  | 459 |  | 2.8 |  | 2.7 |  | 2.7 |  | 0.39 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1075 | [14 empty] | 96.4 | 0.04 | 58.79 | 0.03 | 57.03 | 0.01 | -1.76 | 0.04 | 96.53 | 0.02 | 59.63 | 0.01 | 57.11 | 0.02 | -2.53 | 0.02 |  |  | 71.03 | 0.02 |  |  |  |  | 96 | 0.02 | 70.96 | 0.01 | 56.81 | 0.01 | 14.16 | 0.01 | 95.83 | 0.03 | 62.02 | 0.02 | 56.71 | 0.02 | 5.31 | 0.03 | [46 empty] | 96.92 | 0.04 | 60.8 | 0.07 | 57.33 | 0.02 | 3.47 | 0.08 | 96.98 | 0.06 | 57.36 | 0.03 | -0.95 | 0.22 |  |  | 72.02 | 0.08 |  |  |  |  | 96.71 | 0.04 | 57.21 | 0.02 | 13.78 | 0.04 | 96.63 | 0.04 | 62.11 | 0.02 | 57.16 | 0.02 | 4.95 | 0.03 | 61.26 | 0.06 | [28 empty] | 60.22 | 0.03 | 60.97 | 0.02 | 61.26 | 0.06 | 62.31 | 0.03 | 72.65 | 0.02 | 71.88 | 0.02 | 71.68 | 0.02 | 72.89 | 0.01 | 72.82 | 0.02 |  |  | 57.87 | 0.03 | 71.52 | 0.01 | 71.83 | 0.01 | 62.03 | 0.02 | 61.54 | 0.06 | 58.47 | 0.16 | 72.53 | 0.08 | 72 | 0.02 | 63.9 | 0.03 | 71.03 | 0.02 | 72.02 | 0.08 | 55.28 | 0.06 | 59.9 | 0.01 | 61.78 | 0.02 | 58.85 | 0.06 | 59.73 | 0.07 | 60.97 | 0.02 | 62.31 | 0.03 | [16 empty] | 58.79 | 0.03 | 58.28 | 0.22 | 60.22 | 0.03 | 61.26 | 0.06 | [16 empty] | 70.99 | 0.03 | [12 empty] | 59.79 | 0.01 | 56.7 | 0.12 | 55.92 | 0.05 | 75.41 | 0.02 | 72.98 | 0.05 | 74.89 | 0.02 | 73.95 | 0.05 | 75.7 | 2.9 | 75.8 | 0.02 | 75.4 | 0.03 | 65.86 | 0.12 | 67.03 | 0.26 | 70.28 | 0.08 | 68.79 | 0.12 | 65.52 | 0.12 | 68.04 | 0.11 | 70.24 | 0.06 | 70.2 | 0.06 | 68 | 0.12 | 68.96 | 0.09 | 67.67 | 0.14 | 74.26 | 0.03 | 74.29 | 0.04 | 74.47 | 0.03 | 74.41 | 0.03 | 74.55 | 0.02 | 74.52 | 0.01 | 71.94 | 0.16 | 70.13 | 0.09 |  |  | 73.36 | 0.06 | 75.76 | 0.02 | 75.61 | 0.02 | 74.97 | 0.02 | 73.42 |  | 75.06 | 0.02 | 63.69 | 0.1 |  |  | 65.72 | 0.13 | 66.4 | 0.19 | 74.35 | 0.04 | [62 empty] | Economizer test | 74.984 | 0.003 | 61.996 | 0.011 | 72.147 | 0.007 | 60.444 | 0.006 | 55.001 | 0.017 | 51.006 | 0.018 | 2448.7 | 1.8 | 2362.5 | 1.8 | 0.4 | 0.002 | -0.157 | 0.001 | 0.128 | 0.003 | 1.2157 | 0.0018 | 29.471 | 0.001 | 1077 | 9 | 990 |  | 0.084422 | 199.4464 | 13.03 | 0.157 | 1.1461 | 10903.0268 | 111.0189 | 199.443 | 918.4183 | 9984.6085 | 0.0086304 | 27.0311 | 71.0009 | 13.0296 | 13.4753 | 0.0069843 | 20.7811 | 0.0087818 | 27.606 | 0.0084446 | 26.5455 | 73.3058 | 61.158 | 26.2662
2 | T2-TRN-75A-55-3F-DM-2 | 75T0077 | T2-TRN-75A-55-3F-DM-2 | 3 finger | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/29/2014 | 19:22:58 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.8 | 0 | 3.1 | 0 | 18573 | 26 | 18181 | 148 | 9066 | 124 | 27648 | 132 | 25.4118 | 758 | 1000 |  | 17.0708 | [35 empty] | Econo 3F-open (6.9V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-75A-55-3F-DM-2-SPWC | W/ECO: 6.9 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.972 | 0.004 | 61.995 | 0.024 | 55 | 0.01 | 51.002 | 0.013 | 75 | 0.06 | 68.27 | 0.03 | 69.8 | 0.02 | 0.115 | 0.003 | 1.2433 | 0.0018 | 18573 | 26 | 9066 | 124 | 25.417 | 0.234 | [6 empty] | 459.8 | 1.9 | 459.6 | 1.9 | 460.2 | 1.9 | 3.1 | 0 | 2.8 | 0 | 3.1 | 0 | 1248 | 13.7 | 1134.7 | 18.6 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.8 |  | 0.4 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1085 | [14 empty] | 97.37 | 0.03 | 60.28 | 0.04 | 57.56 | 0.01 | -2.72 | 0.05 | 97.46 | 0.03 | 60.8 | 0.04 | 57.61 | 0.01 | -3.19 | 0.03 |  |  | 68.37 | 0.02 |  |  |  |  | 97.46 | 0.02 | 66.45 | 0.02 | 57.61 | 0.01 | 8.84 | 0.02 | 96.8 | 0.02 | 64.93 | 0.03 | 57.25 | 0.01 | 7.69 | 0.03 | [46 empty] | 98.14 | 0.03 | 57.29 | 0.03 | 57.99 | 0.01 | -0.7 | 0.03 | 98.16 | 0.08 | 58 | 0.04 | -0.58 | 0.23 |  |  | 66.97 | 0.03 |  |  |  |  | 97.67 | 0.07 | 57.73 | 0.04 | 8.66 | 0.17 | 97.67 | 0.03 | 63.53 | 0.03 | 57.72 | 0.02 | 5.81 | 0.03 | 60.28 | 0.22 | [28 empty] | 60.96 | 0.03 | 61.5 | 0.03 | 60.28 | 0.22 | 62.16 | 0.04 | 68.9 | 0.03 | 67.55 | 0.04 | 67.35 | 0.04 | 69.13 | 0.03 | 68.97 | 0.03 |  |  | 60 | 0.02 | 68.57 | 0.02 | 67.43 | 0.02 | 64.51 | 0.02 | 58.16 | 0.03 | 58.73 | 0.14 | 67.48 | 0.03 | 67.54 | 0.13 | 65.41 | 0.02 | 68.37 | 0.02 | 66.97 | 0.03 | 55.08 | 0.03 | 62.1 | 0.02 | 62.41 | 0.01 | 59.43 | 0.07 | 60.24 | 0.06 | 61.5 | 0.03 | 62.16 | 0.04 | [16 empty] | 60.28 | 0.04 | 58.57 | 0.21 | 60.96 | 0.03 | 60.28 | 0.22 | [16 empty] | 66.39 | 0.16 | [12 empty] | 60.94 | 0.02 | 57.76 | 0.18 | 56.19 | 0.06 | 75.43 | 0.03 | 73.46 | 0.04 | 74.93 | 0.02 | 74.4 | 0.05 | 75.83 | 0.39 | 75.8 | 0.03 | 75.37 | 0.03 | 61.22 | 0.1 | 61.29 | 0.11 | 59.57 | 0.12 | 59.92 | 0.1 | 62.56 | 0.12 | 62.68 | 0.15 | 59.25 | 0.19 | 64.52 | 0.21 | 64.73 | 0.11 | 63.89 | 0.15 | 64.78 | 0.1 | 63.85 | 0.15 | 67.16 | 0.09 | 67.1 | 0.09 | 66.67 | 0.12 | 66.82 | 0.19 | 70.2 | 0.14 | 70.78 | 0.1 | 70.33 | 0.09 |  |  | 73.81 | 0.05 | 75.78 | 0.02 | 75.64 | 0.03 | 75.05 | 0.03 | 73.67 |  | 75.08 | 0.03 | 57.19 | 0.09 |  |  | 61.96 | 0.13 | 63.22 | 0.13 | 66.16 | 0.09 | [62 empty] | Economizer test | 74.972 | 0.004 | 61.995 | 0.024 | 68.097 | 0.006 | 58.285 | 0.018 | 55 | 0.01 | 51.002 | 0.013 | 2469.5 | 1.9 | 2397.6 | 1.8 | 0.347 | 0.002 | -0.087 | 0.001 | 0.115 | 0.003 | 1.2433 | 0.0018 | 29.464 | 0.001 | 1088 | 9 | 1000 |  | 0.28615 | 686.0747 | 13.03 | 0.087 | 1.1574 | 11082.6151 | 97.7398 | 686.0618 | 3159.2676 | 7923.3475 | 0.0082704 | 25.6594 | 66.9396 | 13.0295 | 13.3696 | 0.0069824 | 20.7788 | 0.0087839 | 27.6054 | 0.0080508 | 25.1286 | 69.292 | 59.0982 | 24.8467
2 | T2-TRN-75A-55-CE-DM-2 | 75T0078 | T2-TRN-75A-55-CE-DM-2 | closed | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/29/2014 | 12:27:51 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 459.7 | 0 | 3.1 | 0 | 3487 | 19 | 3142 | 47 | 2410 | 70 | 5899 | 75 | 5.353 | 749 | 990 |  | 3.1642 | [35 empty] | Econo closed (2V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton), 2 HP fan motor,--3 turns, 7.25" AK74 pulley (725 rpm), 100% inlet/outlet Meriam, adjust code tester speed to--match total static of run T2-TRN-75A-55-CE-DM-2-SPWCT-SS | W/ECO: 2V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.997 | 0.006 | 61.994 | 0.026 | 55.015 | 0.013 | 50.994 | 0.011 | 75.05 | 0.02 | 73.85 | 0.02 | 74.14 | 0.01 | 0.113 | 0.003 | 1.1672 | 0.0019 | 3487 | 19 | 2410 | 70 | 5.354 | 0.079 | [6 empty] | 459.7 | 2 | 459.9 | 2 | 460.3 | 2 | 3.1 | 0 | 2.8 | 0 | 3.1 | 0 | 1256.1 | 14.5 | 1133.8 | 19.3 | -10 | 0 | 460 |  | 459 |  | 459 |  | 2.7 |  | 2.8 |  | 2.8 |  | 0.4 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1075 | [14 empty] | 95.98 | 0.03 | 57.8 | 0.02 | 56.81 | 0.02 | -0.99 | 0.03 | 95.5 | 0.04 | 59.36 | 0.02 | 56.54 | 0.02 | -2.81 | 0.02 |  |  | 70.57 | 0.02 |  |  |  |  | 95.65 | 0.03 | 71.16 | 0.02 | 56.63 | 0.02 | 14.53 | 0.03 | 95.39 | 0.04 | 60.25 | 0.02 | 56.48 | 0.02 | 3.76 | 0.02 | [46 empty] | 96.46 | 0.03 | 60.23 | 0.02 | 57.08 | 0.01 | 3.15 | 0.03 | 97.1 | 0.03 | 57.43 | 0.02 | -2.31 | 0.05 |  |  | 72.72 | 0.02 |  |  |  |  | 96.21 | 0.03 | 56.94 | 0.02 | 13.99 | 0.04 | 96.17 | 0.03 | 60.42 | 0.02 | 56.92 | 0.01 | 3.5 | 0.02 | 60.85 | 0.03 | [28 empty] | 59.38 | 0.02 | 60.22 | 0.02 | 60.85 | 0.03 | 61.61 | 0.02 | 73.85 | 0.03 | 73.63 | 0.03 | 73.46 | 0.03 | 74.08 | 0.02 | 74.1 | 0.01 |  |  | 56.86 | 0.03 | 71.02 | 0.03 | 71.87 | 0.02 | 60.35 | 0.01 | 60.99 | 0.02 | 59.81 | 0.03 | 73.29 | 0.02 | 72 | 0.02 | 62.78 | 0.02 | 70.57 | 0.02 | 72.72 | 0.02 | 55.62 | 0.04 | 58.3 | 0.03 | 61.04 | 0.02 | 60.69 | 0.03 | 61.73 | 0.02 | 60.22 | 0.02 | 61.61 | 0.02 | [16 empty] | 57.8 | 0.02 | 59.75 | 0.05 | 59.38 | 0.02 | 60.85 | 0.03 | [16 empty] | 70.93 | 0.04 | [12 empty] | 59.55 | 0.01 | 56.16 | 0.09 | 55.78 | 0.06 | 75.32 | 0.02 | 72.91 | 0.04 | 74.76 | 0.02 | 73.8 | 0.04 | 75.59 | 0.55 | 75.7 | 0.02 | 75.34 | 0.02 | 69.38 | 0.12 | 71.46 | 0.06 | 71.41 | 0.04 | 71.92 | 0.09 | 72.28 | 0.08 | 72.29 | 0.05 | 72.77 | 0.03 | 73.36 | 0.05 | 73.95 | 0.03 | 73.38 | 0.04 | 73.83 | 0.04 | 74.78 | 0.02 | 74.79 | 0.02 | 74.7 | 0.02 | 74.06 | 0.16 | 74.86 | 0.02 | 74.6 | 0.03 | 69.73 | 0.12 | 69.49 | 0.09 |  |  | 73.31 | 0.05 | 75.62 | 0.02 | 75.5 | 0.03 | 74.83 | 0.03 | 73.21 |  | 74.99 | 0.02 | 67.96 | 0.15 |  |  | 71.39 | 0.09 | 74.08 | 0.04 | 74.82 | 0.02 | [62 empty] | Economizer test | 74.997 | 0.006 | 61.994 | 0.026 | 73.668 | 0.007 | 61.215 | 0.022 | 55.015 | 0.013 | 50.994 | 0.011 | 2398.7 | 2 | 2314.5 | 1.9 | 0.422 | 0.002 | -0.182 | 0.001 | 0.113 | 0.003 | 1.1672 | 0.0019 | 29.547 | 0.001 | 1102 | 8 | 990 |  | 0.0079572 | 18.4169 | 13.03 | 0.182 | 1.1685 | 10649.0704 | 114.7453 | 18.4167 | 84.8057 | 10564.2647 | 0.008763 | 27.55 | 72.4995 | 13.0298 | 13.515 | 0.0069746 | 20.774 | 0.0087774 | 27.6044 | 0.0085818 | 27.0663 | 74.8384 | 61.9153 | 26.7814
2 | T2-TRN-75A-55-OE-DM-2 | 75T0081 | T2-TRN-75A-55-OE-DM-2 | open | off | off | 3 turns | unsealed | unsealed | 725 | 7.25 |  | 0 | 0 | CUST 5 | 10/29/2014 | 20:10:50 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 0 | 3.2 | 0 | 35784 | 59 | 35405 | 270 | 17140 | 199 | 52940 | 202 | 48.7477 | 748 | 1000 |  | 32.9503 | [35 empty] | Econo fully open (10V), no compressor, 55/51 ambient, 75% airflow (300 cfm/ton),--2 HP fan motor, 3 turns, 7.25" AK74 pulley (725 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-75A-55-OE-DM-2-SP | W/ECO: 10 V No comp: 55/51 amb:2HP blwr mtr 7.25` AK74 mtr. pulley: 3 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.983 | 0.015 | 62.006 | 0.03 | 55.001 | 0.01 | 50.993 | 0.015 | 75.02 | 0.11 | 61.7 | 0.07 | 64.67 | 0.01 | 0.096 | 0.003 | 1.1864 | 0.002 | 35784 | 59 | 17140 | 199 | 48.743 | 0.445 | [6 empty] | 460.3 | 2.1 | 460.2 | 2.1 | 459.9 | 2.1 | 3.2 | 0 | 2.8 | 0 | 3.1 | 0 | 1264.6 | 15.4 | 1122.1 | 20.4 | -10 | 0 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.8 |  | 2.8 |  | 0.4 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1085 | [14 empty] | 97.83 | 0.09 | 60.16 | 0.07 | 57.82 | 0.04 | -2.34 | 0.1 | 96.9 | 0.07 | 58.53 | 0.05 | 57.31 | 0.04 | -1.22 | 0.04 |  |  | 63.01 | 0.03 |  |  |  |  | 96.77 | 0.06 | 60.71 | 0.05 | 57.24 | 0.03 | 3.47 | 0.06 | 96.48 | 0.07 | 65.56 | 0.04 | 57.07 | 0.04 | 8.48 | 0.04 | [46 empty] | 98.03 | 0.04 | 56.96 | 0.05 | 57.93 | 0.02 | -0.97 | 0.04 | 98.19 | 0.05 | 58.02 | 0.03 | -1.36 | 0.11 |  |  | 60.39 | 0.08 |  |  |  |  | 95.48 | 0.09 | 56.52 | 0.05 | 3.03 | 0.08 | 95.99 | 0.1 | 63.41 | 0.05 | 56.8 | 0.06 | 6.6 | 0.08 | 59.36 | 0.14 | [28 empty] | 60.6 | 0.06 | 61.19 | 0.04 | 59.36 | 0.14 | 61.19 | 0.08 | 61.73 | 0.07 | 61.51 | 0.05 | 61.22 | 0.05 | 61.78 | 0.04 | 61.63 | 0.04 |  |  | 59.85 | 0.04 | 62.92 | 0.06 | 61.54 | 0.05 | 65.14 | 0.04 | 57.65 | 0.07 | 59.13 | 0.15 | 61.02 | 0.06 | 60.86 | 0.03 | 65 | 0.04 | 63.01 | 0.03 | 60.39 | 0.08 | 55.04 | 0.11 | 62.11 | 0.02 | 62.18 | 0.03 | 59.66 | 0.09 | 60.05 | 0.05 | 61.19 | 0.04 | 61.19 | 0.08 | [16 empty] | 60.16 | 0.07 | 59.38 | 0.13 | 60.6 | 0.06 | 59.36 | 0.14 | [16 empty] | 59.55 | 0.06 | [12 empty] | 58.59 | 0.04 | 58.58 | 0.22 | 56.65 | 0.08 | 75.32 | 0.04 | 74.7 | 0.05 | 74.99 | 0.06 | 75.77 | 0.06 | 75.76 | 0.06 | 75.77 | 0.06 | 75.54 | 0.06 | 55.08 | 0.07 | 58.01 | 0.14 | 58.85 | 0.16 | 55.05 | 0.13 | 58.46 | 0.13 | 61.39 | 0.26 | 57.94 | 0.24 | 60.54 | 0.28 | 61.38 | 0.17 | 62.25 | 0.24 | 59.71 | 0.16 | 59.17 | 0.15 | 62.88 | 0.11 | 62.7 | 0.16 | 61.49 | 0.19 | 64.54 | 0.17 | 65.23 | 0.14 | 65.02 | 0.14 | 66.92 | 0.16 |  |  | 75.14 | 0.06 | 75.7 | 0.05 | 75.61 | 0.06 | 75.41 | 0.06 | 74.89 |  | 75.06 | 0.05 | 54.97 | 0.13 |  |  | 55.83 | 0.12 | 58.43 | 0.16 | 62.3 | 0.15 | [62 empty] | Economizer test | 74.983 | 0.015 | 62.006 | 0.03 | 61.52 | 0.009 | 54.508 | 0.032 | 55.001 | 0.01 | 50.993 | 0.015 | 2399.5 | 2 | 2355.9 | 2 | 0.305 | 0.003 | -0.045 | 0.001 | 0.096 | 0.003 | 1.1864 | 0.002 | 29.474 | 0.001 | 1086 | 9 | 1000 |  | 0.6142 | 1447.0003 | 13.029 | 0.045 | 1.1932 | 10908.7519 | 84.4154 | 1447.0279 | 6663.4712 | 4245.2807 | 0.0076822 | 23.4353 | 60.3268 | 13.0295 | 13.1977 | 0.0069774 | 20.7736 | 0.0087886 | 27.6132 | 0.0073747 | 22.7908 | 62.7929 | 55.5665 | 22.5005
2 | T2-E-3000-95-CE-B50% | 75T0208 | T2-E-3000-95-CE-B50% | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  |  | 50 | CUST 6 | 8/15/2014 | 19:18:48 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 1.6 | 15 | 0 | 49675 | 64 | 49992 | 438 | 12098 | 64 | 61785 | 85 | 7.3923 | 951 | [38 empty] | 50% evaporator coil blockage, factory charge, 2 HP fan motor, 3 turns, 5.75" AK59 pulley (939 rpm),--Econo Closed damper, adjust code tester speed to match total static of run--T2-E-3000-95-CE-SPWCT-SS. Both stages. | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .; | 74.897 | 0.015 | 62.213 | 0.01 | 95.031 | 0.011 | 74.967 | 0.022 | 75.13 | 0.15 | 56.99 | 0.02 | 60.01 | 0.02 | -0.137 | 0.003 | 0.8759 | 0.0021 | 49675 | 64 | 12098 | 64 | 7.393 | 0.023 | [6 empty] | 460.7 | 2.8 | 460.9 | 2.8 | 459.5 | 2.8 | 15 | 0.1 | 12.9 | 0.1 | 12.7 | 0.1 | 6818.7 | 72 | 3232 | 79.2 | 1539.3 | 61 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.1 |  | 3 |  | 0.54 | 460 |  | 460 |  | 460 |  | 4.9 |  | 4.8 |  | 4.4 |  | 3130 |  | 0.84 | 460 | 460 | 460 | 4.9 | 4.6 | 4.4 | 2960 | 0.81 | 459.8 |  | 1.6 |  | 696.7 |  | 85 |  | 8351.7 | [14 empty] | 215.52 | 0.21 | 106.49 | 0.11 | 106.44 | 0.07 | -0.05 | 0.07 | 241.6 | 0.24 | 174.11 | 0.15 | 114.55 | 0.07 | 59.56 | 0.16 | 210.07 | 0.05 | 100.33 | 0.06 | 104.65 | 0.05 | 4.33 | 0.05 | 70.44 | 0.04 | 46.03 | 0.21 | 41.05 | 0.03 | 4.98 | 0.23 | 69.92 | 0.05 | 52.87 | 0.11 | 40.69 | 0.03 | 12.17 | 0.12 | [46 empty] | 243.71 | 0.24 | 171.99 | 0.15 | 115.18 | 0.07 | 56.8 | 0.16 | 229.1 | 0.34 | 110.75 | 0.1 | 11.87 | 0.12 | 220.47 | 0.05 | 98.57 | 0.08 | 108.03 | 0.05 | 9.49 | 0.05 | 71.42 | 0.09 | 41.71 | 0.06 | 2.5 | 0.38 | 70.59 | 0.1 | 52.96 | 0.25 | 41.15 | 0.07 | 11.81 | 0.28 | 105.28 | 0.1 | [28 empty] | 105.64 | 0.09 | 105.28 | 0.1 | 99.94 | 0.1 | 100.24 | 0.09 | 56.85 | 0.04 | 56.74 | 0.03 |  |  | 56.83 | 0.03 | 57.02 | 0.03 | 56.52 | 0.03 | 105.69 | 0.07 | 101.78 | 0.08 | 46.62 | 0.38 | 52.84 | 0.15 | 171.23 | 0.18 | 100.2 | 0.1 | 98.87 | 0.08 | 44.97 | 0.1 | 54.47 | 0.46 | 100.33 | 0.06 | 98.57 | 0.08 | 94.25 | 0.06 | 106.35 | 0.08 | 105.98 | 0.08 | 100.11 | 0.07 | 100.41 | 0.06 | 99.94 | 0.1 | 100.24 | 0.09 | [12 empty] | 106.49 | 0.11 | 56.52 | 0.03 |  |  | 98.88 | 0.12 | 105.64 | 0.09 | 105.28 | 0.1 | [16 empty] | 44.21 | 0.33 | [12 empty] | 174.36 | 0.09 | 94.93 | 0.11 | 95.5 | 0.19 | 75.68 | 0.09 | 75.47 | 0.09 | 75.24 | 0.08 | 75.93 | 0.05 | 75.99 | 0.08 | 75.92 | 0.09 | 75.7 | 0.1 | 81.45 | 0.16 | 80.46 | 0.13 | 78.88 | 0.09 | 77.27 | 0.09 | 77.41 | 0.07 | 77.05 | 0.06 | 76.72 | 0.07 | 77.08 | 0.06 | 77.01 | 0.07 | 76.92 | 0.07 | 76.4 | 0.09 | 75.42 | 0.1 | 75.82 | 0.09 | 75.86 | 0.09 | 75.99 | 0.09 | 75.54 | 0.08 | 75.38 | 0.06 |  |  | 79.21 | 0.09 |  |  | 75.27 | 0.08 | 75.92 | 0.07 | 75.7 | 0.09 | 75.46 | 0.1 | 75.35 |  | 75.27 | 0.09 |  |  | 82 | 0.1 | 77.95 | 0.07 | 76.08 | 0.1 | 75.59 | 0.1 | [62 empty] | T2-TRN-75A-55-CE-DM-2 | 74.897 | 0.015 | 62.213 | 0.01 | 56.87 | 0.006 | 53.841 | 0.011 | 95.031 | 0.011 | 74.967 | 0.022 | 2506.2 | 3.1 | 2454.6 | 3 | 0.656 | 0.002 | -0.199 | 0.002 | -0.137 | 0.003 | 0.8759 | 0.0021 | 29.194 | 0 | 8358 | 22 | 1480 |  | 0.0079572 | 18.4169 | 13.03 | 0.182 | 1.5969 | 11491.4853 | 189.1689 | 20.0332 | 85.2451 | 11406.2401 | 0.0089824 | 27.8411 | 55.2731 | 14.1004 | 13.0855 | 0.013884 | 38.1247 | 0.0089458 | 27.7642 | 0.0080936 | 22.4405 | 75.0477 | 62.3219 | 22.0515 | 66530.9369 | 54537.5895 | 6878 | 0.35284 | 62125.3303 | 50131.9829 | 7.433 | 0.18538 | -5.7896 | -19.7746 | 50.7731 | 66530.9369 | 61177.4955 | 4470.2624 | 883.179 | 66530.9369 | 100%
2 | T2-HS-2250-95-CF | 75T0149 | T2-HS-2250-95-CF | closed | on | on | 3 turns | unsealed | unsealed | 859 | 7 |  | 0 | 0 | CUST 6 | 7/31/2014 | 11:01:22 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 1.4 | 14.6 | 0 | 51883 | 129 | 52208 | 348 | 13738 | 434 | 65634 | 417 | 7.9876 | 888 |  |  |  | 109.13 | 0.04 | 19.92 | [32 empty] | 75% airflow (300 cfm/ton), 3 HP fan motor, 3 turns, 7" pulley (859 rpm),--both stages, closed damper adjust code tester speed to match total static of run--T2-2250-95-CF-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: 7` BP no name: ID Blw M: MQC 56T17D5563B: Mtr Pulley 3 T/O: With econo: Supply Meriam @85% Return Meriam @75%: Horiz Air Disch: Max Mtr Amp 4.7 | 74.945 | 0.035 | 62.008 | 0.083 | 94.849 | 0.021 | 75.001 | 0.017 | 74.8 | 0.12 | 54.36 | 0.1 | 58.46 | 0.03 | 0.106 | 0.003 | 0.9793 | 0.002 | 51883 | 129 | 13738 | 434 | 7.987 | 0.05 | 81959 | 231 | 9.974 | 0.03 | 19.92 | 0.34 | 460.3 | 2.7 | 460 | 2.7 | 459.7 | 2.7 | 14.6 | 0.1 | 12.8 | 0 | 12.4 | 0.1 | 6608.9 | 64.8 | 3180.9 | 68.7 | 1608.2 | 54.3 | 460 |  | 461 |  | 459 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.52 | 460 |  | 460 |  | 461 |  | 5.1 |  | 5 |  | 4.5 |  | 3160 |  | 0.82 | 459 | 459 | 460 | 4.9 | 4.6 | 4.5 | 3020 | 0.81 | 459.4 |  | 1.6 |  | 701.6 |  | 115 |  | 8236.6 | [14 empty] | 220.39 | 0.14 | 107.1 | 0.07 |  |  |  |  | 245.9 | 0.17 | 177.03 | 0.22 | 115.85 | 0.05 | 61.19 | 0.21 | 211 |  | 100.51 | 0.33 | 108.02 | 0.04 | 7.51 | 0.34 | 72.13 | 0.14 | 46.07 | 0.25 | 42.22 | 0.09 | 3.85 | 0.24 | 71.6 | 0.13 | 54.61 | 0.33 | 41.86 | 0.08 | 12.74 | 0.31 | 619.48 | 1.47 |  | 0.1 | 81959 | 231 | 43050 | 158 | [38 empty] | 248.01 | 0.17 | 172.53 | 0.23 | 116.47 | 0.05 | 56.06 | 0.24 | 231.53 | 0.22 |  |  |  |  | 220 |  | 99.31 | 0.07 | 111.51 | 0.07 | 12.2 | 0.08 | 74.59 | 0.15 | 43.85 | 0.1 | 2.51 | 0.43 | 74.21 | 0.17 | 54.5 | 0.47 | 43.6 | 0.11 | 10.9 | 0.5 | 105.55 | 0.05 | 610.54 | 1.99 | 39.26 | 0.02 | 109.03 | 0.07 | 81959 | 231 | 42593 | 118 | [18 empty] | 106.14 | 0.05 | 105.55 | 0.05 | 100.97 | 0.07 | 101.21 | 0.07 | 54.63 | 0.09 | 54.4 | 0.09 | 54.01 | 0.09 | 54.7 | 0.08 | 54.76 | 0.07 | 54.48 | 0.08 | 106.81 | 0.1 | 101.55 | 0.05 | 46.97 | 0.39 | 53.68 | 0.39 | 171.32 | 0.2 | 101.06 | 0.05 | 100.56 | 0.07 | 46.64 | 0.12 | 54.67 | 0.71 |  |  |  |  | 93.27 | 0.04 | [8 empty] | 100.97 | 0.07 | 101.21 | 0.07 | [12 empty] | 100.51 | 0.33 | 54.48 | 0.08 | 107.1 | 0.07 | 101.41 | 0.08 | 106.14 | 0.05 | 105.55 | 0.05 | [16 empty] | 46.36 | 0.37 | [12 empty] | 175.84 | 0.2 | 94.36 | 0.12 | 94.47 | 0.11 | 75.33 | 0.1 | 75.03 | 0.1 | 74.86 | 0.1 | 75.57 | 0.07 | 75.62 | 0.1 | 75.51 | 0.1 | 75.31 | 0.1 | 80.57 | 0.12 | 79.69 | 0.11 | 77.06 | 0.11 | 77.17 | 0.25 | 78.23 | 0.17 | 78.08 | 0.15 | 77.56 | 0.16 | 75.71 | 0.13 | 75.29 | 0.13 | 75.41 | 0.14 | 74.87 | 0.11 | 74.88 | 0.13 | 74.86 | 0.13 | 75.3 | 0.15 | 74.85 | 0.12 | 75.11 | 0.12 | 75.1 | 0.1 | 75.64 | 0.1 | 76.13 | 0.1 |  |  | 74.92 | 0.08 | 75.59 | 0.11 | 75.35 | 0.1 | 75.08 | 0.11 | 74.94 |  | 74.73 | 0.13 | 80.78 | 0.17 | 81.41 | 0.17 | 77.99 | 0.19 | 75.23 | 0.13 | 74.89 | 0.13 | [62 empty] | T2-TRN-75A-55-CE-DM-2 | 74.945 | 0.035 | 62.008 | 0.083 | 54.629 | 0.048 | 52.211 | 0.055 | 94.849 | 0.021 | 75.001 | 0.017 | 2301.4 | 2.4 | 2272 | 2.4 | 0.672 | 0.002 | -0.283 | 0.002 | 0.106 | 0.003 | 0.9793 | 0.002 | 29.3 | 0 | 8217 | 16 | 1240 |  | 0.0079572 | 18.4169 | 13.03 | 0.182 | 1.4224 | 10600.7698 | 179.3671 | 23.8866 | 101.6712 | 10499.0986 | 0.0088484 | 27.7164 | 53.2066 | 14.0964 | 13.0258 | 0.013958 | 38.1608 | 0.0087989 | 27.6152 | 0.0077201 | 21.4893 | 75.1377 | 62.1518 | 21.143 | 69682.5249 | 55796.7336 | 6977 | 0.34173 | 66062.5847 | 52176.7934 | 8.0397 | 0.14295 | -6.5733 | -21.9311 | 49.5487 | 69682.5249 | 64939.7769 | 3670.5653 | 1072.1827 | 69682.5249 | 100%
2 | T2-HS-2384-95-CF | 75T0150 | 'T2-HS-2384-95-CF | closed | on | on | 4 turns | unsealed | unsealed | 1002 | 6.25 |  | 0 | 0 | CUST 6 | 7/31/2014 | 6:58:01 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.8 | 1.2 | 14.5 | 0 | 52786 | 423 | 51839 | 429 | 12370 | 387 | 65167 | 642 | 7.8552 | 898 |  |  |  | 109.02 | 0.03 | 20.95 | [32 empty] | 79.5% airflow (318 cfm/ton), 3 HP fan motor, 4 turns, 6.25" pulley (1002 rpm),--both stages, closed damper match adjust code tester speed to match total static--of run 'T2-2625-95-CF-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: 6.25` BP no name: ID Blw M: MQC 56T17D5563B: Mtr Pulley 4 T/O: With econo: Supply Meriam @85% Return Meriam @75%: Horiz Air Disch: Max Mtr Amp 4.7 | 75 | 0.018 | 61.996 | 0.083 | 94.853 | 0.009 | 75.006 | 0.019 | 74.72 | 0.09 | 55.34 | 0.06 | 58.74 | 0.02 | 0.213 | 0.025 | 1.08 | 0.016 | 52786 | 423 | 12370 | 387 | 7.855 | 0.077 | 82428 | 288 | 9.936 | 0.039 | 20.95 | 0.72 | 459.8 | 2.4 | 459.6 | 2.4 | 460.3 | 2.4 | 14.5 | 0.1 | 12.8 | 0 | 12.6 | 0.1 | 6574.5 | 59.9 | 3251.8 | 65.6 | 1721.4 | 52 | 457 |  | 461 |  | 454 |  | 2.6 |  | 2.7 |  | 2.7 |  | 0.53 | 460 |  | 461 |  | 456 |  | 5.1 |  | 5 |  | 4.5 |  | 3170 |  | 0.82 | 457 | 460 | 461 | 4.8 | 4.7 | 4.5 | 3030 | 0.82 | 458.9 |  | 1.6 |  | 700.5 |  | 105 |  | 8305.5 | [14 empty] | 220.73 | 0.1 | 107.24 | 0.04 | 108.1267 | 0.03 | 0.87 | 0.02 | 246.48 | 0.15 | 177.81 | 0.16 | 116.01 | 0.04 | -61.8 | 0.16 | 211.6667 | 0.65 | 100.46 | 0.62 | 105.1833 | 0.65 | 4.6967 | 0.61 | 72.51 | 0.12 | 45.6 | 0.2 | 42.46 | 0.08 | 3.14 | 0.17 | 71.98 | 0.12 | 55.16 | 0.32 | 42.11 | 0.08 | 13.05 | 0.27 | 619.83 | 1.49 |  | 0.19 | 82428 | 288 | 43015 | 175 | [38 empty] | 248.96 | 0.15 | 172.43 | 0.43 | 116.74 | 0.04 | 55.69 | 0.46 | 232.17 | 0.26 | 111.73 | 0.15 | 10.0933 | 0.18 | 220.4 | 0.02 | 99.4 | 0.11 | 108.01 | 0.08 | 8.54 | 0.12 | 75.66 | 0.22 | 44.54 | 0.14 | 2.38 | 0.8 | 75.29 | 0.2 | 54.52 | 1.08 | 44.29 | 0.13 | 10.23 | 1.1 | 105.6 | 0.04 | 617.7 | 3.15 | 39.29 | 0.03 | 109.06 | 0.14 | 82428 | 288 | 43099 | 193 | [18 empty] | 106.13 | 0.04 | 105.6 | 0.04 | 101.2 | 0.1 | 101.42 | 0.1 | 55.24 | 0.09 | 54.98 | 0.09 | 55.57 | 3.04 | 55.38 | 0.09 | 55.35 | 0.09 | 55.14 | 0.09 | 106.97 | 0.1 | 101.53 | 0.04 | 46.97 | 0.34 | 54.37 | 0.41 | 171.23 | 0.38 | 101.18 | 0.08 | 100.83 | 0.1 | 47.28 | 0.23 | 53.83 | 1.7 |  |  |  |  | 93.22 | 0.04 | [8 empty] | 101.2 | 0.1 | 101.42 | 0.1 | [14 empty] | 55.14 | 0.09 | 107.24 | 0.04 | 101.64 | 0.12 | 106.13 | 0.04 | 105.6 | 0.04 | [16 empty] | 46.91 | 0.72 | [12 empty] | 176.68 | 0.15 | 94.55 | 0.11 | 94.69 | 0.1 | 75.32 | 0.08 | 75.03 | 0.07 | 74.82 | 0.07 | 75.59 | 0.06 | 75.64 | 0.08 | 75.54 | 0.08 | 75.33 | 0.08 | 80.74 | 0.13 | 79.88 | 0.09 | 77.39 | 0.09 | 77.27 | 0.24 | 78.52 | 0.18 | 78.43 | 0.12 | 77.94 | 0.12 | 75.86 | 0.08 | 75.3 | 0.09 | 75.53 | 0.09 | 74.9 | 0.08 | 74.72 | 0.09 | 74.7 | 0.09 | 75.18 | 0.09 | 74.8 | 0.08 | 74.9 | 0.09 | 74.91 | 0.08 | 75.32 | 0.08 | 75.96 | 0.08 |  |  | 74.89 | 0.06 | 75.54 | 0.07 | 75.3 | 0.08 | 75.04 | 0.08 | 74.9 |  | 74.72 | 0.08 | 81.31 | 0.23 | 81.91 | 0.18 | 78.12 | 0.19 | 75.21 | 0.08 | 74.71 | 0.09 | [62 empty] | T2-TRN-75A-55-CE-DM-2 | 75 | 0.018 | 61.996 | 0.083 | 55.267 | 0.03 | 52.772 | 0.058 | 94.853 | 0.009 | 75.006 | 0.019 | 2419.5 | 18.1 | 2384.4 | 18 | 0.681 | 0.002 | -0.305 | 0.005 | 0.213 | 0.025 | 1.08 | 0.016 | 29.264 | 0.001 | 8296 | 16 | 1300 |  | 0.0079572 | 18.4169 | 13.03 | 0.182 | 1.4169 | 11129.9172 | 190.7618 | 24.7978 | 105.5487 | 11024.3685 | 0.0088271 | 27.7059 | 53.8501 | 14.0965 | 13.0432 | 0.013961 | 38.1656 | 0.008778 | 27.6058 | 0.007877 | 21.8148 | 75.19 | 62.1384 | 21.4698 | 69406.8265 | 57002.7282 | 6996 | 0.34402 | 65620.9964 | 53216.8981 | 7.91 | 0.14694 | -6.2361 | -21.3399 | 50.1743 | 69406.8265 | 64452.3787 | 3839.8733 | 1114.5744 | 69406.8265 | 100%
2 | T2-2250-95-CF | 75T0155 | T2-2250-95-CF | closed | on | on | 3 turns | unsealed | unsealed | 859 | 7 |  | 0 | 0 | CUST 6 | 7/31/2014 | 11:01:22 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 1.4 | 14.6 | 0 | 51883 | 129 | 52208 | 348 | 13738 | 434 | 65634 | 417 | 7.9876 | 888 |  |  |  | 109.13 | 0.04 | 19.92 | [32 empty] | 75% airflow (300 cfm/ton), 3 HP fan motor, 3 turns, 7" pulley (859 rpm),--both stages, closed damper adjust code tester speed to match total static of run--T2-2250-95-CF-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: 7` BP no name: ID Blw M: MQC 56T17D5563B: Mtr Pulley 3 T/O: With econo: Supply Meriam @85% Return Meriam @75%: Horiz Air Disch: Max Mtr Amp 4.7 | 74.945 | 0.035 | 62.008 | 0.083 | 94.849 | 0.021 | 75.001 | 0.017 | 74.8 | 0.12 | 54.36 | 0.1 | 58.46 | 0.03 | 0.106 | 0.003 | 0.9793 | 0.002 | 51883 | 129 | 13738 | 434 | 7.987 | 0.05 | 81959 | 231 | 9.974 | 0.03 | 19.92 | 0.34 | 460.3 | 2.7 | 460 | 2.7 | 459.7 | 2.7 | 14.6 | 0.1 | 12.8 | 0 | 12.4 | 0.1 | 6608.9 | 64.8 | 3180.9 | 68.7 | 1608.2 | 54.3 | 460 |  | 461 |  | 459 |  | 2.6 |  | 2.7 |  | 2.6 |  | 0.52 | 460 |  | 460 |  | 461 |  | 5.1 |  | 5 |  | 4.5 |  | 3160 |  | 0.82 | 459 | 459 | 460 | 4.9 | 4.6 | 4.5 | 3020 | 0.81 | 459.4 |  | 1.6 |  | 701.6 |  | 115 |  | 8236.6 | [14 empty] | 220.39 | 0.14 | 107.1 | 0.07 |  |  |  |  | 245.9 | 0.17 | 177.03 | 0.22 | 115.85 | 0.05 | 61.19 | 0.21 | 211 |  | 100.51 | 0.33 | 108.02 | 0.04 | 7.51 | 0.34 | 72.13 | 0.14 | 46.07 | 0.25 | 42.22 | 0.09 | 3.85 | 0.24 | 71.6 | 0.13 | 54.61 | 0.33 | 41.86 | 0.08 | 12.74 | 0.31 | 619.48 | 1.47 |  | 0.1 | 81959 | 231 | 43050 | 158 | [38 empty] | 248.01 | 0.17 | 172.53 | 0.23 | 116.47 | 0.05 | 56.06 | 0.24 | 231.53 | 0.22 |  |  |  |  | 220 |  | 99.31 | 0.07 | 111.51 | 0.07 | 12.2 | 0.08 | 74.59 | 0.15 | 43.85 | 0.1 | 2.51 | 0.43 | 74.21 | 0.17 | 54.5 | 0.47 | 43.6 | 0.11 | 10.9 | 0.5 | 105.55 | 0.05 | 610.54 | 1.99 | 39.26 | 0.02 | 109.03 | 0.07 | 81959 | 231 | 42593 | 118 | [18 empty] | 106.14 | 0.05 | 105.55 | 0.05 | 100.97 | 0.07 | 101.21 | 0.07 | 54.63 | 0.09 | 54.4 | 0.09 | 54.01 | 0.09 | 54.7 | 0.08 | 54.76 | 0.07 | 54.48 | 0.08 | 106.81 | 0.1 | 101.55 | 0.05 | 46.97 | 0.39 | 53.68 | 0.39 | 171.32 | 0.2 | 101.06 | 0.05 | 100.56 | 0.07 | 46.64 | 0.12 | 54.67 | 0.71 |  |  |  |  | 93.27 | 0.04 | [8 empty] | 100.97 | 0.07 | 101.21 | 0.07 | [12 empty] | 100.51 | 0.33 | 54.48 | 0.08 | 107.1 | 0.07 | 101.41 | 0.08 | 106.14 | 0.05 | 105.55 | 0.05 | [16 empty] | 46.36 | 0.37 | [12 empty] | 175.84 | 0.2 | 94.36 | 0.12 | 94.47 | 0.11 | 75.33 | 0.1 | 75.03 | 0.1 | 74.86 | 0.1 | 75.57 | 0.07 | 75.62 | 0.1 | 75.51 | 0.1 | 75.31 | 0.1 | 80.57 | 0.12 | 79.69 | 0.11 | 77.06 | 0.11 | 77.17 | 0.25 | 78.23 | 0.17 | 78.08 | 0.15 | 77.56 | 0.16 | 75.71 | 0.13 | 75.29 | 0.13 | 75.41 | 0.14 | 74.87 | 0.11 | 74.88 | 0.13 | 74.86 | 0.13 | 75.3 | 0.15 | 74.85 | 0.12 | 75.11 | 0.12 | 75.1 | 0.1 | 75.64 | 0.1 | 76.13 | 0.1 |  |  | 74.92 | 0.08 | 75.59 | 0.11 | 75.35 | 0.1 | 75.08 | 0.11 | 74.94 |  | 74.73 | 0.13 | 80.78 | 0.17 | 81.41 | 0.17 | 77.99 | 0.19 | 75.23 | 0.13 | 74.89 | 0.13 | [62 empty] | T2-TRN-75A-55-CE-DM-2 | 74.945 | 0.035 | 62.008 | 0.083 | 54.629 | 0.048 | 52.211 | 0.055 | 94.849 | 0.021 | 75.001 | 0.017 | 2301.4 | 2.4 | 2272 | 2.4 | 0.672 | 0.002 | -0.283 | 0.002 | 0.106 | 0.003 | 0.9793 | 0.002 | 29.3 | 0 | 8217 | 16 | 1240 |  | 0.0079572 | 18.4169 | 13.03 | 0.182 | 1.4224 | 10600.7698 | 179.3671 | 23.8866 | 101.6712 | 10499.0986 | 0.0088484 | 27.7164 | 53.2066 | 14.0964 | 13.0258 | 0.013958 | 38.1608 | 0.0087989 | 27.6152 | 0.0077201 | 21.4893 | 75.1377 | 62.1518 | 21.143 | 69682.5249 | 55796.7336 | 6977 | 0.34173 | 66062.5847 | 52176.7934 | 8.0397 | 0.14295 | -6.5733 | -21.9311 | 49.5487 | 69682.5249 | 64939.7769 | 3670.5653 | 1072.1827 | 69682.5249 | 100%
2 | 3T-75629575-E6-Retest | 75T0182 | 3T-75629575-E6-Retest | closed | on | on | 6 turns | unsealed | sealed |  | 5.375 |  | 0 | 0 | CUST 8 | 2/21/2014 | 5:10:09 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1-6.4 LBS / CK2-6.2 LBS | 380/460/3 | TU4 | AHRI 210/240 2008 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.3 | 0 | 14.3 | 0 | 54188 | 222 | 52762 | 272 | 12854 | 160 | 67054 | 310 | 8.4313 | 474 | [38 empty] | Factory charge, 6 turns, Econo closed damper unsealed cab, 75% Meriam,--adjust code tester speed to match total static of run 3T-75629575-E6-SPWCT-SS | R22 CK1 : 6.4 lbs /Ck2 : 6.2 lbs: Unsealed cab/ Sealed ductwork: 5.375` blower pulley with AX35 (notched) belt : motor pulley 6 turns opened. with econo Closed Meriam set @ 75%: Horiz airflow. set on floor. | 74.992 | 0.019 | 62.001 | 0.023 | 95.003 | 0.023 | 75.003 | 0.016 | 74.61 | 0.07 | 53.92 | 0.05 | 60.51 | 0.03 | 0.098 | 0.008 | 0.7355 | 0.0059 | 54188 | 222 | 12854 | 160 | 8.432 | 0.046 | [6 empty] | 459.3 | 2.1 | 461.1 | 2.1 | 460.7 | 2.1 | 14.3 | 0 | 12.2 | 0 | 12.6 | 0.1 | 6492.2 | 42.4 | 3209.2 | 50.6 | 1460.5 | 35.6 | 457 |  | 459 |  | 460 |  | 2.3 |  | 2.4 |  | 2.6 |  | 0.46 | 458 |  | 460 |  | 459 |  | 5.1 |  | 5 |  | 4.5 |  | 3180 |  | 0.72 | 460 | 459 | 461 | 5 | 4.7 | 4.4 | 3090 | 0.82 | 458.5 |  | 1.7 |  | 714.7 |  | 115 |  | 7969.7 | [22 empty] | 246.72 | 0.31 | 175.98 | 0.21 | 116.11 | 0.09 | -59.87 | 0.21 |  |  | 100.66 | 0.13 | [6 empty] | 46.62 | 0.53 |  |  |  |  | 72.13 | 0.07 | 55 | 0.37 | 42.27 | 0.05 | 12.72 | 0.38 | [46 empty] | 254.96 | 0.33 | 175.83 | 0.33 | 118.51 | 0.09 | 57.33 | 0.35 | [8 empty] | 97.82 | 0.1 | [10 empty] | 75.44 | 0.17 | 54.35 | 1.23 | 44.45 | 0.11 | 9.9 | 1.27 | 99.01 | 0.08 | [36 empty] | 53.83 | 0.07 | 53.98 | 0.11 | 54.24 | 0.1 | 53.8 | 0.09 | 54.18 | 0.08 | 54.08 | 0.08 | [18 empty] | 100.66 | 0.13 | [12 empty] | 103.78 | 0.13 | 99.14 | 0.11 | 82.09 | 0.26 | 88.17 | 0.15 | 87.03 | 0.19 | 88.56 | 0.16 | 88.16 | 0.37 | 89.5 | 0.29 | [8 empty] | 104.1 | 0.14 | 99.01 | 0.08 | [16 empty] | 46.65 | 0.49 | [14 empty] | 95.92 | 0.24 | 95.2 | 0.12 | 74.71 | 0.08 | 74.77 | 0.07 | 74.76 | 0.06 | 74.67 | 0.09 | 74.68 | 0.08 | 74.68 | 0.08 | 74.66 | 0.07 | 78.29 | 0.1 | 78.83 | 0.12 | 77.97 | 0.08 | 77.15 | 0.08 | 82.35 | 0.19 | 80.32 | 0.15 | 78.25 | 0.11 | 77.44 | 0.09 | 83.64 | 0.13 | 78.63 | 0.11 | 77.18 | 0.11 | 76.67 | 0.12 | 83.89 | 0.18 | 77.7 | 0.1 | 76.04 | 0.07 | 75.25 | 0.1 | 75.78 | 0.1 | 76.15 | 0.12 | 75.29 | 0.07 | 75.27 | 0.06 | [84 empty] | T2-TRN-75A-55-CE-DM-2 | 74.992 | 0.019 | 62.001 | 0.023 | 53.742 | 0.022 | 51.915 | 0.025 | 95.003 | 0.023 | 75.003 | 0.016 | 2284.8 | 9.3 | 2258.6 | 9.2 | 0.56 | 0.005 | -0.286 | 0.003 | 0.098 | 0.008 | 0.7355 | 0.0059 | 29.457 | 0.001 | 7953 | 25 | 870 |  | 0.0079572 | 18.4169 | 13.03 | 0.182 | 0.97286 | 10542.186 | 148.591 | 24.016 | 102.1956 | 10439.9904 | 0.008833 | 27.7118 | 52.7691 | 14.1 | 13.0038 | 0.013923 | 38.16 | 0.0087832 | 27.6095 | 0.0077684 | 21.3257 | 75.1878 | 62.1465 | 21.0888 | 69820.0654 | 56721.9518 | 7083 | 0.34624 | 67357.8964 | 54259.7828 | 8.4695 | 0.11357 | -6.6229 | -22.4186 | 49.8968 | 69820.0654 | 66245.0295 | 2496.8222 | 1078.2138 | 69820.0654 | 100%
2 | 3T-75629575-E6 | 75T0183 | 3T-75629575-E6 | closed | on | on | 6 turns | unsealed | sealed |  | 5.375 |  | 0 | 0 | CUST 13 | 10/20/2013 | 16:59:09 | 10 Ton | 0:30:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | ck1: 6.4 lbs / ck2: 6.2 lbs | 460/480/3 | TU4 | AHRI 340-360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 1.1 | 13 | 0 | 54180 | 178 | 53583 | 306 | 7166 | 536 | 61354 | 427 | 7.6616 | 756 | [38 empty] | Factory charge, 6 turns, Econo closed damper unsealed cab, 75% Merriam, Code VFD @ 30.76% | R22 CK1 : 6.4 lbs /Ck2 : 6.2 lbs: Sealed cab/ Sealed ductwork: 5.375` blower pulley with AX35 (notched) belt : motor pulley 6 turns opened. With econo closed,Meriam set @ 75%: Horiz airflow. set on floor. Code Tester VFD @ 30.76 | 74.986 | 0.017 | 61.973 | 0.102 | 94.913 | 0.016 | 75.106 | 0.033 | 74.59 | 0.12 | 55.29 | 0.08 | 60.35 | 0.03 | -0.405 | 0.003 | 1.1692 | 0.0025 | 54180 | 178 | 7166 | 536 | 7.662 | 0.054 | [6 empty] | 461 | 2.5 | 461.3 | 2.5 | 459 | 2.5 | 13 | 0 | 12.4 | 0.1 | 14.3 | 0.1 | 5944.2 | 42.1 | 3972.6 | 73.8 | 2063.9 | 30 | 460 |  | 460 |  | 460 |  | 2.7 |  | 2.7 |  | 2.9 |  | 0.4 | 460 |  | 460 |  | 460 |  | 4.9 |  | 4.9 |  | 4.6 |  | 3180 |  | 0.84 | 460 | 460 | 460 | 4.8 | 4.6 | 4.6 | 3010 | 0.81 | [8 empty] | 8012 | [22 empty] | 248.28 | 0.2 | 174.11 | 0.18 | 116.53 | 0.06 | 57.57 | 0.16 |  |  | 100.43 | 0.1 | [12 empty] | 74.86 | 0.12 | 56.11 | 0.34 | 44.01 | 0.08 | 12.11 | 0.31 | [46 empty] | 251.53 | 0.21 | 173.1 | 0.22 | 117.49 | 0.06 | 55.61 | 0.23 | [8 empty] | 99.36 | 0.08 | [10 empty] | 76.91 | 0.15 | 55.61 | 0.71 | 45.33 | 0.1 | 10.28 | 0.74 | 100.82 | 0.09 | [36 empty] | 54.25 | 0.08 | 55.25 | 0.08 | 55.04 | 0.07 | 55.17 | 0.08 | 54.96 | 0.09 | 55.19 | 0.08 | [18 empty] | 100.43 | 0.1 | [12 empty] | 104.35 | 0.09 | 100.45 | 0.09 | [20 empty] | 104.16 | 0.1 | 100.82 | 0.09 | 104.35 | 0.09 | 100.45 | 0.09 | [28 empty] | 95.19 | 0.09 | 95.11 | 0.09 | 74.47 | 0.1 | 74.56 | 0.09 | 74.67 | 0.1 | 74.48 | 0.11 | 74.41 | 0.12 | 74.43 | 0.1 | 74.53 | 0.09 | 86.66 | 0.09 | 85.03 | 0.1 | 84.07 | 0.09 | 82.46 | 0.13 | 86.98 | 0.14 | 85.75 | 0.14 | 82.76 | 0.12 | 81.57 | 0.11 | 82.06 | 0.17 | 79.09 | 0.16 | 81.05 | 0.09 | 81.82 | 0.09 | 76.16 | 0.11 | 77.11 | 0.12 | 79.34 | 0.1 | 80.45 | 0.13 | 75.14 | 0.11 | 75.08 | 0.11 | 75.38 | 0.12 | 77.81 | 0.1 | 74.63 | 0.09 | [20 empty] | 93.27 | 0.08 | 93.16 | 0.09 | 93.05 | 0.08 | 93.14 | 0.08 | 93.01 | 0.08 | 92.88 | 0.12 | [50 empty] | T2-TRN-75A-55-CE-DM-2 | 74.986 | 0.017 | 61.973 | 0.102 | 55.468 | 0.06 | 53.686 | 0.069 | 94.913 | 0.016 | 75.106 | 0.033 | 2526.1 | 2.6 | 2472.6 | 2.6 | 0.372 | 0.003 | -0.273 | 0.004 | -0.405 | 0.003 | 1.1692 | 0.0025 | 29.225 | 0.001 | 8008 | 16 | 1015 |  | 0.0079572 | 18.4169 | 13.03 | 0.182 | 1.1103 | 11612.5695 | 108.0592 | 23.4627 | 99.8508 | 11512.7187 | 0.0088114 | 27.6811 | 54.3577 | 14.0986 | 13.0519 | 0.014035 | 38.2613 | 0.0087661 | 27.5894 | 0.0083375 | 22.3638 | 75.159 | 62.1036 | 22.0932 | 64890.4999 | 57973.5479 | 6993 | 0.36781 | 61795.1111 | 54878.1591 | 7.7167 | 0.09937 | -5.588 | -20.8013 | 52.0626 | 64890.4999 | 60682.6862 | 3142.2124 | 1065.6013 | 64890.4999 | 100%
2 | T2-TRN-110A-55-1E-DM | 75T0106 | T2-TRN-110A-55-1E-DM | 10% open | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/21/2014 | 17:38:32 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 4.2 | 0 | 2829 | 24 | 2443 | 117 | 4219 | 86 | 7052 | 89 | 3.1093 | 1060 | 2170 |  | 1.2474 | [35 empty] | Econo 10%-open (2.8V), no compressor, 55/51 ambient, 110% airflow (450 cfm/ton),--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam, adjust--code tester speed to match total static of run T2-TRN-110A-55-1E-DM-SPWCT-SS | W/ECO: Eco set at 2.8v: No Compr:55/51 amb:2HP blwr mtr 5.75 AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.998 | 0.017 | 62.001 | 0.031 | 54.998 | 0.017 | 51.013 | 0.016 | 74.87 | 0.07 | 74.25 | 0.06 | 74.39 | 0.02 | 0.28 | 0.005 | 2.451 | 0.0032 | 2829 | 24 | 4219 | 86 | 3.109 | 0.043 | [6 empty] | 460.5 | 2.1 | 460.6 | 2.1 | 459.2 | 2.1 | 4.2 | 0 | 3.7 | 0 | 3.8 | 0 | 1882.6 | 14.6 | 1090.5 | 17 | 385.6 | 9.7 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.64 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 2255 | [14 empty] | 97.35 | 0.04 | 55.56 | 0.07 | 57.51 | 0.02 | 1.97 | 0.07 | 97.03 | 0.03 | 57.52 | 0.02 | 57.34 | 0.01 | -0.18 | 0.02 |  |  | 69.2 | 0.03 |  |  |  |  | 96.95 | 0.02 | 71.25 | 0.02 | 57.3 | 0.01 | 13.95 | 0.02 | 96.59 | 0.04 | 57.21 | 0.03 | 57.11 | 0.02 | 0.11 | 0.02 | [46 empty] | 97.14 | 0.02 | 57.25 | 0.03 | 57.41 | 0.01 | -0.16 | 0.02 | 97.94 | 0.04 | 57.84 | 0.02 | 1.2 | 0.06 |  |  | 72.91 | 0.03 |  |  |  |  | 97.04 | 0.03 | 57.35 | 0.01 | 13.52 | 0.05 | 96.99 | 0.02 | 59.09 | 0.03 | 57.32 | 0.01 | 1.77 | 0.03 | 57.67 | 0.03 | [28 empty] | 56.82 | 0.05 | 58.05 | 0.04 | 57.67 | 0.03 | 59.42 | 0.07 | 74.2 | 0.05 | 74.14 | 0.04 | 74.05 | 0.04 | 74.43 | 0.02 | 74.46 | 0.02 |  |  | 55.04 | 0.02 | 69.61 | 0.03 | 71.13 | 0.02 | 57.66 | 0.03 | 57.8 | 0.02 | 56.95 | 0.02 | 73.52 | 0.03 | 72.01 | 0.03 | 60.98 | 0.02 | 69.2 | 0.03 | 72.91 | 0.03 | 55.09 | 0.08 | 56.05 | 0.02 | 59.01 | 0.03 | 57.43 | 0.02 | 58.09 | 0.02 | 58.05 | 0.04 | 59.42 | 0.07 | [16 empty] | 55.56 | 0.07 | 56.64 | 0.05 | 56.82 | 0.05 | 57.67 | 0.03 | [16 empty] | 70.87 | 0.05 | [12 empty] | 57.48 | 0.02 | 56.97 | 0.14 | 56.64 | 0.19 | 75.3 | 0.03 | 75.03 | 0.03 | 74.84 | 0.03 | 75.65 | 0.03 | 75.62 | 0.42 | 75.62 | 0.04 | 75.42 | 0.04 | 71.53 | 0.09 | 73.04 | 0.04 | 72.41 | 0.04 | 71.77 | 0.09 | 72.54 | 0.09 | 73.03 | 0.05 | 73.46 | 0.05 | 74.3 | 0.04 | 74.53 | 0.03 | 74.23 | 0.04 | 74.56 | 0.03 | 74.37 | 0.05 | 74.69 | 0.03 | 74.56 | 0.03 | 72.2 | 0.08 | 74.75 | 0.03 | 74.05 | 0.04 | 68.41 | 0.11 | 69.31 | 0.1 |  |  | 75.02 | 0.04 | 75.66 | 0.03 | 75.48 | 0.03 | 75.32 | 0.03 | 74.88 |  | 74.98 | 0.03 | 67.77 | 0.09 | 69.34 | 0.06 | 71.93 | 0.1 | 74.34 | 0.03 | 74.74 | 0.03 | [62 empty] | Economizer test | 74.998 | 0.017 | 62.001 | 0.031 | 74.27 | 0.016 | 61.385 | 0.027 | 54.998 | 0.017 | 51.013 | 0.016 | 3495.9 | 2.3 | 3351.2 | 2.2 | 0.828 | 0.003 | -0.362 | 0.003 | 0.28 | 0.005 | 2.451 | 0.0032 | 29.357 | 0 | 2268 | 11 | 2170 |  | 0 | 0 | 13.03 | 0.362 | 1.691 | 15502.9024 | 325.9836 | 0 | 0 | 15502.9024 | 0.0087818 | 27.6094 | 72.579 | 13.0295 | 13.53 | 0.0069887 | 20.7852 | 0.0087818 | 27.6094 | 0.0085501 | 27.1784 | 74.998 | 62.001 | 26.7662
2 | T2-TRN-110A-55-1F-DM-2 | 75T0107 | T2-TRN-110A-55-1F-DM-2 | 1 finger | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/27/2014 | 23:04:57 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 0 | 4.2 | 0 | 11455 | 39 | 10902 | 91 | 7983 | 157 | 19446 | 155 | 8.6427 | 1057 | 2150 |  | 5.0911 | [35 empty] | Econo 1F-open (5.1V), no compressor, 55/51 ambient, 110% airflow (450 cfm/ton),--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-110A-55-1F-DM-2-SP | W/ECO: 5.1 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.005 | 0.008 | 61.998 | 0.028 | 55.002 | 0.016 | 51.02 | 0.015 | 74.98 | 0.06 | 72.11 | 0.08 | 72.45 | 0.01 | 0.25 | 0.004 | 2.4537 | 0.0031 | 11455 | 39 | 7983 | 157 | 8.645 | 0.081 | [6 empty] | 460 | 2 | 461 | 2 | 460.1 | 2 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1868.1 | 13.8 | 1109.3 | 17.2 | 381.4 | 10.1 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.64 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 2235 | [14 empty] | 97.83 | 0.02 | 60.49 | 0.09 | 57.74 | 0.01 | -2.74 | 0.09 | 97.94 | 0.02 | 59.53 | 0.01 | 57.8 | 0.01 | -1.73 | 0.02 |  |  | 72.15 | 0.02 |  |  |  |  | 97.44 | 0.02 | 71 | 0.02 | 57.52 | 0.01 | 13.48 | 0.02 | 97.26 | 0.02 | 65.11 | 0.02 | 57.42 | 0.01 | 7.69 | 0.02 | [46 empty] | 98.38 | 0.03 | 62.09 | 0.09 | 58.04 | 0.02 | 4.06 | 0.09 | 98.5 | 0.05 | 58.11 | 0.03 | -0.92 | 0.39 |  |  | 71.78 | 0.09 |  |  |  |  | 97.75 | 0.03 | 57.69 | 0.02 | 13.47 | 0.06 | 97.86 | 0.03 | 63.57 | 0.02 | 57.75 | 0.02 | 5.82 | 0.03 | 63.08 | 0.05 | [28 empty] | 61.7 | 0.07 | 61.98 | 0.05 | 63.08 | 0.05 | 63.17 | 0.08 | 72.53 | 0.07 | 71.73 | 0.05 | 71.48 | 0.04 | 72.76 | 0.04 | 72.68 | 0.03 |  |  | 60.3 | 0.04 | 72.41 | 0.04 | 71.77 | 0.04 | 64.66 | 0.04 | 62.64 | 0.1 | 59.16 | 0.32 | 72.34 | 0.09 | 72.32 | 0.02 | 65.48 | 0.04 | 72.15 | 0.02 | 71.78 | 0.09 | 55.26 | 0.03 | 62.72 | 0.02 | 62.84 | 0.02 | 60.16 | 0.22 | 61.32 | 0.15 | 61.98 | 0.05 | 63.17 | 0.08 | [16 empty] | 60.49 | 0.09 | 59.04 | 0.39 | 61.7 | 0.07 | 63.08 | 0.05 | [16 empty] | 71.16 | 0.05 | [12 empty] | 59.6 | 0.03 | 57.52 | 0.19 | 55.99 | 0.05 | 75.42 | 0.02 | 73.27 | 0.03 | 74.87 | 0.02 | 74.25 | 0.04 | 75.83 | 0.66 | 75.78 | 0.02 | 75.4 | 0.03 | 63.59 | 0.17 | 68.33 | 0.1 | 68.43 | 0.3 | 61.32 | 0.07 | 66.07 | 0.11 | 69.34 | 0.07 | 69.93 | 0.04 | 69.54 | 0.05 | 67.41 | 0.07 | 68.9 | 0.08 | 65.81 | 0.08 | 68.57 | 0.07 | 72.11 | 0.07 | 73.03 | 0.07 | 73.54 | 0.05 | 69.56 | 0.09 | 72.7 | 0.06 | 73.23 | 0.06 | 69.48 | 0.07 |  |  | 73.5 | 0.04 | 75.79 | 0.02 | 75.61 | 0.02 | 75.03 | 0.02 | 73.76 |  | 75.1 | 0.02 | 62.03 | 0.08 |  |  | 62.16 | 0.06 | 64.08 | 0.13 | 70.58 | 0.06 | [62 empty] | Economizer test | 75.005 | 0.008 | 61.998 | 0.028 | 71.982 | 0.007 | 60.21 | 0.019 | 55.002 | 0.016 | 51.02 | 0.015 | 3502.3 | 2.2 | 3349.7 | 2.1 | 0.795 | 0.004 | -0.263 | 0.002 | 0.25 | 0.004 | 2.4537 | 0.0031 | 29.179 | 0.001 | 2250 | 11 | 2150 |  | 0.06764 | 226.5732 | 13.03 | 0.263 | 1.6742 | 15600.1241 | 312.8514 | 226.57 | 1043.3297 | 14556.7944 | 0.0086586 | 27.1511 | 70.3078 | 13.0296 | 13.4703 | 0.0069915 | 20.7892 | 0.0087781 | 27.6071 | 0.0083345 | 26.3849 | 73.6713 | 61.3345 | 25.9769
2 | T2-TRN-110A-55-2E-DM | 75T0108 | T2-TRN-110A-55-2E-DM | 20% open | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/21/2014 | 16:35:12 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 0 | 4.2 | 0 | 5393 | 22 | 4993 | 123 | 5355 | 96 | 10753 | 100 | 4.708 | 1060 | 2170 |  | 2.3612 | [35 empty] | Econo 20%-open (3.6V), no compressor, 55/51 ambient, 110% airflow (450 cfm/ton),--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-110A-55-2E-DM-SPWCT-SS | W/ECO: Eco set at 3.6v: No Compr:55/51 amb:2HP blwr mtr 5.75 AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.997 | 0.013 | 61.991 | 0.014 | 55.015 | 0.011 | 51.006 | 0.012 | 74.8 | 0.04 | 73.51 | 0.05 | 73.83 | 0.02 | 0.284 | 0.005 | 2.484 | 0.0032 | 5393 | 22 | 5355 | 96 | 4.708 | 0.049 | [6 empty] | 460.7 | 1.9 | 460.7 | 1.9 | 459.3 | 1.9 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1891.9 | 14.3 | 1091.5 | 15.7 | 392 | 9.7 | 460 |  | 460 |  | 459 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.64 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 2255 | [14 empty] | 97.39 | 0.03 | 55.61 | 0.06 | 57.54 | 0.02 | 1.93 | 0.05 | 97.34 | 0.02 | 57.56 | 0.02 | 57.51 | 0.01 | -0.06 | 0.02 |  |  | 69.72 | 0.02 |  |  |  |  | 97.24 | 0.03 | 71.51 | 0.03 | 57.47 | 0.01 | 14.04 | 0.03 | 96.85 | 0.02 | 57.23 | 0.01 | 57.25 | 0.01 | -0.02 | 0.02 | [46 empty] | 97.44 | 0.01 | 57.3 | 0.01 | 57.57 | 0.01 | -0.27 | 0.01 | 98.25 | 0.04 | 58.02 | 0.02 | 1.24 | 0.05 |  |  | 73.07 | 0.02 |  |  |  |  | 97.35 | 0.01 | 57.52 | 0.01 | 13.55 | 0.04 | 97.28 | 0.01 | 59.12 | 0.02 | 57.49 | 0.01 | 1.63 | 0.02 | 57.83 | 0.04 | [28 empty] | 56.9 | 0.04 | 58.19 | 0.04 | 57.83 | 0.04 | 59.56 | 0.06 | 73.59 | 0.04 | 73.38 | 0.03 | 73.25 | 0.02 | 73.81 | 0.02 | 73.83 | 0.02 |  |  | 54.97 | 0.02 | 70.25 | 0.04 | 71.44 | 0.03 | 57.54 | 0.01 | 57.86 | 0.02 | 57.04 | 0.02 | 73.66 | 0.03 | 72.1 | 0.02 | 60.85 | 0.02 | 69.72 | 0.02 | 73.07 | 0.02 | 54.86 | 0.05 | 55.9 | 0.02 | 59.05 | 0.02 | 57.52 | 0.01 | 58.16 | 0.02 | 58.19 | 0.04 | 59.56 | 0.06 | [16 empty] | 55.61 | 0.06 | 56.78 | 0.06 | 56.9 | 0.04 | 57.83 | 0.04 | [16 empty] | 71.08 | 0.05 | [12 empty] | 57.43 | 0.01 | 56.97 | 0.21 | 56.55 | 0.19 | 75.2 | 0.02 | 74.93 | 0.02 | 74.78 | 0.02 | 75.47 | 0.02 | 75.28 | 0.92 | 75.41 | 0.02 | 75.25 | 0.02 | 66.78 | 0.19 | 72.24 | 0.04 | 71.57 | 0.05 | 67.88 | 0.09 | 69.22 | 0.11 | 70.16 | 0.09 | 71.35 | 0.06 | 73.35 | 0.04 | 72.88 | 0.09 | 72.19 | 0.08 | 72.87 | 0.09 | 72.94 | 0.04 | 74.56 | 0.03 | 74.59 | 0.02 | 73.03 | 0.16 | 74.72 | 0.02 | 74.29 | 0.02 | 68.89 | 0.12 | 67.85 | 0.09 |  |  | 74.91 | 0.02 | 75.45 | 0.02 | 75.31 | 0.02 | 75.18 | 0.02 | 74.8 |  | 74.91 | 0.02 | 65.52 | 0.08 | 64.8 | 0.1 | 69.12 | 0.09 | 71.63 | 0.11 | 74.6 | 0.03 | [62 empty] | Economizer test | 74.997 | 0.013 | 61.991 | 0.014 | 73.597 | 0.014 | 61.033 | 0.015 | 55.015 | 0.011 | 51.006 | 0.012 | 3517.3 | 2.3 | 3376.2 | 2.2 | 0.813 | 0.004 | -0.339 | 0.002 | 0.284 | 0.005 | 2.484 | 0.0032 | 29.362 | 0 | 2284 | 11 | 2170 |  | 0 | 0 | 13.03 | 0.339 | 1.6817 | 15618.1321 | 322.4659 | 0 | 0 | 15618.1321 | 0.0087754 | 27.6022 | 71.9153 | 13.0299 | 13.5124 | 0.006981 | 20.781 | 0.0087754 | 27.6022 | 0.0084807 | 26.9385 | 74.997 | 61.991 | 26.5285
2 | T2-TRN-110A-55-2F-DM-2 | 75T0109 | T2-TRN-110A-55-2F-DM-2 | 2 finger | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/27/2014 | 22:27:59 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 0 | 4.2 | 0 | 16623 | 25 | 16169 | 72 | 10457 | 159 | 27090 | 163 | 11.9287 | 1057 | 2170 |  | 7.3197 | [35 empty] | Econo 2F-open (6V), no compressor, 55/51 ambient, 110% airflow (450 cfm/ton), 2 HP fan motor,--1 turn, 5.75" AK59 pulley (1060 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-110A-55-2F-DM-2-SPWC | W/ECO: 6 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.994 | 0.001 | 61.993 | 0.027 | 54.99 | 0.008 | 50.98 | 0.014 | 74.97 | 0.08 | 70.73 | 0.08 | 71.33 | 0 | 0.246 | 0.006 | 2.486 | 0.0029 | 16623 | 25 | 10457 | 159 | 11.925 | 0.094 | [6 empty] | 460.8 | 2 | 461.4 | 2 | 459.1 | 2 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1906 | 14.4 | 1082.6 | 16 | 365.4 | 10.2 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.6 |  | 3.6 |  | 0.64 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 2255 | [14 empty] | 98.41 | 0.03 | 60.78 | 0.09 | 58.05 | 0.02 | -2.72 | 0.09 | 98.43 | 0.02 | 59.88 | 0.03 | 58.06 | 0.01 | -1.82 | 0.03 |  |  | 71.49 | 0.03 |  |  |  |  | 98.18 | 0.02 | 69.42 | 0.02 | 57.93 | 0.01 | 11.49 | 0.03 | 97.8 | 0.02 | 65.71 | 0.02 | 57.72 | 0.01 | 7.99 | 0.02 | [46 empty] | 99.05 | 0.03 | 62.2 | 0.07 | 58.4 | 0.02 | 3.79 | 0.09 | 99.05 | 0.04 | 58.4 | 0.02 | -0.34 | 0.21 |  |  | 70.71 | 0.12 |  |  |  |  | 98.22 | 0.04 | 57.95 | 0.02 | 11.7 | 0.05 | 98.49 | 0.03 | 63.92 | 0.01 | 58.1 | 0.02 | 5.82 | 0.02 | 62.95 | 0.05 | [28 empty] | 61.78 | 0.08 | 62.16 | 0.06 | 62.95 | 0.05 | 63.19 | 0.09 | 71.33 | 0.07 | 70.28 | 0.05 | 69.98 | 0.04 | 71.51 | 0.04 | 71.41 | 0.04 |  |  | 60.64 | 0.02 | 71.63 | 0.06 | 70.26 | 0.05 | 65.18 | 0.03 | 62.71 | 0.09 | 58.99 | 0.14 | 71.25 | 0.11 | 70.77 | 0.04 | 65.72 | 0.03 | 71.49 | 0.03 | 70.71 | 0.12 | 54.98 | 0.05 | 63.09 | 0.01 | 63.05 | 0.02 | 60.15 | 0.14 | 61.31 | 0.11 | 62.16 | 0.06 | 63.19 | 0.09 | [16 empty] | 60.78 | 0.09 | 58.77 | 0.21 | 61.78 | 0.08 | 62.95 | 0.05 | [16 empty] | 69.65 | 0.06 | [12 empty] | 59.93 | 0.07 | 57.97 | 0.23 | 56.03 | 0.05 | 75.38 | 0.03 | 73.29 | 0.04 | 74.88 | 0.02 | 74.27 | 0.05 | 75.78 | 0.14 | 75.74 | 0.03 | 75.35 | 0.03 | 62.53 | 0.34 | 60.07 | 0.12 | 60.14 | 0.08 | 59.37 | 0.09 | 64.64 | 0.38 | 64.68 | 0.22 | 66.59 | 0.36 | 68.41 | 0.07 | 66.97 | 0.11 | 67.16 | 0.14 | 67.07 | 0.15 | 66.28 | 0.19 | 69.77 | 0.08 | 71.12 | 0.06 | 71.46 | 0.04 | 68.96 | 0.1 | 71.07 | 0.08 | 72.48 | 0.06 | 72.98 | 0.06 |  |  | 73.54 | 0.05 | 75.79 | 0.02 | 75.61 | 0.02 | 75.04 | 0.03 | 73.81 |  | 75.08 | 0.02 | 59.01 | 0.18 |  |  | 63.44 | 0.12 | 63.26 | 0.31 | 67.92 | 0.09 | [62 empty] | Economizer test | 74.994 | 0.001 | 61.993 | 0.027 | 70.631 | 0.006 | 59.475 | 0.024 | 54.99 | 0.008 | 50.98 | 0.014 | 3521.5 | 2.1 | 3376.1 | 2 | 0.764 | 0.004 | -0.22 | 0.002 | 0.246 | 0.006 | 2.486 | 0.0029 | 29.18 | 0.001 | 2271 | 12 | 2170 |  | 0.13362 | 451.1255 | 13.029 | 0.22 | 1.6877 | 15726.9623 | 303.0217 | 451.1287 | 2077.4688 | 13649.4935 | 0.0085391 | 26.7005 | 68.9433 | 13.0292 | 13.4349 | 0.0069731 | 20.7663 | 0.0087774 | 27.6037 | 0.0081896 | 25.8974 | 72.3591 | 60.6698 | 25.4862
2 | T2-TRN-110A-55-3E-DM | 75T0110 | T2-TRN-110A-55-3E-DM | 30% open | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/21/2014 | 15:30:49 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 4.2 | 0 | 8623 | 20 | 8230 | 68 | 6918 | 88 | 15548 | 83 | 6.7836 | 1060 | 2170 |  | 3.7622 | [35 empty] | Econo 30%-open (4.4V), no compressor, 55/51 ambient, 110% airflow (450 cfm/ton),--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-110A-55-3E-DM-SPWCT-SS | W/ECO: Eco set at 4.4v: No Compr:55/51 amb:2HP blwr mtr 5.75 AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.989 | 0.012 | 61.999 | 0.03 | 55.039 | 0.013 | 51.005 | 0.015 | 74.88 | 0.03 | 72.74 | 0.04 | 73.14 | 0.02 | 0.266 | 0.004 | 2.497 | 0.0035 | 8623 | 20 | 6918 | 88 | 6.783 | 0.053 | [6 empty] | 460.6 | 2.6 | 460.7 | 2.6 | 459.4 | 2.6 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1894.8 | 18.2 | 1093.7 | 21.6 | 397.3 | 12.2 | 460 |  | 459 |  | 459 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.64 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 2255 | [14 empty] | 97.88 | 0.03 | 57.15 | 0.05 | 57.82 | 0.01 | 0.66 | 0.05 | 97.55 | 0.02 | 57.52 | 0.03 | 57.63 | 0.01 | 0.11 | 0.03 |  |  | 70.26 | 0.04 |  |  |  |  | 97.43 | 0.02 | 71.35 | 0.02 | 57.57 | 0.01 | 13.78 | 0.02 | 97.05 | 0.02 | 57.23 | 0.01 | 57.36 | 0.01 | -0.12 | 0.01 | [46 empty] | 97.62 | 0.02 | 57.41 | 0.02 | 57.67 | 0.01 | -0.27 | 0.02 | 98.42 | 0.04 | 58.11 | 0.02 | 1.18 | 0.04 |  |  | 72.94 | 0.03 |  |  |  |  | 97.56 | 0.02 | 57.64 | 0.01 | 13.46 | 0.03 | 97.51 | 0.02 | 59.17 | 0.04 | 57.62 | 0.01 | 1.57 | 0.03 | 57.78 | 0.03 | [28 empty] | 56.65 | 0.04 | 58.09 | 0.03 | 57.78 | 0.03 | 59.38 | 0.04 | 73.08 | 0.03 | 72.45 | 0.03 | 72.28 | 0.03 | 73.26 | 0.02 | 73.19 | 0.02 |  |  | 56.76 | 0.21 | 70.78 | 0.03 | 71.64 | 0.02 | 57.65 | 0.02 | 58.01 | 0.02 | 57.16 | 0.02 | 73.51 | 0.04 | 72.17 | 0.04 | 60.94 | 0.03 | 70.26 | 0.04 | 72.94 | 0.03 | 54.84 | 0.04 | 56.29 | 0.05 | 59.07 | 0.03 | 57.73 | 0.01 | 58.45 | 0.01 | 58.09 | 0.03 | 59.38 | 0.04 | [16 empty] | 57.15 | 0.05 | 56.93 | 0.05 | 56.65 | 0.04 | 57.78 | 0.03 | [16 empty] | 71.09 | 0.03 | [12 empty] | 57.43 | 0.01 | 57.27 | 0.22 | 56.79 | 0.23 | 75.32 | 0.02 | 75.09 | 0.03 | 74.88 | 0.02 | 75.66 | 0.03 | 75.66 | 0.03 | 75.6 | 0.04 | 75.4 | 0.04 | 63.57 | 0.14 | 68.19 | 0.22 | 71.23 | 0.08 | 64.75 | 0.13 | 64.35 | 0.14 | 67.81 | 0.18 | 69.98 | 0.1 | 71.52 | 0.11 | 69.18 | 0.18 | 69.22 | 0.19 | 70.14 | 0.24 | 72.12 | 0.06 | 74.35 | 0.04 | 74.59 | 0.02 | 74.54 | 0.05 | 73.87 | 0.07 | 74.48 | 0.02 | 69.56 | 0.12 | 68.71 | 0.11 |  |  | 75.04 | 0.02 | 75.66 | 0.04 | 75.47 | 0.03 | 75.3 | 0.03 | 74.97 |  | 75 | 0.03 | 65.43 | 0.11 | 65.49 | 0.11 | 64.47 | 0.16 | 70.49 | 0.17 | 74.44 | 0.04 | [62 empty] | Economizer test | 74.989 | 0.012 | 61.999 | 0.03 | 72.746 | 0.013 | 60.593 | 0.031 | 55.039 | 0.013 | 51.005 | 0.015 | 3524 | 2.5 | 3388 | 2.4 | 0.8 | 0.003 | -0.308 | 0.002 | 0.266 | 0.004 | 2.497 | 0.0035 | 29.368 | 0.001 | 2292 | 13 | 2170 |  | 0.028221 | 95.6112 | 13.03 | 0.308 | 1.6795 | 15673.6599 | 318.4186 | 95.6128 | 440.2592 | 15233.4007 | 0.0087318 | 27.4163 | 71.0665 | 13.0304 | 13.4901 | 0.0069748 | 20.7801 | 0.0087826 | 27.6081 | 0.0083985 | 26.6411 | 74.4304 | 61.7211 | 26.2318
2 | T2-TRN-110A-55-3F-DM-2 | 75T0111 | T2-TRN-110A-55-3F-DM-2 | 3 finger | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 0:04:41 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 4.2 | 0 | 22518 | 32 | 21963 | 113 | 13246 | 163 | 35777 | 173 | 15.6573 | 1057 | 2190 |  | 9.8547 | [35 empty] | Econo 3F-open (6.9V), no compressor, 55/51 ambient, 110% airflow (450 cfm/ton),--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-110A-55-3F-DM-2-SP | W/ECO: 6.9 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.001 | 0.004 | 62.003 | 0.033 | 54.997 | 0.011 | 50.988 | 0.008 | 74.81 | 0.08 | 69.08 | 0.08 | 70.09 | 0.01 | 0.252 | 0.005 | 2.5149 | 0.0039 | 22518 | 32 | 13246 | 163 | 15.656 | 0.105 | [6 empty] | 460.2 | 1.9 | 461.1 | 1.9 | 459.8 | 1.9 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1895 | 13.5 | 1102.7 | 15.7 | 390 | 8.9 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.65 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 |  | 2275 | [14 empty] | 98.81 | 0.06 | 61.02 | 0.08 | 58.27 | 0.03 | -2.75 | 0.07 | 98.85 | 0.04 | 60.24 | 0.02 | 58.3 | 0.02 | -1.94 | 0.02 |  |  | 69.72 | 0.04 |  |  |  |  | 98.74 | 0.06 | 67.5 | 0.01 | 58.24 | 0.03 | 9.26 | 0.03 | 98.31 | 0.05 | 66.22 | 0.02 | 58 | 0.02 | 8.22 | 0.03 | [46 empty] | 99.06 | 0.04 | 57.8 | 0.07 | 58.4 | 0.02 | -0.61 | 0.08 | 99.12 | 0.08 | 58.44 | 0.04 | -3.32 | 0.08 |  |  | 67.97 | 0.06 |  |  |  |  | 98.21 | 0.05 | 57.95 | 0.03 | 8.37 | 0.1 | 98.3 | 0.04 | 64.29 | 0.02 | 57.99 | 0.02 | 6.29 | 0.02 | 61.27 | 0.11 | [28 empty] | 61.59 | 0.07 | 61.98 | 0.05 | 61.27 | 0.11 | 62.1 | 0.08 | 69.83 | 0.06 | 68.67 | 0.05 | 68.36 | 0.05 | 69.9 | 0.04 | 69.77 | 0.04 |  |  | 60.9 | 0.03 | 69.55 | 0.07 | 68.36 | 0.07 | 65.48 | 0.06 | 58.47 | 0.1 | 61.81 | 0.07 | 68.59 | 0.05 | 67.68 | 0.05 | 66.1 | 0.02 | 69.72 | 0.04 | 67.97 | 0.06 | 54.76 | 0.04 | 63.23 | 0.02 | 63 | 0.02 | 59.94 | 0.12 | 60.96 | 0.12 | 61.98 | 0.05 | 62.1 | 0.08 | [16 empty] | 61.02 | 0.08 | 61.76 | 0.08 | 61.59 | 0.07 | 61.27 | 0.11 | [16 empty] | 66.32 | 0.08 | [12 empty] | 60.17 | 0.04 | 58.24 | 0.26 | 56.1 | 0.08 | 75.23 | 0.03 | 73.45 | 0.04 | 74.8 | 0.03 | 74.27 | 0.05 | 75.5 | 0.3 | 75.56 | 0.04 | 75.19 | 0.04 | 61.94 | 0.15 | 59.27 | 0.11 | 58.11 | 0.08 | 59.26 | 0.15 | 61.6 | 0.16 | 62.24 | 0.18 | 60.25 | 0.27 | 65.33 | 0.14 | 64.86 | 0.13 | 64.2 | 0.17 | 65 | 0.12 | 63.73 | 0.22 | 66.76 | 0.1 | 67.72 | 0.09 | 67.79 | 0.08 | 67.02 | 0.24 | 68.93 | 0.17 | 70.65 | 0.12 | 71.24 | 0.08 |  |  | 73.7 | 0.05 | 75.74 | 0.03 | 75.57 | 0.03 | 75.06 | 0.03 | 73.9 |  | 75.06 | 0.02 | 56.82 | 0.09 |  |  | 63.67 | 0.15 | 64.33 | 0.12 | 65.51 | 0.11 | [62 empty] | Economizer test | 75.001 | 0.004 | 62.003 | 0.033 | 69.125 | 0.006 | 58.665 | 0.023 | 54.997 | 0.011 | 50.988 | 0.008 | 3538.1 | 2.8 | 3400.2 | 2.7 | 0.726 | 0.004 | -0.174 | 0.002 | 0.252 | 0.005 | 2.5149 | 0.0039 | 29.175 | 0.001 | 2285 | 11 | 2190 |  | 0.20876 | 709.8198 | 13.029 | 0.174 | 1.7045 | 15847.4936 | 290.0055 | 709.8302 | 3268.7515 | 12578.742 | 0.0084097 | 26.2 | 67.4205 | 13.0294 | 13.3956 | 0.0069757 | 20.7708 | 0.0087824 | 27.6108 | 0.0080417 | 25.369 | 70.8857 | 59.9205 | 24.9539
2 | T2-TRN-110A-55-OE-DM-2 | 75T0114 | T2-TRN-110A-55-OE-DM-2 | open | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/28/2014 | 1:36:14 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 4.2 | 0 | 48516 | 85 | 47919 | 365 | 26221 | 213 | 74761 | 243 | 32.604 | 1057 | 2190 |  | 21.1583 | [35 empty] | Econo fully open, no compressor, 55/51 ambient, 110% airflow (450 cfm/ton), 2 HP fan motor,--1 turn, 5.75" AK59 pulley (1060 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-110A-55-OE-DM-2-SPWCT- | W/ECO: 10 V No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.981 | 0.017 | 62.008 | 0.021 | 54.99 | 0.013 | 50.95 | 0.012 | 74.86 | 0.11 | 62.29 | 0.08 | 64.37 | 0.02 | 0.245 | 0.004 | 2.4608 | 0.0032 | 48516 | 85 | 26221 | 213 | 32.604 | 0.183 | [6 empty] | 460.2 | 1.9 | 461.1 | 1.9 | 459.8 | 1.9 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1898.9 | 13.7 | 1105.3 | 16.2 | 393.8 | 9.4 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.65 | [23 empty] | 0.6 |  | 0 |  | 0 |  | 85 | [16 empty] | 97.87 | 0.09 | 60.95 | 0.08 | 57.78 | 0.04 | -3.18 | 0.07 | 98.36 | 0.06 | 59.79 | 0.04 | 58.04 | 0.03 | -1.75 | 0.05 |  |  | 62.07 | 0.04 |  |  |  |  | 98.1 | 0.06 | 59.25 | 0.03 | 57.89 | 0.03 | 1.36 | 0.05 | 97.5 | 0.07 | 66.67 | 0.02 | 57.56 | 0.04 | 9.11 | 0.05 | [46 empty] | 99.26 | 0.07 | 57.9 | 0.04 | 58.53 | 0.04 | -0.63 | 0.03 | 98 | 0.08 | 57.84 | 0.04 | -0.69 | 0.76 |  |  | 58.62 | 0.11 |  |  |  |  | 93.53 | 0.22 | 55.34 | 0.13 | 3.4 | 0.2 | 93.47 | 0.2 | 64.44 | 0.03 | 55.31 | 0.12 | 9.14 | 0.11 | 59.11 | 0.61 | [28 empty] | 61.52 | 0.06 | 62.08 | 0.06 | 59.11 | 0.61 | 59.78 | 0.1 | 62.68 | 0.09 | 62.22 | 0.07 | 61.85 | 0.06 | 62.49 | 0.06 | 62.28 | 0.05 |  |  | 60.64 | 0.03 | 61.56 | 0.07 | 59.62 | 0.07 | 66.09 | 0.04 | 58.81 | 0.05 | 58.82 | 0.65 | 59.19 | 0.12 | 59.94 | 0.05 | 66.14 | 0.03 | 62.07 | 0.04 | 58.62 | 0.11 | 54.77 | 0.11 | 63.14 | 0.02 | 63.02 | 0.02 | 60.02 | 0.56 | 61.21 | 0.69 | 62.08 | 0.06 | 59.78 | 0.1 | [16 empty] | 60.95 | 0.08 | 58.47 | 0.78 | 61.52 | 0.06 | 59.11 | 0.61 | [16 empty] | 58.75 | 0.09 | [12 empty] | 59.75 | 0.07 | 59.16 | 0.3 | 56.85 | 0.1 | 75.13 | 0.04 | 74.69 | 0.05 | 74.82 | 0.05 | 75.49 | 0.05 | 75.47 | 0.1 | 75.48 | 0.05 | 75.3 | 0.06 | 54.62 | 0.13 | 58.82 | 0.14 | 58.71 | 0.14 | 53.91 | 0.13 | 60.81 | 0.13 | 61.95 | 0.12 | 57.94 | 0.16 | 59.74 | 0.19 | 61.71 | 0.11 | 61.82 | 0.13 | 61.89 | 0.1 | 61.48 | 0.11 | 61.85 | 0.1 | 60.89 | 0.13 | 58.95 | 0.16 | 63.97 | 0.19 | 63.75 | 0.15 | 61.5 | 0.22 | 63.63 | 0.22 |  |  | 74.95 | 0.06 | 75.57 | 0.05 | 75.44 | 0.06 | 75.27 | 0.06 | 74.9 |  | 74.97 | 0.05 | 54.17 | 0.13 |  |  | 56.99 | 0.14 | 60.17 | 0.13 | 61.77 | 0.11 | [62 empty] | Economizer test | 74.981 | 0.017 | 62.008 | 0.021 | 62.26 | 0.01 | 54.695 | 0.019 | 54.99 | 0.013 | 50.95 | 0.012 | 3478.6 | 2.3 | 3386.9 | 2.2 | 0.65 | 0.004 | -0.098 | 0.001 | 0.245 | 0.004 | 2.4608 | 0.0032 | 29.202 | 0.001 | 2293 | 11 | 2190 |  | 0.5493 | 1860.4146 | 13.029 | 0.098 | 1.7386 | 15792.8377 | 258.6312 | 1860.4189 | 8567.3973 | 7225.4404 | 0.0077959 | 23.8901 | 60.5214 | 13.0291 | 13.2159 | 0.0069571 | 20.749 | 0.0087904 | 27.6147 | 0.0073069 | 22.897 | 64.1527 | 56.3097 | 22.4741
2 | T2-TRN-110A-55-CE-DM-2 | 75T0213 | T2-TRN-110A-55-CE-DM-2 | closed | off | off |  | unsealed | unsealed | [5 empty] | CUST 5 | 10/27/2014 | 8:10:31 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 0 | 4.1 | 0 | 2345 | 33 | 1695 | 110 | 2308 | 143 | 4655 | 163 | 2.1016 | 1059 | 2090 |  | 1.0587 | [35 empty] | Econo closed (2V), no compressor, 55/51 ambient, 110% airflow (450 cfm/ton), 2 HP fan motor,--1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam, adjust code tester speed to--match total static of run T2-TRN-110A-55-CE-DM-2-SPWCT-SS | W/ECO: No comp: 55/51 amb:2HP blwr mtr 5.75` AK59 mtr. pulley: 1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.031 | 0.03 | 61.996 | 0.021 | 54.982 | 0.022 | 51.009 | 0.02 | 74.96 | 0.04 | 74.51 | 0.03 | 74.57 | 0.03 | 0.25 | 0.005 | 2.3738 | 0.0035 | 2345 | 33 | 2308 | 143 | 2.102 | 0.074 | [6 empty] | 460.2 | 1.9 | 461 | 2 | 459.8 | 1.9 | 4.1 | 0 | 3.6 | 0 | 3.8 | 0 | 1855.7 | 14.3 | 1099.9 | 16 | 358.7 | 9.3 | 460 |  | 459 |  | 459 |  | 3.6 |  | 3.6 |  | 3.6 |  | 0.62 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 2175 | [14 empty] | 97.06 | 0.03 | 57.24 | 0.09 | 57.33 | 0.02 | 0.08 | 0.08 | 95.82 | 0.03 | 59.41 | 0.02 | 56.64 | 0.02 | -2.77 | 0.01 |  |  | 72.19 | 0.03 |  |  |  |  | 96.55 | 0.03 | 72.48 | 0.03 | 57.03 | 0.01 | 15.44 | 0.03 | 95.69 | 0.05 | 60.97 | 0.04 | 56.55 | 0.02 | 4.42 | 0.04 | [46 empty] | 96.99 | 0.03 | 59.8 | 0.02 | 57.28 | 0.02 | 2.53 | 0.02 | 97.58 | 0.03 | 57.61 | 0.02 | 0.75 | 0.07 |  |  | 73.83 | 0.03 |  |  |  |  | 96.78 | 0.03 | 57.16 | 0.02 | 15.06 | 0.03 | 96.65 | 0.03 | 60.43 | 0.03 | 57.09 | 0.01 | 3.34 | 0.03 | 58.95 | 0.06 | [28 empty] | 57.16 | 0.04 | 59.14 | 0.03 | 58.95 | 0.06 | 59.53 | 0.05 | 74.5 | 0.03 | 74.31 | 0.03 | 74.14 | 0.03 | 74.78 | 0.03 | 74.8 | 0.02 |  |  | 56.94 | 0.04 | 72.62 | 0.02 | 72.89 | 0.02 | 60.99 | 0.03 | 60.51 | 0.02 | 57.1 | 0.03 | 74.44 | 0.03 | 73.39 | 0.03 | 61.72 | 0.02 | 72.19 | 0.03 | 73.83 | 0.03 | 55.41 | 0.12 | 58.23 | 0.06 | 60.26 | 0.02 | 57.98 | 0.06 | 59.06 | 0.1 | 59.14 | 0.03 | 59.53 | 0.05 | [16 empty] | 57.24 | 0.09 | 56.85 | 0.08 | 57.16 | 0.04 | 58.95 | 0.06 | [16 empty] | 72.22 | 0.03 | [12 empty] | 59.57 | 0.01 | 56.32 | 0.1 | 55.7 | 0.07 | 75.41 | 0.03 | 73.19 | 0.04 | 74.84 | 0.04 | 74.21 | 0.05 | 75.81 | 0.03 | 75.81 | 0.03 | 75.46 | 0.04 | 67.61 | 0.11 | 72.53 | 0.05 | 71.95 | 0.04 | 69.5 | 0.15 | 71.23 | 0.08 | 71.99 | 0.05 | 72.55 | 0.04 | 73.22 | 0.04 | 73.22 | 0.05 | 72.9 | 0.05 | 72.48 | 0.04 | 74.2 | 0.04 | 74.66 | 0.04 | 74.74 | 0.03 | 74.53 | 0.06 | 74.92 | 0.04 | 74.76 | 0.03 | 70.2 | 0.18 | 69.08 | 0.09 |  |  | 73.5 | 0.06 | 75.78 | 0.03 | 75.6 | 0.04 | 75.01 | 0.04 | 73.54 |  | 75.04 | 0.03 | 68.09 | 0.08 |  |  | 70.42 | 0.1 | 71.92 | 0.05 | 74.46 | 0.04 | [62 empty] | Economizer test | 75.031 | 0.03 | 61.996 | 0.021 | 74.406 | 0.026 | 61.598 | 0.019 | 54.982 | 0.022 | 51.009 | 0.02 | 3450.3 | 2.5 | 3287.4 | 2.4 | 0.856 | 0.004 | -0.345 | 0.003 | 0.25 | 0.005 | 2.3738 | 0.0035 | 29.2 | 0.001 | 2215 | 11 | 2090 |  | 0 | 0 | 13.029 | 0.345 | 1.6353 | 15295.8172 | 330.5913 | 0 | 0 | 15295.8172 | 0.0087707 | 27.6053 | 72.7707 | 13.0291 | 13.5343 | 0.0069904 | 20.7831 | 0.0087707 | 27.6053 | 0.008657 | 27.3285 | 75.031 | 61.996 | 26.9297
2 | T2-MF11-85C1-85C2-110A-95-CCE | 75T0031 | T2-MF11-85C1-85C2-110A-95-CCE | closed | on | on | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 30 | 0 | CUST 5 | 10/11/2014 | 2:36:26 | 10 Ton | 0:15:05 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 5.44 lbs/CK2: 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 460.1 | 1.4 | 16.4 | 0 | 57252 | 93 | 56857 | 432 | 191 | 114 | 57409 | 123 | 5.9197 | 1062 |  |  | 5.9035 | [35 empty] | MF11, 85% charge CK1 and CK2, 110% airflow (450 cfm/ton), 30% condenser coil blockage,--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), adjust code tester speed to--match total static of run T2-MF7-100C1-100C2-110A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 1 turns open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 25.25` of 62` coil | 75.034 | 0.011 | 61.99 | 0.02 | 94.979 | 0.039 | 75.002 | 0.031 | 75.04 | 0.11 | 59.89 | 0.02 | 62.36 | 0.02 | 0.261 | 0.004 | 2.4376 | 0.0034 | 57252 | 93 | 191 | 114 | 5.92 | 0.017 | [6 empty] | 460.1 | 2.6 | 461.5 | 2.6 | 459.9 | 2.5 | 16.4 | 0 | 14.2 | 0 | 14.2 | 0 | 7510.3 | 49.6 | 3284.3 | 60.4 | 2188.2 | 38.7 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.65 | 460 |  | 460 |  | 460 |  | 5.4 |  | 5.2 |  | 4.7 |  | 3470 |  | 0.85 | 460 | 460 | 460 | 5.3 | 5 | 4.6 | 3270 | 0.83 | 459.1 |  | 1.6 |  | 673.9 |  | 85 |  | 9698.9 | [14 empty] | 237.05 | 0.2 | 112.53 | 0.06 | 113.2 | 0.06 | 0.67 | 0.04 | 271.6 | 0.19 | 200.92 | 0.21 | 123.18 | 0.05 | -77.75 | 0.18 | 225.7 | 0.05 | 108.77 | 0.06 | 109.7 | 0.05 | 0.92667 | 0.05 | 74.24 | 0.04 | 68.9 | 0.07 | 43.62 | 0.03 | 25.28 | 0.05 | 73.63 | 0.04 | 72.14 | 0.07 | 43.22 | 0.03 | 28.92 | 0.05 | [46 empty] | 275.16 | 0.2 | 182.28 | 0.09 | 124.15 | 0.05 | 58.12 | 0.09 | 250.74 | 0.26 | 117.27 | 0.08 | 2.31 | 0.07 | 236.8 | 0.05 | 108.67 | 0.06 | 113.73 | 0.05 | 5.0267 | 0.05 | 81.39 | 0.07 | 48.18 | 0.04 | 3.18 | 0.28 | 81.03 | 0.05 | 62.57 | 0.16 | 47.98 | 0.03 | 14.59 | 0.1 | 115.45 | 0.1 | [28 empty] | 111.47 | 0.06 | 111.25 | 0.06 | 115.45 | 0.1 | 115.57 | 0.07 | 59.3 | 0.03 | 60.04 | 0.03 | 59.92 | 0.02 | 59.68 | 0.03 | 59.68 | 0.03 |  |  | 112.32 | 0.06 | 106.23 | 0.06 | 69.68 | 0.09 | 72.69 | 0.08 | 182.5 | 0.09 | 115.44 | 0.11 | 107.17 | 0.04 | 51.9 | 0.24 | 62.57 | 0.16 | 108.77 | 0.06 | 108.67 | 0.06 | 93.16 | 0.23 | 112.42 | 0.05 | 111.49 | 0.06 | 116.19 | 0.06 | 116.33 | 0.07 | 111.25 | 0.06 | 115.57 | 0.07 | [16 empty] | 112.53 | 0.06 | 114.96 | 0.11 | 111.47 | 0.06 | 115.45 | 0.1 | [16 empty] | 51.36 | 0.26 | [12 empty] | 202.15 | 0.21 | 94.08 | 0.11 | 93.61 | 0.11 | 75.32 | 0.05 | 75.54 | 0.05 | 75.06 | 0.05 | 75.8 | 0.06 | 75.66 | 0.05 | 75.68 | 0.06 | 75.49 | 0.06 | 79.88 | 0.12 | 76.76 | 0.06 | 76.77 | 0.05 | 78.28 | 0.08 | 78.2 | 0.07 | 77.41 | 0.06 | 76.81 | 0.05 | 75.76 | 0.06 | 75.42 | 0.07 | 75.83 | 0.07 | 75.12 | 0.07 | 75.27 | 0.07 | 75.21 | 0.07 | 75.22 | 0.06 | 75.62 | 0.06 | 75.38 | 0.07 | 75.37 | 0.05 | 76.38 | 0.06 | 76.38 | 0.07 |  |  | 75.12 | 0.06 | 75.41 | 0.05 | 75.55 | 0.06 | 75.38 | 0.06 | 75.47 |  | 75.16 | 0.07 |  |  | 81.82 | 0.07 | 78.78 | 0.07 | 75.5 | 0.07 | 75.26 | 0.07 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 75.034 | 0.011 | 61.99 | 0.02 | 59.783 | 0.017 | 56.433 | 0.02 | 94.979 | 0.039 | 75.002 | 0.031 | 3450.4 | 2.4 | 3377.2 | 2.3 | 0.856 | 0.003 | -0.377 | 0.002 | 0.261 | 0.004 | 2.4376 | 0.0034 | 29.313 | 0.001 | 9698 | 16 | 2200 |  | 0 | 0 | 13.029 | 0.345 | 1.682 | 15724.5877 | 339.6219 | 0 | 0 | 15724.5877 | 0.008766 | 27.6009 | 58.101 | 14.0994 | 13.1656 | 0.013928 | 38.1594 | 0.008766 | 27.6009 | 0.0089004 | 24.0275 | 75.034 | 61.99 | 23.6172 | 62642.6686 | 63903.3751 | 7498 | 0.40852 | 56293.198 | 57553.9045 | 5.8046 | 0.19251 | -3.9837 | -16.933 | 54.0642 | 62642.6686 | 56190.5402 | 6452.1284 | 0 | 62642.6686 | 100%
2 | T2-MF26-115C1-115C2-110A-95-CE | 75T0037 | T2-MF26-115C1-115C2-110A-95-CE | closed | on | on | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/8/2014 | 5:10:07 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 7.36 lbs/CK2- 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 460.3 | 1.3 | 16 | 0 | 62478 | 72 | 62057 | 458 | 4530 | 100 | 67012 | 103 | 7.132 | 1060 |  |  | 6.6494 | [35 empty] | MF26, 115% charge CK1 and CK2, 110% airflow (450 cfm/ton), 2 HP fan motor,--1 turn, 5.75" AK59 pulley (1060 rpm), adjust code tester speed to match total static--of run T2-MF25-115C1-100C2-110A-95-CE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 1 turns open: AX 35 belt: 100% inlet-outlet Meriam. | 74.993 | 0.011 | 61.998 | 0.016 | 94.993 | 0.014 | 74.997 | 0.018 | 74.87 | 0.14 | 58.19 | 0.1 | 61.04 | 0.01 | 0.319 | 0.003 | 1.6111 | 0.0031 | 62478 | 72 | 4530 | 100 | 7.132 | 0.017 | [6 empty] | 460.3 | 2.4 | 461.2 | 2.3 | 459.8 | 2.3 | 16 | 0 | 13.9 | 0 | 13.7 | 0 | 7322 | 47.2 | 3239 | 54.9 | 2074.4 | 35.7 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.65 | 460 |  | 460 |  | 460 |  | 5.1 |  | 4.9 |  | 4.4 |  | 3210 |  | 0.83 | 460 | 460 | 460 | 5.2 | 4.8 | 4.5 | 3190 | 0.82 | 459.3 |  | 1.6 |  | 700.4 |  | 85 |  | 9395.4 | [14 empty] | 228.08 | 0.14 | 100.46 | 0.1 | 110.45 | 0.04 | 9.98 | 0.09 | 251.09 | 0.14 | 173.05 | 0.07 | 117.37 | 0.04 | 55.68 | 0.05 | 221.5 | 0.05 | 99.25 | 0.06 | 108.37 | 0.05 | 9.07 | 0.05 | 77.13 | 0.03 | 49.44 | 0.15 | 45.5 | 0.02 | 3.94 | 0.15 | 76.49 | 0.03 | 55.74 | 0.11 | 45.08 | 0.02 | 10.66 | 0.11 | [46 empty] | 264.17 | 0.16 | 176.58 | 0.3 | 121.11 | 0.04 | 55.47 | 0.32 | 247.72 | 0.34 | 116.39 | 0.1 | 17.98 | 0.1 | 236.4 | 0.05 | 92.6 | 0.05 | 113 | 0.05 | 20.4 | 0.05 | 79.68 | 0.19 | 47.11 | 0.12 | 4.11 | 1.39 | 79.31 | 0.16 | 57.16 | 0.1 | 46.88 | 0.1 | 10.28 | 0.13 | 97.95 | 0.06 | [28 empty] | 100.64 | 0.09 | 100.51 | 0.08 | 97.95 | 0.06 | 98.23 | 0.09 | 57.69 | 0.08 | 58.26 | 0.06 | 58.16 | 0.05 | 57.87 | 0.07 | 57.94 | 0.06 |  |  | 99.94 | 0.07 | 98.05 | 0.11 | 50.35 | 0.3 | 55.42 | 0.13 | 176.59 | 0.38 | 95.86 | 0.07 | 92.18 | 0.04 | 51.36 | 1.48 | 59.25 | 0.61 | 99.25 | 0.06 | 98.41 | 0.06 | 93.05 | 0.14 | 101.26 | 0.07 | 101.09 | 0.07 | 99.14 | 0.07 | 99.35 | 0.06 | 100.51 | 0.08 | 98.23 | 0.09 | [16 empty] | 100.46 | 0.1 | 98.41 | 0.06 | 100.64 | 0.09 | 97.95 | 0.06 | [16 empty] | 51.2 | 1.28 | [12 empty] | 174.02 | 0.09 | 95.15 | 0.07 | 95.08 | 0.07 | 75.17 | 0.06 | 75.45 | 0.05 | 75.03 | 0.04 | 75.64 | 0.07 | 75.52 | 0.06 | 75.59 | 0.07 | 75.4 | 0.06 | 78.92 | 0.08 | 76.89 | 0.06 | 77.1 | 0.05 | 77.87 | 0.09 | 78.15 | 0.09 | 77.48 | 0.08 | 76.93 | 0.06 | 75.59 | 0.07 | 75.24 | 0.08 | 75.63 | 0.09 | 75.04 | 0.07 | 75.27 | 0.07 | 75.2 | 0.06 | 75.23 | 0.06 | 76.64 | 0.07 | 75.38 | 0.07 | 75.47 | 0.05 | 79.84 | 0.12 | 79.46 | 0.18 |  |  | 75.06 | 0.05 | 75.41 | 0.04 | 75.58 | 0.05 | 75.38 | 0.06 | 75.45 |  | 75.14 | 0.06 | 81.11 | 0.05 | 81.08 | 0.06 | 78.74 | 0.09 | 75.33 | 0.08 | 75.25 | 0.07 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 74.993 | 0.011 | 61.998 | 0.016 | 58.196 | 0.015 | 55.366 | 0.019 | 94.993 | 0.014 | 74.997 | 0.018 | 3401.3 | 3.3 | 3338.9 | 3.2 | 0.851 | 0.003 | -0.371 | 0.002 | 0.319 | 0.003 | 1.6111 | 0.0031 | 29.309 | 0.001 | 9396 | 17 | 2210 |  | 0 | 0 | 13.029 | 0.345 | 1.7152 | 15550.6311 | 333.809 | 0 | 0 | 15550.6311 | 0.008781 | 27.6073 | 56.4808 | 14.0997 | 13.1235 | 0.01392 | 38.1543 | 0.008781 | 27.6073 | 0.0086508 | 23.3691 | 74.993 | 61.998 | 22.9508 | 72410.783 | 69090.5117 | 7186 | 0.3387 | 66007.3432 | 62687.0719 | 7.025 | 0.15302 | -4.6565 | -18.5122 | 53.1361 | 72410.783 | 65906.7686 | 6504.0144 | 0 | 72410.783 | 100%
2 | T2-MF29-85C1-85C2-110A-95-CE | 75T0038 | T2-MF29-85C1-85C2-110A-95-CE | closed | on | on | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/8/2014 | 7:45:37 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 5.44 lbs/CK2- 5.27 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 5.44 | 5.27 | 6.4 | 6.2 | 460 | 1.5 | 15.7 | 0 | 58375 | 92 | 57792 | 407 | 1542 | 173 | 59919 | 201 | 6.5845 | 1060 |  |  | 6.4148 | [35 empty] | MF29, 85% charge CK1 and CK2, 110% airflow (450 cfm/ton), 2 HP fan motor,--1 turn, 5.75" AK59 pulley (1060 rpm), adjust code tester speed to match total--static of run T2-MF25-3260-95-C-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75" mtr. pulley: 1 turns open: AX 35 belt: 100% inlet-outlet Meriam. ; | 75.032 | 0.015 | 62.004 | 0.029 | 94.991 | 0.027 | 75.003 | 0.015 | 74.87 | 0.13 | 59.3 | 0.07 | 61.94 | 0.02 | 0.314 | 0.004 | 1.6114 | 0.0033 | 58375 | 92 | 1542 | 173 | 6.584 | 0.025 | [6 empty] | 460 | 2.5 | 461.2 | 2.5 | 459.8 | 2.5 | 15.7 | 0 | 13.6 | 0 | 13.4 | 0 | 7159.6 | 49.9 | 3219.1 | 60.2 | 1940.7 | 37.5 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.8 |  | 3.9 |  | 0.65 | 460 |  | 460 |  | 460 |  | 5 |  | 4.8 |  | 4.3 |  | 3110 |  | 0.83 | 460 | 460 | 460 | 4.9 | 4.6 | 4.3 | 2970 | 0.8 | 459 |  | 1.6 |  | 700.9 |  | 85 |  | 8970.9 | [14 empty] | 210.68 | 0.18 | 104.48 | 0.1 | 104.89 | 0.06 | 0.41 | 0.09 | 242.7 | 0.16 | 190.04 | 0.21 | 114.9 | 0.05 | 75.14 | 0.22 | 198.9 | 0.05 | 100.55 | 0.07 | 100.93 | 0.05 | 0.32 | 0.05 | 72.03 | 0.04 | 69.43 | 0.08 | 42.17 | 0.03 | 27.26 | 0.06 | 71.44 | 0.04 | 71.59 | 0.08 | 41.77 | 0.03 | 29.82 | 0.06 | [46 empty] | 246.89 | 0.16 | 170.15 | 0.11 | 116.14 | 0.05 | 54.01 | 0.1 | 223.23 | 0.23 | 108.93 | 0.07 | 1.39 | 0.07 | 211.9 | 0.05 | 100.33 | 0.07 | 105.28 | 0.05 | 4.95 | 0.05 | 80.21 | 0.05 | 47.46 | 0.03 | 4.39 | 0.36 | 79.86 | 0.05 | 72.55 | 0.09 | 47.24 | 0.03 | 25.31 | 0.11 | 106.91 | 0.08 | [28 empty] | 103 | 0.1 | 102.44 | 0.08 | 106.91 | 0.08 | 106.72 | 0.1 | 58.78 | 0.07 | 59.41 | 0.06 | 59.34 | 0.06 | 59.02 | 0.06 | 59.09 | 0.05 |  |  | 103.09 | 0.05 | 99.23 | 0.11 | 69.9 | 0.13 | 71.28 | 0.11 | 170.17 | 0.12 | 103.98 | 0.06 | 99.62 | 0.05 | 51.63 | 0.42 | 60.76 | 0.16 | 100.55 | 0.07 | 107.54 | 0.09 | 93.24 | 0.14 | 104.52 | 0.05 | 102.99 | 0.06 | 107.49 | 0.04 | 107.64 | 0.05 | 102.44 | 0.08 | 106.72 | 0.1 | [16 empty] | 104.48 | 0.1 | 107.54 | 0.09 | 103 | 0.1 | 106.91 | 0.08 | [16 empty] | 51.85 | 0.35 | [12 empty] | 191.19 | 0.21 | 95.25 | 0.08 | 95.18 | 0.09 | 75.23 | 0.06 | 75.5 | 0.06 | 75.07 | 0.05 | 75.7 | 0.07 | 75.58 | 0.07 | 75.63 | 0.07 | 75.44 | 0.07 | 78.99 | 0.09 | 76.92 | 0.05 | 77.12 | 0.05 | 77.94 | 0.11 | 78.21 | 0.1 | 77.54 | 0.09 | 76.97 | 0.07 | 75.59 | 0.08 | 75.27 | 0.16 | 75.66 | 0.09 | 75.03 | 0.07 | 75.3 | 0.07 | 75.23 | 0.07 | 75.27 | 0.07 | 76.63 | 0.07 | 75.41 | 0.07 | 75.6 | 0.05 | 79.86 | 0.09 | 79.48 | 0.11 |  |  | 75.1 | 0.06 | 75.45 | 0.05 | 75.59 | 0.06 | 75.4 | 0.06 | 75.44 |  | 75.13 | 0.07 | 81.15 | 0.06 | 81.5 | 0.07 | 78.79 | 0.11 | 75.34 | 0.09 | 75.29 | 0.07 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 75.032 | 0.015 | 62.004 | 0.029 | 59.308 | 0.017 | 56.107 | 0.024 | 94.991 | 0.027 | 75.003 | 0.015 | 3402.5 | 3.4 | 3337.6 | 3.4 | 0.852 | 0.003 | -0.371 | 0.002 | 0.314 | 0.004 | 1.6114 | 0.0033 | 29.346 | 0 | 9100 | 17 | 2190 |  | 0 | 0 | 13.029 | 0.345 | 1.6999 | 15521.2214 | 334.0712 | 0 | 0 | 15521.2214 | 0.0087757 | 27.6111 | 57.6081 | 14.0997 | 13.153 | 0.013926 | 38.1602 | 0.0087757 | 27.6111 | 0.0088205 | 23.8247 | 75.032 | 62.004 | 23.41 | 65204.8664 | 64905.7936 | 6910 | 0.36169 | 58870.5813 | 58571.5085 | 6.4693 | 0.18103 | -4.201 | -17.4239 | 53.7566 | 65204.8664 | 58769.1057 | 6435.7607 | 0 | 65204.8664 | 100%
2 | T2-MF39-100C1-100C2-110A-95-CE | 75T0042 | T2-MF39-100C1-100C2-110A-95-CE | closed | on | on | 1 turn | unsealed | unsealed | 1056 | 5.75 |  | 0 | 0 | CUST 5 | 10/9/2014 | 11:07:57 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 1.5 | 16 | 0 | 62291 | 67 | 61956 | 385 | 2648 | 149 | 64941 | 160 | 7.0169 | 1060 |  |  | 6.7305 | [35 empty] | MF39, 100% charge CK1 and CK2, 108% airflow (425 cfm/ton), 2 HP fan motor--1 turn, 5.75" AK59 pulley (1056 rpm), adjust code tester speed to match total--static of run T2-MF39-100C1-100C2-110A-95-CE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 1 turns open: AX 35 belt: 100% inlet-outlet Meriam | 75.022 | 0.012 | 61.984 | 0.026 | 95.014 | 0.016 | 75.008 | 0.016 | 75.01 | 0.12 | 58.47 | 0.07 | 61.27 | 0.01 | 0.272 | 0.004 | 2.4126 | 0.0038 | 62291 | 67 | 2648 | 149 | 7.017 | 0.022 | [6 empty] | 460.7 | 2.8 | 461.3 | 2.8 | 459.3 | 2.8 | 16 | 0 | 13.9 | 0 | 13.5 | 0 | 7319.8 | 55.2 | 3207 | 66.8 | 1934.9 | 42.3 | 460 |  | 459 |  | 459 |  | 3.8 |  | 3.7 |  | 3.7 |  | 0.65 | 460 |  | 459 |  | 459 |  | 5.2 |  | 4.8 |  | 4.5 |  | 3200 |  | 0.83 | 460 | 459 | 459 | 5.1 | 4.6 | 4.4 | 3060 | 0.82 | 459.7 |  | 1.6 |  | 701.2 |  | 85 |  | 9246.2 | [14 empty] | 219.51 | 0.13 | 107.3 | 0.09 | 107.75 | 0.04 | 0.45 | 0.06 | 250.61 | 0.15 | 176.04 | 0.09 | 117.23 | 0.04 | 58.81 | 0.07 | 210.4 | 0.05 | 104.15 | 0.05 | 104.78 | 0.05 | 0.63 | 0.05 | 77.59 | 0.04 | 54.19 | 0.34 | 45.79 | 0.02 | 8.39 | 0.33 | 76.94 | 0.04 | 59.2 | 0.11 | 45.38 | 0.03 | 13.82 | 0.09 | [46 empty] | 254.47 | 0.18 | 172.84 | 0.26 | 118.35 | 0.05 | 54.49 | 0.28 | 237.23 | 0.28 | 113.26 | 0.09 | 11.47 | 0.07 | 225.5 | 0.07 | 95.86 | 0.05 | 109.64 | 0.07 | 13.78 | 0.07 | 80.03 | 0.19 | 47.34 | 0.12 | 4.07 | 1.22 | 79.68 | 0.15 | 60.48 | 0.1 | 47.12 | 0.09 | 13.36 | 0.12 | 101.41 | 0.08 | [28 empty] | 106.36 | 0.08 | 105.79 | 0.07 | 101.41 | 0.08 | 101.73 | 0.1 | 58.01 | 0.06 | 58.59 | 0.05 | 58.42 | 0.04 | 58.18 | 0.05 | 58.2 | 0.05 |  |  | 105.75 | 0.05 | 102.34 | 0.09 | 54.78 | 0.29 | 58.88 | 0.14 | 172.89 | 0.31 | 99.19 | 0.06 | 95.16 | 0.04 | 51.67 | 1.23 | 59.79 | 0.49 | 104.15 | 0.05 | 101.79 | 0.07 | 93.51 | 0.1 | 107.13 | 0.04 | 106.39 | 0.05 | 102.21 | 0.07 | 102.54 | 0.04 | 105.79 | 0.07 | 101.73 | 0.1 | [16 empty] | 107.3 | 0.09 | 101.79 | 0.07 | 106.36 | 0.08 | 101.41 | 0.08 | [16 empty] | 51.42 | 1.12 | [12 empty] | 177 | 0.12 | 95.57 | 0.09 | 95.3 | 0.08 | 75.19 | 0.05 | 75.45 | 0.04 | 75.03 | 0.04 | 75.65 | 0.06 | 75.52 | 0.06 | 75.6 | 0.06 | 75.42 | 0.05 | 79.58 | 0.09 | 76.94 | 0.06 | 77.07 | 0.06 | 78.05 | 0.08 | 78.33 | 0.09 | 77.61 | 0.07 | 77.03 | 0.06 | 75.71 | 0.07 | 75.4 | 0.06 | 75.76 | 0.07 | 75.1 | 0.06 | 75.29 | 0.06 | 75.22 | 0.06 | 75.28 | 0.07 | 76.56 | 0.06 | 75.39 | 0.06 | 75.59 | 0.05 | 79.34 | 0.11 | 78.92 | 0.11 |  |  | 75.07 | 0.05 | 75.34 | 0.05 | 75.53 | 0.06 | 75.36 | 0.06 | 75.38 |  | 75.12 | 0.06 | 81.48 | 0.06 | 81.5 | 0.08 | 78.79 | 0.08 | 75.43 | 0.07 | 75.28 | 0.06 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 75.022 | 0.012 | 61.984 | 0.026 | 58.396 | 0.013 | 55.618 | 0.019 | 95.014 | 0.016 | 75.008 | 0.016 | 3427.5 | 2.7 | 3365.4 | 2.7 | 0.846 | 0.004 | -0.369 | 0.002 | 0.272 | 0.004 | 2.4126 | 0.0038 | 29.337 | 0 | 9255 | 18 | 2200 |  | 0 | 0 | 13.029 | 0.345 | 1.6932 | 15663.4444 | 334.4815 | 0 | 0 | 15663.4444 | 0.0087649 | 27.5968 | 56.7028 | 14.1003 | 13.1293 | 0.013924 | 38.1646 | 0.0087649 | 27.5968 | 0.0087499 | 23.5256 | 75.022 | 61.984 | 23.1127 | 70236.7397 | 68866.0514 | 7055 | 0.34282 | 63869.7252 | 62499.0369 | 6.9011 | 0.14864 | -4.4841 | -18.3192 | 53.5044 | 70236.7397 | 63768.5555 | 6468.1842 | 0 | 70236.7397 | 100%
2 | T2-MF7-100C1-100C2-110A-95-CCE | 75T0045 | T2-MF7-100C1-100C2-110A-95-CCE | closed | on | on | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 30 | 0 | CUST 5 | 10/10/2014 | 23:04:29 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460 | 1.3 | 16.7 | 0 | 59682 | 68 | 59493 | 462 | 2038 | 163 | 61722 | 152 | 6.2151 | 1060 |  |  | 6.0097 | [35 empty] | MF7, 100% charge CK1 and CK2, 110% airflow (450 cfm/ton), 30% condenser coil blockage,--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), adjust code tester speed to match--total static of run T2-MF7-100C1-100C2-110A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 1 turn open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 25.25" of 62" coil | 75.004 | 0.014 | 62.008 | 0.021 | 95.005 | 0.044 | 75 | 0.021 | 75.01 | 0.12 | 59.16 | 0.02 | 61.85 | 0.01 | 0.26 | 0.004 | 2.435 | 0.0032 | 59682 | 68 | 2038 | 163 | 6.215 | 0.018 | [6 empty] | 460 | 2.5 | 461.6 | 2.5 | 459.9 | 2.5 | 16.7 | 0 | 14.5 | 0 | 14.5 | 0 | 7641.5 | 49.5 | 3302.7 | 57.8 | 2289.9 | 37.8 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.65 | 460 |  | 460 |  | 460 |  | 5.5 |  | 5.3 |  | 4.8 |  | 3560 |  | 0.85 | 460 | 460 | 460 | 5.3 | 5.1 | 4.8 | 3410 | 0.84 | 458.9 |  | 1.6 |  | 672.3 |  | 85 |  | 9927.3 | [14 empty] | 247.99 | 0.15 | 115.62 | 0.05 | 116.45 | 0.04 | 0.84 | 0.03 | 280.52 | 0.16 | 189 | 0.06 | 125.6 | 0.04 | 63.4 | 0.06 | 239.3 | 0.05 | 112.89 | 0.05 | 113.87 | 0.05 | 0.97333 | 0.05 | 78.66 | 0.03 | 53.2 | 0.22 | 46.46 | 0.02 | 6.74 | 0.22 | 78.01 | 0.03 | 60.34 | 0.07 | 46.04 | 0.02 | 14.3 | 0.07 | [46 empty] | 286.2 | 0.18 | 187.08 | 0.28 | 127.12 | 0.05 | 59.96 | 0.3 | 269.43 | 0.38 | 122.57 | 0.11 | 15.67 | 0.12 | 257.3 | 0.05 | 101.79 | 0.05 | 119.51 | 0.05 | 17.6967 | 0.05 | 80.75 | 0.2 | 47.77 | 0.12 | 3.3 | 1.12 | 80.39 | 0.15 | 61.84 | 0.06 | 47.55 | 0.09 | 14.3 | 0.11 | 107.55 | 0.09 | [28 empty] | 115.24 | 0.06 | 115.1 | 0.05 | 107.55 | 0.09 | 107.98 | 0.09 | 58.65 | 0.03 | 59.29 | 0.03 | 59.18 | 0.03 | 59.04 | 0.03 | 59.02 | 0.03 |  |  | 115.77 | 0.05 | 110.07 | 0.06 | 54.81 | 0.27 | 61.09 | 0.08 | 187.26 | 0.34 | 107.37 | 0.09 | 100.66 | 0.04 | 51.84 | 1.04 | 62.02 | 0.7 | 112.89 | 0.05 | 101.79 | 0.05 | 93.1 | 0.22 | 115.53 | 0.04 | 115.51 | 0.05 | 109.83 | 0.05 | 110.12 | 0.07 | 115.1 | 0.05 | 107.98 | 0.09 | [16 empty] | 115.62 | 0.05 | 106.91 | 0.1 | 115.24 | 0.06 | 107.55 | 0.09 | [16 empty] | 51.06 | 1.02 | [12 empty] | 190.14 | 0.08 | 94.06 | 0.12 | 93.55 | 0.12 | 75.35 | 0.06 | 75.59 | 0.05 | 75.1 | 0.06 | 75.86 | 0.06 | 75.74 | 0.06 | 75.78 | 0.07 | 75.57 | 0.06 | 79.81 | 0.11 | 76.78 | 0.06 | 76.84 | 0.07 | 78.16 | 0.09 | 78.2 | 0.08 | 77.43 | 0.07 | 76.86 | 0.06 | 75.8 | 0.07 | 75.49 | 0.07 | 75.8 | 0.08 | 75.15 | 0.07 | 75.31 | 0.08 | 75.26 | 0.08 | 75.25 | 0.07 | 75.65 | 0.06 | 75.44 | 0.07 | 75.35 | 0.05 | 76.32 | 0.06 | 76.36 | 0.06 |  |  | 75.17 | 0.06 | 75.45 | 0.05 | 75.59 | 0.07 | 75.41 | 0.07 | 75.48 |  | 75.22 | 0.07 |  |  | 81.69 | 0.08 | 78.73 | 0.08 | 75.54 | 0.07 | 75.31 | 0.08 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 75.004 | 0.014 | 62.008 | 0.021 | 59.112 | 0.008 | 56.008 | 0.014 | 95.005 | 0.044 | 75 | 0.021 | 3449.7 | 2.3 | 3374.5 | 2.2 | 0.854 | 0.003 | -0.376 | 0.002 | 0.26 | 0.004 | 2.435 | 0.0032 | 29.264 | 0.002 | 9931 | 17 | 2200 |  | 0 | 0 | 13.029 | 0.345 | 1.681 | 15742.5899 | 338.5575 | 0 | 0 | 15742.5899 | 0.008785 | 27.6144 | 57.431 | 14.1 | 13.1479 | 0.01392 | 38.157 | 0.008785 | 27.6144 | 0.0088086 | 23.764 | 75.004 | 62.008 | 23.354 | 67068.5586 | 66394.7392 | 7731 | 0.39342 | 60715.4553 | 60041.6358 | 6.1137 | 0.1749 | -4.2603 | -17.573 | 53.706 | 67068.5586 | 60613.8169 | 6454.7417 | 0 | 67068.5586 | 100%
2 | T2-MF8-115C1-115C2-110A-95-CCE | 75T0046 | T2-MF8-115C1-115C2-110A-95-CCE | closed | on | on | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 30 | 0 | CUST 5 | 10/11/2014 | 0:50:04 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 7.36 lbs/CK2: 7.13 lbs | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 7.36 | 7.13 | 6.4 | 6.2 | 460.2 | 1.4 | 16.9 | 0 | 61256 | 72 | 61031 | 408 | 3331 | 141 | 64590 | 143 | 6.3648 | 1060 |  |  | 6.0363 | [35 empty] | MF8, 115% charge CK1 and CK2, 110% airflow (450 cfm/ton), 30% condenser coil blockage,--2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), adjust code tester speed to match total--static of run T2-MF7-100C1-100C2-110A-95-CCE-SPWCT-SS | With econo: both stages: 95/75 amb: 2 HP blower motor: 5.75` mtr. pulley: 1 turns open: AX 35 belt: 100% inlet-outlet Meriam: condenser coil blocked 25.25` of 62` coil | 74.987 | 0.012 | 61.995 | 0.022 | 95.068 | 0.034 | 74.99 | 0.02 | 74.99 | 0.11 | 58.75 | 0.03 | 61.48 | 0.02 | 0.261 | 0.004 | 2.4345 | 0.0032 | 61256 | 72 | 3331 | 141 | 6.365 | 0.017 | [6 empty] | 460.2 | 2.5 | 461.5 | 2.5 | 459.9 | 2.5 | 16.9 | 0 | 14.7 | 0 | 14.7 | 0 | 7758.7 | 48.1 | 3319.7 | 57.3 | 2389.7 | 38.2 | 460 |  | 460 |  | 460 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.65 | 460 |  | 460 |  | 460 |  | 5.6 |  | 5.4 |  | 4.8 |  | 3620 |  | 0.86 | 460 | 460 | 460 | 5.7 | 5.3 | 4.9 | 3570 | 0.84 | 459 |  | 1.6 |  | 671.2 |  | 85 |  | 10146.2 | [14 empty] | 262.28 | 0.19 | 108.09 | 0.09 | 120.57 | 0.05 | 12.48 | 0.08 | 285.2 | 0.21 | 188.21 | 0.21 | 126.85 | 0.06 | 61.36 | 0.24 | 256.3 | 0.05 | 107.32 | 0.09 | 118.86 | 0.05 | 11.51 | 0.05 | 78.32 | 0.08 | 49.7 | 0.28 | 46.24 | 0.05 | 3.46 | 0.31 | 77.69 | 0.08 | 56.93 | 0.41 | 45.84 | 0.05 | 11.09 | 0.44 | [46 empty] | 299.85 | 0.21 | 192.46 | 0.22 | 130.69 | 0.05 | 61.78 | 0.24 | 284.42 | 0.38 | 126.65 | 0.1 | 23.32 | 0.09 | 271.8 | 0.05 | 98.61 | 0.05 | 123.22 | 0.05 | 24.6367 | 0.05 | 80.59 | 0.17 | 47.67 | 0.11 | 2.77 | 0.71 | 80.26 | 0.12 | 58.69 | 0.35 | 47.46 | 0.08 | 11.23 | 0.34 | 104.03 | 0.07 | [28 empty] | 108.85 | 0.1 | 109.43 | 0.09 | 104.03 | 0.07 | 104.63 | 0.06 | 58.17 | 0.04 | 58.88 | 0.03 | 58.75 | 0.03 | 58.53 | 0.03 | 58.54 | 0.03 |  |  | 108.56 | 0.11 | 104.86 | 0.1 | 50.9 | 0.62 | 57.77 | 0.43 | 192.72 | 0.28 | 103.8 | 0.06 | 97.6 | 0.06 | 51.25 | 0.58 | 61.42 | 0.53 | 107.32 | 0.09 | 98.61 | 0.05 | 92.92 | 0.24 | 109.36 | 0.12 | 109.57 | 0.1 | 106.94 | 0.06 | 107.26 | 0.06 | 109.43 | 0.09 | 104.63 | 0.06 | [16 empty] | 108.09 | 0.09 | 103.33 | 0.07 | 108.85 | 0.1 | 104.03 | 0.07 | [16 empty] | 50.44 | 0.63 | [12 empty] | 189.38 | 0.24 | 94.03 | 0.13 | 93.5 | 0.12 | 75.28 | 0.05 | 75.53 | 0.05 | 75.06 | 0.05 | 75.79 | 0.05 | 75.66 | 0.05 | 75.72 | 0.06 | 75.51 | 0.06 | 79.74 | 0.12 | 76.7 | 0.06 | 76.78 | 0.06 | 78.12 | 0.09 | 78.14 | 0.08 | 77.35 | 0.07 | 76.81 | 0.06 | 75.76 | 0.07 | 75.41 | 0.07 | 75.77 | 0.07 | 75.12 | 0.06 | 75.23 | 0.07 | 75.17 | 0.07 | 75.19 | 0.07 | 75.58 | 0.06 | 75.34 | 0.07 | 75.28 | 0.04 | 76.26 | 0.05 | 76.29 | 0.06 |  |  | 75.13 | 0.06 | 75.37 | 0.05 | 75.53 | 0.06 | 75.36 | 0.07 | 75.43 |  | 75.17 | 0.07 |  |  | 81.62 | 0.08 | 78.67 | 0.07 | 75.49 | 0.07 | 75.21 | 0.07 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 74.987 | 0.012 | 61.995 | 0.022 | 58.692 | 0.008 | 55.7 | 0.017 | 95.068 | 0.034 | 74.99 | 0.02 | 3448.2 | 2.3 | 3375.7 | 2.2 | 0.854 | 0.003 | -0.377 | 0.002 | 0.261 | 0.004 | 2.4345 | 0.0032 | 29.263 | 0.003 | 10148 | 16 | 2200 |  | 0 | 0 | 13.029 | 0.345 | 1.6802 | 15749.2514 | 338.6779 | 0 | 0 | 15749.2514 | 0.0087804 | 27.6052 | 57.0118 | 14.1014 | 13.1366 | 0.013896 | 38.1462 | 0.0087804 | 27.6052 | 0.0087278 | 23.5737 | 74.987 | 61.995 | 23.1639 | 69947.3775 | 67943.0035 | 7948 | 0.38781 | 63594.6851 | 61590.3111 | 6.2667 | 0.16684 | -4.4413 | -17.9752 | 53.4123 | 69947.3775 | 63494.0037 | 6453.3738 | 0 | 69947.3775 | 100%
2 | T2-HS-3200-95-CF-C | 75T0153 | T2-HS-3200-95-CF-C | closed | on | on | 1.5 turns | unsealed | unsealed |  | 5.25 |  | 0 | 0 | CUST 6 | 7/31/2014 | 3:20:21 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 459.9 | 1 | 16.5 | 0 | 54859 | 121 | 56228 | 421 | 1254 | 369 | 56115 | 391 | 5.5576 | 1224 |  |  |  | 109.48 | 0.1 | 35.15 | [32 empty] | 106% airflow (425 cfm/ton), factory charge, closed damper, 3 HP fan motor, 1.5 turns,--5.25" pulley, 95F Test, adjust code tester speed to match total static of run 'T2-3200-95+CF-C-SPWCT-SS | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: AK54H BP: ID Blw M: MQC 56T17D5563B: Mtr Pulley 1.5 T/O: With econo: Supply Meriam @85% Return Meriam @75%: Horiz Air Disch: Max Mtr Amp 4.7 | 75.027 | 0.023 | 61.885 | 0.077 | 94.835 | 0.007 | 75.009 | 0.02 | 75.24 | 0.13 | 59.46 | 0.06 | 61.69 | 0.03 | 0.202 | 0.004 | 1.4854 | 0.0028 | 54859 | 121 | 1254 | 369 | 5.558 | 0.04 | 86527 | 209 | 8.57 | 0.026 | 35.15 | 0.38 | 459.9 | 2.4 | 460.1 | 2.4 | 460.3 | 2.5 | 16.5 | 0.1 | 14.8 | 0 | 14.5 | 0.1 | 7567.2 | 61.1 | 3308.3 | 66.1 | 2529.5 | 53.2 | 460 |  | 460 |  | 460 |  | 4.4 |  | 4.5 |  | 4.4 |  | 0.74 | 460 |  | 460 |  | 460 |  | 5.1 |  | 5 |  | 4.5 |  | 3190 |  | 0.82 | 460 | 460 | 460 | 5 | 4.7 | 4.5 | 3050 | 0.82 | 458.9 |  | 1.6 |  | 702.3 |  | 115 |  | 10067.3 | [14 empty] | 221.27 | 0.18 | 107.27 | 0.07 | 108.3 | 0.06 | 1 | 0.05 | 249.71 | 0.15 | 176.76 | 0.22 | 116.96 | 0.04 | 59.79 | 0.21 | 210.3 | 0.05 | 100.63 | 0.29 | 104.75 | 0.05 | 4.43 | 0.3 | 76.82 | 0.1 | 49.61 | 0.54 | 45.3 | 0.07 | 4.32 | 0.54 | 76.26 | 0.1 | 58.09 | 0.4 | 44.94 | 0.07 | 13.15 | 0.37 | 637.23 | 1.81 |  | 0.09 | 86527 | 209 | 44482 | 178 | [38 empty] | 252.39 | 0.15 | 171.06 | 0.32 | 117.74 | 0.04 | 53.31 | 0.34 | 233.61 | 0.25 | 112.18 | 0.05 | 10.25 | 0.05 | 221.63 |  | 99.71 | 0.09 | 112.15 | 0.08 | 12.44 | 0.11 | 80.65 | 0.15 | 47.72 | 0.09 | 2.51 | 0.52 | 80.25 | 0.15 | 57.56 | 0.63 | 47.47 | 0.1 | 10.09 | 0.68 | 105.5 | 0.08 | 653.67 | 2.1 | 39.39 | 0.03 | 109.35 | 0.09 | 86527 | 209 | 45730 | 121 | [18 empty] | 106.03 | 0.07 | 105.5 | 0.08 | 101.56 | 0.08 | 101.78 | 0.08 | 59.82 | 0.08 | 59.55 | 0.08 | 59.12 | 0.07 | 59.98 | 0.08 | 59.89 | 0.08 | 59.74 | 0.07 | 107.94 | 0.09 | 101.39 | 0.09 | 51.44 | 0.66 | 57.71 | 0.48 | 169.96 | 0.28 | 101.51 | 0.08 | 101.22 | 0.09 | 50.66 | 0.16 | 57.62 | 1.04 |  |  |  |  | 92.86 | 0.05 | [8 empty] | 101.56 | 0.08 | 101.78 | 0.08 | [14 empty] | 59.74 | 0.07 | 107.27 | 0.07 | 101.97 | 0.09 | 106.03 | 0.07 | 105.5 | 0.08 | [16 empty] | 50.22 | 0.47 | [12 empty] | 175.69 | 0.22 | 94.03 | 0.13 | 94.17 | 0.11 | 75.9 | 0.12 | 75.7 | 0.13 | 75.42 | 0.12 | 76.23 | 0.11 | 76.22 | 0.12 | 76.12 | 0.13 | 75.95 | 0.13 | 82.87 | 0.13 | 81.68 | 0.14 | 77.71 | 0.12 | 77.25 | 0.14 | 79.81 | 0.18 | 79.42 | 0.18 | 78.45 | 0.15 | 76.83 | 0.13 | 75.87 | 0.13 | 76.25 | 0.13 | 75.52 | 0.11 | 75.31 | 0.14 | 75.28 | 0.16 | 75.64 | 0.16 | 75.4 | 0.14 | 75.45 | 0.12 | 75.41 | 0.11 | 75.62 | 0.11 | 75.99 | 0.1 |  |  | 75.52 | 0.1 | 76.27 | 0.13 | 75.98 | 0.13 | 75.75 | 0.13 | 75.6 |  | 75.46 | 0.14 | 84.06 | 0.15 | 83.63 | 0.14 | 79.16 | 0.14 | 75.85 | 0.14 | 75.29 | 0.14 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 75.027 | 0.023 | 61.885 | 0.077 | 59.626 | 0.031 | 56.147 | 0.058 | 94.835 | 0.007 | 75.009 | 0.02 | 3268.1 | 3.1 | 3201.6 | 3 | 1.238 | 0.002 | -0.511 | 0.003 | 0.202 | 0.004 | 1.4854 | 0.0028 | 29.3 | 0.001 | 10097 | 20 | 3010 |  | 0 | 0 | 13.029 | 0.345 | 2.4278 | 14899.4556 | 465.6427 | 0 | 0 | 14899.4556 | 0.0086985 | 27.5254 | 57.1982 | 14.0961 | 13.1606 | 0.013968 | 38.1688 | 0.0086985 | 27.5254 | 0.0087688 | 23.846 | 75.027 | 61.885 | 23.2539 | 63642.0313 | 63753.3108 | 7087 | 0.38006 | 54958.1399 | 55069.4194 | 5.443 | 0.16742 | -4.2714 | -17.8288 | 53.613 | 63642.0313 | 54819.8535 | 8822.1778 | 0 | 63642.0313 | 100%
2 | T2-3240-95-CF | 75T0158 | T2-3240-95-CF | closed | on | on | 1 turn | unsealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 7/30/2014 | 14:54:17 | 10 Ton | 0:05:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.4 | 1.4 | 15.8 | 0 | 59658 | 195 | 62899 | 555 | 4050 | 414 | 63712 | 417 | 6.9124 | 1056 |  |  |  | 109.39 | 0.05 | 25.89 | [32 empty] | . | Installed FM:SG:FD:LSV on 2 circuits: unsealed cab: dampers on S/R: AX35 belt: AK59 5.75 diam BP: ID Blw M: MQC 56T17D5563B: Mtr Pulley 1 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch, Motor Max Amps 3.6 | 75.045 | 0.016 | 62.029 | 0.084 | 94.831 | 0.011 | 74.994 | 0.016 | 75.47 | 0.08 | 58.12 | 0.1 | 60.73 | 0.05 | 0.195 | 0.005 | 1.533 | 0.003 | 59658 | 195 | 4050 | 414 | 6.913 | 0.044 | 85975 | 265 | 9.327 | 0.03 | 25.89 | 0.31 | 460.4 | 2.4 | 460.3 | 2.4 | 459.7 | 2.5 | 15.8 | 0.1 | 13.9 | 0 | 13.6 | 0.1 | 7218.2 | 65.2 | 3306.9 | 72.2 | 1999.4 | 56.1 | 461 |  | 461 |  | 460 |  | 3.7 |  | 3.6 |  | 3.6 |  | 0.65 | 461 |  | 461 |  | 460 |  | 5.1 |  | 5 |  | 4.5 |  | 3190 |  | 0.83 | 460 | 460 | 461 | 5 | 4.7 | 4.6 | 3060 | 0.82 | 459.4 |  | 1.6 |  | 702.2 |  | 115 |  | 9207.2 | [14 empty] | 221.48 | 0.18 | 107.53 | 0.06 |  |  |  |  | 249.51 | 0.18 | 176.94 | 0.17 | 116.92 | 0.05 | -60.03 | 0.15 |  |  | 101.79 | 0.45 | 108.38 | 0.06 | 6.58 | 0.46 | 76.54 | 0.09 | 49.02 | 0.3 | 45.13 | 0.06 | 3.89 | 0.25 | 75.98 | 0.09 | 58.24 | 0.33 | 44.76 | 0.05 | 13.46 | 0.28 | 637.43 | 1.31 |  | 0.14 | 85975 | 265 | 44201 | 163 | [38 empty] | 251.63 | 0.2 | 170.57 | 0.41 | 117.53 | 0.06 | 53.04 | 0.41 | 233.03 | 0.19 | [6 empty] | 100.02 | 0.09 | 111.98 | 0.06 | 11.98 | 0.13 | 79.94 | 0.19 | 47.28 | 0.11 | 2.59 | 0.48 | 79.54 | 0.18 | 57.14 | 0.63 | 47.04 | 0.11 | 10.11 | 0.64 | 105.67 | 0.05 | 650.97 | 2.38 | 39.48 | 0.03 | 109.32 | 0.08 | 85975 | 265 | 45459 | 137 | [18 empty] | 106.2 | 0.05 | 105.67 | 0.05 | 101.81 | 0.08 | 102.04 | 0.08 | 58.73 | 0.09 | 58.44 | 0.08 | 58.09 | 0.09 | 59.03 | 0.11 | 59.24 | 0.11 | 58.88 | 0.1 | 107.95 | 0.06 | 101.6 | 0.08 | 50.99 | 0.4 | 57.79 | 0.38 | 169.72 | 0.37 | 101.82 | 0.08 | 101.52 | 0.09 | 50.34 | 0.17 | 57.07 | 0.94 |  |  |  |  | 93.27 | 0.04 | [8 empty] | 101.81 | 0.08 | 102.04 | 0.08 | [12 empty] | 101.79 | 0.45 | 58.88 | 0.1 | 107.53 | 0.06 | 102.34 | 0.09 | 106.2 | 0.05 | 105.67 | 0.05 | [16 empty] | 49.82 | 0.41 | [12 empty] | 176.08 | 0.17 | 94.04 | 0.2 | 94.17 | 0.19 | 76.05 | 0.18 | 75.8 | 0.17 | 75.62 | 0.17 | 76.38 | 0.16 | 76.4 | 0.17 | 76.27 | 0.17 | 76.06 | 0.16 | 79.78 | 0.11 | 79.41 | 0.11 | 78.41 | 0.09 | 76.22 | 0.1 | 78.15 | 0.15 | 78.09 | 0.13 | 77.35 | 0.13 | 76.04 | 0.11 | 75.8 | 0.1 | 75.63 | 0.09 | 75.59 | 0.09 | 75.63 | 0.13 | 75.6 | 0.15 | 76.53 | 0.15 | 75.81 | 0.15 | 75.87 | 0.11 | 75.87 | 0.08 | 76.6 | 0.09 | 76.77 | 0.07 |  |  | 75.64 | 0.13 | 76.39 | 0.19 | 76.11 | 0.17 | 75.85 | 0.17 | 75.73 |  | 75.58 | 0.17 | 83.38 | 0.15 | 81.72 | 0.14 | 77.41 | 0.14 | 75.92 | 0.11 | 75.64 | 0.13 | [62 empty] | T2-TRN-110A-55-CE-DM-2 | 75.045 | 0.016 | 62.029 | 0.084 | 58.591 | 0.038 | 55.569 | 0.069 | 94.831 | 0.011 | 74.994 | 0.016 | 3315 | 3.2 | 3258.6 | 3.3 | 0.773 | 0.003 | -0.355 | 0.003 | 0.195 | 0.005 | 1.533 | 0.003 | 29.342 | 0.001 | 9217 | 20 | 2140 |  | 0 | 0 | 13.029 | 0.345 | 1.7311 | 15144.2985 | 295.9209 | 0 | 0 | 15144.2985 | 0.0087891 | 27.6289 | 56.8599 | 14.0959 | 13.1337 | 0.013956 | 38.1544 | 0.0087891 | 27.6289 | 0.0086753 | 23.492 | 75.045 | 62.029 | 23.0699 | 69043.0933 | 66096.2268 | 7077 | 0.34984 | 62749.2514 | 59802.3849 | 6.808 | 0.16702 | -4.559 | -18.1851 | 53.2137 | 69043.0933 | 62650.1131 | 6392.9802 | 0 | 69043.0933 | 100%
2 | T2-TRN-110A-55-T1E-DM | 75T0116 | T2-TRN-110A-55-T1E-DM | 10% open | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/21/2014 | 11:46:42 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 4.2 | 0 | 1118 | 30 | 666 | 128 | 3454 | 83 | 4575 | 77 | 2.0208 | 1061 | 2150 |  | 0.49382 | [35 empty] | Econo 10%-open (2.8V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--110% airflow (450 cfm/ton), 2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match to | W/ECO: Eco set at 2.8v: No Compr:55/51 amb:2HP blwr mtr 5.75 AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.034 | 0.024 | 61.998 | 0.03 | 55 | 0.01 | 51.008 | 0.013 | 74.98 | 0.05 | 74.83 | 0.04 | 74.81 | 0.02 | 0.285 | 0.005 | 2.4349 | 0.0036 | 1118 | 30 | 3454 | 83 | 2.021 | 0.036 | [6 empty] | 460.6 | 2 | 461.6 | 2.1 | 459.5 | 2 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1890.1 | 16.1 | 1085.5 | 17.4 | 373.9 | 11.4 | 460 |  | 459 |  | 459 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.64 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 2235 | [14 empty] | 96.67 | 0.03 | 55.7 | 0.05 | 57.17 | 0.01 | 1.47 | 0.05 | 96.2 | 0.02 | 57.52 | 0.02 | 56.91 | 0.01 | -0.61 | 0.03 |  |  | 69.23 | 0.02 |  |  |  |  | 96.02 | 0.03 | 71.4 | 0.04 | 56.81 | 0.02 | 14.58 | 0.04 | 95.69 | 0.02 | 57.23 | 0.02 | 56.63 | 0.01 | 0.6 | 0.02 | [46 empty] | 96.39 | 0.03 | 56.83 | 0.03 | 57.02 | 0.02 | -0.19 | 0.02 | 97.26 | 0.03 | 57.49 | 0.02 | 1.08 | 0.03 |  |  | 72.94 | 0.02 |  |  |  |  | 96.25 | 0.03 | 56.94 | 0.02 | 14.07 | 0.03 | 96.33 | 0.03 | 59.05 | 0.02 | 56.98 | 0.01 | 2.06 | 0.03 | 57.7 | 0.05 | [28 empty] | 56.82 | 0.03 | 58.3 | 0.02 | 57.7 | 0.05 | 59.7 | 0.04 | 74.81 | 0.05 | 74.66 | 0.03 | 74.52 | 0.04 | 75.05 | 0.04 | 75.05 | 0.04 |  |  | 55.12 | 0.02 | 69.81 | 0.03 | 71.38 | 0.03 | 57.7 | 0.02 | 57.44 | 0.01 | 56.65 | 0.02 | 73.5 | 0.02 | 72.09 | 0.03 | 61.01 | 0.02 | 69.23 | 0.02 | 72.94 | 0.02 | 55.19 | 0.03 | 56.11 | 0.02 | 59.1 | 0.02 | 57.13 | 0.01 | 57.81 | 0.02 | 58.3 | 0.02 | 59.7 | 0.04 | [16 empty] | 55.7 | 0.05 | 56.42 | 0.03 | 56.82 | 0.03 | 57.7 | 0.05 | [16 empty] | 71 | 0.03 | [12 empty] | 57.51 | 0.02 | 56.7 | 0.11 | 56.54 | 0.15 | 75.34 | 0.03 | 75.08 | 0.04 | 74.88 | 0.03 | 75.68 | 0.03 | 75.67 | 0.04 | 75.66 | 0.04 | 75.47 | 0.04 | 72.37 | 0.08 | 73.58 | 0.04 | 73.18 | 0.04 | 71.9 | 0.08 | 73.06 | 0.06 | 73.3 | 0.06 | 73.92 | 0.05 | 74.57 | 0.04 | 74.61 | 0.04 | 74.51 | 0.05 | 74.64 | 0.04 | 74.55 | 0.04 | 74.75 | 0.04 | 74.56 | 0.04 | 72.37 | 0.11 | 74.79 | 0.04 | 73.97 | 0.06 | 69.13 | 0.14 | 69.29 | 0.13 |  |  | 75.07 | 0.03 | 75.62 | 0.03 | 75.46 | 0.04 | 75.31 | 0.04 | 74.9 |  | 74.98 | 0.04 | 69.84 | 0.09 | 70.55 | 0.08 | 72.5 | 0.06 | 74.49 | 0.05 | 74.78 | 0.04 | [62 empty] | Economizer test | 75.034 | 0.024 | 61.998 | 0.03 | 74.761 | 0.025 | 61.614 | 0.028 | 55 | 0.01 | 51.008 | 0.013 | 3480.5 | 2.6 | 3343.6 | 2.4 | 0.84 | 0.004 | -0.38 | 0.002 | 0.285 | 0.005 | 2.4349 | 0.0036 | 29.444 | 0 | 2264 | 11 | 2150 |  | 0 | 0 | 13.03 | 0.38 | 1.678 | 15420.1225 | 329.958 | 0 | 0 | 15420.1225 | 0.0087713 | 27.6067 | 73.083 | 13.0295 | 13.5427 | 0.0069856 | 20.7823 | 0.0087713 | 27.6067 | 0.0085836 | 27.3348 | 75.034 | 61.998 | 26.9257
2 | T2-TRN-110A-55-T2E-DM | 75T0117 | T2-TRN-110A-55-T2E-DM | 20% open | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/21/2014 | 13:31:35 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 4.2 | 0 | 3626 | 28 | 3240 | 123 | 4527 | 103 | 8158 | 113 | 3.597 | 1061 | 2160 |  | 1.5988 | [35 empty] | Econo 20%-open (3.6V), tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--110% airflow (450 cfm/ton), 2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match to | W/ECO: Eco set at 3.6v: No Compr:55/51 amb:2HP blwr mtr 5.75 AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.04 | 0.025 | 62 | 0.021 | 55.013 | 0.009 | 50.999 | 0.018 | 74.89 | 0.08 | 74.06 | 0.09 | 74.28 | 0.03 | 0.264 | 0.004 | 2.4422 | 0.0037 | 3626 | 28 | 4527 | 103 | 3.598 | 0.053 | [6 empty] | 460.5 | 2.1 | 461.4 | 2.1 | 459.5 | 2.1 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1888.1 | 15 | 1089 | 17 | 379.4 | 10 | 460 |  | 460 |  | 459 |  | 3.7 |  | 3.6 |  | 3.7 |  | 0.64 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 2245 | [14 empty] | 97.02 | 0.03 | 55.66 | 0.1 | 57.35 | 0.02 | 1.7 | 0.1 | 96.83 | 0.01 | 57.51 | 0.03 | 57.25 | 0.01 | -0.27 | 0.03 |  |  | 69.49 | 0.03 |  |  |  |  | 96.71 | 0.01 | 71.44 | 0.03 | 57.17 | 0.01 | 14.27 | 0.04 | 96.33 | 0.01 | 57.21 | 0.02 | 56.97 | 0.01 | 0.24 | 0.02 | [46 empty] | 96.93 | 0.03 | 57.17 | 0.03 | 57.3 | 0.01 | -0.14 | 0.02 | 97.67 | 0.03 | 57.71 | 0.02 | 1.14 | 0.08 |  |  | 73.05 | 0.03 |  |  |  |  | 96.78 | 0.02 | 57.22 | 0.01 | 13.81 | 0.07 | 96.86 | 0.02 | 59.06 | 0.03 | 57.26 | 0.01 | 1.8 | 0.03 | 57.53 | 0.13 | [28 empty] | 56.85 | 0.07 | 58.25 | 0.05 | 57.53 | 0.13 | 59.64 | 0.09 | 74.11 | 0.08 | 73.9 | 0.06 | 73.77 | 0.04 | 74.36 | 0.03 | 74.37 | 0.03 |  |  | 55.04 | 0.03 | 69.97 | 0.06 | 71.43 | 0.05 | 57.61 | 0.03 | 57.74 | 0.03 | 56.83 | 0.02 | 73.66 | 0.03 | 72.11 | 0.03 | 60.96 | 0.01 | 69.49 | 0.03 | 73.05 | 0.03 | 55.09 | 0.04 | 56.05 | 0.02 | 59.16 | 0.02 | 57.38 | 0.01 | 58.02 | 0.02 | 58.25 | 0.05 | 59.64 | 0.09 | [16 empty] | 55.66 | 0.1 | 56.57 | 0.07 | 56.85 | 0.07 | 57.53 | 0.13 | [16 empty] | 71.02 | 0.07 | [12 empty] | 57.47 | 0.02 | 56.94 | 0.19 | 56.55 | 0.18 | 75.32 | 0.02 | 75.09 | 0.02 | 74.86 | 0.02 | 75.64 | 0.02 | 75.63 | 0.03 | 75.62 | 0.03 | 75.42 | 0.03 | 68.7 | 0.19 | 72.38 | 0.06 | 72.53 | 0.05 | 69.86 | 0.08 | 71.07 | 0.08 | 71.29 | 0.07 | 72.01 | 0.05 | 73.92 | 0.06 | 73.42 | 0.08 | 72.8 | 0.07 | 73.65 | 0.08 | 74.32 | 0.04 | 74.74 | 0.04 | 74.65 | 0.03 | 72.32 | 0.11 | 74.77 | 0.05 | 74.24 | 0.05 | 68.17 | 0.1 | 69.06 | 0.11 |  |  | 75.03 | 0.02 | 75.64 | 0.02 | 75.47 | 0.03 | 75.32 | 0.03 | 74.93 |  | 75.01 | 0.03 | 67.54 | 0.08 | 66.82 | 0.11 | 70.93 | 0.06 | 73.08 | 0.09 | 74.76 | 0.04 | [62 empty] | Economizer test | 75.04 | 0.025 | 62 | 0.021 | 74.099 | 0.021 | 61.279 | 0.019 | 55.013 | 0.009 | 50.999 | 0.018 | 3486.9 | 2.6 | 3347.9 | 2.6 | 0.831 | 0.003 | -0.352 | 0.002 | 0.264 | 0.004 | 2.4422 | 0.0037 | 29.398 | 0.001 | 2268 | 11 | 2160 |  | 0 | 0 | 13.03 | 0.352 | 1.6848 | 15468.2073 | 326.8426 | 0 | 0 | 15468.2073 | 0.0087712 | 27.6081 | 72.4142 | 13.0298 | 13.5254 | 0.0069778 | 20.777 | 0.0087712 | 27.6081 | 0.0085216 | 27.1055 | 75.04 | 62 | 26.6948
2 | T2-TRN-110A-55-T3E-DM | 75T0118 | T2-TRN-110A-55-T3E-DM | 30% open | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/21/2014 | 14:36:07 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.5 | 0 | 4.2 | 0 | 7053 | 29 | 6781 | 110 | 6167 | 77 | 13226 | 76 | 5.7983 | 1060 | 2160 |  | 3.0921 | [35 empty] | Econo 30%-open (4.4V), tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 110% airflow (450 cfm/ton), 2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm),--100% inlet/outlet Meriam, adjust code tester speed to match to | W/ECO: Eco set at 4.4v: No Compr:55/51 amb:2HP blwr mtr 5.75 AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 74.976 | 0.011 | 62.001 | 0.018 | 55.004 | 0.011 | 51.004 | 0.015 | 74.97 | 0.06 | 73.2 | 0.06 | 73.44 | 0.01 | 0.26 | 0.006 | 2.4683 | 0.0053 | 7053 | 29 | 6167 | 77 | 5.799 | 0.046 | [6 empty] | 460.5 | 2 | 460.8 | 2 | 459.5 | 2 | 4.2 | 0 | 3.7 | 0 | 3.9 | 0 | 1886.4 | 14.2 | 1095.3 | 17 | 394.2 | 9.9 | 460 |  | 459 |  | 459 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.64 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 2245 | [14 empty] | 97.48 | 0.05 | 57.01 | 0.07 | 57.59 | 0.03 | 0.6 | 0.07 | 97.17 | 0.02 | 57.58 | 0.02 | 57.42 | 0.01 | -0.15 | 0.03 |  |  | 70.13 | 0.02 |  |  |  |  | 97.04 | 0.02 | 71.47 | 0.03 | 57.35 | 0.01 | 14.12 | 0.03 | 96.66 | 0.02 | 57.27 | 0.02 | 57.14 | 0.01 | 0.13 | 0.02 | [46 empty] | 97.28 | 0.03 | 57.3 | 0.02 | 57.48 | 0.01 | -0.19 | 0.02 | 98.03 | 0.04 | 57.9 | 0.03 | 1.12 | 0.05 |  |  | 72.93 | 0.01 |  |  |  |  | 97.12 | 0.03 | 57.4 | 0.02 | 13.79 | 0.06 | 97.2 | 0.03 | 59.21 | 0.03 | 57.44 | 0.02 | 1.77 | 0.03 | 57.76 | 0.04 | [28 empty] | 56.82 | 0.05 | 58.16 | 0.04 | 57.76 | 0.04 | 59.53 | 0.07 | 73.52 | 0.05 | 72.9 | 0.04 | 72.7 | 0.03 | 73.7 | 0.02 | 73.65 | 0.02 |  |  | 56.25 | 0.14 | 70.73 | 0.03 | 71.75 | 0.03 | 57.76 | 0.02 | 57.93 | 0.02 | 57.02 | 0.02 | 73.51 | 0.03 | 72.21 | 0.02 | 60.99 | 0.01 | 70.13 | 0.02 | 72.93 | 0.01 | 54.93 | 0.04 | 56.07 | 0.02 | 59.08 | 0.02 | 57.56 | 0.01 | 58.29 | 0.02 | 58.16 | 0.04 | 59.53 | 0.07 | [16 empty] | 57.01 | 0.07 | 56.79 | 0.06 | 56.82 | 0.05 | 57.76 | 0.04 | [16 empty] | 71.2 | 0.05 | [12 empty] | 57.52 | 0.02 | 57.13 | 0.22 | 56.66 | 0.2 | 75.36 | 0.02 | 75.13 | 0.02 | 74.91 | 0.02 | 75.7 | 0.02 | 75.67 | 0.1 | 75.63 | 0.03 | 75.44 | 0.03 | 65.22 | 0.13 | 68.13 | 0.21 | 71.51 | 0.07 | 65.81 | 0.14 | 65.58 | 0.16 | 68.68 | 0.14 | 70.7 | 0.1 | 71.75 | 0.1 | 69.02 | 0.19 | 69.59 | 0.14 | 69.52 | 0.35 | 73.01 | 0.04 | 74.62 | 0.03 | 74.66 | 0.02 | 74.3 | 0.13 | 74.16 | 0.05 | 74.46 | 0.02 | 69.24 | 0.13 | 69.04 | 0.1 |  |  | 75.08 | 0.02 | 75.66 | 0.03 | 75.48 | 0.03 | 75.32 | 0.03 | 75 |  | 75.02 | 0.02 | 66.1 | 0.11 | 66.47 | 0.08 | 66.1 | 0.16 | 70.19 | 0.35 | 74.66 | 0.03 | [62 empty] | Economizer test | 74.976 | 0.011 | 62.001 | 0.018 | 73.134 | 0.01 | 60.807 | 0.019 | 55.004 | 0.011 | 51.004 | 0.015 | 3504 | 3.8 | 3367.7 | 3.7 | 0.806 | 0.004 | -0.32 | 0.002 | 0.26 | 0.006 | 2.4683 | 0.0053 | 29.378 | 0.001 | 2281 | 11 | 2160 |  | 0.0081114 | 27.3166 | 13.03 | 0.32 | 1.6808 | 15572.933 | 318.8846 | 27.3162 | 125.7883 | 15447.1447 | 0.0087724 | 27.5545 | 71.4532 | 13.0296 | 13.5003 | 0.0069825 | 20.7799 | 0.008787 | 27.6097 | 0.0084443 | 26.7858 | 74.8152 | 61.9212 | 26.3761
2 | T2-TRN-110A-55-TCE-DM | 75T0119 | T2-TRN-110A-55-TCE-DM | closed | off | off | 1 turn | unsealed | unsealed | 1060 | 5.75 |  | 0 | 0 | CUST 5 | 10/21/2014 | 10:52:16 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1: 6.4 lbs/CK2: 6.2 lb | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 0 | 4.2 | 0 | 942 | 24 | 490 | 137 | 3372 | 88 | 4317 | 92 | 1.9144 | 1061 | 2170 |  | 0.41774 | [35 empty] | Econo closed, tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient--110% airflow (450 cfm/ton), 2 HP fan motor, 1 turn, 5.75" AK59 pulley (1060 rpm), 100% inlet/outlet Meriam,--adjust code tester speed to match total static | W/ECO: Eco set at 2v: No Compr:55/51 amb:2HP blwr mtr 5.75 AK59 mtr. pulley:1 turns open: AX35 new belt browning tensioning tool 8 lbs:100% inlet-outlet Meriam: | 75.038 | 0.023 | 62.006 | 0.021 | 55.002 | 0.011 | 51.003 | 0.017 | 75 | 0.06 | 74.9 | 0.04 | 74.86 | 0.02 | 0.265 | 0.005 | 2.4181 | 0.0036 | 942 | 24 | 3372 | 88 | 1.915 | 0.042 | [6 empty] | 460.6 | 1.9 | 461.7 | 1.9 | 459.5 | 1.9 | 4.2 | 0 | 3.6 | 0 | 3.9 | 0 | 1887.9 | 14.2 | 1084.9 | 16.2 | 366.7 | 9.8 | 460 |  | 459 |  | 459 |  | 3.7 |  | 3.7 |  | 3.6 |  | 0.65 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 2255 | [14 empty] | 96.76 | 0.03 | 55.83 | 0.05 | 57.23 | 0.01 | 1.4 | 0.06 | 96.13 | 0.02 | 57.49 | 0.01 | 56.87 | 0.01 | -0.62 | 0.01 |  |  | 69.2 | 0.03 |  |  |  |  | 96.19 | 0.02 | 71.43 | 0.03 | 56.9 | 0.01 | 14.53 | 0.03 | 95.63 | 0.02 | 57.23 | 0.02 | 56.59 | 0.01 | 0.64 | 0.02 | [46 empty] | 96.43 | 0.02 | 56.78 | 0.03 | 57.05 | 0.01 | -0.27 | 0.03 | 97.32 | 0.03 | 57.53 | 0.02 | 1.08 | 0.05 |  |  | 72.94 | 0.03 |  |  |  |  | 96.3 | 0.02 | 56.97 | 0.01 | 14.09 | 0.04 | 96.42 | 0.02 | 59.01 | 0.02 | 57.03 | 0.01 | 1.98 | 0.02 | 57.73 | 0.03 | [28 empty] | 56.76 | 0.03 | 58.27 | 0.04 | 57.73 | 0.03 | 59.66 | 0.05 | 74.88 | 0.05 | 74.72 | 0.04 | 74.59 | 0.03 | 75.13 | 0.03 | 75.14 | 0.03 |  |  | 55.19 | 0.01 | 69.78 | 0.04 | 71.45 | 0.03 | 57.69 | 0.01 | 57.39 | 0.02 | 56.68 | 0.01 | 73.53 | 0.02 | 72.15 | 0.02 | 61.03 | 0.02 | 69.2 | 0.03 | 72.94 | 0.03 | 55.23 | 0.04 | 56.06 | 0.01 | 59.14 | 0.02 | 57.13 | 0.01 | 57.81 | 0.01 | 58.27 | 0.04 | 59.66 | 0.05 | [16 empty] | 55.83 | 0.05 | 56.45 | 0.05 | 56.76 | 0.03 | 57.73 | 0.03 | [16 empty] | 71.06 | 0.05 | [12 empty] | 57.49 | 0.01 | 56.77 | 0.12 | 56.51 | 0.14 | 75.37 | 0.03 | 75.12 | 0.03 | 74.91 | 0.03 | 75.71 | 0.03 | 75.7 | 0.03 | 75.7 | 0.04 | 75.51 | 0.04 | 72.68 | 0.07 | 73.71 | 0.04 | 73.29 | 0.04 | 71.28 | 0.1 | 72.82 | 0.05 | 73.1 | 0.05 | 73.91 | 0.04 | 74.51 | 0.04 | 74.52 | 0.04 | 74.38 | 0.05 | 74.54 | 0.04 | 74.4 | 0.04 | 74.75 | 0.04 | 74.58 | 0.04 | 71.94 | 0.12 | 74.78 | 0.05 | 74.09 | 0.05 | 68.65 | 0.12 | 68.85 | 0.12 |  |  | 75.09 | 0.04 | 75.65 | 0.04 | 75.49 | 0.04 | 75.34 | 0.04 | 74.93 |  | 75.01 | 0.04 | 70.3 | 0.08 | 71.21 | 0.07 | 72.21 | 0.07 | 74.18 | 0.04 | 74.78 | 0.04 | [62 empty] | Economizer test | 75.038 | 0.023 | 62.006 | 0.021 | 74.811 | 0.02 | 61.644 | 0.016 | 55.002 | 0.011 | 51.003 | 0.017 | 3468.1 | 2.6 | 3332.3 | 2.5 | 0.845 | 0.004 | -0.38 | 0.002 | 0.265 | 0.005 | 2.4181 | 0.0036 | 29.453 | 0 | 2255 | 10 | 2170 |  | 0 | 0 | 13.03 | 0.38 | 1.7019 | 15363.6764 | 330.8003 | 0 | 0 | 15363.6764 | 0.0087756 | 27.6124 | 73.1091 | 13.0296 | 13.544 | 0.0069825 | 20.7794 | 0.0087756 | 27.6124 | 0.0085914 | 27.3555 | 75.038 | 62.006 | 26.9406
2 | T2-TRN-55-T1FER-DM | 75T0103 | T2-TRN-55-T1FER-DM | 1 finger | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/13/2014 | 11:39:08 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 1.4 | 3.7 | 0 | 8238 | 14 | 8597 | 64 | 5609 | 93 | 13852 | 91 | 7.8839 | 949 | 1660 | [37 empty] | Econo 1F-open, tape around damper perimeter inside/outside frame gaps, no compressor--55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-55- | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;2F Open: Jade Control set to 6.9V | 74.968 | 0.006 | 61.998 | 0.023 | 54.977 | 0.01 | 51.006 | 0.017 | 74.88 | 0.05 | 72.31 | 0.04 | 72.92 | 0.01 | 0.217 | 0.004 | 1.2906 | 0.0026 | 8238 | 14 | 5609 | 93 | 7.883 | 0.08 | [6 empty] | 460.7 | 2.4 | 460.3 | 2.4 | 459.4 | 2.3 | 3.7 | 0 | 3.3 | 0 | 3.4 | 0 | 1616.5 | 20.7 | 1097.6 | 22.7 | 140.8 | 16.6 | 460 |  | 459 |  | 459 |  | 3.2 |  | 3.2 |  | 3.2 |  | 0.58 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1745 | [14 empty] | 102.06 | 0.07 | 58.68 | 0.04 | 60.09 | 0.03 | 1.43 | 0.05 | 100.63 | 0.1 | 59.52 | 0.03 | 59.32 | 0.05 | -0.19 | 0.03 |  |  | 73.41 | 0.02 |  |  |  |  | 100.99 | 0.1 | 71.47 | 0.02 | 59.52 | 0.05 | 11.94 | 0.04 | 100.13 | 0.09 | 58.9 | 0.05 | 59.06 | 0.05 | -0.16 | 0.02 | [46 empty] | 102.18 | 0.08 | 59.65 | 0.05 | 60.16 | 0.04 | -0.52 | 0.02 | 102.47 | 0.09 | 60.32 | 0.05 | 0.65 | 0.04 |  |  | 72.58 | 0.01 |  |  |  |  | 102.13 | 0.07 | 60.14 | 0.04 | 11.21 | 0.07 | 101.69 | 0.08 | 60.78 | 0.03 | 59.9 | 0.04 | 0.87 | 0.03 | 59.48 | 0.03 | [28 empty] | 59.45 | 0.04 | 59.48 | 0.03 | 59.64 | 0.04 | 59.83 | 0.05 | 72.27 | 0.05 | 72.42 | 0.04 |  |  | 72.59 | 0.02 | 72.94 | 0.02 | 72.79 | 0.02 | 58.58 | 0.03 | 73.64 | 0.04 | 71.81 | 0.03 | 59.05 | 0.05 | 60.08 | 0.04 | 59.92 | 0.05 | 73.28 | 0.02 | 72.28 | 0.02 | 60.44 | 0.05 | 73.41 | 0.02 | 72.58 | 0.01 | 55.45 | 0.02 | 59.91 | 0.03 | 59.3 | 0.03 | 60.44 | 0.05 | 61.14 | 0.05 | 59.64 | 0.04 | 59.83 | 0.05 | [12 empty] | 58.68 | 0.04 | 72.79 | 0.02 |  |  | 59.68 | 0.04 | 59.45 | 0.04 | 59.48 | 0.03 | [16 empty] | 71.35 | 0.04 | [12 empty] | 59.43 | 0.03 | 60.15 | 0.21 | 56.13 | 0.12 | 75.42 | 0.02 | 75.34 | 0.01 | 75.02 | 0.01 | 75.74 | 0.01 | 75.73 | 0.02 | 75.7 | 0.01 | 75.52 | 0.01 | 64.31 | 0.12 | 62.9 | 0.2 | 65.92 | 0.28 | 74.3 | 0.06 | 64.35 | 0.15 | 69.49 | 0.12 | 70.85 | 0.29 | 71.1 | 0.05 | 68.25 | 0.2 | 70.7 | 0.07 | 73.11 | 0.13 | 74.82 | 0.02 | 73.98 | 0.06 | 71.74 | 0.05 | 72.31 | 0.07 | 74.9 | 0.02 | 74.65 | 0.02 | 73.66 | 0.05 | 73.14 | 0.04 |  |  | 75.12 | 0.01 | 75.77 | 0.02 | 75.55 | 0.02 | 75.39 | 0.02 | 75.26 |  | 75.09 | 0.01 |  |  | 66.78 | 0.09 | 66.63 | 0.1 | 74.9 | 0.02 | 74.86 | 0.02 | [62 empty] | Economizer test | 74.968 | 0.006 | 61.998 | 0.023 | 72.506 | 0.004 | 60.551 | 0.016 | 54.977 | 0.01 | 51.006 | 0.017 | 3068.6 | 3.2 | 2959.5 | 3.1 | 0.611 | 0.003 | -0.199 | 0.002 | 0.217 | 0.004 | 1.2906 | 0.0026 | 29.452 | 0.001 | 1757 | 14 | 1660 |  | 0.047621 | 140.9356 | 13.029 | 0.199 | 1.5072 | 13654.0952 | 212.4343 | 140.9355 | 649.0246 | 13005.0706 | 0.0087015 | 27.2832 | 70.9988 | 13.029 | 13.4843 | 0.0069899 | 20.7814 | 0.0087869 | 27.6077 | 0.0084283 | 26.6152 | 74.0207 | 61.5268 | 26.2478
2 | T2-TRN-55-T2FER-DM | 75T0104 | T2-TRN-55-T2FER-DM | 2 finger | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/13/2014 | 10:30:36 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 1.4 | 3.7 | 0 | 13640 | 32 | 13867 | 115 | 8004 | 86 | 21651 | 103 | 12.2253 | 949 | 1660 | [37 empty] | Econo 2F-pen, tape around damper perimeter inside/outside frame gaps, no compressor--55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-55-T | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;2F Open: Jade Control set to 6.9V | 74.972 | 0.011 | 62.009 | 0.026 | 55.017 | 0.019 | 51.002 | 0.019 | 74.99 | 0.04 | 70.87 | 0.02 | 71.56 | 0 | 0.186 | 0.004 | 1.3105 | 0.0025 | 13640 | 32 | 8004 | 86 | 12.228 | 0.114 | [6 empty] | 461 | 2.4 | 460.5 | 2.4 | 459.2 | 2.4 | 3.7 | 0 | 3.3 | 0 | 3.4 | 0 | 1633.5 | 20.5 | 1089.5 | 23.2 | 137.3 | 16.6 | 460 |  | 460 |  | 459 |  | 3.2 |  | 3.2 |  | 3.2 |  | 0.58 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1745 | [14 empty] | 102.89 | 0.03 | 59.49 | 0.02 | 60.55 | 0.01 | 1.07 | 0.03 | 101.7 | 0.02 | 60.27 | 0.03 | 59.91 | 0.02 | -0.35 | 0.04 |  |  | 72.91 | 0.02 |  |  |  |  | 101.91 | 0.03 | 69.82 | 0.02 | 60.03 | 0.02 | 9.79 | 0.03 | 101.02 | 0.03 | 59.52 | 0.02 | 59.55 | 0.01 | -0.03 | 0.02 | [46 empty] | 103 | 0.04 | 60.09 | 0.02 | 60.6 | 0.02 | -0.51 | 0.02 | 103.3 | 0.03 | 60.77 | 0.02 | 0.45 | 0.03 |  |  | 70.8 | 0.02 |  |  |  |  | 102.91 | 0.02 | 60.56 | 0.01 | 9.12 | 0.09 | 102.86 | 0.02 | 60.69 | 0.07 | 60.53 | 0.01 | 0.15 | 0.07 | 59.99 | 0.02 | [28 empty] | 60.06 | 0.03 | 59.99 | 0.02 | 60.16 | 0.02 | 60.32 | 0.02 | 70.72 | 0.03 | 70.87 | 0.03 |  |  | 70.99 | 0.03 | 71.42 | 0.02 | 71.2 | 0.02 | 59.22 | 0.02 | 73.3 | 0.01 | 70.23 | 0.02 | 59.67 | 0.02 | 60.63 | 0.02 | 60.46 | 0.02 | 71.43 | 0.01 | 70.24 | 0.14 | 60.81 | 0.02 | 72.91 | 0.02 | 70.8 | 0.02 | 55.3 | 0.03 | 60.53 | 0.01 | 59.91 | 0.02 | 60.93 | 0.02 | 61.59 | 0.01 | 60.16 | 0.02 | 60.32 | 0.02 | [12 empty] | 59.49 | 0.02 | 71.2 | 0.02 |  |  | 60.32 | 0.03 | 60.06 | 0.03 | 59.99 | 0.02 | [16 empty] | 69.68 | 0.08 | [12 empty] | 59.86 | 0.02 | 61.03 | 0.31 | 56.32 | 0.16 | 75.51 | 0.03 | 75.41 | 0.03 | 75.1 | 0.02 | 75.84 | 0.03 | 75.84 | 0.03 | 75.81 | 0.04 | 75.61 | 0.04 | 62.82 | 0.15 | 63.85 | 0.16 | 62.96 | 0.18 | 72.07 | 0.1 | 66.05 | 0.12 | 64.63 | 0.18 | 62.21 | 0.14 | 68.48 | 0.16 | 67.88 | 0.09 | 67.73 | 0.13 | 72.31 | 0.13 | 74.75 | 0.03 | 71.56 | 0.09 | 69.34 | 0.07 | 69.93 | 0.07 | 74.89 | 0.03 | 73.75 | 0.05 | 71.01 | 0.06 | 70.39 | 0.05 |  |  | 75.21 | 0.03 | 75.83 | 0.02 | 75.62 | 0.03 | 75.44 | 0.03 | 75.31 |  | 75.12 | 0.03 |  |  | 61.83 | 0.09 | 63.82 | 0.11 | 74.82 | 0.03 | 74.8 | 0.03 | [62 empty] | Economizer test | 74.972 | 0.011 | 62.009 | 0.026 | 70.921 | 0.006 | 59.72 | 0.024 | 55.017 | 0.019 | 51.002 | 0.019 | 3088.1 | 2.9 | 2987.1 | 2.9 | 0.581 | 0.002 | -0.136 | 0.002 | 0.186 | 0.004 | 1.3105 | 0.0025 | 29.459 | 0.001 | 1771 | 14 | 1660 |  | 0.12784 | 381.8638 | 13.03 | 0.136 | 1.5019 | 13783.1669 | 203.8877 | 381.8625 | 1758.3966 | 12024.7703 | 0.0085617 | 26.7433 | 69.4191 | 13.0299 | 13.4429 | 0.0069784 | 20.7786 | 0.0087932 | 27.6155 | 0.0082749 | 26.0613 | 72.4336 | 60.7323 | 25.6953
2 | T2-TRN-55-T3FER-DM | 75T0105 | T2-TRN-55-T3FER-DM | 3 finger | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/13/2014 | 8:34:53 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.3 | 3.8 | 0 | 18825 | 29 | 19088 | 196 | 9941 | 176 | 28776 | 169 | 16.1391 | 949 | 1660 | [37 empty] | Econo 3F-open, tape around damper perimeter inside/outside frame gaps, no compressor,--55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-55 | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;2F Open: Jade Control set to 6.9V | 74.988 | 0.009 | 62.004 | 0.029 | 54.979 | 0.008 | 50.998 | 0.015 | 74.97 | 0.05 | 69.34 | 0.03 | 70.26 | 0.01 | 0.17 | 0.004 | 1.3287 | 0.0027 | 18825 | 29 | 9941 | 176 | 16.143 | 0.16 | [6 empty] | 461.1 | 2.5 | 460.6 | 2.5 | 458.9 | 2.5 | 3.8 | 0 | 3.3 | 0 | 3.4 | 0 | 1648.7 | 21 | 1081.3 | 23.5 | 134 | 16.2 | 460 |  | 459 |  | 460 |  | 3.2 |  | 3.2 |  | 3.2 |  | 0.57 | [23 empty] | 0.4 |  | 0 |  | 0 |  | 85 |  | 1745 | [14 empty] | 105.7 | 0.03 | 60.99 | 0.03 | 62.04 | 0.02 | 1.04 | 0.04 | 102.91 | 0.02 | 61.2 | 0.02 | 60.56 | 0.01 | -0.64 | 0.03 |  |  | 71.7 | 0.02 |  |  |  |  | 103.61 | 0.03 | 67.26 | 0.02 | 60.93 | 0.02 | 6.33 | 0.03 | 102.33 | 0.04 | 62.97 | 0.11 | 60.25 | 0.02 | 2.69 | 0.13 | [46 empty] | 103.62 | 0.08 | 60.81 | 0.03 | 60.94 | 0.04 | -0.13 | 0.04 | 104.32 | 0.06 | 61.31 | 0.04 | 0.63 | 0.03 |  |  | 66.41 | 0.92 |  |  |  |  | 103.49 | 0.12 | 60.87 | 0.06 | 5.24 | 0.11 | 103.56 | 0.12 | 63.93 | 0.17 | 60.9 | 0.06 | 3.02 | 0.18 | 61.58 | 0.04 | [28 empty] | 61.68 | 0.03 | 61.58 | 0.04 | 61.35 | 0.03 | 61.1 | 0.04 | 69.18 | 0.03 | 69.39 | 0.03 |  |  | 69.45 | 0.03 | 69.98 | 0.02 | 69.76 | 0.03 | 60.81 | 0.03 | 72.21 | 0.01 | 67.53 | 0.02 | 60.65 | 0.02 | 61.36 | 0.06 | 60.73 | 0.02 | 66.62 | 0.85 | 63.65 | 0.4 | 62.14 | 0.08 | 71.7 | 0.02 | 66.41 | 0.92 | 55.25 | 0.04 | 62.23 | 0.04 | 61.63 | 0.06 | 61.38 | 0.02 | 62.1 | 0.04 | 61.35 | 0.03 | 61.1 | 0.04 | [12 empty] | 60.99 | 0.03 | 69.76 | 0.03 |  |  | 60.68 | 0.04 | 61.68 | 0.03 | 61.58 | 0.04 | [16 empty] | 66.11 | 0.11 | [12 empty] | 61.2 | 0.02 | 61.22 | 0.22 | 56.42 | 0.21 | 75.58 | 0.03 | 75.45 | 0.03 | 75.16 | 0.03 | 75.9 | 0.03 | 75.9 | 0.03 | 75.85 | 0.04 | 75.65 | 0.04 | 59.62 | 0.15 | 61.15 | 0.14 | 60.33 | 0.16 | 67.16 | 0.17 | 61.95 | 0.11 | 64.06 | 0.12 | 61.03 | 0.23 | 63.92 | 0.21 | 64.94 | 0.09 | 65.37 | 0.14 | 69.95 | 0.25 | 71.86 | 0.05 | 70.44 | 0.15 | 67.31 | 0.1 | 67.97 | 0.09 | 74.95 | 0.03 | 72.76 | 0.06 | 69.28 | 0.11 | 68.41 | 0.08 |  |  | 75.25 | 0.04 | 75.86 | 0.03 | 75.64 | 0.03 | 75.46 | 0.03 | 75.35 |  | 75.18 | 0.04 |  |  | 58.5 | 0.52 | 61.19 | 0.13 | 72.64 | 0.1 | 74.34 | 0.04 | [62 empty] | Economizer test | 74.988 | 0.009 | 62.004 | 0.029 | 69.433 | 0.005 | 58.955 | 0.017 | 54.979 | 0.008 | 50.998 | 0.015 | 3106 | 3.1 | 3011.8 | 3.1 | 0.559 | 0.003 | -0.076 | 0.001 | 0.17 | 0.004 | 1.3287 | 0.0027 | 29.454 | 0 | 1783 | 14 | 1660 |  | 0.20316 | 611.873 | 13.029 | 0.076 | 1.4952 | 13903.0956 | 197.7894 | 611.873 | 2817.7435 | 11085.3521 | 0.0084211 | 26.2265 | 67.9378 | 13.029 | 13.4042 | 0.0069852 | 20.7768 | 0.0087861 | 27.6117 | 0.0081482 | 25.5604 | 70.9434 | 59.96 | 25.1961
2 | T2-TRN-95-TOER-DM | 75T0137 | T2-TRN-95-TOER-DM | open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/11/2014 | 20:48:54 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.6 | 15.4 | 0 | 33751 | 84 | 32959 | 362 | 0 | 0 | 33726 | 84 | 3.8663 | 949 |  |  | 3.8692 | [35 empty] | Econo fully open, tape around damper perimeter inside/outside frame gaps, both stages,--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-9 | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.017 | 0.046 | 62 | 0.026 | 94.993 | 0.025 | 74.88 | 0.019 | 74.83 | 0.12 | 64.3 | 0.03 | 66.02 | 0.03 | 0.009 | 0.003 | 1.2188 | 0.0024 | 33751 | 84 | 0 | 0 | 3.866 | 0.014 | [6 empty] | 460.8 | 2.7 | 460.8 | 2.7 | 459.3 | 2.7 | 15.4 | 0.1 | 13.4 | 0 | 13 | 0.1 | 7019.2 | 72.2 | 3218.1 | 77 | 1704.4 | 61.4 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.5 |  | 3190 |  | 0.87 | 460 | 460 | 460 | 5 | 4.6 | 4.5 | 3060 | 0.82 | 459.9 |  | 1.6 |  | 705.8 |  | 85 |  | 8690.8 | [14 empty] | 217.83 | 0.24 | 107.11 | 0.09 | 107.21 | 0.08 | 0.1 | 0.05 | 251.63 | 0.25 | 174.73 | 0.1 | 117.53 | 0.07 | -57.2 | 0.08 | 209.33 | 0.05 | 99.5 | 0.07 | 104.44 | 0.05 | 4.95 | 0.05 | 83.42 | 0.06 | 59.35 | 0.33 | 49.44 | 0.04 | 9.9 | 0.33 | 82.29 | 0.04 | 63.84 | 0.13 | 48.75 | 0.02 | 15.09 | 0.12 | [46 empty] | 256.29 | 0.25 | 166.56 | 0.11 | 118.88 | 0.07 | 47.68 | 0.1 | 231.02 | 0.32 | 111.36 | 0.1 | 8.39 | 0.08 | 217.2 | 0.05 | 102.05 | 0.11 | 107.01 | 0.05 | 4.89 | 0.05 | 93.08 | 0.06 | 55.13 | 0.03 | 4.24 | 0.36 | 92.28 | 0.07 | 65.89 | 0.19 | 54.67 | 0.04 | 11.22 | 0.17 | 105.33 | 0.09 | [28 empty] | 105.78 | 0.09 | 105.33 | 0.09 | 102.88 | 0.11 | 103.2 | 0.1 | 64.28 | 0.04 | 64.03 | 0.05 | 63.67 | 0.05 | 64.58 | 0.04 | 64.43 | 0.04 | 64.36 | 0.04 | 106.14 | 0.07 | 101.08 | 0.08 | 60.72 | 0.36 | 64.11 | 0.14 | 166.22 | 0.12 | 103.35 | 0.11 | 102.55 | 0.11 | 58.53 | 0.15 | 68.17 | 0.2 | 99.5 | 0.07 | 102.05 | 0.11 | 93.34 | 0.07 | 106.68 | 0.09 | 106.47 | 0.08 | 103.46 | 0.07 | 102.94 | 0.07 | 102.88 | 0.11 | 103.2 | 0.1 | [12 empty] | 107.11 | 0.09 | 64.36 | 0.04 |  |  | 102.98 | 0.11 | 105.78 | 0.09 | 105.33 | 0.09 | [16 empty] | 59.38 | 0.36 | [12 empty] | 175.16 | 0.1 | 94.23 | 0.14 | 94.89 | 0.15 | 75.55 | 0.09 | 75.41 | 0.09 | 75.16 | 0.08 | 76.09 | 0.07 | 75.91 | 0.09 | 75.83 | 0.09 | 75.62 | 0.09 | 92.69 | 0.23 | 93.19 | 0.25 | 91.25 | 0.15 | 92.31 | 0.2 | 89.98 | 0.22 | 86.92 | 0.13 | 86.49 | 0.12 | 85.99 | 0.13 | 87.2 | 0.12 | 85.87 | 0.12 | 88.89 | 0.17 | 87.95 | 0.18 | 86.61 | 0.13 | 86.81 | 0.12 | 86.84 | 0.11 | 79.62 | 0.14 | 85 | 0.23 | 88.2 | 0.13 | 88.63 | 0.11 |  |  | 75.26 | 0.08 | 75.96 | 0.07 | 75.68 | 0.08 | 75.47 | 0.09 | 75.39 |  | 75.19 | 0.09 |  |  | 93.41 | 0.22 | 92.76 | 0.2 | 90.5 | 0.21 | 86.97 | 0.13 | [62 empty] | No appropriate economizer test for this fault test | 75.017 | 0.046 | 62 | 0.026 | 64.242 | 0.023 | 61.168 | 0.03 | 94.993 | 0.025 | 74.88 | 0.019 | 2969.7 | 3 | 2880.8 | 2.9 | 0.414 | 0.002 | -0.127 | 0.001 | 0.009 | 0.003 | 1.2188 | 0.0024 | 29.363 | 0.001 | 8723 | 21 | 1650 |  | 0.4 | 800 | 13.03 | 0.04 | 1.6015 | 13403.7137 | 140.113 | 1482.7979 | 6310.2792 | 7093.4344 | 0.01115 | 32.5201 | 62.6405 | 14.0989 | 13.2935 | 0.013817 | 38.0414 | 0.0087766 | 27.6084 | 0.010786 | 27.1697 | 84.4669 | 68.5213 | 26.7777 | 76970.0869 | 70213.0179 | 7073 | 0.31363 | 71816.8427 | 65059.7737 | 8.233 | 0.14143 | -5.7424 | -21.8264 | 59.0451 | 76970.0869 | 5880.3957 | 5254.5325 | 65835.1587 | 76970.0869 | 100%
2 | T2-TRN-95-T1FER-DM | 75T0131 | T2-TRN-95-T1FER-DM | 1 finger | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/13/2014 | 5:44:45 | 10 Ton | 0:15:00 | 75/62 95/72 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 72 | 6.4 | 6.2 | 6.4 | 6.2 | 460.3 | 1.4 | 15.2 | 0 | 54326 | 86 | 54407 | 543 | 989 | 121 | 55316 | 98 | 6.4516 | 950 |  |  | 6.3361 | [35 empty] | Econo 1F-open, tape around damper perimeter inside/outside frame gaps, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-TRN-95-T1 | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;2F Open: Jade Control set to 5.1V | 74.99 | 0.014 | 61.994 | 0.021 | 94.997 | 0.041 | 75.01 | 0.028 | 75.21 | 0.17 | 58.79 | 0.03 | 61.05 | 0.01 | 0.216 | 0.003 | 1.2813 | 0.0029 | 54326 | 86 | 989 | 121 | 6.451 | 0.022 | [6 empty] | 460.3 | 2.6 | 460.6 | 2.6 | 459.7 | 2.6 | 15.2 | 0.1 | 13.2 | 0 | 12.9 | 0.1 | 6891.4 | 59.1 | 3253.8 | 69.6 | 1682.8 | 48 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.36 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.4 |  | 3140 |  | 0.85 | 460 | 460 | 460 | 4.8 | 4.6 | 4.4 | 2990 | 0.81 | 459.4 |  | 1.6 |  | 705.9 |  | 85 |  | 8600.9 | [14 empty] | 215.04 | 0.34 | 106.21 | 0.16 | 106.32 | 0.11 | 0.11 | 0.1 | 243.83 | 0.38 | 172.74 | 0.1 | 115.25 | 0.11 | -57.49 | 0.12 | 209 |  | 99.12 | 0.11 | 104.33 |  | 5.21 |  | 76.04 | 0.06 | 50.5 | 0.46 | 44.82 | 0.04 | 5.68 | 0.48 | 75.42 | 0.03 | 57.26 | 0.19 | 44.43 | 0.02 | 12.83 | 0.19 | [46 empty] | 247.03 | 0.37 | 168.53 | 0.15 | 116.2 | 0.11 | 52.33 | 0.15 | 228.33 | 0.47 | 110.54 | 0.14 | 10.55 | 0.17 | 216 | 0.12 | 99.56 | 0.13 | 106.62 | 0.16 | 7.06 | 0.18 | 81.68 | 0.05 | 48.39 | 0.03 | 2.58 | 0.3 | 80.58 | 0.08 | 59.45 | 0.24 | 47.71 | 0.05 | 11.74 | 0.24 | 104.84 | 0.14 | [28 empty] | 105.25 | 0.14 | 104.84 | 0.14 | 100.68 | 0.14 | 100.98 | 0.13 | 58.74 | 0.04 | 58.41 | 0.04 |  |  | 58.96 | 0.03 | 58.7 | 0.03 | 58.73 | 0.04 | 105.45 | 0.12 | 100.39 | 0.12 | 51.73 | 0.68 | 57.48 | 0.25 | 167.75 | 0.19 | 101.02 | 0.14 | 99.96 | 0.13 | 51.22 | 0.1 | 61.46 | 0.35 | 99.12 | 0.11 | 99.56 | 0.13 | 93.25 | 0.09 | 106.03 | 0.13 | 105.81 | 0.12 | 101.11 | 0.1 | 101.21 | 0.1 | 100.68 | 0.14 | 100.98 | 0.13 | [14 empty] | 58.73 | 0.04 |  |  | 99.99 | 0.19 | 105.25 | 0.14 | 104.84 | 0.14 | [16 empty] | 50.98 | 0.29 | [12 empty] | 173.35 | 0.11 | 94.48 | 0.16 | 94.31 | 0.24 | 75.91 | 0.07 | 75.73 | 0.08 | 75.47 | 0.07 | 76.27 | 0.05 | 76.26 | 0.07 | 76.19 | 0.08 | 75.97 | 0.08 | 85.22 | 0.19 | 85.17 | 0.23 | 82.84 | 0.24 | 77.18 | 0.14 | 84.26 | 0.2 | 80.97 | 0.14 | 80.12 | 0.22 | 79.1 | 0.08 | 81.5 | 0.19 | 79.85 | 0.12 | 76.76 | 0.16 | 75.5 | 0.09 | 76.03 | 0.11 | 77.77 | 0.1 | 76.95 | 0.1 | 75.58 | 0.08 | 75.64 | 0.08 | 76.11 | 0.09 | 76.67 | 0.08 |  |  | 75.52 | 0.08 | 76.15 | 0.06 | 75.89 | 0.08 | 75.66 | 0.09 | 75.56 |  | 75.47 | 0.1 |  |  | 83.12 | 0.13 | 82.27 | 0.13 | 75.84 | 0.1 | 75.47 | 0.09 | [62 empty] | T2-TRN-55-T1FER-DM | 74.99 | 0.014 | 61.994 | 0.021 | 58.593 | 0.008 | 55.859 | 0.015 | 94.997 | 0.041 | 75.01 | 0.028 | 3026.1 | 3.4 | 2979.6 | 3.4 | 0.599 | 0.003 | -0.212 | 0.002 | 0.216 | 0.003 | 1.2813 | 0.0029 | 29.414 | 0 | 8574 | 24 | 1680 |  | 0.047621 | 140.9356 | 13.029 | 0.199 | 1.5122 | 13823.0438 | 209.6766 | 151.3265 | 643.9463 | 13179.0975 | 0.009019 | 28.0965 | 57.0808 | 14.0999 | 13.135 | 0.01393 | 38.1668 | 0.008779 | 27.6045 | 0.0088441 | 23.676 | 75.9304 | 62.69 | 23.3071 | 66204.096 | 62533.9476 | 6894 | 0.3554 | 61185.8822 | 57515.7338 | 7.1362 | 0.152 | -4.7894 | -18.8495 | 53.7022 | 66204.096 | 54303.658 | 5098.8252 | 6801.6128 | 66204.096 | 100%
2 | T2-TRN-95-T2FER-DM | 75T0133 | T2-TRN-95-T2FER-DM | 2 finger | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/13/2014 | 3:50:43 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 1.1 | 15.2 | 0 | 50232 | 59 | 50229 | 451 | 0 | 0 | 50228 | 59 | 5.8439 | 949 |  |  | 5.8443 | [35 empty] | Econo 2F-open, tape around damper perimeter inside/outside frame gaps, both stages,--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam, | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;2F Open: Jade Control set to 5.95V | 75.003 | 0.012 | 62.003 | 0.024 | 95.005 | 0.038 | 74.995 | 0.025 | 75.18 | 0.13 | 59.86 | 0.04 | 61.87 | 0.01 | 0.171 | 0.004 | 1.2674 | 0.0029 | 50232 | 59 | 0 | 0 | 5.844 | 0.018 | [6 empty] | 460.2 | 2.5 | 460.7 | 2.5 | 459.7 | 2.4 | 15.2 | 0.1 | 13.2 | 0 | 13 | 0.1 | 6908.6 | 59.4 | 3252.1 | 65.2 | 1686.1 | 48.8 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.4 |  | 3140 |  | 0.85 | 460 | 460 | 460 | 4.9 | 4.6 | 4.4 | 3000 | 0.81 | 459.4 |  | 1.6 |  | 705.3 |  | 85 |  | 8560.3 | [14 empty] | 215.37 | 0.28 | 106.34 | 0.12 | 106.43 | 0.09 | 0.09 | 0.09 | 244.59 | 0.32 | 172.92 | 0.09 | 115.47 | 0.09 | 57.45 | 0.07 | 208.17 | 0.05 | 99.05 | 0.09 | 104.06 | 0.05 | 5.09 | 0.05 | 76.59 | 0.05 | 51.24 | 0.42 | 45.18 | 0.03 | 6.06 | 0.43 | 75.95 | 0.02 | 57.82 | 0.14 | 44.77 | 0.02 | 13.05 | 0.14 | [46 empty] | 248.7 | 0.32 | 168.08 | 0.11 | 116.69 | 0.09 | 51.4 | 0.09 | 228.62 | 0.42 | 110.63 | 0.13 | 9.96 | 0.09 | 215.5 | 0.05 | 99.91 | 0.12 | 106.45 | 0.05 | 6.55 | 0.05 | 84.57 | 0.04 | 50.15 | 0.02 | 2.71 | 0.32 | 83.48 | 0.07 | 61.34 | 0.17 | 49.49 | 0.04 | 11.85 | 0.18 | 104.89 | 0.12 | [28 empty] | 105.32 | 0.11 | 104.89 | 0.12 | 100.99 | 0.13 | 101.29 | 0.11 | 59.85 | 0.05 | 59.51 | 0.04 | 59.1 | 0.04 | 60.11 | 0.03 | 59.83 | 0.03 | 59.84 | 0.03 | 105.54 | 0.09 | 100.41 | 0.1 | 52.55 | 0.6 | 57.94 | 0.19 | 167.38 | 0.13 | 101.33 | 0.12 | 100.35 | 0.12 | 52.91 | 0.1 | 63.45 | 0.25 | 99.05 | 0.09 | 99.91 | 0.12 | 93.27 | 0.09 | 106.13 | 0.11 | 105.81 | 0.14 | 101.57 | 0.08 | 101.52 | 0.1 | 100.99 | 0.13 | 101.29 | 0.11 | [12 empty] | 106.34 | 0.12 | 59.84 | 0.03 |  |  | 100.67 | 0.12 | 105.32 | 0.11 | 104.89 | 0.12 | [16 empty] | 52.86 | 0.3 | [12 empty] | 173.51 | 0.1 | 94.37 | 0.14 | 94.34 | 0.21 | 75.84 | 0.07 | 75.67 | 0.07 | 75.39 | 0.07 | 76.21 | 0.05 | 76.18 | 0.07 | 76.11 | 0.08 | 75.89 | 0.08 | 87.05 | 0.29 | 85.39 | 0.18 | 87.05 | 0.26 | 79.5 | 0.11 | 84.37 | 0.15 | 84.56 | 0.16 | 85.55 | 0.13 | 82.84 | 0.24 | 81.14 | 0.09 | 82.66 | 0.18 | 77.21 | 0.11 | 75.62 | 0.08 | 77.54 | 0.1 | 80.13 | 0.1 | 78.93 | 0.09 | 75.52 | 0.08 | 76.25 | 0.08 | 78.19 | 0.09 | 78.75 | 0.07 |  |  | 75.44 | 0.07 | 76.11 | 0.06 | 75.85 | 0.07 | 75.62 | 0.08 | 75.53 |  | 75.43 | 0.08 |  |  | 88.05 | 0.2 | 85.06 | 0.17 | 76.1 | 0.09 | 75.43 | 0.08 | [62 empty] | T2-TRN-55-T2FER-DM | 75.003 | 0.012 | 62.003 | 0.024 | 59.687 | 0.004 | 56.932 | 0.011 | 95.005 | 0.038 | 74.995 | 0.025 | 3012.9 | 3.4 | 2958.6 | 3.4 | 0.559 | 0.003 | -0.145 | 0.002 | 0.171 | 0.004 | 1.2674 | 0.0029 | 29.402 | 0 | 8595 | 23 | 1630 |  | 0.12784 | 381.8638 | 13.03 | 0.136 | 1.4865 | 13730.6911 | 194.2957 | 410.1666 | 1745.3905 | 11985.3006 | 0.0094344 | 28.9507 | 58.2005 | 14.1 | 13.1657 | 0.013915 | 38.1522 | 0.0087819 | 27.6108 | 0.0092201 | 24.3517 | 77.5663 | 63.8744 | 23.9889 | 68130.2415 | 63817.4223 | 6965 | 0.34891 | 63230.1827 | 58917.3635 | 7.3566 | 0.14929 | -4.9619 | -19.3658 | 54.8021 | 68130.2415 | 44749.1309 | 4982.1794 | 18398.9312 | 68130.2415 | 100%
2 | T2-TRN-95-T3FER-DM | 75T0135 | T2-TRN-95-T3FER-DM | 3 finger | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/13/2014 | 2:26:32 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 1.3 | 15.2 | 0 | 46598 | 58 | 46877 | 500 | 0 | 0 | 46589 | 58 | 5.4048 | 949 |  |  | 5.4058 | [35 empty] | Econo 3F-open, tape around damper perimeter inside/outside frame gaps, both stages,--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-TRN-95-T | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6: .;3F Open: Jade Control set to 6.9V | 74.997 | 0.017 | 61.932 | 0.012 | 95 | 0.037 | 75.019 | 0.026 | 74.9 | 0.14 | 60.52 | 0.04 | 62.76 | 0.01 | 0.14 | 0.003 | 1.2654 | 0.0026 | 46598 | 58 | 0 | 0 | 5.405 | 0.016 | [6 empty] | 460.2 | 2.3 | 460.6 | 2.3 | 459.8 | 2.3 | 15.2 | 0.1 | 13.2 | 0 | 13 | 0.1 | 6908.4 | 56.9 | 3264.4 | 65.4 | 1711.9 | 47.4 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.57 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.9 |  | 4.4 |  | 3140 |  | 0.86 | 460 | 460 | 460 | 4.9 | 4.6 | 4.5 | 3020 | 0.8 | 459.3 |  | 1.6 |  | 705.3 |  | 85 |  | 8590.3 | [14 empty] | 215.58 | 0.3 | 106.15 | 0.13 | 106.49 | 0.1 | 0.34 | 0.08 | 245.67 | 0.33 | 173.11 | 0.18 | 115.79 | 0.1 | 57.32 | 0.16 | 209.8 | 0.05 | 98.74 | 0.1 | 104.6 | 0.05 | 5.94 | 0.05 | 77.76 | 0.06 | 52.71 | 0.42 | 45.93 | 0.03 | 6.79 | 0.44 | 77.01 | 0.03 | 59.07 | 0.11 | 45.45 | 0.02 | 13.63 | 0.12 | [46 empty] | 250.13 | 0.35 | 167.69 | 0.08 | 117.1 | 0.1 | 50.59 | 0.07 | 228.89 | 0.46 | 110.71 | 0.14 | 9.69 | 0.09 | 217.83 | 0.05 | 100.2 | 0.12 | 107.22 | 0.05 | 7.09 | 0.05 | 86.63 | 0.06 | 51.39 | 0.03 | 3.07 | 0.33 | 85.73 | 0.06 | 62.72 | 0.14 | 50.85 | 0.04 | 11.87 | 0.13 | 104.66 | 0.13 | [28 empty] | 105.08 | 0.13 | 104.66 | 0.13 | 101.06 | 0.13 | 101.29 | 0.12 | 60.64 | 0.04 | 60.41 | 0.04 | 60.01 | 0.05 | 60.83 | 0.03 | 60.55 | 0.03 | 60.67 | 0.03 | 105.44 | 0.09 | 99.71 | 0.11 | 53.63 | 0.57 | 58.85 | 0.17 | 166.8 | 0.12 | 101.54 | 0.13 | 100.74 | 0.12 | 54.36 | 0.11 | 64.89 | 0.2 | 98.74 | 0.1 | 100.2 | 0.12 | 93.22 | 0.09 | 106.11 | 0.13 | 105.93 | 0.11 | 101.85 | 0.1 | 101.87 | 0.09 | 101.06 | 0.13 | 101.29 | 0.12 | [12 empty] | 106.15 | 0.13 | 60.67 | 0.03 |  |  | 101.01 | 0.14 | 105.08 | 0.13 | 104.66 | 0.13 | [16 empty] | 54.46 | 0.32 | [12 empty] | 173.62 | 0.11 | 94.14 | 0.16 | 94.25 | 0.23 | 75.74 | 0.07 | 75.6 | 0.08 | 75.37 | 0.06 | 76.12 | 0.04 | 76.07 | 0.07 | 75.98 | 0.07 | 75.78 | 0.08 | 87.88 | 0.21 | 87.32 | 0.18 | 88.38 | 0.18 | 80.94 | 0.17 | 86.28 | 0.17 | 85.64 | 0.14 | 86.75 | 0.23 | 85.75 | 0.22 | 84.96 | 0.17 | 84.66 | 0.14 | 79.67 | 0.14 | 77.52 | 0.09 | 81.07 | 0.13 | 83.16 | 0.15 | 82.47 | 0.12 | 75.68 | 0.08 | 77.7 | 0.08 | 80.95 | 0.13 | 81.42 | 0.1 |  |  | 75.36 | 0.07 | 76.15 | 0.06 | 75.89 | 0.08 | 75.66 | 0.09 | 75.57 |  | 75.45 | 0.09 |  |  | 90.26 | 0.24 | 87.26 | 0.2 | 77.36 | 0.12 | 76.49 | 0.1 | [62 empty] | T2-TRN-55-T3FER-DM | 74.997 | 0.017 | 61.932 | 0.012 | 60.705 | 0.013 | 57.907 | 0.018 | 95 | 0.037 | 75.019 | 0.026 | 3013.9 | 3.2 | 2951.9 | 3.1 | 0.529 | 0.002 | -0.08 | 0.001 | 0.14 | 0.003 | 1.2654 | 0.0026 | 29.395 | 0 | 8620 | 24 | 1640 |  | 0.20316 | 611.873 | 13.029 | 0.076 | 1.5109 | 13705.5505 | 183.452 | 653.0618 | 2778.9764 | 10926.5741 | 0.0097911 | 29.7122 | 59.1941 | 14.1001 | 13.1942 | 0.013937 | 38.1755 | 0.0087365 | 27.5597 | 0.0095679 | 24.9786 | 79.0834 | 64.9065 | 24.6096 | 69933.6854 | 65422.4797 | 6980 | 0.34065 | 64962.4871 | 60451.2813 | 7.5363 | 0.14566 | -5.1026 | -19.8893 | 55.8032 | 69933.6854 | 35374.7897 | 5057.7091 | 29501.1867 | 69933.6854 | 100%
2 | T2-CAN-55-1ER-DM | 75T0120 | T2-CAN-55-1ER-DM | 10% open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/6/2014 | 21:01:46 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 0.8 | 3.6 | 0 | 14014 | 92 | 28532 | 428 | 8129 | 232 | 22152 | 190 | 13.0306 | 952 | 1570 | [37 empty] | Econo 10%-open, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN-55-1E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.012 | 0.023 | 61.971 | 0.047 | 54.938 | 0.024 | 50.995 | 0.025 | 74.9 | 0.03 | 65.5 | 0.13 | 71.38 | 0.01 | 0.211 | 0.004 | 1.0923 | 0.0021 | 14014 | 92 | 8129 | 232 | 13.037 | 0.154 | [6 empty] | 460.9 | 2.1 | 459.8 | 2.1 | 459.2 | 2.1 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1578.5 | 17.4 | 1097 | 19.6 | 120.9 | 12.9 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.55 | [29 empty] | 85 |  | 1655 | [166 empty] | 63.83 | 0.03 | 62.24 | 0.03 | 64.74 | 0.02 | 63.49 | 0.03 | 70.63 | 0.03 | 70.41 | 0.02 | 70.06 | 0.03 | 70.95 | 0.03 | 70.87 | 0.02 | 70.75 | 0.02 | 60.95 | 0.07 | 67.96 | 0.01 | 69.71 | 0.01 | 62.91 | 0.02 | 64.18 | 0.02 | 61.79 | 0.04 | 70.61 | 0.03 | 69.25 | 0.02 | 62.44 | 0.02 | 68.19 | 0.02 | 69.96 | 0.05 | 54.53 | 0.06 | 64.62 | 0.03 | 63.32 | 0.04 | 64.91 | 0.03 | 66.49 | 0.03 | [18 empty] | 70.75 | 0.02 | [38 empty] | 59.15 | 0.03 | 54.5 | 0.32 | 54.72 | 0.27 | 75.53 | 0.04 | 75.33 | 0.05 | 74.95 | 0.06 | 74.63 | 0.11 | 75.92 | 0.04 | 75.83 | 0.03 | 75.55 | 0.05 | 70.43 | 0.09 | 69.56 | 0.13 | 71.64 | 0.04 | 73.93 | 0.04 | 73.76 | 0.04 | 73.27 | 0.03 | 72.71 | 0.04 | 73.36 | 0.05 | 73.7 | 0.05 | 73.55 | 0.06 | 73.45 | 0.04 | 72.24 | 0.04 | 72.76 | 0.1 | 71.04 | 0.23 | 72.75 | 0.04 | 64.8 | 0.09 | 68.34 | 0.1 | 64.23 | 0.26 | 57.66 | 0.08 |  |  | 74.54 | 0.14 | 75.84 | 0.04 | 75.61 | 0.04 | 75.44 | 0.04 | 75.24 |  | 75.18 | 0.04 |  |  |  |  | 74.23 | 0.03 | 72.8 | 0.04 | 72.4 | 0.04 | [62 empty] | Economizer test | 75.012 | 0.023 | 61.971 | 0.047 | 70.437 | 0.043 | 59.395 | 0.03 | 54.938 | 0.024 | 50.995 | 0.025 | 2827.5 | 2.7 | 2715.8 | 2.6 | 0.509 | 0.003 | -0.151 | 0.003 | 0.211 | 0.004 | 1.0923 | 0.0021 | 29.24 | 0 | 1700 | 14 | 1570 |  | 0.1492 | 405.1918 | 13.028 | 0.151 | 1.5842 | 12632.2229 | 162.398 | 405.1922 | 1866.0951 | 10766.1278 | 0.0084979 | 26.5812 | 68.8528 | 13.028 | 13.4299 | 0.0069933 | 20.7755 | 0.0087587 | 27.5875 | 0.0081853 | 25.8454 | 72.0547 | 60.4933 | 25.4595
2 | T2-CAN-55-2ER-DM | 75T0121 | T2-CAN-55-2ER-DM | 20% open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/6/2014 | 20:03:25 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.1 | 3.6 | 0 | 15769 | 102 | 15317 | 135 | 8291 | 269 | 24068 | 359 | 14.2583 | 952 | 1550 | [37 empty] | Econo 20%-open, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN-55-2E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75 | 0.015 | 62 | 0.067 | 55.08 | 0.119 | 51.323 | 0.14 | 74.82 | 0.03 | 69.76 | 0.05 | 70.81 | 0.04 | 0.195 | 0.003 | 1.0655 | 0.0021 | 15769 | 102 | 8291 | 269 | 14.256 | 0.246 | [6 empty] | 460.8 | 2.2 | 460 | 2.2 | 459.2 | 2.3 | 3.6 | 0 | 3.2 | 0 | 3.4 | 0 | 1576.3 | 18.5 | 1094.8 | 22.2 | 112 | 14.1 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.1 |  | 3.1 |  | 0.55 | [29 empty] | 85 |  | 1635 | [166 empty] | 63.19 | 0.05 | 62.29 | 0.05 | 64.45 | 0.04 | 63.24 | 0.05 | 69.91 | 0.07 | 69.74 | 0.07 | 69.47 | 0.07 | 70.23 | 0.06 | 70.22 | 0.06 | 70.1 | 0.07 | 59.04 | 0.13 | 68.17 | 0.05 | 69.73 | 0.04 | 63.28 | 0.03 | 64.35 | 0.03 | 61.73 | 0.04 | 70.6 | 0.05 | 69.01 | 0.05 | 62.65 | 0.03 | 68.2 | 0.04 | 69.93 | 0.05 | 54.37 | 0.18 | 61.56 | 0.14 | 60.83 | 0.09 | 64.52 | 0.04 | 66.13 | 0.05 | [18 empty] | 70.1 | 0.07 | [38 empty] | 59.31 | 0.06 | 54.58 | 0.42 | 54.84 | 0.36 | 75.42 | 0.04 | 75.29 | 0.04 | 74.89 | 0.05 | 74.65 | 0.1 | 75.82 | 0.04 | 75.76 | 0.04 | 75.5 | 0.05 | 66.35 | 0.19 | 65.28 | 0.16 | 69.55 | 0.09 | 73.72 | 0.04 | 72 | 0.05 | 72.46 | 0.05 | 72.39 | 0.06 | 73.36 | 0.04 | 73.44 | 0.04 | 73.44 | 0.04 | 73.47 | 0.04 | 72.44 | 0.05 | 72.63 | 0.06 | 71.85 | 0.11 | 72.96 | 0.04 | 67.5 | 0.14 | 68.13 | 0.1 | 66.19 | 0.13 | 58.25 | 0.17 |  |  | 74.59 | 0.11 | 75.75 | 0.04 | 75.53 | 0.04 | 75.36 | 0.04 | 75.18 |  | 75.1 | 0.04 |  |  |  |  | 73.48 | 0.04 | 73.09 | 0.04 | 72.61 | 0.05 | [62 empty] | Economizer test | 75 | 0.015 | 62 | 0.067 | 69.783 | 0.037 | 59.158 | 0.08 | 55.08 | 0.119 | 51.323 | 0.14 | 2791.2 | 2.8 | 2683.2 | 2.6 | 0.489 | 0.002 | -0.133 | 0.002 | 0.195 | 0.003 | 1.0655 | 0.0021 | 29.234 | 0.001 | 1688 | 14 | 1550 |  | 0.18208 | 488.5525 | 13.033 | 0.133 | 1.5894 | 12485.4035 | 154.1441 | 488.5473 | 2249.1726 | 10236.2309 | 0.0084841 | 26.4116 | 68.1936 | 13.0327 | 13.4134 | 0.0071347 | 20.9636 | 0.0087806 | 27.6086 | 0.0081917 | 25.6932 | 71.4203 | 60.2369 | 25.3059
2 | T2-CAN-55-3ER-DM | 75T0122 | T2-CAN-55-3ER-DM | 30% open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/6/2014 | 18:12:31 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 1.4 | 3.6 | 0 | [9 empty] | 952 | 1550 | [37 empty] | Econo 30%-open, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-CAN-55-3E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.996 | 0.015 | 61.99 | 0.038 | 54.967 | 0.022 | 51.063 | 0.032 | 74.68 | 0.06 | 67.58 | 0.05 | 69.06 | 0.01 | 0.182 | 0.003 | 1.0408 | 0.0022 | 21909 | 39 | 11859 | 144 | 20.061 | 0.193 | [6 empty] | 460.7 | 2.6 | 459.5 | 2.6 | 459 | 2.6 | 3.6 | 0 | 3.2 | 0 | 3.3 | 0 | 1567.3 | 20.7 | 1097 | 23.9 | 116.5 | 15.4 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3 |  | 3.1 |  | 0.55 | [29 empty] | 85 |  | 1635 | [166 empty] | 63.74 | 0.04 | 62.63 | 0.04 | 64.05 | 0.03 | 63.04 | 0.05 | 67.71 | 0.06 | 67.59 | 0.05 | 67.4 | 0.03 | 67.91 | 0.02 | 67.92 | 0.02 | 67.88 | 0.02 | 61.33 | 0.1 | 67.34 | 0.22 | 69.02 | 0.04 | 64.5 | 0.03 | 58.54 | 0.05 | 63.61 | 0.03 | 70.83 | 0.02 | 63.59 | 0.2 | 63.22 | 0.03 | 67.67 | 0.19 | 70.34 | 0.01 | 53.6 | 0.05 | 65.24 | 0.01 | 63.94 | 0.02 | 66.23 | 0.03 | 67.7 | 0.02 | [18 empty] | 67.88 | 0.02 | [38 empty] | 59.15 | 0.04 | 54.52 | 0.29 | 54.92 | 0.28 | 75.38 | 0.05 | 75.29 | 0.05 | 74.94 | 0.05 | 75.1 | 0.08 | 75.75 | 0.05 | 75.69 | 0.04 | 75.5 | 0.04 | 54.58 | 0.1 | 58.48 | 0.14 | 59.25 | 0.16 | 70.18 | 0.1 | 57.08 | 0.11 | 71.74 | 0.08 | 70.7 | 0.08 | 73.57 | 0.05 | 69.64 | 0.12 | 72.26 | 0.05 | 69.82 | 0.11 | 72.06 | 0.05 | 72.31 | 0.07 | 72.76 | 0.06 | 72.3 | 0.05 | 72.78 | 0.06 | 61.92 | 0.15 | 60.9 | 0.25 | 56.89 | 0.09 |  |  | 74.87 | 0.07 | 75.71 | 0.04 | 75.49 | 0.05 | 75.32 | 0.05 | 75.21 |  | 75.06 | 0.04 | 63.15 | 1.95 |  |  | 61.72 | 0.09 | 71.14 | 0.08 | 72 | 0.06 | [62 empty] | Economizer test | 74.996 | 0.015 | 61.99 | 0.038 | 67.682 | 0.015 | 57.906 | 0.026 | 54.967 | 0.022 | 51.063 | 0.032 | 2753.4 | 2.9 | 2657.6 | 2.8 | 0.447 | 0.002 | -0.091 | 0.003 | 0.182 | 0.003 | 1.0408 | 0.0022 | 29.243 | 0 | 1684 | 14 | 1550 |  | 0.28429 | 755.5232 | 13.029 | 0.091 | 1.6213 | 12367.4042 | 139.5604 | 755.5228 | 3479.2705 | 8888.1337 | 0.008282 | 25.6921 | 66.0607 | 13.029 | 13.358 | 0.0070226 | 20.8144 | 0.008775 | 27.6015 | 0.0079178 | 24.8824 | 69.3743 | 59.1481 | 24.4876
2 | T2-CAN-55-CE-DM | 75T0123 | T2-CAN-55-CE-DM | closed | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/6/2014 | 22:33:40 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 1 | 3.7 | 0 | [9 empty] | 952 | 1570 | [37 empty] | Econo closed, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN-55-CE-DM-SPWCT-SS | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.001 | 0.011 | 61.994 | 0.043 | 54.983 | 0.035 | 51.081 | 0.045 | 74.9 | 0.03 | 70 | 0.12 | 71.64 | 0.01 | 0.217 | 0.003 | 1.1074 | 0.0024 | [12 empty] | 460.9 | 2.2 | 460.3 | 2.2 | 459.1 | 2.2 | 3.7 | 0 | 3.2 | 0 | 3.4 | 0 | 1591.6 | 18.7 | 1088.4 | 20.5 | 115.1 | 14.9 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.55 | [29 empty] | 85 |  | 1655 | [166 empty] | 64.34 | 0.02 | 62.56 | 0.03 | 65.17 | 0.01 | 64.09 | 0.02 | 71.04 | 0.02 | 70.8 | 0.02 | 70.41 | 0.02 | 71.36 | 0.02 | 71.26 | 0.02 | 71.13 | 0.02 | 62.19 | 0.02 | 67.74 | 0.02 | 69.52 | 0.01 | 63.07 | 0.01 | 64.6 | 0.03 | 61.83 | 0.02 | 70.35 | 0.04 | 69.06 | 0.02 | 62.7 | 0.02 | 68.04 | 0.02 | 69.71 | 0.04 | 54.75 | 0.04 | 65.44 | 0.01 | 64.27 | 0.01 | 65.16 | 0.04 | 66.72 | 0.04 | [18 empty] | 71.13 | 0.02 | [38 empty] | 59.5 | 0.02 | 54.33 | 0.36 | 54.59 | 0.31 | 75.5 | 0.03 | 75.29 | 0.05 | 74.92 | 0.07 | 74.49 | 0.11 | 75.91 | 0.03 | 75.83 | 0.03 | 75.53 | 0.05 | 71.39 | 0.06 | 71.25 | 0.09 | 72.69 | 0.04 | 74.12 | 0.03 | 74.26 | 0.03 | 73.67 | 0.04 | 72.77 | 0.05 | 73.24 | 0.05 | 73.7 | 0.07 | 73.47 | 0.07 | 73.52 | 0.04 | 72.2 | 0.05 | 72.41 | 0.05 | 70.64 | 0.24 | 72.58 | 0.04 | 62.97 | 0.09 | 66.59 | 0.13 | 59.72 | 0.26 | 57.28 | 0.09 |  |  | 74.42 | 0.15 | 75.8 | 0.03 | 75.58 | 0.03 | 75.4 | 0.03 | 75.21 |  | 75.16 | 0.03 |  |  |  |  | 74.47 | 0.03 | 72.67 | 0.04 | 72.38 | 0.05 | [62 empty] | Economizer test | 75.001 | 0.011 | 61.994 | 0.043 | 70.834 | 0.012 | 59.615 | 0.046 | 54.983 | 0.035 | 51.081 | 0.045 | 2846.4 | 3.1 | 2735 | 3 | 0.519 | 0.002 | -0.16 | 0.003 | 0.217 | 0.003 | 1.1074 | 0.0024 | 29.266 | 0.001 | 1707 | 13 | 1570 |  | 0.12973 | 354.8204 | 13.029 | 0.16 | 1.57 | 12706.8106 | 166.7592 | 354.8264 | 1633.9602 | 11072.8504 | 0.0085517 | 26.7325 | 69.264 | 13.0294 | 13.4404 | 0.0070284 | 20.8246 | 0.0087764 | 27.6043 | 0.0082295 | 25.9904 | 72.434 | 60.7169 | 25.6079
2 | T2-CAN-55-OER-DM | 75T0124 | T2-CAN-55-OER-DM | open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/6/2014 | 7:00:16 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 1.1 | 3.7 | 0 | 41781 | 70 | 40102 | 275 | 21130 | 173 | 62931 | 200 | 35.9195 | 950 | 1620 | [37 empty] | Econo fully open, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley,--3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester--speed to match total static of run T2-CAN-55-OE-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.005 | 0.01 | 61.996 | 0.024 | 55.004 | 0.023 | 51.116 | 0.042 | 74.53 | 0.1 | 61.68 | 0.04 | 63.84 | 0.01 | 0.176 | 0.004 | 1.1123 | 0.0023 | 41781 | 70 | 21130 | 173 | 35.919 | 0.304 | [6 empty] | 460.9 | 2.4 | 460 | 2.4 | 459.4 | 2.4 | 3.7 | 0 | 3.3 | 0 | 3.4 | 0 | 1606.9 | 21.3 | 1100.8 | 23.2 | 145.5 | 16.6 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.2 |  | 3.1 |  | 0.56 | [29 empty] | 85 |  | 1705 | [166 empty] | 63.04 | 0.04 | 63.11 | 0.04 | 63.51 | 0.02 | 62.85 | 0.04 | 61.71 | 0.05 | 61.44 | 0.04 |  |  | 61.97 | 0.05 | 61.87 | 0.05 | 61.85 | 0.05 | 61.54 | 0.13 | 66.22 | 0.03 | 63.87 | 0.04 | 66.31 | 0.04 | 62.88 | 0.6 | 63.77 | 0.05 | 64.31 | 0.02 | 59.42 | 0.16 | 63.79 | 0.05 | 66.1 | 0.02 | 63.4 | 0.02 | 54.19 | 0.11 | 62.48 | 0.07 | 62.4 | 0.06 | 66.84 | 0.03 | 68.04 | 0.02 | [18 empty] | 61.85 | 0.05 | [38 empty] | 61.86 | 0.03 | 55.84 | 0.78 | 55.96 | 0.51 | 75.44 | 0.09 | 75.3 | 0.09 | 75.03 | 0.09 | 75.86 | 0.08 | 75.85 | 0.09 | 75.79 | 0.09 | 75.57 | 0.09 | 57.41 | 0.28 | 59.48 | 0.31 | 55.3 | 0.49 | 57.29 | 0.24 | 63.89 | 0.31 | 62.43 | 0.38 | 57.44 | 0.15 | 62.04 | 0.11 | 62.69 | 0.23 | 60.67 | 0.14 | 60.33 | 0.24 | 58.6 | 0.15 | 62.45 | 0.15 | 60.34 | 0.15 | 60.55 | 0.13 | 72.32 | 0.1 | 72.95 | 0.07 | 72.7 | 0.05 | 72.43 | 0.05 |  |  | 75.12 | 0.08 | 75.69 | 0.08 | 75.48 | 0.09 | 75.28 | 0.1 | 75.13 |  | 74.99 | 0.1 | 56.38 | 0.86 | 56.73 | 0.24 | 58.34 | 0.2 | 57.99 | 0.18 | 60.53 | 0.16 | [62 empty] | Economizer test | 75.005 | 0.01 | 61.996 | 0.024 | 61.608 | 0.009 | 54.412 | 0.016 | 55.004 | 0.023 | 51.116 | 0.042 | 2826.9 | 2.9 | 2770 | 2.9 | 0.414 | 0.003 | -0.044 | 0.001 | 0.176 | 0.004 | 1.1123 | 0.0023 | 29.361 | 0.001 | 1752 | 14 | 1620 |  | 0.58782 | 1628.2631 | 13.03 | 0.044 | 1.6432 | 12850.2299 | 134.7241 | 1628.2678 | 7497.7361 | 5352.4937 | 0.0077647 | 23.6608 | 59.9648 | 13.0301 | 13.1993 | 0.0070421 | 20.8446 | 0.0087768 | 27.6057 | 0.0072995 | 22.7304 | 63.3504 | 55.9338 | 22.3307
2 | T2-CAN-95-1ER-DM | 75T0138 | T2-CAN-95-1ER-DM | 10% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 22:31:40 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.2 | 1.3 | 15.4 | 0 | 47478 | 73 | 47252 | 512 | 51 | 30 | 47492 | 82 | 5.5663 | 952 | [38 empty] | Econo 10%-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static--of run T2-CAN-95-1E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.044 | 0.025 | 61.986 | 0.015 | 95.067 | 0.011 | 74.996 | 0.016 | 75.17 | 0.17 | 59.35 | 0.03 | 61.9 | 0.03 | 0.184 | 0.004 | 1.0523 | 0.0024 | 47478 | 73 | 51 | 30 | 5.566 | 0.017 | [6 empty] | 461.2 | 2.6 | 461.8 | 2.6 | 458.7 | 2.6 | 15.4 | 0.1 | 13 | 0 | 12.6 | 0.1 | 6998 | 56.6 | 3084.7 | 62.8 | 1533.8 | 42.2 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.5 |  | 3150 |  | 0.85 | 460 | 460 | 460 | 5 | 4.6 | 4.4 | 3010 | 0.81 | 460.2 |  | 1.6 |  | 696.2 |  | 85 |  | 8481.2 | [14 empty] | 215.54 | 0.24 | 106.06 | 0.16 | 106.44 | 0.08 | 0.39 | 0.12 | 243.53 | 0.28 | 172.78 | 0.09 | 115.13 | 0.08 | -57.65 | 0.11 | 206.73 | 0.05 | 100.03 | 0.09 | 103.55 | 0.05 | 3.58 | 0.05 | 75.08 | 0.06 | 48.55 | 0.35 | 44.13 | 0.03 | 4.42 | 0.37 | 74.5 | 0.05 | 56.08 | 0.19 | 43.75 | 0.03 | 12.33 | 0.19 | [46 empty] | 247.26 | 0.27 | 167.57 | 0.23 | 116.23 | 0.08 | 51.34 | 0.23 | 227.91 | 0.4 | 110.37 | 0.12 | 10.4 | 0.17 | 215.7 | 0.05 | 99.15 | 0.11 | 106.49 | 0.05 | 7.36 | 0.05 | 81.29 | 0.08 | 48.08 | 0.05 | 2.96 | 0.39 | 80.85 | 0.09 | 58.96 | 0.43 | 47.81 | 0.06 | 11.16 | 0.46 | 105.02 | 0.11 | [28 empty] | 105.47 | 0.09 | 105.02 | 0.11 | 100.24 | 0.12 | 100.58 | 0.11 | 59.38 | 0.03 | 58.97 | 0.03 | 58.5 | 0.04 | 59.6 | 0.03 | 59.16 | 0.05 | 59.28 | 0.02 | 105.61 | 0.11 | 101.37 | 0.1 | 49.78 | 0.61 | 55.87 | 0.28 | 167.21 | 0.26 | 100.78 | 0.11 | 99.55 | 0.11 | 51.33 | 0.11 | 60.46 | 0.64 | 100.03 | 0.09 | 99.15 | 0.11 | 94.11 | 0.08 | 106.17 | 0.1 | 105.95 | 0.14 | 100.95 | 0.08 | 100.76 | 0.09 | 100.24 | 0.12 | 100.58 | 0.11 | [14 empty] | 59.28 | 0.02 |  |  | 99.97 | 0.17 | 105.47 | 0.09 | 105.02 | 0.11 | [16 empty] | 51.04 | 0.35 | [12 empty] | 173.36 | 0.11 | 94.44 | 0.23 | 93.94 | 0.19 | 75.88 | 0.1 | 75.76 | 0.1 | 75.62 | 0.1 | 77.22 | 0.09 | 76.23 | 0.1 | 76.16 | 0.1 | 76.03 | 0.1 | 79.45 | 0.11 | 79.54 | 0.11 | 78.32 | 0.1 | 76.34 | 0.11 | 76.43 | 0.12 | 76.85 | 0.1 | 77.14 | 0.11 | 77.02 | 0.11 | 76.25 | 0.1 | 76.36 | 0.11 | 76.26 | 0.09 | 77.22 | 0.1 | 77.16 | 0.11 | 77.68 | 0.18 | 76.83 | 0.1 | 83.03 | 0.15 | 80.18 | 0.1 | 84.3 | 0.21 | 88.94 | 0.33 |  |  | 76.05 | 0.12 | 76.21 | 0.1 | 75.9 | 0.1 | 75.67 | 0.11 | 75.54 |  | 75.4 | 0.1 |  |  |  |  | 76.14 | 0.12 | 77.08 | 0.09 | 77.13 | 0.09 | [62 empty] | T2-CAN-55-1ER-DM | 75.044 | 0.025 | 61.986 | 0.015 | 59.15 | 0.009 | 56.232 | 0.012 | 95.067 | 0.011 | 74.996 | 0.016 | 2753.9 | 3.2 | 2684.9 | 3.2 | 0.486 | 0.002 | -0.156 | 0.004 | 0.184 | 0.004 | 1.0523 | 0.0024 | 29.182 | 0 | 8532 | 23 | 1540 |  | 0.1492 | 405.1918 | 13.028 | 0.151 | 1.5689 | 12565.4931 | 153.2955 | 428.4771 | 1823.1187 | 10742.3744 | 0.0095068 | 29.1292 | 57.5811 | 14.1015 | 13.1498 | 0.013901 | 38.1521 | 0.008761 | 27.5979 | 0.0089314 | 23.9068 | 77.9723 | 64.1193 | 23.5241 | 70431.2767 | 61494.2897 | 6992 | 0.33882 | 65698.4544 | 56761.4674 | 7.7002 | 0.15885 | -5.6051 | -20.3913 | 53.7302 | 70431.2767 | 46380.1766 | 4809.6139 | 19241.4862 | 70431.2767 | 100%
2 | T2-CAN-95-2ER-DM | 75T0139 | T2-CAN-95-2ER-DM | 20% open | on | on | 3 turns | unsealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 21:13:27 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.2 | 15.3 | 0 | 47292 | 64 | 47480 | 549 | 918 | 171 | 48211 | 176 | 5.6626 |  |  |  | 5.5546 | [35 empty] | . | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.003 | 0.02 | 62.006 | 0.023 | 95.207 | 0.04 | 74.991 | 0.019 | 75.05 | 0.17 | 58.92 | 0.04 | 61.51 | 0.02 | 0.182 | 0.004 | 1.0217 | 0.0024 | 47292 | 64 | 918 | 171 | 5.663 | 0.026 | [6 empty] | 461.1 | 2.5 | 461.4 | 2.5 | 458.9 | 2.4 | 15.3 | 0.1 | 13 | 0 | 12.6 | 0.1 | 6947.5 | 53.9 | 3123.9 | 61.3 | 1565.8 | 41.7 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.4 |  | 3130 |  | 0.86 | 460 | 460 | 460 | 5 | 4.5 | 4.4 | 3000 | 0.81 | 460.2 |  | 1.6 |  | 696.1 |  | 85 |  | 8451.1 | [14 empty] | 215.66 | 0.31 | 105.9 | 0.18 | 106.48 | 0.1 | 0.58 | 0.14 | 243.29 | 0.34 | 172.97 | 0.14 | 115.05 | 0.1 | -57.92 | 0.16 | 209.8 | 0.05 | 99.75 | 0.11 | 104.53 | 0.05 | 4.93 | 0.05 | 74.34 | 0.08 | 47.83 | 0.42 | 43.64 | 0.05 | 4.19 | 0.43 | 73.77 | 0.08 | 55.38 | 0.33 | 43.26 | 0.05 | 12.12 | 0.32 | [46 empty] | 247.57 | 0.32 | 167.62 | 0.14 | 116.32 | 0.09 | 51.3 | 0.12 | 227.86 | 0.42 | 110.35 | 0.13 | 10.12 | 0.1 | 215.8 | 0.05 | 99.23 | 0.1 | 106.62 | 0.05 | 7.4 | 0.05 | 81.75 | 0.04 | 48.36 | 0.03 | 2.77 | 0.25 | 81.4 | 0.05 | 59.06 | 0.2 | 48.14 | 0.03 | 10.92 | 0.2 | 105.04 | 0.13 | [28 empty] | 105.48 | 0.12 | 105.04 | 0.13 | 100.3 | 0.12 | 100.59 | 0.11 | 59.13 | 0.04 | 58.75 | 0.04 | 58.26 | 0.03 | 59.34 | 0.04 | 58.72 | 0.05 | 59.01 | 0.03 | 105.54 | 0.13 | 101.35 | 0.13 | 48.97 | 0.68 | 55.16 | 0.43 | 167.39 | 0.17 | 100.83 | 0.11 | 99.6 | 0.1 | 51.49 | 0.09 | 60.71 | 0.3 | 99.75 | 0.11 | 99.23 | 0.1 | 94.18 | 0.05 | 106.21 | 0.12 | 106.03 | 0.13 | 101.14 | 0.07 | 100.69 | 0.12 | 100.3 | 0.12 | 100.59 | 0.11 | [14 empty] | 59.01 | 0.03 |  |  | 100.24 | 0.13 | 105.48 | 0.12 | 105.04 | 0.13 | [16 empty] | 51.13 | 0.24 | [12 empty] | 173.53 | 0.17 | 94.52 | 0.25 | 93.96 | 0.2 | 75.74 | 0.1 | 75.59 | 0.09 | 75.4 | 0.09 | 76.87 | 0.08 | 76.1 | 0.1 | 76.04 | 0.09 | 75.88 | 0.09 | 82.21 | 0.16 | 82.69 | 0.14 | 79.39 | 0.11 | 76.55 | 0.1 | 77.42 | 0.1 | 77.37 | 0.09 | 77.2 | 0.1 | 76.81 | 0.1 | 76.37 | 0.09 | 76.31 | 0.09 | 76.1 | 0.09 | 76.8 | 0.09 | 76.66 | 0.1 | 77.27 | 0.27 | 76.53 | 0.1 | 80.37 | 0.28 | 79.48 | 0.1 | 81.64 | 0.16 | 84.37 | 1.3 |  |  | 75.76 | 0.1 | 76.07 | 0.09 | 75.78 | 0.11 | 75.54 | 0.11 | 75.39 |  | 75.28 | 0.11 |  |  |  |  | 76.86 | 0.11 | 76.66 | 0.08 | 76.73 | 0.09 | [62 empty] | T2-CAN-55-2ER-DM | 75.003 | 0.02 | 62.006 | 0.023 | 58.942 | 0.014 | 56.03 | 0.015 | 95.207 | 0.04 | 74.991 | 0.019 | 2713.3 | 3.2 | 2645.4 | 3.1 | 0.468 | 0.002 | -0.141 | 0.004 | 0.182 | 0.004 | 1.0217 | 0.0024 | 29.158 | 0 | 8514 | 23 | 1540 |  | 0.18208 | 488.5525 | 13.033 | 0.133 | 1.6007 | 12385.7212 | 145.4462 | 523.3048 | 2226.087 | 10159.6342 | 0.0096968 | 29.5058 | 57.3413 | 14.1047 | 13.144 | 0.013863 | 38.1447 | 0.0087839 | 27.6129 | 0.0088618 | 23.7803 | 78.6618 | 64.6288 | 23.3899 | 75750.203 | 63376.657 | 6974 | 0.31422 | 70990.5908 | 58617.0448 | 8.3381 | 0.15686 | -6.1159 | -21.3205 | 53.3747 | 75750.203 | 47469.3135 | 4836.2252 | 23444.6643 | 75750.203 | 100%
2 | T2-CAN-95-3ER-DM | 75T0140 | T2-CAN-95-3ER-DM | 30% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 23:32:52 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.2 | 15.4 | 0 | 44651 | 123 | 43958 | 570 | 0 | 0 | 44649 | 123 | 5.2473 | 952 | [38 empty] | Econo 30%-open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-CAN-95-3E-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.062 | 0.046 | 62.035 | 0.027 | 94.983 | 0.012 | 75.01 | 0.02 | 75.02 | 0.19 | 59.88 | 0.02 | 62.43 | 0.03 | 0.149 | 0.004 | 0.9986 | 0.0025 | 44651 | 123 | 0 | 0 | 5.248 | 0.02 | [6 empty] | 461.1 | 2.4 | 461.9 | 2.4 | 458.6 | 2.4 | 15.4 | 0.1 | 12.9 | 0 | 12.6 | 0.1 | 6996.9 | 51.4 | 3074.1 | 59.1 | 1511.8 | 39.1 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.4 |  | 3140 |  | 0.85 | 460 | 460 | 460 | 5.1 | 4.6 | 4.4 | 3000 | 0.81 | 460.2 |  | 1.6 |  | 696.5 |  | 85 |  | 8461.5 | [14 empty] | 215.47 | 0.23 | 105.84 | 0.17 | 106.42 | 0.07 | 0.59 | 0.13 | 243.12 | 0.28 | 172.6 | 0.19 | 115.01 | 0.08 | -57.6 | 0.18 | 210.07 | 0.05 | 99.73 | 0.08 | 104.64 | 0.05 | 4.85 | 0.05 | 74.27 | 0.08 | 47.63 | 0.24 | 43.6 | 0.05 | 4.03 | 0.24 | 73.7 | 0.08 | 55.34 | 0.23 | 43.23 | 0.05 | 12.11 | 0.21 | [46 empty] | 248.53 | 0.27 | 166.37 | 0.14 | 116.6 | 0.08 | 49.76 | 0.13 | 226.66 | 0.37 | 109.99 | 0.12 | 9.09 | 0.13 | 216.4 | 0.05 | 100.06 | 0.1 | 106.71 | 0.05 | 6.66 | 0.05 | 85.46 | 0.04 | 50.63 | 0.02 | 3 | 0.33 | 84.89 | 0.05 | 61.18 | 0.25 | 50.28 | 0.03 | 10.9 | 0.24 | 105.07 | 0.11 | [28 empty] | 105.51 | 0.08 | 105.07 | 0.11 | 101.06 | 0.11 | 101.36 | 0.1 | 59.88 | 0.04 | 59.51 | 0.05 | 59.02 | 0.04 | 60.07 | 0.03 | 59.71 | 0.04 | 59.73 | 0.03 | 105.38 | 0.12 | 101.22 | 0.1 | 48.8 | 0.45 | 55.11 | 0.3 | 166.24 | 0.17 | 101.39 | 0.14 | 100.45 | 0.11 | 53.69 | 0.1 | 63.11 | 0.34 | 99.73 | 0.08 | 100.06 | 0.1 | 94.29 | 0.06 | 106.21 | 0.12 | 105.91 | 0.12 | 101.78 | 0.06 | 101.3 | 0.09 | 101.06 | 0.11 | 101.36 | 0.1 | [14 empty] | 59.73 | 0.03 |  |  | 100.89 | 0.14 | 105.51 | 0.08 | 105.07 | 0.11 | [16 empty] | 53.64 | 0.33 | [12 empty] | 173.54 | 0.12 | 94.39 | 0.23 | 93.79 | 0.19 | 75.79 | 0.14 | 75.57 | 0.13 | 75.38 | 0.13 | 76.56 | 0.09 | 76.15 | 0.14 | 76.04 | 0.13 | 75.84 | 0.13 | 91.75 | 0.18 | 87.86 | 0.12 | 88.19 | 0.16 | 78.14 | 0.15 | 87.94 | 0.16 | 78.08 | 0.15 | 77.86 | 0.14 | 76.55 | 0.14 | 78.73 | 0.15 | 77.07 | 0.15 | 77.53 | 0.14 | 76.7 | 0.13 | 76.81 | 0.13 | 76.48 | 0.14 | 76.75 | 0.15 | 76.8 | 0.13 | 81.02 | 0.21 | 81.88 | 0.21 | 86.21 | 0.17 |  |  | 75.57 | 0.12 | 76.1 | 0.15 | 75.81 | 0.16 | 75.55 | 0.15 | 75.44 |  | 75.27 | 0.15 |  |  |  |  | 84.15 | 0.13 | 77.28 | 0.12 | 76.53 | 0.14 | [62 empty] | T2-CAN-55-3ER-DM | 75.062 | 0.046 | 62.035 | 0.027 | 59.688 | 0.014 | 56.778 | 0.023 | 94.983 | 0.012 | 75.01 | 0.02 | 2683.4 | 3.4 | 2613.1 | 3.3 | 0.428 | 0.002 | -0.109 | 0.004 | 0.149 | 0.004 | 0.9986 | 0.0025 | 29.189 | 0.001 | 8509 | 22 | 1540 |  | 0.28429 | 755.5232 | 13.029 | 0.091 | 1.6375 | 12229.7062 | 131.3908 | 860.1774 | 3660.4365 | 8569.2697 | 0.010329 | 30.7859 | 58.0505 | 14.0996 | 13.165 | 0.013934 | 38.1671 | 0.0087891 | 27.633 | 0.0091278 | 24.2517 | 81.0635 | 66.3211 | 23.852 | 84799.3934 | 67546.0689 | 6969 | 0.28049 | 79991.8101 | 62738.4856 | 9.4008 | 0.14935 | -6.9339 | -23.013 | 54.0101 | 84799.3934 | 41352.6374 | 4887.3342 | 38559.4218 | 84799.3934 | 100%
2 | T2-CAN-95-CE-DM | 75T0141 | T2-CAN-95-CE-DM | closed | on | on | 3 turns | unsealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 18:41:07 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.2 | 15.1 | 0 | 48955 | 97 | 48988 | 523 | 1233 | 162 | 50189 | 123 | 5.9164 | 952 | [38 empty] | . | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.021 | 0.033 | 61.998 | 0.014 | 94.919 | 0.017 | 75.006 | 0.015 | 75.16 | 0.18 | 58.87 | 0.03 | 61.33 | 0.01 | 0.207 | 0.003 | 1.0654 | 0.0023 | 48955 | 97 | 1233 | 162 | 5.916 | 0.02 | [6 empty] | 461.1 | 2.5 | 460.5 | 2.5 | 459.2 | 2.5 | 15.1 | 0.1 | 13.1 | 0 | 12.6 | 0.1 | 6858.2 | 58.9 | 3189.1 | 64.9 | 1625.1 | 47.7 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.55 | 460 |  | 460 |  | 460 |  | 4.6 |  | 4.8 |  | 4.4 |  | 3120 |  | 0.85 | 460 | 460 | 460 | 4.9 | 4.5 | 4.4 | 2990 | 0.81 | 460.1 |  | 1.6 |  | 696.6 |  | 85 |  | 8441.6 | [14 empty] | 213.2 | 0.22 | 105.28 | 0.14 | 105.68 | 0.07 | 0.39 | 0.11 | 241.5 | 0.24 | 171.68 | 0.09 | 114.51 | 0.07 | -57.17 | 0.1 | 207.03 | 0.05 | 99.17 | 0.07 | 103.64 | 0.05 | 4.51 | 0.05 | 75.13 | 0.05 | 48.65 | 0.33 | 44.15 | 0.03 | 4.5 | 0.35 | 74.55 | 0.05 | 55.96 | 0.17 | 43.77 | 0.03 | 12.19 | 0.17 | [46 empty] | 245.23 | 0.24 | 166.84 | 0.31 | 115.62 | 0.07 | 51.22 | 0.33 | 226.13 | 0.35 | 109.81 | 0.11 | 10.39 | 0.16 | 215.17 | 0.05 | 98.72 | 0.12 | 106.31 | 0.05 | 7.68 | 0.05 | 80.67 | 0.1 | 47.68 | 0.06 | 2.83 | 0.44 | 80.2 | 0.12 | 58.39 | 0.63 | 47.39 | 0.08 | 11.01 | 0.67 | 104.21 | 0.1 | [28 empty] | 104.59 | 0.09 | 104.21 | 0.1 | 99.76 | 0.13 | 100.04 | 0.12 | 58.91 | 0.04 | 58.53 | 0.03 | 58.13 | 0.04 | 59.17 | 0.03 | 58.62 | 0.04 | 58.87 | 0.03 | 104.83 | 0.09 | 100.51 | 0.08 | 49.94 | 0.57 | 55.88 | 0.25 | 166.59 | 0.32 | 100.28 | 0.12 | 99.1 | 0.12 | 50.96 | 0.12 | 59.91 | 0.88 | 99.17 | 0.07 | 98.72 | 0.12 | 93.19 | 0.04 | 105.32 | 0.09 | 105.26 | 0.09 | 100.46 | 0.08 | 100.04 | 0.09 | 99.76 | 0.13 | 100.04 | 0.12 | [14 empty] | 58.87 | 0.03 |  |  | 99.41 | 0.16 | 104.59 | 0.09 | 104.21 | 0.1 | [16 empty] | 50.52 | 0.4 | [12 empty] | 172.37 | 0.11 | 92.24 | 0.16 | 94.47 | 0.18 | 75.86 | 0.1 | 75.77 | 0.1 | 75.58 | 0.1 | 77.28 | 0.1 | 76.21 | 0.1 | 76.16 | 0.1 | 76.04 | 0.1 | 79.12 | 0.11 | 79.31 | 0.1 | 77.33 | 0.1 | 76.24 | 0.1 | 76.09 | 0.11 | 76.45 | 0.11 | 77.13 | 0.1 | 77.16 | 0.1 | 76.27 | 0.11 | 76.47 | 0.11 | 76.17 | 0.11 | 77.23 | 0.09 | 77.03 | 0.1 | 78.26 | 0.17 | 76.99 | 0.09 | 83.54 | 0.07 | 81.17 | 0.1 | 86.66 | 0.19 | 89 | 0.12 |  |  | 76.11 | 0.12 | 76.2 | 0.1 | 75.9 | 0.11 | 75.67 | 0.11 | 75.55 |  | 75.4 | 0.11 |  |  |  |  | 76.01 | 0.11 | 77.13 | 0.09 | 77.13 | 0.09 | [62 empty] | T2-CAN-55-CE-DM | 75.021 | 0.033 | 61.998 | 0.014 | 58.742 | 0.005 | 55.901 | 0.007 | 94.919 | 0.017 | 75.006 | 0.015 | 2771.6 | 3 | 2701.3 | 3 | 0.516 | 0.003 | -0.166 | 0.003 | 0.207 | 0.003 | 1.0654 | 0.0023 | 29.137 | 0 | 8483 | 22 | 1550 |  | 0.12973 | 354.8204 | 13.029 | 0.16 | 1.5571 | 12656.9442 | 163.7524 | 375.9471 | 1599.9953 | 11056.9489 | 0.009428 | 28.9415 | 57.1849 | 14.0981 | 13.1387 | 0.013945 | 38.1644 | 0.0087743 | 27.6069 | 0.0088334 | 23.7007 | 77.557 | 63.8619 | 23.3209 | 71139.0917 | 61883.6224 | 6933 | 0.33262 | 66407.8286 | 57152.3593 | 7.8283 | 0.15565 | -5.6206 | -20.3721 | 53.4295 | 71139.0917 | 49439.981 | 4807.1718 | 16891.939 | 71139.0917 | 100%
2 | T2-CAN-95-OER-DM | 75T0142 | T2-CAN-95-OER-DM | open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/8/2014 | 0:52:06 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461.1 | 1.3 | 15.5 | 0 | 32547 | 80 | 32052 | 354 | 0 | 0 | 32530 | 80 | 3.7577 | 952 | [38 empty] | Econo fully open, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run--T2-CAN-95-OE-DM-SPWCT-SSR | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.707 | 0.014 | 62.115 | 0.013 | 94.886 | 0.041 | 75.001 | 0.035 | 74.66 | 0.12 | 63.33 | 0.02 | 65.22 | 0.02 | 0.115 | 0.005 | 0.9835 | 0.0024 | 32547 | 80 | 0 | 0 | 3.758 | 0.014 | [6 empty] | 461.1 | 2.9 | 461.7 | 2.9 | 459 | 2.9 | 15.5 | 0.1 | 13.1 | 0 | 12.8 | 0.1 | 7037.5 | 74.3 | 3125.7 | 79.2 | 1619.8 | 61.5 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3 |  | 0.56 | 460 |  | 460 |  | 460 |  | 4.7 |  | 4.9 |  | 4.5 |  | 3220 |  | 0.86 | 460 | 460 | 460 | 5.1 | 4.6 | 4.5 | 3080 | 0.81 | 460.1 |  | 1.6 |  | 695.4 |  | 85 |  | 8610.4 | [14 empty] | 218.63 | 0.22 | 107.44 | 0.08 | 107.44 | 0.07 | 0.01 | 0.05 | 252.61 | 0.25 | 175.07 | 0.09 | 117.79 | 0.07 | 57.28 | 0.1 | 210.93 | 0.05 | 99.99 | 0.06 | 104.94 | 0.05 | 4.96 | 0.05 | 84.26 | 0.08 | 59.9 | 0.48 | 49.91 | 0.05 | 9.99 | 0.46 | 83.61 | 0.08 | 64.45 | 0.2 | 49.51 | 0.05 | 14.94 | 0.19 | [46 empty] | 255.06 | 0.25 | 167.39 | 0.26 | 118.5 | 0.07 | 48.89 | 0.28 | 231.4 | 0.35 | 111.46 | 0.11 | 8.7 | 0.13 | 220.93 | 0.05 | 101.79 | 0.12 | 108.18 | 0.05 | 6.36 | 0.05 | 89.29 | 0.07 | 52.9 | 0.04 | 4.82 | 1.14 | 88.74 | 0.1 | 63.43 | 0.51 | 52.58 | 0.05 | 10.85 | 0.53 | 105.58 | 0.08 | [28 empty] | 106.02 | 0.08 | 105.58 | 0.08 | 102.61 | 0.12 | 102.91 | 0.11 | 63.31 | 0.05 | 63.07 | 0.04 | 62.71 | 0.05 | 63.49 | 0.05 | 63.09 | 0.06 | 63.3 | 0.04 | 106.45 | 0.07 | 101.17 | 0.07 | 61.1 | 0.45 | 64.67 | 0.22 | 167.23 | 0.28 | 103.04 | 0.11 | 102.21 | 0.11 | 56.86 | 0.51 | 65.73 | 0.61 | 99.99 | 0.06 | 101.79 | 0.12 | 93.66 | 0.12 | 106.81 | 0.09 | 106.57 | 0.08 | 102.95 | 0.08 | 102.53 | 0.08 | 102.61 | 0.12 | 102.91 | 0.11 | [14 empty] | 63.3 | 0.04 |  |  | 102.76 | 0.12 | 106.02 | 0.08 | 105.58 | 0.08 | [16 empty] | 57.7 | 1.14 | [12 empty] | 175.63 | 0.09 | 95.73 | 0.2 | 94.99 | 0.15 | 75.23 | 0.08 | 75.06 | 0.08 | 74.79 | 0.08 | 75.64 | 0.07 | 75.61 | 0.07 | 75.52 | 0.08 | 75.3 | 0.07 | 89 | 0.37 | 86.64 | 0.36 | 88.41 | 0.73 | 92.51 | 0.29 | 85.41 | 0.79 | 83.18 | 0.55 | 87.56 | 0.35 | 85.83 | 0.23 | 85 | 0.6 | 85.17 | 0.14 | 86.98 | 0.4 | 89.54 | 0.31 | 85.02 | 0.37 | 85.46 | 0.16 | 85.26 | 0.13 | 77.4 | 0.09 | 75.46 | 0.07 | 75.3 | 0.07 | 76.24 | 0.11 |  |  | 74.89 | 0.07 | 75.58 | 0.09 | 75.32 | 0.09 | 75.09 | 0.08 | 74.98 |  | 74.85 | 0.09 |  |  |  |  | 88.73 | 0.43 | 91.07 | 0.34 | 87.17 | 0.3 | [62 empty] | T2-CAN-55-OER-DM | 74.707 | 0.014 | 62.115 | 0.013 | 63.202 | 0.01 | 60.318 | 0.026 | 94.886 | 0.041 | 75.001 | 0.035 | 2670.6 | 3.3 | 2581.8 | 3.2 | 0.379 | 0.002 | -0.044 | 0.005 | 0.115 | 0.005 | 0.9835 | 0.0024 | 29.199 | 0 | 8657 | 23 | 1530 |  | 0.58782 | 1628.2631 | 13.03 | 0.044 | 1.6654 | 12079.865 | 114.9547 | 1693.6339 | 7208.3597 | 4871.5053 | 0.011923 | 33.9402 | 61.5366 | 14.0972 | 13.2647 | 0.013949 | 38.1601 | 0.0089258 | 27.696 | 0.010483 | 26.5855 | 86.7925 | 70.238 | 26.1781 | 93765.8387 | 73220.8583 | 7127 | 0.25942 | 88936.2892 | 68391.3089 | 10.2733 | 0.1275 | -7.7622 | -25.2558 | 57.8461 | 93765.8387 | 13414.9814 | 4921.7723 | 75429.085 | 93765.8387 | 100%
2 | T2-CAN-55-T1ER-DM | 75T0125 | T2-CAN-55-T1ER-DM | 10% open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 2:20:10 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 0.5 | 3.6 | 0 | [9 empty] | 952 | [38 empty] | Econo 10%-open, tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient,--2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.004 | 0.012 | 62.005 | 0.049 | 54.854 | 0.023 | 50.993 | 0.041 | 74.99 | 0.04 | 72.15 | 0.12 | 73.49 | 0.01 | 0.197 | 0.003 | 1.0018 | 0.0022 | [12 empty] | 460.9 | 2.1 | 460.2 | 2.1 | 459.1 | 2.1 | 3.6 | 0 | 3.2 | 0 | 3.3 | 0 | 1558.4 | 16.7 | 1089.6 | 19.5 | 86.4 | 12.6 | 460 |  | 460 |  | 460 |  | 3.2 |  | 3.1 |  | 3.1 |  | 0.54 | [23 empty] | 0.5 |  | 0 |  | 0 |  | 85 |  | 1595 | [166 empty] | 62.72 | 0.02 | 61.51 | 0.02 | 61.88 | 0.05 | 61.56 | 0.06 | 73.09 | 0.01 | 72.93 | 0.02 | 72.67 | 0.02 | 73.42 | 0.02 | 73.44 | 0.02 | 73.33 | 0.02 | 60.36 | 0.03 | 71.43 | 0.01 | 71.76 | 0.02 | 61.11 | 0.01 | 62.38 | 0.05 | 60.86 | 0.06 | 72.61 | 0.05 | 71.74 | 0.01 | 61.45 | 0.03 | 71.44 | 0.01 | 71.96 | 0.07 | 55.48 | 0.02 | 63.23 | 0.02 | 62.24 | 0.02 | 64.1 | 0.05 | 65.41 | 0.04 | [18 empty] | 73.33 | 0.02 | [38 empty] | 57.72 | 0.04 | 54.09 | 0.32 | 54.29 | 0.28 | 75.51 | 0.04 | 75.33 | 0.05 | 74.96 | 0.06 | 74.82 | 0.12 | 75.91 | 0.04 | 75.85 | 0.03 | 75.56 | 0.05 | 72.32 | 0.06 | 72.46 | 0.05 | 72.75 | 0.04 | 74.28 | 0.04 | 74.24 | 0.04 | 73.85 | 0.04 | 73.15 | 0.04 | 73.45 | 0.04 | 73.96 | 0.04 | 73.76 | 0.05 | 73.73 | 0.04 | 72.62 | 0.04 | 72.62 | 0.06 | 71.99 | 0.11 | 72.87 | 0.04 | 70.68 | 0.06 | 70.53 | 0.04 | 69.41 | 0.05 | 69.46 | 0.06 |  |  | 74.55 | 0.13 | 75.82 | 0.03 | 75.6 | 0.04 | 75.44 | 0.04 | 75.23 |  | 75.16 | 0.05 |  |  |  |  | 74.49 | 0.04 | 73.16 | 0.04 | 72.86 | 0.04 | [62 empty] | Economizer test | 75.004 | 0.012 | 62.005 | 0.049 | 72.978 | 0.008 | 60.771 | 0.045 | 54.854 | 0.023 | 50.993 | 0.041 | 2711.7 | 2.9 | 2594.7 | 2.9 | 0.515 | 0.003 | -0.192 | 0.002 | 0.197 | 0.003 | 1.0018 | 0.0022 | 29.258 | 0.001 | 1645 | 13 | 1510 |  | 0.021141 | 54.8557 | 13.026 | 0.192 | 1.5956 | 12055.1218 | 156.9855 | 54.8558 | 252.6743 | 11802.4475 | 0.0087459 | 27.4689 | 71.3824 | 13.026 | 13.4965 | 0.0070119 | 20.7754 | 0.008783 | 27.6122 | 0.008458 | 26.7627 | 74.583 | 61.7974 | 26.3738
2 | T2-CAN-55-T2ER-DM | 75T0126 | T2-CAN-55-T2ER-DM | 20% open | off | off | 3 turns | unsealed | unsealed |  | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 3:42:08 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 0.8 | 3.6 | 0 | [9 empty] | 953 | 1490 | [37 empty] | . | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.999 | 0.013 | 62.001 | 0.06 | 55.003 | 0.02 | 50.987 | 0.032 | 75.01 | 0.04 | 71.56 | 0.12 | 72.93 | 0.01 | 0.181 | 0.003 | 0.9616 | 0.0019 | [12 empty] | 460.9 | 2.2 | 460.2 | 2.2 | 459 | 2.1 | 3.6 | 0 | 3.1 | 0 | 3.3 | 0 | 1550.7 | 17.9 | 1087.8 | 19.5 | 75.1 | 13.6 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3 |  | 3 |  | 0.53 | [29 empty] | 85 |  | 1575 | [166 empty] | 63.28 | 0.03 | 61.87 | 0.03 | 63.34 | 0.05 | 62.05 | 0.05 | 72.41 | 0.03 | 72.26 | 0.02 | 72.03 | 0.02 | 72.7 | 0.02 | 72.75 | 0.02 | 72.64 | 0.02 | 60.87 | 0.03 | 72.21 | 0.01 | 72.14 | 0.01 | 61.6 | 0.02 | 63.68 | 0.02 | 60.8 | 0.02 | 72.29 | 0.03 | 71.7 | 0.02 | 61.96 | 0.01 | 72.25 | 0.01 | 71.49 | 0.04 | 55.29 | 0.03 | 63.93 | 0.02 | 62.91 | 0.02 | 63.7 | 0.02 | 65.11 | 0.02 | [18 empty] | 72.64 | 0.02 | [38 empty] | 58.2 | 0.04 | 54.38 | 0.38 | 54.56 | 0.3 | 75.5 | 0.04 | 75.41 | 0.04 | 74.98 | 0.04 | 74.91 | 0.07 | 75.91 | 0.04 | 75.87 | 0.03 | 75.6 | 0.03 | 69.44 | 0.07 | 69.48 | 0.07 | 71.21 | 0.04 | 74.01 | 0.04 | 73.02 | 0.05 | 73.17 | 0.04 | 72.85 | 0.05 | 73.66 | 0.03 | 73.81 | 0.03 | 73.81 | 0.04 | 73.7 | 0.03 | 72.73 | 0.03 | 72.91 | 0.07 | 72.99 | 0.04 | 73.17 | 0.03 | 72.26 | 0.06 | 70.52 | 0.04 | 70.19 | 0.05 | 69.76 | 0.09 |  |  | 74.72 | 0.08 | 75.82 | 0.03 | 75.61 | 0.04 | 75.46 | 0.05 | 75.32 |  | 75.17 | 0.04 |  |  |  |  | 74.03 | 0.04 | 73.4 | 0.03 | 72.95 | 0.03 | [62 empty] | Economizer test | 74.999 | 0.013 | 62.001 | 0.06 | 72.295 | 0.005 | 60.389 | 0.05 | 55.003 | 0.02 | 50.987 | 0.032 | 2655.1 | 2.6 | 2543 | 2.6 | 0.482 | 0.003 | -0.168 | 0.002 | 0.181 | 0.003 | 0.9616 | 0.0019 | 29.252 | 0.001 | 1626 | 13 | 1490 |  | 0.054211 | 137.8582 | 13.03 | 0.168 | 1.619 | 11819.242 | 143.9987 | 137.8556 | 634.8153 | 11184.4267 | 0.0086844 | 27.242 | 70.676 | 13.0295 | 13.4785 | 0.0069737 | 20.7702 | 0.0087815 | 27.6094 | 0.0083746 | 26.505 | 73.9284 | 61.4673 | 26.1105
2 | T2-CAN-55-T3ER-DM | 75T0127 | T2-CAN-55-T3ER-DM | 30% open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 5:07:29 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.9 | 0.8 | 3.6 | 0 | 13083 | 23 | 14804 | 312 | 7644 | 135 | 20735 | 142 | 12.7994 | 952 | [38 empty] | Econo 30%-open, tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN-55 | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75 | 0.009 | 61.995 | 0.049 | 54.972 | 0.028 | 51.038 | 0.033 | 74.94 | 0.04 | 69.71 | 0.12 | 71.33 | 0.01 | 0.171 | 0.003 | 0.9366 | 0.0023 | 13083 | 23 | 7644 | 135 | 12.8 | 0.14 | [6 empty] | 460.9 | 2.1 | 460.2 | 2.1 | 459.3 | 2.1 | 3.6 | 0 | 3.1 | 0 | 3.3 | 0 | 1542.8 | 17.6 | 1094.7 | 19.1 | 77.2 | 13.5 | 460 |  | 460 |  | 460 |  | 3 |  | 3.1 |  | 3 |  | 0.52 | [29 empty] | 85 |  | 1575 | [166 empty] | 64.06 | 0.03 | 62.22 | 0.02 | 64.6 | 0.03 | 63.21 | 0.04 | 70.41 | 0.03 | 70.26 | 0.02 | 70.11 | 0.02 | 70.76 | 0.02 | 70.81 | 0.02 | 70.74 | 0.03 | 61.89 | 0.02 | 72.1 | 0.02 | 71.86 | 0.02 | 62.48 | 0.03 | 64.54 | 0.02 | 61.27 | 0.03 | 71.95 | 0.05 | 70.79 | 0.02 | 62.41 | 0.02 | 72.15 | 0.01 | 71.16 | 0.07 | 54.76 | 0.07 | 65.1 | 0.02 | 63.97 | 0.03 | 64.37 | 0.03 | 65.8 | 0.04 | [18 empty] | 70.74 | 0.03 | [38 empty] | 58.99 | 0.03 | 54.25 | 0.3 | 54.49 | 0.27 | 75.44 | 0.04 | 75.34 | 0.03 | 74.98 | 0.03 | 75.27 | 0.09 | 75.87 | 0.03 | 75.78 | 0.04 | 75.56 | 0.03 | 57.56 | 0.07 | 58.62 | 0.06 | 65.72 | 0.08 | 72.22 | 0.06 | 62.61 | 0.15 | 71.24 | 0.07 | 71.88 | 0.05 | 73.64 | 0.04 | 71.28 | 0.08 | 72.67 | 0.04 | 72.06 | 0.05 | 73.21 | 0.04 | 72.55 | 0.06 | 72.97 | 0.03 | 72.68 | 0.04 | 73.43 | 0.05 | 69.02 | 0.04 | 69.22 | 0.04 | 68.95 | 0.09 |  |  | 74.97 | 0.07 | 75.75 | 0.04 | 75.53 | 0.04 | 75.37 | 0.04 | 75.23 |  | 75.09 | 0.04 |  |  |  |  | 65.77 | 0.09 | 72.58 | 0.06 | 72.71 | 0.04 | [62 empty] | Economizer test | 75 | 0.009 | 61.995 | 0.049 | 70.389 | 0.008 | 59.387 | 0.038 | 54.972 | 0.028 | 51.038 | 0.033 | 2616.2 | 3.2 | 2514 | 3.1 | 0.437 | 0.002 | -0.126 | 0.001 | 0.171 | 0.003 | 0.9366 | 0.0023 | 29.253 | 0.001 | 1620 | 13 | 1490 |  | 0.14734 | 370.4221 | 13.029 | 0.126 | 1.6552 | 11689.2272 | 129.066 | 370.4221 | 1705.8351 | 9983.3921 | 0.0085191 | 26.6119 | 68.7338 | 13.029 | 13.4288 | 0.0070081 | 20.7999 | 0.0087773 | 27.605 | 0.0081916 | 25.8407 | 72.0853 | 60.5378 | 25.4374
2 | T2-CAN-55-TCE-DM | 75T0128 | T2-CAN-55-TCE-DM | closed | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 0:26:49 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 3 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 460.7 | 1.1 | 3.6 | 0 | [9 empty] | 952 | 1520 | [37 empty] | Econo closed, tape around damper perimeter frame gaps, no compressor, 55/51 ambient,--2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), 100% inlet/outlet Meriam, adjust code tester speed--to match total static of run T2-CAN-55-TCE-DM-SPWCT-SS | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.988 | 0.019 | 61.997 | 0.047 | 54.941 | 0.02 | 51.16 | 0.046 | 74.98 | 0.04 | 72.34 | 0.12 | 73.7 | 0.01 | 0.211 | 0.005 | 1.012 | 0.0028 |  |  |  |  | 5.577 | 0.063 | [6 empty] | 460.7 | 2.3 | 460.4 | 2.3 | 459 | 2.2 | 3.6 | 0 | 3.1 | 0 | 3.3 | 0 | 1564.9 | 18.1 | 1087 | 20.6 | 87.2 | 13.3 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.1 |  | 3 |  | 0.55 | [29 empty] | 85 |  | 1605 | [166 empty] | 62.01 | 0.03 | 61.18 | 0.02 | 60.5 | 0.05 | 60.34 | 0.03 | 73.37 | 0.03 | 73.23 | 0.02 | 73 | 0.02 | 73.67 | 0.02 | 73.71 | 0.03 | 73.59 | 0.02 | 59.96 | 0.01 | 70.97 | 0.02 | 71.44 | 0.02 | 61.21 | 0.01 | 57.46 | 0.03 | 58.08 | 0.06 | 72.48 | 0.01 | 71.4 | 0.01 | 60.76 | 0.02 | 70.97 | 0.01 | 71.9 | 0.01 | 55.43 | 0.03 | 62.59 | 0.02 | 61.76 | 0.02 | 61.96 | 0.19 | 63.4 | 0.22 | [18 empty] | 73.59 | 0.02 | [38 empty] | 58.84 | 0.02 | 54.21 | 0.41 | 54.38 | 0.33 | 75.46 | 0.04 | 75.29 | 0.05 | 74.95 | 0.06 | 74.72 | 0.09 | 75.84 | 0.04 | 75.8 | 0.04 | 75.51 | 0.05 | 72.85 | 0.05 | 73.15 | 0.05 | 73.29 | 0.05 | 74.39 | 0.03 | 74.44 | 0.04 | 74.13 | 0.04 | 73.27 | 0.04 | 73.3 | 0.05 | 74 | 0.04 | 73.65 | 0.06 | 73.83 | 0.04 | 72.7 | 0.05 | 72.78 | 0.06 | 71.15 | 0.13 | 72.73 | 0.04 | 70.61 | 0.07 | 70.3 | 0.05 | 69.22 | 0.06 | 69.41 | 0.08 |  |  | 74.53 | 0.11 | 75.76 | 0.04 | 75.56 | 0.04 | 75.4 | 0.04 | 75.23 |  | 75.14 | 0.05 |  |  |  |  | 74.6 | 0.04 | 73.17 | 0.03 | 72.99 | 0.04 | [62 empty] | Economizer test | 74.988 | 0.019 | 61.997 | 0.047 | 73.231 | 0.014 | 60.918 | 0.044 | 54.941 | 0.02 | 51.16 | 0.046 | 2725 | 3.8 | 2608.3 | 3.6 | 0.521 | 0.003 | -0.2 | 0.002 | 0.211 | 0.005 | 1.012 | 0.0028 | 29.279 | 0 | 1652 | 13 | 1520 |  | 0.0078316 | 20.4272 | 13.029 | 0.2 | 1.5972 | 12108.2455 | 159.6469 | 20.427 | 94.0701 | 12014.1754 | 0.0087683 | 27.5543 | 71.6338 | 13.0288 | 13.5032 | 0.0070804 | 20.8708 | 0.0087815 | 27.6066 | 0.0084929 | 26.8625 | 74.8327 | 61.9213 | 26.4732
2 | T2-CAN-55-TOER-DM | 75T0129 | T2-CAN-55-TOER-DM | open | off | off | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 6:41:54 | 10 Ton | 0:15:00 | 75/62 55/51 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 55 | 51 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 1.1 | 3.7 | 0 | 40355 | 72 | 39128 | 286 | 22767 | 394 | 63143 | 411 | 36.7752 | 950 | [38 empty] | Econo fully open, tape around damper perimeter inside/outside frame gaps, no compressor, 55/51 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN- | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.017 | 0.02 | 61.991 | 0.083 | 55.041 | 0.044 | 51.007 | 0.094 | 74.7 | 0.09 | 61.86 | 0.06 | 64.04 | 0.02 | 0.2 | 0.003 | 1.0606 | 0.0023 | 40355 | 72 | 22767 | 394 | 36.781 | 0.386 | [6 empty] | 461 | 2.4 | 460.4 | 2.5 | 459 | 2.4 | 3.7 | 0 | 3.2 | 0 | 3.4 | 0 | 1601.9 | 21.5 | 1087.1 | 23.4 | 114.9 | 16.2 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.2 |  | 3.1 |  | 0.55 | [29 empty] | 85 |  | 1655 | [166 empty] | 64.28 | 0.02 | 63.73 | 0.03 | 63.02 | 0.07 | 63.88 | 0.03 | 61.9 | 0.06 | 61.59 | 0.05 | 61.29 | 0.05 | 62.19 | 0.06 | 62.11 | 0.06 | 62.06 | 0.06 | 63.16 | 0.01 | 62.9 | 0.03 | 62.44 | 0.03 | 65.76 | 0.01 | 59.02 | 0.07 | 61.52 | 0.17 | 63.96 | 0.02 | 58.86 | 0.07 | 64.63 | 0.02 | 62.87 | 0.02 | 63.31 | 0.02 | 55.94 | 0.08 | 65.82 | 0.02 | 64.77 | 0.02 | 61.77 | 0.05 | 61.37 | 0.05 | [18 empty] | 62.06 | 0.06 | [38 empty] | 59.91 | 0.08 | 55.7 | 1.04 | 55.96 | 0.78 | 75.39 | 0.09 | 75.26 | 0.09 | 74.98 | 0.08 | 75.82 | 0.07 | 75.82 | 0.08 | 75.74 | 0.09 | 75.52 | 0.09 | 57.77 | 0.33 | 59.94 | 0.34 | 55.78 | 0.42 | 57.27 | 0.28 | 65.52 | 0.22 | 60.62 | 0.4 | 57.19 | 0.14 | 60.52 | 0.12 | 63.38 | 0.16 | 59.63 | 0.19 | 62.25 | 0.15 | 58.97 | 0.18 | 61.63 | 0.11 | 59.82 | 0.16 | 60.05 | 0.19 | 71.56 | 0.12 | 72.47 | 0.09 | 70.21 | 0.1 | 70.03 | 0.04 |  |  | 75.1 | 0.08 | 75.61 | 0.09 | 75.39 | 0.09 | 75.21 | 0.09 | 75.09 |  | 74.93 | 0.09 | 45.52 | 1.17 |  |  | 58.54 | 0.22 | 57.88 | 0.22 | 60.77 | 0.13 | [62 empty] | Economizer test | 75.017 | 0.02 | 61.991 | 0.083 | 61.766 | 0.014 | 54.186 | 0.057 | 55.041 | 0.044 | 51.007 | 0.094 | 2764.7 | 3.1 | 2700.2 | 3 | 0.385 | 0.002 | -0.031 | 0.001 | 0.2 | 0.003 | 1.0606 | 0.0023 | 29.269 | 0.001 | 1717 | 14 | 1570 |  | 0.58125 | 1569.4845 | 13.03 | 0.031 | 1.6382 | 12564.9152 | 122.1298 | 1569.5142 | 7226.9597 | 5337.9555 | 0.0077381 | 23.6789 | 60.1278 | 13.0305 | 13.202 | 0.0069754 | 20.7812 | 0.0087707 | 27.6019 | 0.0071347 | 22.5894 | 63.5434 | 55.9662 | 22.191
2 | T2-CAN-95-T1ER-DM | 75T0143 | T2-CAN-95-T1ER-DM | 10% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 15:28:05 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 1.5 | 15 | 0 | 51701 | 97 | 51903 | 750 | 7918 | 352 | 59627 | 337 | 7.0782 | 953 |  |  | 6.1373 | [35 empty] | Econo 10%-open, tape around damper perimeter inside/outside frame gaps, both stages--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-CAN-95-T | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.993 | 0.056 | 62.001 | 0.032 | 94.902 | 0.011 | 75.006 | 0.012 | 74.89 | 0.26 | 56.99 | 0.05 | 60.09 | 0.03 | 0.205 | 0.003 | 0.9777 | 0.002 | 51701 | 97 | 7918 | 352 | 7.079 | 0.045 | [6 empty] | 460.6 | 2.8 | 460.2 | 2.8 | 459 | 2.8 | 15 | 0.1 | 13 | 0 | 12.6 | 0.1 | 6809.1 | 65 | 3196.2 | 74.3 | 1614.9 | 52.5 | 460 |  | 459 |  | 460 |  | 3.1 |  | 3.1 |  | 3 |  | 0.54 | 460 |  | 459 |  | 460 |  | 4.5 |  | 4.8 |  | 4.4 |  | 3120 |  | 0.85 | 460 | 460 | 459 | 4.9 | 4.5 | 4.4 | 2990 | 0.81 | 459.7 |  | 1.6 |  | 696.5 |  | 85 |  | 8421.5 | [14 empty] | 213 | 0.19 | 105.27 | 0.13 | 105.62 | 0.06 | 0.35 | 0.1 | 240.54 | 0.23 | 171.89 | 0.16 | 114.23 | 0.07 | -57.65 | 0.17 | 207 | 0.05 | 98.82 | 0.06 | 103.64 | 0.05 | 4.83 | 0.05 | 73.89 | 0.08 | 47.48 | 0.37 | 43.35 | 0.05 | 4.13 | 0.38 | 73.32 | 0.08 | 55.09 | 0.31 | 42.98 | 0.05 | 12.11 | 0.31 | [46 empty] | 243.38 | 0.21 | 166.83 | 0.37 | 115.08 | 0.06 | 51.75 | 0.37 | 225.42 | 0.33 | 109.59 | 0.1 | 9.79 | 0.13 | 215 | 0.05 | 98.75 | 0.09 | 106.27 | 0.05 | 7.52 | 0.04 | 77.56 | 0.07 | 45.74 | 0.05 | 2.62 | 0.22 | 77.09 | 0.1 | 55.55 | 0.71 | 45.43 | 0.06 | 10.12 | 0.73 | 104.25 | 0.09 | [28 empty] | 104.64 | 0.09 | 104.25 | 0.09 | 99.85 | 0.09 | 100.18 | 0.08 | 57.37 | 0.06 | 57.01 | 0.05 | 56.51 | 0.05 | 57.48 | 0.03 | 57.09 | 0.07 | 57.15 | 0.04 | 104.79 | 0.08 | 100.27 | 0.07 | 48.49 | 0.59 | 54.86 | 0.4 | 166.63 | 0.35 | 100.32 | 0.09 | 99.07 | 0.09 | 48.75 | 0.08 | 56.89 | 0.98 | 98.82 | 0.06 | 98.75 | 0.09 | 92.95 | 0.03 | 105.33 | 0.08 | 105.27 | 0.09 | 100.58 | 0.06 | 100.09 | 0.14 | 99.85 | 0.09 | 100.18 | 0.08 | [12 empty] | 105.27 | 0.13 | 57.15 | 0.04 |  |  | 99.79 | 0.11 | 104.64 | 0.09 | 104.25 | 0.09 | [16 empty] | 48.37 | 0.2 | [12 empty] | 172.52 | 0.18 | 94.29 | 0.17 | 94.33 | 0.17 | 75.71 | 0.17 | 75.52 | 0.17 | 75.39 | 0.15 | 76.96 | 0.13 | 76.04 | 0.17 | 75.92 | 0.17 | 75.79 | 0.17 | 77.94 | 0.17 | 77.84 | 0.17 | 77.29 | 0.16 | 76.06 | 0.18 | 76.15 | 0.19 | 76.36 | 0.19 | 76.74 | 0.18 | 76.82 | 0.17 | 76.02 | 0.17 | 76.11 | 0.18 | 75.92 | 0.16 | 76.75 | 0.15 | 76.58 | 0.17 | 76.96 | 0.18 | 76.6 | 0.16 | 78.25 | 0.1 | 78.41 | 0.12 | 79.39 | 0.12 | 79.29 | 0.13 |  |  | 75.86 | 0.16 | 76.01 | 0.15 | 75.72 | 0.18 | 75.47 | 0.19 | 75.36 |  | 75.17 | 0.19 |  |  |  |  | 75.9 | 0.19 | 76.7 | 0.14 | 76.62 | 0.16 | [62 empty] | T2-CAN-55-T1ER-DM | 74.993 | 0.056 | 62.001 | 0.032 | 57.164 | 0.02 | 54.35 | 0.024 | 94.902 | 0.011 | 75.006 | 0.012 | 2648.2 | 2.7 | 2594.5 | 2.7 | 0.51 | 0.003 | -0.195 | 0.002 | 0.205 | 0.003 | 0.9777 | 0.002 | 29.193 | 0.001 | 8424 | 24 | 1530 |  | 0.021141 | 54.8557 | 13.026 | 0.192 | 1.6105 | 12134.1043 | 155.4494 | 57.5117 | 244.7714 | 11889.333 | 0.0088872 | 27.8224 | 55.5535 | 14.0977 | 13.0947 | 0.01395 | 38.1647 | 0.0087829 | 27.6095 | 0.0083118 | 22.7491 | 75.3983 | 62.3033 | 22.3567 | 66321.4892 | 57791.6467 | 6894 | 0.35478 | 61630.1479 | 53100.3054 | 7.316 | 0.15917 | -5.4657 | -19.8448 | 51.7968 | 66321.4892 | 58975.7894 | 4762.0835 | 2583.6163 | 66321.4892 | 100%
2 | T2-CAN-95-T2ER-DM | 75T0144 | T2-CAN-95-T2ER-DM | 20% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 13:49:15 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.8 | 1.4 | 15 | 0 | 50215 | 63 | 47935 | 310 | 6330 | 76 | 56550 | 103 | 6.7185 | 952 |  |  | 5.9659 | [35 empty] | Econo 20%-open, tape around damper perimeter inside/outside frame gaps, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm),--unsealed cab, 100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN-95-T | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.002 | 0.013 | 61.998 | 0.012 | 94.907 | 0.007 | 75.003 | 0.013 | 74.2 | 0.12 | 57.4 | 0.04 | 60.32 | 0.02 | 0.205 | 0.003 | 0.947 | 0.0022 | 50215 | 63 | 6330 | 76 | 6.719 | 0.023 | [6 empty] | 460.8 | 2.8 | 460.2 | 2.8 | 459.3 | 2.8 | 15 | 0.1 | 13.1 | 0 | 12.6 | 0.1 | 6791.3 | 68.3 | 3214.6 | 76.3 | 1626 | 56.3 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3 |  | 3 |  | 0.54 | 460 |  | 460 |  | 460 |  | 4.5 |  | 4.8 |  | 4.4 |  | 3120 |  | 0.86 | 460 | 460 | 460 | 4.9 | 4.5 | 4.5 | 2970 | 0.8 | 459.8 |  | 1.6 |  | 696.9 |  | 85 |  | 8371.9 | [14 empty] | 213.23 | 0.2 | 105.35 | 0.12 | 105.7 | 0.06 | 0.35 | 0.09 | 240.64 | 0.24 | 172.02 | 0.11 | 114.27 | 0.07 | -57.75 | 0.1 | 207 | 0.01 | 98.82 | 0.07 | 103.64 | 0.03 | 4.82 | 0.05 | 73.59 | 0.05 | 47.16 | 0.22 | 43.17 | 0.03 | 3.99 | 0.24 | 73.03 | 0.04 | 54.8 | 0.13 | 42.8 | 0.03 | 12 | 0.13 | [46 empty] | 244.24 | 0.23 | 166.25 | 0.1 | 115.34 | 0.07 | 50.91 | 0.11 | 225.07 | 0.31 | 109.49 | 0.1 | 9.18 | 0.09 | 214 |  | 99.23 | 0.1 | 105.95 |  | 6.71 |  | 79.67 | 0.04 | 47.08 | 0.03 | 2.51 | 0.15 | 79.04 | 0.04 | 56.71 | 0.23 | 46.69 | 0.03 | 10.02 | 0.23 | 104.3 | 0.1 | [28 empty] | 104.71 | 0.09 | 104.3 | 0.1 | 100.34 | 0.09 | 100.68 | 0.08 | 57.6 | 0.03 | 57.23 | 0.03 | 56.71 | 0.03 | 57.65 | 0.03 | 57.39 | 0.05 | 57.3 | 0.03 | 104.83 | 0.09 | 100.2 | 0.08 | 48.12 | 0.43 | 54.46 | 0.19 | 165.86 | 0.12 | 100.73 | 0.09 | 99.53 | 0.09 | 49.85 | 0.08 | 58.18 | 0.33 | 98.82 | 0.07 | 99.23 | 0.1 | 93.17 | 0.04 | 105.36 | 0.08 | 105.18 | 0.14 | 100.82 | 0.08 | 100.61 | 0.08 | 100.34 | 0.09 | 100.68 | 0.08 | [14 empty] | 57.3 | 0.03 |  |  | 100.31 | 0.1 | 104.71 | 0.09 | 104.3 | 0.1 | [16 empty] | 49.59 | 0.14 | [12 empty] | 172.58 | 0.11 | 94.38 | 0.18 | 94.44 | 0.17 | 75.1 | 0.1 | 74.93 | 0.1 | 74.77 | 0.09 | 76.26 | 0.09 | 75.44 | 0.09 | 75.37 | 0.08 | 75.21 | 0.08 | 80.45 | 0.11 | 80.53 | 0.12 | 78.63 | 0.08 | 75.64 | 0.09 | 77.31 | 0.1 | 76.45 | 0.09 | 76.57 | 0.09 | 76.13 | 0.09 | 75.69 | 0.08 | 75.55 | 0.08 | 75.36 | 0.08 | 76.15 | 0.08 | 75.7 | 0.09 | 75.92 | 0.09 | 75.77 | 0.09 | 76.72 | 0.06 | 78.02 | 0.06 | 78.45 | 0.07 | 79.04 | 0.1 |  |  | 75.12 | 0.09 | 75.39 | 0.1 | 75.12 | 0.1 | 74.88 | 0.1 | 74.78 |  | 74.54 | 0.09 |  |  |  |  | 75.9 | 0.1 | 76.01 | 0.07 | 76.03 | 0.08 | [62 empty] | T2-CAN-55-T2ER-DM | 75.002 | 0.013 | 61.998 | 0.012 | 57.4 | 0.007 | 54.638 | 0.009 | 94.907 | 0.007 | 75.003 | 0.013 | 2604.4 | 3 | 2554.4 | 3 | 0.466 | 0.002 | -0.169 | 0.002 | 0.205 | 0.003 | 0.947 | 0.0022 | 29.243 | 0.001 | 8417 | 23 | 1500 |  | 0.054211 | 137.8582 | 13.03 | 0.168 | 1.6212 | 11927.1971 | 139.8427 | 143.8216 | 612.1041 | 11315.093 | 0.009044 | 28.1488 | 55.7788 | 14.0978 | 13.1015 | 0.013946 | 38.1617 | 0.0087788 | 27.6072 | 0.0084201 | 22.9243 | 76.0326 | 62.7634 | 22.5291 | 67027.146 | 57977.286 | 6917 | 0.35221 | 62384.9292 | 53335.0692 | 7.4118 | 0.15256 | -5.6197 | -20.2539 | 52.1325 | 67027.146 | 55853.5276 | 4713.1479 | 6460.4705 | 67027.146 | 100%
2 | T2-CAN-95-T3ER-DM | 75T0145 | T2-CAN-95-T3ER-DM | 30% open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 11:58:22 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.6 | 1.5 | 15 | 0 | 45515 | 86 | 44027 | 392 | 1343 | 155 | 46860 | 175 | 5.5607 | 953 |  |  | 5.4011 | [35 empty] | Econo 30%-open, tape around damper perimeter inside/outside frame gaps, both stages--95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab, 100% inlet/outlet Meriam,--adjust code tester speed to match total static of run T2-CAN-95-T | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.982 | 0.028 | 61.991 | 0.027 | 94.893 | 0.021 | 75.01 | 0.024 | 74.36 | 0.14 | 58.54 | 0.05 | 61.49 | 0.02 | 0.178 | 0.004 | 0.9083 | 0.0024 | 45515 | 86 | 1343 | 155 | 5.561 | 0.026 | [6 empty] | 460.6 | 2.6 | 460.2 | 2.6 | 459.3 | 2.5 | 15 | 0.1 | 13 | 0 | 12.6 | 0.1 | 6792.8 | 67.2 | 3216.8 | 71.3 | 1634.2 | 55.8 | 460 |  | 460 |  | 459 |  | 3 |  | 3 |  | 3 |  | 0.53 | 460 |  | 459 |  | 459 |  | 4.5 |  | 4.8 |  | 4.4 |  | 3100 |  | 0.85 | 459 | 459 | 459 | 4.9 | 4.6 | 4.4 | 3020 | 0.82 | 459.7 |  | 1.6 |  | 697.6 |  | 85 |  | 8412.6 | [14 empty] | 213.61 | 0.24 | 105.63 | 0.13 | 105.83 | 0.08 | 0.21 | 0.09 | 241.51 | 0.27 | 171.66 | 0.1 | 114.54 | 0.08 | -57.12 | 0.13 | 208 | 0.07 | 98.53 | 0.07 | 103.98 | 0.06 | 5.46 | 0.04 | 74.1 | 0.05 | 47.15 | 0.15 | 43.52 | 0.03 | 3.63 | 0.15 | 73.55 | 0.05 | 54.81 | 0.21 | 43.16 | 0.03 | 11.65 | 0.2 | [46 empty] | 246.12 | 0.25 | 164.62 | 0.16 | 115.91 | 0.07 | 48.71 | 0.17 | 224.28 | 0.33 | 109.25 | 0.1 | 8.22 | 0.25 | 213 | 0.2 | 100.45 | 0.15 | 105.6 | 0.05 | 5.18 | 0.06 | 83.6 | 0.04 | 49.53 | 0.02 | 3.17 | 0.32 | 83.09 | 0.04 | 59.06 | 0.24 | 49.22 | 0.03 | 9.84 | 0.24 | 104.42 | 0.1 | [28 empty] | 104.83 | 0.1 | 104.42 | 0.1 | 101.47 | 0.13 | 101.85 | 0.12 | 58.8 | 0.03 | 58.48 | 0.03 | 57.97 | 0.05 | 58.83 | 0.03 | 58.52 | 0.05 | 58.5 | 0.03 | 104.94 | 0.09 | 100 | 0.08 | 47.96 | 0.28 | 54.38 | 0.27 | 164.12 | 0.13 | 101.92 | 0.12 | 100.77 | 0.12 | 52.58 | 0.15 | 60.89 | 0.32 | 98.53 | 0.07 | 100.45 | 0.12 | 93.39 | 0.05 | 105.51 | 0.09 | 105.42 | 0.09 | 101.98 | 0.08 | 101.63 | 0.07 | 101.47 | 0.13 | 101.85 | 0.12 | [12 empty] | 105.63 | 0.13 | 58.5 | 0.03 |  |  | 101.02 | 0.23 | 104.83 | 0.1 | 104.42 | 0.1 | [16 empty] | 52.7 | 0.32 | [12 empty] | 172.15 | 0.13 | 94.46 | 0.2 | 94.56 | 0.2 | 75.15 | 0.09 | 74.95 | 0.08 | 74.77 | 0.08 | 75.91 | 0.07 | 75.46 | 0.09 | 75.38 | 0.08 | 75.2 | 0.08 | 90.88 | 0.21 | 88.16 | 0.17 | 83.75 | 0.16 | 77.92 | 0.1 | 88.19 | 0.18 | 77.88 | 0.1 | 77.33 | 0.1 | 76.19 | 0.09 | 78.45 | 0.1 | 76.73 | 0.09 | 77.78 | 0.12 | 76.26 | 0.08 | 76.12 | 0.09 | 76.09 | 0.08 | 76.46 | 0.08 | 75.34 | 0.08 | 79.23 | 0.07 | 79.23 | 0.06 | 79.84 | 0.12 |  |  | 74.94 | 0.08 | 75.43 | 0.09 | 75.15 | 0.09 | 74.91 | 0.09 | 74.81 |  | 74.6 | 0.09 |  |  |  |  | 84.57 | 0.12 | 77.52 | 0.1 | 76.75 | 0.09 | [62 empty] | T2-CAN-55-T3ER-DM | 74.982 | 0.028 | 61.991 | 0.027 | 58.633 | 0.014 | 55.813 | 0.019 | 94.893 | 0.021 | 75.01 | 0.024 | 2551.8 | 3.3 | 2498.5 | 3.2 | 0.421 | 0.002 | -0.123 | 0.003 | 0.178 | 0.004 | 0.9083 | 0.0024 | 29.278 | 0.001 | 8427 | 22 | 1510 |  | 0.14734 | 370.4221 | 13.029 | 0.126 | 1.691 | 11655.822 | 123.5738 | 380.6969 | 1620.2767 | 10035.5453 | 0.0094985 | 29.0712 | 56.942 | 14.0975 | 13.1358 | 0.013955 | 38.1687 | 0.0087789 | 27.6024 | 0.0088077 | 23.6462 | 77.7723 | 64.0385 | 23.2337 | 68040.9418 | 58270.5884 | 6917 | 0.34696 | 63309.0693 | 53538.7159 | 7.5126 | 0.14819 | -5.8375 | -20.8303 | 53.3181 | 68040.9418 | 46113.0346 | 4807.5658 | 17120.3414 | 68040.9418 | 100%
2 | T2-CAN-95-TCE-DM | 75T0146 | T2-CAN-95-TCE-DM | closed | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 16:42:46 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 4 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 461 | 1.5 | 15 | 0 | 52104 | 97 | 53279 | 701 | 8612 | 180 | 60724 | 183 | 7.205 | 952 |  |  | 6.1822 | [35 empty] | Econo closed, tape around damper perimeter frame gaps, both stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley,--3 turns (939 rpm), 100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN-95-TCE-DM-SPWCT-SS | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 75.003 | 0.018 | 61.999 | 0.024 | 94.911 | 0.013 | 74.998 | 0.018 | 75.12 | 0.22 | 56.79 | 0.07 | 60.01 | 0.03 | 0.196 | 0.004 | 0.9824 | 0.0032 | 52104 | 97 | 8612 | 180 | 7.205 | 0.031 | [6 empty] | 461 | 2.8 | 460.5 | 2.8 | 459.3 | 2.8 | 15 | 0.1 | 13 | 0 | 12.6 | 0.1 | 6820.2 | 64.2 | 3197.4 | 72.7 | 1607.8 | 50.4 | 460 |  | 460 |  | 460 |  | 3.1 |  | 3.1 |  | 3.2 |  | 0.53 | 460 |  | 460 |  | 460 |  | 4.5 |  | 4.8 |  | 4.4 |  | 3110 |  | 0.86 | 460 | 460 | 460 | 4.9 | 4.5 | 4.4 | 2960 | 0.81 | 460 |  | 1.6 |  | 696.6 |  | 85 |  | 8276.6 | [14 empty] | 213.09 | 0.2 | 105.28 | 0.13 | 105.64 | 0.06 | 0.37 | 0.1 | 240.67 | 0.23 | 171.81 | 0.13 | 114.27 | 0.07 | -57.54 | 0.15 | 207 |  | 98.88 | 0.06 | 103.64 |  | 4.76 |  | 74.11 | 0.06 | 47.59 | 0.37 | 43.49 | 0.04 | 4.1 | 0.37 | 73.54 | 0.05 | 55.15 | 0.28 | 43.11 | 0.04 | 12.03 | 0.27 | [46 empty] | 243.2 | 0.23 | 167.3 | 0.29 | 115.03 | 0.07 | 52.28 | 0.3 | 225.54 | 0.33 | 109.63 | 0.1 | 10.29 | 0.12 | 214 |  | 98.8 | 0.1 | 105.95 |  | 7.14 |  | 77.13 | 0.07 | 45.46 | 0.05 | 2.47 | 0.23 | 76.53 | 0.09 | 55.25 | 0.65 | 45.06 | 0.06 | 10.19 | 0.67 | 104.24 | 0.09 | [28 empty] | 104.64 | 0.09 | 104.24 | 0.09 | 99.82 | 0.1 | 100.1 | 0.09 | 57.25 | 0.04 | 56.87 | 0.04 | 56.43 | 0.04 | 57.39 | 0.05 | 56.86 | 0.1 | 57.07 | 0.05 | 104.84 | 0.08 | 100.22 | 0.08 | 48.66 | 0.58 | 55.04 | 0.35 | 166.89 | 0.29 | 100.26 | 0.1 | 99.11 | 0.09 | 48.45 | 0.1 | 56.54 | 0.94 | 98.88 | 0.06 | 98.8 | 0.1 | 92.91 | 0.04 | 105.29 | 0.08 | 105.17 | 0.12 | 100.39 | 0.07 | 99.83 | 0.19 | 99.82 | 0.1 | 100.1 | 0.09 | [14 empty] | 57.07 | 0.05 |  |  | 99.34 | 0.12 | 104.64 | 0.09 | 104.24 | 0.09 | [16 empty] | 47.93 | 0.21 | [12 empty] | 172.47 | 0.15 | 94.25 | 0.17 | 94.29 | 0.18 | 75.88 | 0.13 | 75.76 | 0.13 | 75.57 | 0.12 | 77.15 | 0.11 | 76.23 | 0.13 | 76.16 | 0.13 | 76.04 | 0.13 | 77.59 | 0.12 | 77.49 | 0.12 | 76.96 | 0.13 | 76.14 | 0.13 | 76.11 | 0.15 | 76.29 | 0.14 | 76.84 | 0.13 | 77.12 | 0.13 | 76.18 | 0.13 | 76.37 | 0.14 | 76.06 | 0.12 | 76.98 | 0.12 | 76.93 | 0.13 | 77.75 | 0.15 | 76.87 | 0.12 | 78.59 | 0.07 | 78.82 | 0.08 | 79.89 | 0.09 | 79.57 | 0.09 |  |  | 76.06 | 0.13 | 76.18 | 0.11 | 75.88 | 0.13 | 75.63 | 0.14 | 75.53 |  | 75.39 | 0.13 |  |  |  |  | 76.01 | 0.14 | 76.91 | 0.11 | 76.81 | 0.12 | [62 empty] | T2-CAN-55-TCE-DM | 75.003 | 0.018 | 61.999 | 0.024 | 57.078 | 0.012 | 54.222 | 0.02 | 94.911 | 0.013 | 74.998 | 0.018 | 2655.6 | 4.3 | 2600 | 4.2 | 0.525 | 0.003 | -0.202 | 0.002 | 0.196 | 0.004 | 0.9824 | 0.0032 | 29.167 | 0.001 | 8428 | 23 | 1510 |  | 0.0078316 | 20.4272 | 13.029 | 0.2 | 1.5766 | 12170.4149 | 160.3606 | 21.3545 | 90.8842 | 12079.5307 | 0.0088178 | 27.6866 | 55.5014 | 14.0978 | 13.0921 | 0.01394 | 38.1568 | 0.0087793 | 27.6079 | 0.0082595 | 22.6714 | 75.1531 | 62.1111 | 22.2872 | 65713.4035 | 57400.3809 | 6918 | 0.3593 | 61107.0844 | 52794.0618 | 7.2505 | 0.1648 | -5.3994 | -19.6516 | 51.6239 | 65713.4035 | 60079.3401 | 4675.3338 | 958.7296 | 65713.4035 | 100%
2 | T2-CAN-95-TOER-DM | 75T0147 | T2-CAN-95-TOER-DM | open | on | on | 3 turns | unsealed | unsealed | 939 | 5.75 |  | 0 | 0 | CUST 6 | 8/7/2014 | 10:15:20 | 10 Ton | 0:15:00 | 75/62 95/75 | ENG 1 | TECH 2 | RTU2 | RTU2 | 7.5 | R22 | PSC Air Handler | CK1- 6.40 lbs/CK2- 6.20 | 460/460/3 | TU4 | AHRI 340/360 | 75 | 62 | 95 | 75 | 6.4 | 6.2 | 6.4 | 6.2 | 460.2 | 1.5 | 14.9 | 0 | 31615 | 46 | 31917 | 315 | 0 | 0 | 31593 | 45 | 3.7064 | 953 |  |  | 3.7089 | [35 empty] | Econo fully open, tape around damper perimeter inside/outside frame gaps, both--stages, 95/75 ambient, 2 HP fan motor, 5.75" pulley, 3 turns (939 rpm), unsealed cab,--100% inlet/outlet Meriam, adjust code tester speed to match total static of run T2-CAN-9 | Installed:SG:FD:LSV on 2 circuits: Unsealed cab: dampers on S/R: AX35 belt: 5.75 BP: ID Blw 2 HP GE: Mtr Pulley 3 T/O: With econo: Supply Meriam @100% Return Meriam @100%: Horiz Air Disch: Max Mtr Amp 3.6 | 74.999 | 0.008 | 62.066 | 0.012 | 94.931 | 0.016 | 74.696 | 0.008 | 74.72 | 0.1 | 63.4 | 0.07 | 65.65 | 0.01 | 0.184 | 0.003 | 0.9854 | 0.0021 | 31615 | 46 | 0 | 0 | 3.706 | 0.011 | [6 empty] | 460.2 | 2.5 | 460 | 2.5 | 459.8 | 2.5 | 14.9 | 0.1 | 13.1 | 0 | 12.8 | 0.1 | 6784.7 | 66.6 | 3268.8 | 71.7 | 1739.6 | 55.7 | 460 |  | 459 |  | 459 |  | 3.1 |  | 3.1 |  | 3.1 |  | 0.54 | 460 |  | 460 |  | 459 |  | 4.5 |  | 4.9 |  | 4.5 |  | 3130 |  | 0.86 | 460 | 459 | 459 | 4.9 | 4.6 | 4.5 | 3000 | 0.82 | 459.2 |  | 1.6 |  | 697.2 |  | 85 |  | 8422.2 | [14 empty] | 211.82 | 0.21 | 105.18 | 0.09 | 105.25 | 0.07 | 0.07 | 0.05 | 246.97 | 0.23 | 172.92 | 0.1 | 116.16 | 0.07 | 56.76 | 0.1 | 203 | 0.06 | 97.66 | 0.07 | 102.31 | 0.06 | 4.65 | 0.05 | 84.69 | 0.07 | 61.73 | 0.38 | 50.19 | 0.04 | 11.54 | 0.39 | 84.04 | 0.06 | 65.06 | 0.16 | 49.8 | 0.04 | 15.26 | 0.16 | [46 empty] | 249.73 | 0.24 | 164.27 | 0.2 | 116.97 | 0.07 | 47.3 | 0.2 | 224.19 | 0.33 | 109.22 | 0.1 | 7.28 | 0.11 | 212 | 0.1 | 100.97 | 0.12 | 105.3 |  | 4.33 |  | 90.92 | 0.07 | 53.87 | 0.04 | 7.77 | 0.84 | 90.39 | 0.06 | 64.66 | 0.38 | 53.56 | 0.03 | 11.1 | 0.37 | 103.24 | 0.09 | [28 empty] | 103.76 | 0.08 | 103.24 | 0.09 | 101.77 | 0.12 | 102.17 | 0.11 | 63.85 | 0.03 | 63.57 | 0.03 | 63.17 | 0.03 | 64.01 | 0.04 | 63.78 | 0.05 | 63.79 | 0.03 | 104.03 | 0.07 | 99.1 | 0.07 | 62.55 | 0.37 | 65.37 | 0.18 | 163.78 | 0.22 | 102.2 | 0.12 | 101.39 | 0.12 | 60.77 | 1.34 | 66.71 | 0.39 | 97.66 | 0.07 | 100.97 | 0.12 | 87.44 | 0.2 | 104.52 | 0.09 | 104.46 | 0.08 | 102.18 | 0.08 | 101.83 | 0.08 | 101.77 | 0.12 | 102.17 | 0.11 | [12 empty] | 105.18 | 0.09 | 63.79 | 0.03 |  |  | 101.95 | 0.12 | 103.76 | 0.08 | 103.24 | 0.09 | [16 empty] | 61.62 | 0.87 | [12 empty] | 173.47 | 0.12 | 94.54 | 0.2 | 95.1 | 0.19 | 75.33 | 0.06 | 75.16 | 0.06 | 74.92 | 0.05 | 75.72 | 0.05 | 75.69 | 0.05 | 75.63 | 0.05 | 75.42 | 0.05 | 90.38 | 0.32 | 88.79 | 0.36 | 90.73 | 0.39 | 88.47 | 0.32 | 83.39 | 0.35 | 85.22 | 0.43 | 89.32 | 0.18 | 87.29 | 0.14 | 84.53 | 0.26 | 86.9 | 0.2 | 85.77 | 0.23 | 87.31 | 0.24 | 85.29 | 0.16 | 87.16 | 0.2 | 86.53 | 0.19 | 77.32 | 0.09 | 76.28 | 0.07 | 78.43 | 0.12 | 78.5 | 0.04 |  |  | 75.03 | 0.05 | 75.55 | 0.07 | 75.35 | 0.06 | 75.15 | 0.06 | 75.02 |  | 74.82 | 0.07 |  |  |  |  | 88.96 | 0.35 | 88.27 | 0.29 | 86.72 | 0.21 | [62 empty] | T2-CAN-55-TOER-DM | 74.999 | 0.008 | 62.066 | 0.012 | 63.786 | 0.011 | 60.93 | 0.016 | 94.931 | 0.016 | 74.696 | 0.008 | 2670.6 | 2.9 | 2586.3 | 2.8 | 0.365 | 0.002 | -0.036 | 0.004 | 0.184 | 0.003 | 0.9854 | 0.0021 | 29.281 | 0 | 8524 | 22 | 1510 |  | 0.58125 | 1569.4845 | 13.03 | 0.031 | 1.6487 | 12064.5604 | 110.9014 | 1759.1575 | 7487.8473 | 4576.7131 | 0.011833 | 33.9926 | 62.1373 | 14.0961 | 13.2815 | 0.013672 | 37.8655 | 0.0088244 | 27.6563 | 0.01074 | 27.0074 | 87.4109 | 70.3104 | 26.6039 | 89141.9433 | 73179.6138 | 7014 | 0.26855 | 84366.8197 | 68404.4902 | 9.8976 | 0.12008 | -7.3887 | -25.2736 | 58.6884 | 89141.9433 | 7828.5679 | 4868.5694 | 76444.806 | 89141.9433 | 100%
Note on XM147: Zhang, Zhiqin: Blank replaced with 400
Note on XC344: Zhang, Zhiqin: For RTU3, C8-55-OE3, the return static pressure -0.487 is obviously too high for an open economizer, leading to unreasonable OA correction.
Note on XC398: Zhang, Zhiqin: Revised from -0.079 to -0.15
Note on XC541: Zhang, Zhiqin: Static pressure is changed to -0.044 based on T2-CAN-95-OER-DM from -0.01