## TOC
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Table of Contents
Worksheet | Explanation
TOC | Table of Contents -- this worksheet.
Summary | Overview of impact evaluation findings for specific sampled applications, and in the aggregate. Shows running total of findings.
Methodology | Description of steps taken for each sampled application in the impact evaluation process.
AC Tuneup + Tstat Eq Rev | Review of values used in annual energy savings calculations for AC tune-up and programmable thermostat measures. Shows research and draft findings to date.
Refrig Tuneup Eq Rev | Review of values used in annual energy savings calculations for refrigeration tune-up measure. Shows research and draft findings to date.
Ltg Fixt kW Variances | Listing of lighting fixtures where kW values disagree between ASW, RLW, and/or SPC. Includes recommended values for impact evaluation (draft). Also includes fixture-specific analyses of inferred SPC kW's for efficient magnetic ballasts (of use in evaluating ASW- and RLW-inferred fixture kW data).
EIG Fixture kW Issues | Mapping of ASW/EIG fixture types and wattages to SPC corresponding information.
[Various numbers] | Step by step calculation of impact evaluation conducted for each sampled application. Worksheet numbers pertain to the customer [application ID] record.
Cust Size | Analysis of sampled customer sizes. Includes S&A "sanity check" assessment.
CFL Issue | Quantifies the portion of gross lighting annual kWh savings that pertain to CFLs.

## Summary
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Summary of Findings
Gross Annual kWh Savings
Customer ID | Completed date sample bin | Nominal Reporting Tranche | Step 1 "Measure Status" TBL Value | Step 1 "Details" TBL Value | Step 1 Paperwork | Step 2 | Step 3 | Step 4 | Step 5 | Ratio | Primary Factor (ratio <.95 or >1.05) | Weight | Error | Variance
23079 | 2002-10-01 | Interim Rpt #1 | 2402 | 2402 | 2402 | 2402.4 | 2631.2 | 2686.2528 | 2686.2528 | 1.1183 | fixture kW value | 6.087 | 369.5661 | 4229045.6525
23086 | 2002-10-01 | Interim Rpt #1 | 3034 | 3034 | 3034 | 3033.888 | 3125.824 | 3134.2397 | 3134.2397 | 1.033 |  | 6.087 | 208.0001 | 1339630.7755
16023 | 2002-11-01 | Interim Rpt #1 | 1533 | 1693 | 1697 | 1690.624 | 1743.872 | 1748.567 | 1748.567 | 1.1406 | fixture kW value | 6.087 | 270.0155 | 2257540.9724
17041 | 2002-12-01 | Interim Rpt #1 | 2995 | 1747 | 2995 | 2995.2 | 1913.6 | 1918.752 | 1918.752 | 0.64065 | fixture kW value (error correction) | 6.087 | -969.8728 | 29126466.2094
23173 | 2002-12-01 | Interim Rpt #1 | 16628 | 15822 | 15826 | 15826.5763 | 5940.801 | 6474.5874 | 6474.5874 | 0.38938 | refrig. tune-up constants | 6.087 | -9562.8261 | 2831592417.051
23271 | 2002-12-01 | Interim Rpt #1 | 15215 | 15215 | 15215 | 15214.628 | 13037.128 | 12486.9043 | 12486.9043 | 0.8207 | fixtures dropped; op hours | 6.087 | -2187.6955 | 148194464.5432
19058 | 2003-01-01 | Interim Rpt #1 | 2113 | 2194 | 2113 | 2112.7392 | 2663.0799 | 2483.5391 | 2483.5391 | 1.1754 | tstat constants | 6.087 | 445.5878 | 6147872.1857
23525 | 2003-01-01 | Interim Rpt #1 | 23374 | 23375 | 23374 | 23374.26 | 25509.12 | 25577.7984 | 25577.7984 | 1.0943 | fixture kW value | 6.087 | 3033.9866 | 285026695.6195
16090 | 2003-02-01 | Interim Rpt #1 | 6956 | 6956 | 6956 | 6956.04 | 7618.52 | 7639.0314 | 7639.0314 | 1.0982 | fixture kW value | 6.087 | 930.0918 | 26786120.9576
17044 | 2003-02-01 | Interim Rpt #1 | 1262 | 1262 | 1262 | 1262.56 | 1706.5425 | 1708.9155 | 1708.9155 | 1.3541 | AC tuneup constants | 6.087 | 491.7387 | 7487330.5014
22110 | 2003-02-01 | Interim Rpt #1 | 4093 | 4903 | 4093 | 4092.816 | 3642.912 | 3652.7198 | 3652.7198 | 0.89243 | fixture type correction | 6.087 | -294.9067 | 2692944.3545
23581 | 2003-02-01 | Interim Rpt #1 | 4004 | 3993 | 4004 | 3993.08 | 4000.36 | 4011.1302 | 4011.1302 | 1.0018 |  | 6.087 | 149.3426 | 690598.8563
23587 | 2003-02-01 | Interim Rpt #1 | 5127 | 5119 | 5127 | 5113.264 | 5246.488 | 4743.1758 | 4743.1758 | 0.92514 | op hours | 6.087 | -201.7255 | 1260027.0275
11040 | 2003-03-01 | Interim Rpt #1 | 9935 | 9915 | 9935 | 9934.704 | 10296.624 | 11268.4968 | 11268.4968 | 1.1342 | op hours; fixture kW value | 6.087 | 1686.3641 | 88056396.2049
16085 | 2003-03-01 | Interim Rpt #1 | 2523 | 2523 | 2523 | 2522.52 | 2762.76 | 2896.1163 | 2896.1163 | 1.1479 | fixture kW value | 6.087 | 462.7272 | 6629919.456
23711 | 2003-03-01 | Interim Rpt #1 | 13296 | 13296 | 13296 | 13296.192 | 13339.872 | 16560.4982 | 16560.4982 | 1.2455 | op hours | 6.087 | 3736.7401 | 432358517.7938
23752 | 2003-03-01 | Interim Rpt #1 | 16363 | 16298 | 16363 | 16365.07 | 10006.2832 | 10364.7437 | 10364.7437 | 0.63343 | refrig. tune-up constants | 6.087 | -5417.082 | 908634117.596
23755 | 2003-03-01 | Interim Rpt #1 | 15200 | 15205 | 15200 | 15200.38 | 16069.82 | 17469.9763 | 17469.9763 | 1.1493 | op hours; fixture kW value | 6.087 | 2809.8437 | 244468290.5455
16107 | 2003-04-01 | Interim Rpt #1 | 1579 | 1579 | 1579 | 1579.032 | 1713.348 | 1799.7685 | 1799.7685 | 1.1398 | op hours; fixture kW value | 6.087 | 276.8508 | 2373284.3857
17029 | 2003-04-01 | Interim Rpt #1 | 3894 | 4380 | 3894 | 3893.76 | 3926.208 | 4428.8759 | 4428.8759 | 1.1374 | op hours | 6.087 | 673.1814 | 14032091.8085
17048 | 2003-04-01 | Interim Rpt #1 | 2970 | 2953 | 2970 | 2970.24 | 3139.968 | 2951.6454 | 2951.6454 | 0.99382 |  | 6.087 | 87.1326 | 235082.3593
20180 | 2003-04-01 | Interim Rpt #1 | 1949 | 1949 | 1949 | 1949.09 | 1732.4092 | 1732.4092 | 1732.4092 | 0.88887 | AC tuneup constants | 6.087 | -147.367 | 672447.678
23652 | 2003-04-01 | Interim Rpt #1 | 10940 | 11198 | 10490 | 10940.384 | 11905.712 | 11937.7658 | 11937.7658 | 1.0912 | fixture kW value | 6.087 | 1386.3283 | 59510061.3584
23766 | 2003-04-01 | Interim Rpt #1 | 38351 | 38342 | 38351 | 38351.04 | 38001.6 | 36516.249 | 36516.249 | 0.95216 |  | 6.087 | -472.6158 | 6916315.2621
23789 | 2003-04-01 | Interim Rpt #1 | 32376 | 32376 | 32376 | 32375.616 | 34688.16 | 14492.313 | 14492.313 | 0.44763 | op hours | 6.087 | -16733.7695 | 8670532850.5985
23797 | 2003-04-01 | Interim Rpt #1 | 21128 | 21128 | 21128 | 21128.016 | 22789.312 | 23021.4785 | 23021.4785 | 1.0896 | op hours | 6.087 | 2643.8942 | 216444400.4528
17052 | 2003-05-01 | Interim Rpt #1 | 4156 | 3703 | 4156 | 4389.4519 | 3174.5622 | 3059.5627 | 3059.5627 | 0.73618 | refrig. tune-up constants | 6.087 | -948.8262 | 27876072.7372
22093 | 2003-05-01 | Interim Rpt #1 | 3713 | 3692 | 3713 | 3712.8 | 3924.96 | 3935.5272 | 3935.5272 | 1.0599 | fixture kW value | 6.087 | 354.404 | 3889157.2049
23767 | 2003-05-01 | Interim Rpt #1 | 14640 | 14378 | 14640 | 14639.664 | 14634.984 | 14072.1689 | 14072.1689 | 0.96121 |  | 6.087 | -47.8536 | 70906.6681
23817 | 2003-05-01 | Interim Rpt #1 | 7362 | 7362 | 7362 | 7361.536 | 7827.456 | 7848.5299 | 7848.5299 | 1.0661 | fixture kW value | 6.087 | 748.0104 | 17325011.5027
23818 | 2003-05-01 | Interim Rpt #1 | 5137 | 5105 | 5422 | 5422.144 | 5136.768 | 5150.5978 | 5150.5978 | 1.0026 |  | 6.087 | 196.0516 | 1190142.958
14023 | 2003-06-01 | Interim Rpt #1 | 3774 | 3769 | 3774 | 3773.952 | 3966.144 | 3976.8221 | 3976.8221 | 1.0537 |  | 6.087 | 336.8655 | 3513752.9228
17054 | 2003-06-01 | Interim Rpt #1 | 6238 | 6205 | 6238 | 6237.504 | 6683.04 | 6701.0328 | 6701.0328 | 1.0742 | fixture kW value | 6.087 | 684.5915 | 14511799.7399
17072 | 2003-06-01 | Interim Rpt #1 | 20049 | 20049 | 20049 | 20049.12 | 20049.12 | 22097.4534 | 22097.4534 | 1.1022 | op hours | 6.087 | 2760.5456 | 235965263.0359
23478 | 2003-06-01 | Interim Rpt #1 | 13123 | 11721 | 13123 | 13122.72 | 13322.4 | 12245.079 | 12245.079 | 0.9331 | op hours | 6.087 | -411.8236 | 5251468.7212
23847 | 2003-06-01 | Interim Rpt #1 | 20177 | 20132 | 20177 | 20177.248 | 20905.976 | 26490.7698 | 26490.7698 | 1.3129 | op hours | 6.087 | 7030.4082 | 1530450595.0599
23849 | 2003-06-01 | Interim Rpt #1 | 81302 | 81302 | 81302 | 81301.584 | 85357.636 | 89477.4019 | 89477.4019 | 1.1006 | op hours; fixture kW value | 6.087 | 11063.0531 | 3789729553.3085
17058 | 2003-07-01 | Interim Rpt #2 | 1245 | 1238 | 1245 | 1244.88 | 1316.016 | 1319.5591 | 1319.5591 | 1.0599 | fixture kW value | 6.087 | 118.7785 | 436851.7258
23836 | 2003-07-01 | Interim Rpt #2 | 131201 | 127565 | 131201 | 131200.7162 | 128803.1105 | 127615.1527 | 127615.1527 | 0.97267 |  | 6.087 | 1074.0963 | 35722728.9889
23840 | 2003-07-01 | Interim Rpt #2 | 204102 | 204105 | 204102 | 204102.496 | 204102.496 | 209320.8269 | 209320.8269 | 1.0256 |  | 6.087 | 12468.0384 | 4813428053.5433
23845 | 2003-07-01 | Interim Rpt #2 | 36971 | 36936 | 36971 | 36970.752 | 37656.528 | 33565.855 | 33565.855 | 0.9079 | op hours | 6.087 | -2092.0242 | 135516325.5483
23874 | 2003-07-01 | Interim Rpt #2 | 67641 | 67640 | 67641 | 67641.0134 | 69725.7792 | 44742.3768 | 44742.3768 | 0.66147 | op hours | 6.087 | -20496.1778 | 13007804003.6661
16145 | 2003-08-01 | Interim Rpt #2 | 10297 | 9492 | 10297 | 9492.392 | 9771.58 | 9797.8881 | 9797.8881 | 0.95153 |  | 6.087 | -133.3873 | 550917.9526
17089 | 2003-08-01 | Interim Rpt #2 | 433 | 0 | 433 | 433.3056 | 792.1368 | 792.1368 | 792.1368 | 1.8294 | tstat constants | 6.087 | 374.5159 | 4343089.5665
23862 | 2003-08-01 | Interim Rpt #2 | 3639 | 3639 | 3639 | 3639.3504 | 5629.6201 | 5629.6201 | 5629.6201 | 1.547 | tstat constants | 6.087 | 2119.8687 | 139147733.3893
23915 | 2003-08-01 | Interim Rpt #2 | 3517 | 3517 | 3517 | 3516.864 | 3610.464 | 3190.968 | 3190.968 | 0.9073 | fixture dropped | 6.087 | -201.1166 | 1252432.1096
23921 | 2003-08-01 | Interim Rpt #2 | 3517 | 3517 | 3517 | 3516.864 | 3610.464 | 3221.3135 | 3221.3135 | 0.91593 | op hours | 6.087 | -170.7712 | 902998.9254
23901 | 2003-09-01 | Interim Rpt #2 | 18371 | 18371 | 18371 | 18371.184 | 16916.432 | 18981.0456 | 18981.0456 | 1.0332 |  | 6.087 | 1262.5393 | 49356916.4352
23918 | 2003-09-01 | Interim Rpt #2 | 20968 | 20968 | 20968 | 20965.494 | 19929.4722 | 19929.4722 | 19929.4722 | 0.95047 |  | 6.087 | -293.7949 | 2672679.2863
23924 | 2003-09-01 | Interim Rpt #2 | 41681 | 41681 | 41681 | 41681.1331 | 42313.487 | 42313.487 | 42313.487 | 1.0152 |  | 6.087 | 2112.8958 | 138233840.7083
23925 | 2003-09-01 | Interim Rpt #2 | 15493 | 15494 | 15493 | 15493.401 | 14847.3864 | 14847.3864 | 14847.3864 | 0.95833 |  | 6.087 | -95.3396 | 281452.0742
23919 | 2003-10-01 | Final Rpt | 75915 | 75937 | 75915 | 75915.424 | 77583.792 | 77781.2659 | 77781.2659 | 1.0246 |  | 6.087 | 4562.5839 | 644584636.2702
23931 | 2003-10-01 | Final Rpt | 29651 | 29651 | 29651 | 29651.049 | 29588.0726 | 30341.3057 | 30341.3057 | 1.0233 |  | 6.087 | 1743.4378 | 94117661.4338
23954 | 2003-10-01 | Final Rpt | 1592 | 1606 | 1592 | 1593.28 | 1618.24 | 1622.5968 | 1622.5968 | 1.0192 |  | 6.087 | 87.1408 | 235126.386
28986 | 2003-10-01 | Final Rpt | 25561 | 25737 | 25561 | 25560.6 | 26340.6 | 26411.517 | 26411.517 | 1.0333 |  | 6.087 | 1758.3822 | 95738090.7636
17096 | 2003-11-01 | Final Rpt | 17816 | 17815 | 17816 | 17815.6123 | 16022.257 | 15221.1442 | 15221.1442 | 0.85435 | fixture kW value; persistence | 6.087 | -1962.0744 | 119203546.5456
23913 | 2003-11-01 | Final Rpt | 88671 | 88671 | 88671 | 88671.44 | 86258.48 | 86258.48 | 86258.48 | 0.97279 |  | 6.087 | 736.8604 | 16812357.5337
23965 | 2003-11-01 | Final Rpt | 29195 | 29194 | 29195 | 29194.88 | 29756.32 | 29756.32 | 29756.32 | 1.0192 |  | 6.087 | 1598.2561 | 79095351.2944
23985 | 2003-11-01 | Final Rpt | 4524 | 4525 | 4524 | 4524.2921 | 4640.0429 | 4640.0429 | 4640.0429 | 1.0257 |  | 6.087 | 276.7245 | 2371118.9217
23991 | 2003-11-01 | Final Rpt | 6494 | 6494 | 6494 | 6494.488 | 6830.824 | 6849.2147 | 6849.2147 | 1.0547 |  | 6.087 | 585.8659 | 10628077.1032
23914 | 2003-12-01 | Final Rpt | 78589 | 78589 | 78589 | 78589.24 | 76722.76 | 76722.76 | 76722.76 | 0.97625 |  | 6.087 | 925.052 | 26496622.7822
23951 | 2003-12-01 | Final Rpt | 72014 | 72014 | 72014 | 72013.76 | 73285.12 | 73285.12 | 73285.12 | 1.0177 |  | 6.087 | 3828.8838 | 453944342.0797
23952 | 2003-12-01 | Final Rpt | 70838 | 70837 | 70838 | 70838.304 | 68395.152 | 68395.152 | 68395.152 | 0.96552 |  | 6.087 | 73.1472 | 165673.5109
23958 | 2003-12-01 | Final Rpt | 32580 | 32581 | 32580 | 32579.8 | 34214.4 | 34214.4 | 34214.4 | 1.0502 |  | 6.087 | 2791.5631 | 241297673.1154
23964 | 2003-12-01 | Final Rpt | 68413 | 68413 | 68413 | 68412.96 | 69574.56 | 69574.56 | 69574.56 | 1.017 |  | 6.087 | 3591.425 | 399385070.7235
23968 | 2003-12-01 | Final Rpt | 58255 | 58255 | 58258 | 58254.9 | 53842.58 | 53842.58 | 53842.58 | 0.92426 | fixture kW value | 6.087 | -2343.3427 | 170031677.1877
23971 | 2003-12-01 | Final Rpt | 6817 | 19192 | 6817 | 6817.2911 | 1697.844 | 1697.844 | 1697.844 | 0.24906 | op hours; refrig. tune-up constants | 6.087 | -4877.0326 | 736494552.1149
23993 | 2004-01-01 | Final Rpt | 16480 | 16490 | 16480 | 16485.0761 | 1435.5187 | 717.7594 | 717.7594 | 0.043553 | persistence; refrig. tune-up constants | 6.087 | -15176.9107 | 7132224167.4558
23998 | 2004-01-01 | Final Rpt | 4502 | 4509 | 4502 | 4502.16 | 4642.56 | 4655.0592 | 4655.0592 | 1.034 |  | 6.087 | 312.9594 | 3032733.2928
Total Sample |  |  | 1685894 | 1690948 | 1685094 | 1684946.2458 | 1655608.6655 | 1626015.1055 | 1626015.1055
Realization Rate (Step 1 Database Value = 1.000) |  |  | 1 | 1.003 | 0.99953 | 0.99944 | 0.98204 | 0.96448 | 0.96448
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Summary of Findings
Sample-based Statistics, assuming Simple Random Sampling and Ratio Estimation of Realization Rate
Mean (Ex Ante; gross annual kWh savings) | [10 empty] | 24433.2464
Max (Ex Ante; gross annual kWh savings) | [10 empty] | 204102
Min (Ex Ante; gross annual kWh savings) | [10 empty] | 433
Mean (Ex Post; gross annual kWh savings) | [10 empty] | 23565.4363
Max (Ex Post; gross annual kWh savings) | [10 empty] | 209320.8269
Min (Ex Post; gross annual kWh savings) | [10 empty] | 717.7594
Sample Size (n) | [10 empty] | 69
Case Weight (w) | [10 empty] | 6.087
Sum, (w * Step 5 Ex Post values; gross annual kWh savings) | [10 empty] | 9897483.2506
Sum, (w * Step 1 "measure status" TBL Ex Ante values; gross annual kWh savings) | [10 empty] | 10261963.4783
Realization Rate | [10 empty] | 0.96448
Standard Error | [10 empty] | 0.02139
Error Bound @ 90% confidence level | [10 empty] | 0.035187
Upper Error Bound re Realization Rate | [10 empty] | 0.99967
Lower Error Bound re Realization Rate | [10 empty] | 0.9293
Relative Precision | [10 empty] | 3.648%
Population Size (per Program Tracking System; N) | [10 empty] | 420
Tracking Savings (= population * sample Ex Ante mean; gross annual kWh savings) | [10 empty] | 10261963.4783
Total Gross Ex Post Annual kWh Savings (= Tracking Savings * Realization Rate) | [10 empty] | 9897483.2506
Standard Error (gross annual kWh savings) | [10 empty] | 219506.2121
Error Bound @ 90% confidence level (gross annual kWh savings) | [10 empty] | 361087.7189
Upper Error Bound re Realization Rate (gross annual kWh savings) | [10 empty] | 10258570.9695
Lower Error Bound re Realization Rate (gross annual kWh savings) | [10 empty] | 9536395.5317
Program Goal Gross Annual kWh Savings | [10 empty] | 9792750
S&A estimate of Gross Annual kWh Savings as % of Goal | [10 empty] | 101.1%
Upper Error Bound - S&A estimate of Gross Annual kWh Savings as % of Goal | [10 empty] | 104.8%
Lower Error Bound - S&A estimate of Gross Annual kWh Savings as % of Goal | [10 empty] | 97.38%
Selected Population Statistics
Program Tracking System Gross Annual kWh Savings (ex ante) | [10 empty] | 11122899
Mean Gross Annual kWh Savings (ex ante) per Program Participant | [10 empty] | 26483.0929
Sample Mean as % of Population Mean: Gross Annual kWh Savings (ex ante) per Participant | [10 empty] | 92.26%
Note on L103: PAS: per 4/5/04 database extract
Note on L111: PAS: per 2003 Q4 PIP workbook
Note on L117: PAS: per 4/5/04 database extract

## Methodology
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Methodology - General Overview
Step 1: Reference Information for sampled applications
Database value is starting point for impact evaluations
Possible process evaluation issue TBD: whether EEM-specific database and paperwork savings data ever disagree
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Note: EEM-specific paperwork must be included in sampled application packets, otherwise EEM-specific claimed energy savings
will be zeroed out (OK if initially missing documentation provided subsequently).
Maximize use of paperwork-based data in conducting reverse engineering; fill in as needed using database values
Mainly involves determining whether listed savings data were developed "to spec")
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
Calculations generally rely on Step 2 data, except as noted below
Data considered "innocent until proven guilty" (i.e., ASW values not overridden unless "preponderence of the evidence" indicates
that a change is warranted)
Lighting EEM: verify (or modify using) SPC table and/or manufacturer kW/fixture values, as appropriate
Certain fixture kW data derived /assessed using inferred values for lamps and/or ballasts
Refrig. Tune-up, AC Tune-up, and T-stat EEM's: use alternative values for constants in equations as appropriate
Alternate values based on S&A research of 1) ASW-/RLW-provided source documents and/or 2) product/industry research
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
Adjustments are made relative to data derived in Step 3; example: .9 factor means gross savings reduced by 10%
Adjustments are based on a series of multiplicative factors (e.g., .9 factor * .9 factor = .81, implying 19% reduction in gross savings)
and/or lighting operating hour-related calculations
Lighting fixture quantities adjusted as appropriate based on cross-checks with Lighting Installation Report
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4)
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
Adjustments are made relative to data derived in Step 4
Each factor is binary: values are either 1 (no adjustment to gross savings) or 0 (zeroing out); factors are multiplicative
Service address acceptable?
must be in Santa Barbara, San Bernardino, Riverside, Ventura, or [rural part of] L.A. County, per Impl. Plan, pages 2 & 15;
S&A assessment based on service address as found in paperwork
Per ASW decisions, L.A. County east of 57/210 and High Desert areas (Palmdale, etc.) allowable locations
S&A assessment based on service address as found in paperwork
Equipment scope appropriate?
Must be lighting, refrig. tune-up, AC tune-up, and/or prog. t-stat, per Impl. Plan, page 15; CFL's OK per Impl. Plan, page 6
S&A assessment based on EEM information as found in paperwork (preferably per pages showing annual kWh savings)
Completion date(s) acceptable?
Must be >10/1/02 or <1/31/04, per S&A EM&V R Plan, page 8 (original <12/31/03 value updated to reflect late 2003 commitments
closed in early 2004)
S&A assessment based on checklist sheet, attached check copy, and/or invoice copy
Note: "paperwork available?" step noted in the EM&V research plan as being a part of this particular adjustment process has been made
a part of Step 2 to not double count that aspect of any adjustments

## AC Tuneup + Tstat Eq Rev
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Measure Energy Savings Review: AC tune-up and Programmable Thermostat
kWh/yr equation: tons * kW/ton * load factor * hr/yr * % savings
Variable | ASW/RLW value(s) | ASW/RLW value(s) basis | S&A notes re ASW/RLW value(s) basis | S&A recommendation | S&A recommendation notes
tons | per field audit | determined by audit | appropriate | per field audit | determined by audit
kW/ton | 1 | either 1) SCE "End-Use Metered Data for Commercial Buildings, Annual Report 1995", 12/96, (per C Baginski/ASW email to P Sisson/S&A, 1/22/04) or 2) SMUD "Small Commercial A/C and Refrigeration Maintenance Program Draft Report", 1/01 (per K Moore/RLW email to P Sisson/S&A, 12/5/03) | neither kW/ton nor even basic AC tonnage data found in either of the two documents mentioned. Hence data appear untied to specific "hard" documentation. | 1.3 if unit <= 5 tons, 1.1 if unit > 5 tons | S&A research conducted 2/04 for package rooftop units; kW data appear to apply to core cooling system compressor; S&A data are at the conservative (i.e., low) end of the findings. Note further that these data pertain to new models; corresponding data for models 5-20 years old if anything would be significantly higher, owing to lower SEER's / EER's.
load factor | values range between .26 and .70 | SCE "End-Use Metered Data for Commercial Buildings, Annual Report 1995", 12/96, (per C Baginski/ASW email to P Sisson/S&A, 1/22/04) | SCE document provides load factors at the building level for 3 different building types within each of 5 season/day types, but not across the overall year, and not with any sort of delineation for Coastal/Inland or economizer/no economizer. See for example page 2-8 of the SCE document for available data re offices. Hence, data appear untied to specific "hard" documentation. | ASW values (.26 - .70) | SCE data appear "about right", if tied to annual AC hours of operation (as opposed to overall annual business hours or overall annual HVAC hours of operation). Note that weather variations between northern & southern Calif. are significant but not "show stoppers" (given that the northern Calif. program operates in a decidedly inland portion of the Bay Area).
hr/yr | ASW: business hours; RLW: AC operating hours | ASW: per C Baginski/ASW email to P Sisson/S&A, 12/8/03; RLW: per reviews of data for sample records in the Customer Information, Tstat Detail, and HVAC Detail tables of the tracking system database | RLW approach probably appears more appropriate, given the climate zones and load factor values involved. Consider for example the inland office load factor for no economizer: .62. Even in the Inland Empire or Desert areas, there are very limited AC loads in the 3 months of Dec-Feb.; a factor of .62 in combination with AC loads during the remaining 75% of the year would imply either near "flat-out" (i.e., 82% (= 62%/75%)) AC unit utilization during Mar-Nov (very unrealistic) or drastic AC unit undersizing (also very unrealistic). | AC operating hours | see prior S&A discussion. Note that an AC unit should be sized to meet design [weather] load (likely in the mid 90s or warmer in almost all of the operational areas of the SBEA). For ASW records, may involve designating 75%, 75%, and 83% of annual business hrs as AC hours for offices, retail stores, and restaurants, respectively (surrogates for approx. 9, 9, and 10 months of cooling loads, respectively).
% savings for AC tuneup | 5% | more conservative than average savings reported in SMUD "SML CML A/C and Refrigeration Maintenance Program Draft Rpt", 1/01 (per C Baginski/ASW email to P Sisson/S&A, 12/8/03) | data verified in indicated document, page 16: 4.5% savings for filter change + condenser coil cleaning, and 6.1% if overcharge condition also addressed. Note, however, that refrigerant charge change condition is identified but not conducted as part of the SBE AC tune-up (such work happens optionally/subsequently, and at separate cost incurred by customer). | 5% | reflects SMUD study findings for filter change + condenser coil cleaning, then backs out filter change effect (since not part of tune-up), then adds in effect of evaporative coil cleaning (since part of tune-up).
% savings for T-stat | 8% | less than the 20-30% claimed by SCE (per C Baginski/ASW email of PDF of SCE web site screen shot sent to P Sisson/S&A, 12/8/03) | SCE web site figure is for residential applications. Hence, cited figure is largely non-applicable. | 15% | low end of 15-25% range claimed for small CML customers per Flex Your Power web site, 2/04; see http://www.fypower.com/com/tools/products_results.html?id=100133
Notes:
1. Rooftop AC unit research:
Mfr | Model | kW | Tons | kw/Ton | Notes
Carrier | 48TM | 4 | 3 | 1.3333
Carrier | 48TM | 5.3 | 4 | 1.325
Carrier | 48TM | 6.7 | 5 | 1.34
Carrier | 48TM | 7 | 6 | 1.1667
Carrier | 48TM | 8.7 | 7.5 | 1.16
Carrier | 48TM | 9.9 | 8.5 | 1.1647
Carrier | 48TM | 11.3 | 10 | 1.13
Carrier | 48TM | 14.3 | 12.5 | 1.144
Carrier | 48TMD | 17.064 | 15 | 1.1376
Carrier | 48TMD | 21.166 | 18 | 1.1759
Carrier | 48TMD | 24.832 | 20 | 1.2416
Carrier | 48TMD | 28.535 | 25 | 1.1414
Trane | YSC036A1 | 3.91 | 3 | 1.3033
Trane | YSC048A1 | 5.28 | 4 | 1.32
Trane | YSC060A1 | 6.86 | 5 | 1.372
Trane | YSC072A3 | 6.77 | 6 | 1.1283
Trane | YSC090A3 | 8.91 | 7.5 | 1.188
Trane | YSC102A3 | 9.9 | 8.5 | 1.1647
Trane | YSC120A3 | 11.18 | 10 | 1.118
Trane | YHC036A1 | 3.33 | 3 | 1.11 | high effic unit
Trane | YHC048A1 | 4.48 | 4 | 1.12 | high effic unit
Trane | YHC060A1 | 5.73 | 5 | 1.146 | high effic unit
Trane | YHC072A1 | 6.09 | 6 | 1.015 | high effic unit
Trane | YHC092A1 | 7.83 | 7.5 | 1.044 | high effic unit
Trane | YHC102A1 | 8.52 | 8.5 | 1.0024 | high effic unit
Trane | YHC120A1 | 9.73 | 10 | 0.973 | high effic unit
Data sources:
Carrier models up to 12.5 tons: http://www.commercial.carrier.com/wcs/prod_physicaldata/0,1180,CLI1_DIV12_ETI440_PRD558,00.html
Carrier models 15-25 tons: Carrier Product Data PDF for Models 48TM004-0028, page 103; has 2002 copyright date
Trane models: Packaged Gas/Electric Rooftop Units, 2/04, pp. 14-26
2. Load factors assumed by ASW/RLW are as follows:
Location | Bus. Type | Economizer Cycle | Load Factor
Coastal | Restaurant | Yes | 0.4
Coastal | Restaurant | No | 0.62
Coastal | SML Office | Yes | 0.26
Coastal | SML Office | No | 0.54
Coastal | SML Retail | Yes | 0.24
Coastal | SML Retail | No | 0.52
Inland | Restaurant | Yes | 0.52
Inland | Restaurant | No | 0.7
Inland | SML Office | Yes | 0.37
Inland | SML Office | No | 0.62
Inland | SML Retail | Yes | 0.38
Inland | SML Retail | No | 0.58

## Refrig Tuneup Eq Rev
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Measure Energy Savings Review: Refrigeration tuneup
kWh/yr equation: ft * kBtuh/ft * 1/12 ton/kBtuh * kW/ton * hr/yr * load factor * hr/yr * % savings
Variable | ASW/RLW value(s) | ASW/RLW value(s) basis | S&A notes re ASW/RLW value(s) basis | S&A recommendation | S&A recommendation notes
ft (LF for cases; sq ft for walk-in units) | per field audit | determined by audit | appropriate | per field audit | determined by audit
kBtuh/ft | cases range from 1.07 (cold drinks) to 1.53 kBtuh/LF (frozen food); walk-ins range from .5 (meat freezer) to .6 kBtuh/sq ft (coolers) | simulations and work with refrigeration contractor (per C Baginski/ASW email to P Sisson/S&A, 12/8/03) | simulation/contractor materials not provided (though useful ADL DOE 1996 study cited at right was provided); counter-intuitive findings re walk-in freezers being less loads-intensive than walk-in coolers | Cases: 1.5 kBtu/LF for all med. temp cases, 2.08 for low temp cases. Walk-ins: .06 kBtuh/sq ft for coolers, .20 kBtuh/sq ft for freezers. | All data per ADL "Energy Savings Potential for Commercial Refrigeration Equipment" 1996 study for DOE, Table 4.5 (page 14). For walk-in freezers, data adjusted from .08 to .20 kBtuh/sq ft based on S&A 4/04 research re actual Kolpak units (similar research re walk-in coolers found ADL data were highly accurate)
tons/kBtuh | 1/12 | engineering constant | appropriate | 1/12 | engineering constant
kW/ton | 1.549 for all but frozen food case; frozen food case is 2.548 | simulations and work with refrigeration contractor (per C Baginski/ASW email to P Sisson/S&A, 12/8/03) | simulation/contractor materials not provided, so evaluated using selected product spec sheets. | 2.0 for all but frozen food case; frozen food case = 2.55 | S&A 4/04 spot checks of Delfield equipment (i.e., 500-CRR deli cases, 6100XL reach-in freezers) indicate kW/ton values range between 1.92 and 2.78, so 2.00 used to be relatively conservative; data not found for frozen food cases, so left unchanged
hr/yr | 8760 | assumes 24/7 operation for food safety purposes | appropriate | assumes 24/7 operation for food safety purposes | appropriate
load factor | 80% | less than the 82% inferred from SCE Book of Standards, action 7.4 (8/1/82); 82% = 610 run hr/mo / 720 total hr/mo. 80% value is intended to be slightly conservative | very dated source (1982), but value appears generally reasonable (based on past S&A staff audits of grocery stores) | 80% | ASW/RLW assumption appears prudently reasonable for default value
% savings for Refrig. Tune-up | 6% | more conservative than average finding in SMUD "Small Commercial A/C and Refrigeration Maintenance Program Draft Report", 1/01 (per C Baginski/ASW email to P Sisson/S&A, 12/8/03); less than SCE Book of Standards' 20% savings for coil cleaning; less then Efficiency Maine 2003 materials claim of 25% savings for coil cleaning | SMUD study savings for refrigeration system tune-up are only 0.73% (page 16), but only involved condenser coil cleaning (while SBEA measure also cleans evaporator coils); SCE value verified (but is from very dated (1982) source; Efficiency Maine value makes note of monthly cleaning cycle, and almost certainly applies to extremely filthy prior conditions | 1.5% | round up SMUD study value (0.73%) to 1% (to take into account the typical small business/poorly maintained unit targeted by the SBEA program), and take half again (.5%) allowance for evaporator coils also being cleaned. Not appropriate to claim savings associated with refrigerant charge, suction line insulation, or filter change, since those items are information-only.
Notes:
1. kBtuh/ft values (per ASW, and S&A recommended revisions)
kBtuh/Ft
Equip. Type | Temp | Data | ASW | S&A | S&A notes re mapping from ADL study, p. 14
Meat | 28 | LF | 1.48 | 1.5 | medium temp multideck meat case
Meat | 25 | LF | 1.53 | 1.5 | medium temp multideck meat case
Juice | 40 | LF | 1.07 | 1.5 | medium temp multideck other case
Yogurt | 42 | LF | 1.22 | 1.5 | medium temp multideck other case
Milk | 35 | LF | 1.38 | 1.5 | medium temp multideck other case
Cheese & | 35 | LF | 1.45 | 1.5 | medium temp multideck other case
Produce | 40 | LF | 1.22 | 1.5 | medium temp multideck other case
Produce | 45 | LF | 1.22 | 1.5 | medium temp multideck other case
Tofu | 32 | LF | 1.22 | 1.5 | medium temp multideck other case
Apples | 37 | LF | 1.16 | 1.5 | medium temp multideck other case
Persimmons | 35 | LF | 1.18 | 1.5 | medium temp multideck other case
Grapes | 38 | LF | 1.16 | 1.5 | medium temp multideck other case
Cold Drinks | 42 | LF | 1.07 | 1.5 | medium temp multideck other case
Beer Wine | 34 | LF | 1.22 | 1.5 | medium temp multideck other case
Frozen Food | 0 | LF | 1.53 | 2.08 | low temp reach-in case
Deli | 42 | LF | 1.22 | 1.5 | medium temp multideck other case
Meat Freezer | 28 | sq ft | 0.5 | 0.08 | low temp walk-in freezer
Meat Cooler | 25 | sq ft | 0.6 | 0.06 | medium temp meat walk-in cooler
Groc Cooler | 40 | sq ft | 0.6 | 0.06 | medium temp other walk-in cooler
Produce Cooler | 42 | sq ft | 0.6 | 0.06 | medium temp other walk-in cooler
Produce Cooler | 35 | sq ft | 0.6 | 0.06 | medium temp other walk-in cooler
2. Standard information sources yielded little information regarding refrigeration system tune-ups. Calmac and ACEEE research focuses on refrigeration system hardware, and neither
the CEC nor LBL had any information on refrigeration system O&M measures (e.g., tune-ups). Research regarding 2004-2005 CPUC-approved energy efficiency programs revealed few (if any)
true peers for the SBEA refrigeration tune-up measure; Express Efficiency, PG&E-East Bay Partnership, and PECI Smart Grocer refrigeration measures all pertain to new hardware, while
the Kema-Xenergy "BEST" program refrigeration measures all primarily involve controls.

## Ltg Fixt kW Variances
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Common Lighting Fixtures with kW Disagreements between ASW, RLW, and/or SPC, and Recommended Values for Impact Evaluation
General Notes re Fixtures
1. RLW requests that Sylvania be used exclusively (basis: Ken Moore/RLW email to Phil Sisson/S&A, 12/11/03)
2. ASW has flexibility regarding vendors, but uses high-end (usually G2) product (basis: Mark Hinrichs/ASW email to Phil Sisson/S&A, 12/11/03)
3. Variances of 1-2 watts either side of SPC tables - or in general - are acceptable for any given fixture type (basis: John Clint/AESC email and phone calls with Phil Sisson/S&A, 3/2/04)
Data Sources Prioritized |  |  |  |  | Notes
directly applicable product catalog |  |  |  |  | highest priority / attractiveness (since so closely related to the product installed, and current, and reflects lamp-ballast interactions)
new SPC database (from 2003)
old SPC database (from prior to 2003) |  |  |  |  | dropped "SE" fixture kW values haven't changed (per John Clint/AESC communications with Phil Sisson/S&A, 3/2/04)
inferences from either new or old SPC database |  |  |  |  | least closely related to the product installed
Fixture Values Analysis
|  | ASW Base Value |  | RLW Base Value |  | 2003 SPC |  |  | ASW EM&V Value |  |  | RLW EM&V Value
Fixture | Type | kW | Basis | kW | Basis | G1 kW | G2 kW | G3 kW | kW | Basis | Impact on Base Energy Savings (re this fixture) | kW | Basis | Impact on Base Energy Savings (re this fixture) | Notes
F41ILL-R | replacement | 0.027 | SPC database (2/13/98) | 0.026 | F42ILL-R per 2002 Sylvania catalog is .051; value halved and rounded up | NA | NA | 0.025 | 0.026 | RLW value | increase | 0.026 | base value | none
F41SE | existing | 0.05 | SPC database (2/13/98) | 0.049 | 2003 SPC for F41EE is .043; add 6 watts (40-34) for SE | NA | NA | NA | 0.05 | ASW value | none | 0.049 | base value | none | RLW base value within 2 watts of ASW base value, so kept as-is
F42ILL | replacement | NA | NA | 0.059 | 2002 Sylvania catalog | 0.059 | 0.059 | 0.054 | NA | NA | none | 0.059 | base value | none | catalog value most accurate
F42ILL-H | replacement | NA | NA | 0.077 | 2002 Sylvania catalog | 0.065 | 0.065 | NA | NA | NA | none | 0.077 | base value | none | not obvious why 2003 SPC is so much different
F42ILL-R | replacement | 0.052 | SPC database (2/13/98) | 0.051 | 2002 Sylvania catalog | 0.052 | 0.052 | 0.048 | 0.051 | RLW value | increase | 0.051 | base value | none | catalog value most accurate
F42SE | existing | 0.086 | SPC database (2/13/98) | 0.084 | 2003 SPC for F42EE is .072; add 12 watts (2*(40-34)) for SE | NA | NA | NA | 0.086 | ASW value | none | 0.084 | base value | none | RLW base value within 2 watts of ASW base value, so kept as-is
F43ILL-R | replacement | 0.078 | SPC database (2/13/98) | 0.076 | 2002 Sylvania catalog | 0.078 | 0.078 | 0.073 | 0.076 | RLW value | increase | 0.076 | base value | none | catalog value most accurate
F43SE | existing | 0.14 | SPC database (2/13/98) | 0.128 | derived from data for F42SE: ((3 lamps * 40 watts/lamp) + (2 ballasts * 4 watts/ballast) | NA | NA | NA | 0.14 | ASW value | none | 0.14 | ASW value | increase | RLW base value not within 2 watts of ASW base value, so ASW value used
F44ILL-R | replacement | 0.1024 | SPC database (2/13/98) | 0.098 | 2002 Sylvania catalog | 0.102 | 0.102 | 0.094 | 0.098 | RLW value | increase | 0.098 | base value | none | catalog value most accurate
F44SE | existing | 0.172 | SPC database (2/13/98) | 0.168 | derived from data for F42SE: ((4 lamps * 40 watts/lamp) + (2 ballasts * 4 watts/ballast) | NA | NA | NA | 0.172 | ASW value | none | 0.172 | ASW value | increase | RLW base value not within 2 watts of ASW base value, so ASW value used
Related Topic: S&A Observations re Inferred Loads per Magnetic Ballast (from SPC Tables)
SPC value
Fixture | 1998 version | 2003 version | Total fixture watts | Lamps | watts/lamp | Ballasts | inferred watts/ magnetic ballast
F41SE | X |  | 50 | 1 | 40 | 1 | 10
F41EE | X | X | 43 | 1 | 34 | 1 | 9
F42SE | X |  | 86 | 2 | 40 | 1 | 6
F42EE | X | X | 72 | 2 | 34 | 1 | 4
F43SE | X |  | 140 | 3 | 40 | 2 | 10
F43EE | X | X | 115 | 3 | 34 | 2 | 6.5
F44SE | X |  | 172 | 4 | 40 | 2 | 6
F44EE | X | X | 144 | 4 | 34 | 2 | 4
Questions for AESC (and John Clint-provided responses to Phil Sisson, 3/2/04)
1. Regarding the SE fixtures included in the 1998 SPC materials but dropped from the 2003 SPC materials: is there any reason to
believe that the wattages would have changed (as based on subsequent research, corrective changes, and/or changes in product definition)?
no
2. Does the draw for an efficient magnetic ballast really vary THAT much within this relatively small universe of relatively similar fixtures?
low: 4 watts for F42EE or F44EE
high: 10 watts for F41SE or F43SE
Even within the "EE" fixture figures, the inferred load varies between 4 and 9 watts.
single lamp ballasts are less efficient than multiple lamp ballasts
Or are there alternative hardwired values for ballast loads that should be used instead?
data that are truly accurate are for specific ballasts in combination with specific lamps; even the 34 and 40 watt lamp values are nominal only;
having a range of several watts for a given fixture type is absolutely to be expected.
Was a mistake made in the above analysis? If so, briefly describe.
no

## EIG Fixture kW Issues
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
S&A Mapping of ASW/EIG Fixture Types and Wattages to SPC Corresponding Information
(see notes at bottom of table)
Retrofit Number | PreFixture | Pre Watts | S&A-Assumed SPC Fixture | SPC watts | Post Fixture | Post Watts | S&A-Assumed SPC Fixture | SPC watts
T3-10 | 2ft 2 lamp T-12 U-tube | 72 | FU2EE | 72 | 2ft 2 lamp T-8,U-Tube | 52 | FU2ILL | 59
T3-100 | Inca, AC only | 40 | EI20/2 | 40 | LED | 2 | ELED2/2 | 9
T3-101 | LED, w/ battery or dual circuit | 40 | EI20/2 | TBD | ELED2/2 | 3 | ELED2/2 | 9
T3-11 | 2ft 2 lamp T-12 U-tube | 72 | FU2EE | 72 | 2ft 2 lamp T-8,REF | 33 | F22ILL | 33
T3-12 | 2ft 2 lamp T-8 U-tube | 62 | FU2ILL | 59 | 2ft 2 lamp T-8, exst bllst, REF | 33 | F22ILL | 33
T3-13 | 3ft 1 lamp T-12 | 46 | F31SS | 46 | 3ft 1 lamp T-8 | 22 | F31ILL | 26
T3-14 | 3ft 2 lamp T-12 | 60 | F32EE | 66 | 3ft 2 lamp T-8 | 46 | F32ILL | 46
T3-15 | 3ft 3 lamp T-12 | 106 | F33SE | 120 | 3ft 3 lamp T-8 | 66 | F33ILL | 67
T3-16 | 3ft 4 lamp T-12 | 120 | F34SE | 148 | 3ft 4 lamp T-8 | 86 | F34ILL | 87
T3-17 | 4ft 1 lamp T-12 | 43 | F41EE | 43 | 4ft 1 lamp T-8-LP | 27 | F41ILL-R | 25
T3-18 | 4ft 1 lamp T-12 | 43 | F41EE | 43 | 4ft 1 lamp ULTRA LP WM | 23 | F41WLL-R | 24
T3-19 | 4ft 1 lamp T-12 | 43 | F41EE | 43 | 4ft 1 lamp T-8-T/W-LP | 25.5 | F41ILL/T4-R | 26
T3-20 | 4ft 1 lamp T-12 | 43 | F41EE | 43 | 4ft 1 lamp ULTRA T/W - LP WM | 23 | F41WLL-R | 24
T3-21 | 4ft 2 lamp T-12 | 72 | F42EE | 72 | 4ft 2 lamp T-8-LP | 51 | F42ILL-R | 52
T3-22 | 4ft 2 lamp T-12 | 72 | F42EE | 72 | 4ft 2 lamp ULTRA LP WM | 46 | F42WLL-R | 45
T3-23 | 4ft 2 lamp T-12 | 72 | F42EE | 72 | 4ft 2 lamp T-8-T/W LP | 49 | F42ILL/T4-R | 51
T3-24 | 4ft 2 lamp T-12 | 72 | F42EE | 72 | 4ft 2 lamp T/W ULTRA LP WM | 44 | 1/2 OF F44WLL/T2-R = F42WLL/T2 | 45
T3-25 | 4ft 2 lamp T-12 | 72 | F42EE | 72 | 4ft 1 lamp T-8,REF | 31 | F41EL | 32
T3-26 | 4ft 3 lamp T-12 | 115 | F43EE | 115 | 4ft 3 lamp T-8 LP | 78 | F43ILL-R | 78
T3-27 | 4ft 3 lamp T-12 | 115 | F43EE | 115 | 4ft 3 lamp ULTRA LP WM | 67 | F43WLL-R | 67
T3-28 | 4ft 3 lamp T-12 | 115 | F43EE | 115 | 4ft 2 lamp T-8,REF | 58 | F42ILL | 59
T3-29 | 4ft 3 lamp T-12 | 115 | F43EE | 115 | 4ft 2 lamp ULTRA WM REF | 51 | F42WLL | 51
T3-30 | 4ft 4 lamp T-12 | 144 | F44EE | 144 | 4ft 4 lamp T-8 LP | 98 | F44ILL-R | 102
T3-31 | 4ft 4 lamp T-12 | 144 | F44EE | 144 | 4ft 4 lamp ULTRA LP WM | 88 | F44WLL-R | 90
T3-32 | 4ft 4 lamp T-12 | 144 | F44EE | 144 | 4ft 2 lamp T-8,REF | 58 | F42ILL | 59
T3-33 | 4ft 4 lamp T-12 | 144 | F44EE | 144 | 4ft 2 lamp ULTRA WM REF | 51 | F42WLL | 51
T3-34 | 4ft 4 lamp T-8 | 110 | F44LE | 112 | 4ft 2 lamp exstg blst, REF | 72 | F42EE | 72
T3-35 | 6ft 1 lamp T-12 | 66 | F61SS | 76 | 3ft 2 lamp T-8,KIT | 46 | F32ILL-R | 46
T3-36 | 6ft 2 lamp T-12 | 122 | F62SE | 122 | 3ft 4 lamp T-8,KIT | 86 | F34ILL-R | 86
T3-37 | 6ft 2 lamp T-12 HO | 194 | F62SHE | 194 | 3ft 4 lamp T-8,KIT, High Ballast Factor Ballast | 96 | F34ILL | 87
T3-38 | 8ft 1-8ft lamp T-12 | 81 | F81ES | 75 | 4ft 2 lamp T-8,KIT-LP | 51 | F42ILL-R | 52
T3-39 | 8ft 1-8ft lamp T-12 | 81 | F81ES | 75 | 4ft 2 lamp ULTRA KIT LP WM | 46 | F42WLL-R | 45
T3-40 | 8ft 2-4ft lamp T-12 | 72 | F42EE | 72 | 4ft 2 lamp T-8-LP | 51 | F42ILL-R | 52
T3-41 | 8ft 2-4ft lamp T-12 | 72 | F42EE | 72 | 4ft 2 lamp ULTRA LP WM | 46 | F42WLL-R | 45
T3-42 | 8ft 2-8ft lamp T-12 | 123 | F82EE | 123 | 4ft 4 lamp T-8,KIT LP | 98 | F44ILL-R | 102
T3-43 | 8ft 2-8ft lamp T-12 | 123 | F82EE | 123 | 4ft 4 lamp ULTRA KIT LP WM | 88 | F44WLL-R | 90
T3-44 | 8ft 2-8ft lamp T-12 | 123 | F82EE | 123 | 4ft 2 lamp T-8,REF LP | 58 | F42ILL-R | 52
T3-45 | 8ft 2-8ft lamp T-12 | 123 | F82EE | 123 | 4ft 2 lamp ULTRA REF WM | 51 | F42WLL | 51
T3-46 | 8ft 3 lamp T-12 | 185 | F83EE | 210 | 4ft 6 lamp T-8,KIT | 156 | F46ILL-R | 156
T3-47 | 8ft 3 lamp T-12 | 185 | F83EE | 210 | 4ft 4 lamp T-8,REF | 112 | F44ILL | 112
T3-48 | 8ft 4-4ft lamp T-12 | 144 | F43EE | 144 | 4ft 4 lamp T-8-LP | 98 | F44ILL-R | 102
T3-49 | 8ft 4-4ft lamp T-12 | 144 | F43EE | 144 | 4ft 4 lamp ULTRA LP WM | 88 | F44WLL-R | 90
T3-50 | 8ft 4-8ft lamp T-12 | 246 | F84EE | 246 | 4ft 8 lamp T-8,KIT | 204 | F48ILL-R | 204
T3-51 | 8ft 4-8ft lamp T-12 | 246 | F84EE | 246 | 4ft 6 lamp T-8,REF | 177 | F46ILL | 175
T3-52 | 8ft 1 lamp T-12 HO | 112 | F81EHS | 112 | 4ft 2 lamp T-8,REF | 58 | F42ILL | 59
T3-53 | 8ft 1 lamp T-12 HO | 112 | F81EHS | 112 | 4ft 2 lamp ULTRA WM REF | 51 | F42WLL | 51
T3-54 | 8ft 2 lamp T-12 HO | 207 | F82EHS | 227 | 4ft 4 lamp T-8,REF | 112 | F44ILL | 112
T3-55 | 8ft 2 lamp T-12 HO | 207 | F82EHS | 227 | 4ft 4 lamp ULTRA WM REF | 98 | F44WLL-R | 102
T3-56 | 8ft 3 lamp T-12 HO | 319 | F83EHS | 380 | 4ft 6 lamp T-8,REF | 177 | F46ILL | 175
T3-57 | 25 watt Incand | 25 | I25/1 | 25 | 9W CFL S/I | 11 | CF9/1-SCRW | 9
T3-58 | 25 watt Incand | 25 | I25/1 | 25 | 9W CFL NEW FIX | 11 | CF9/1-SCRW | 9
T3-59 | 40 watt Incand | 40 | I40/1 | 40 | 11W CFL S/I | 14 | CF11/1-SCRW | 11
T3-60 | 40 watt Incand | 40 | I40/1 | 40 | 11W CFL NEW FIX | 14 | CF11/1-SCRW | 11
T3-61 | 60 watt Incand | 60 | I60/1 | 60 | 13W CFL S/I | 17 | CF13/1-SCRW | 13
T3-62 | 60 watt Incand | 60 | I60/1 | 60 | 13W CFL NEW FIX | 17 | CF13/1-SCRW | 13
T3-63 | 75 watt Incand | 75 | I75/1 | 75 | 18W CFL S/I | 24 | CF18/1-SCRW | 18
T3-64 | 75 watt Incand | 75 | I75/1 | 75 | 18W CFL NEW FIX | 24 | CF18/1-SCRW | 18
T3-65 | 100 watt Incand | 100 | I100/1 | 100 | 26W CFL S/I | 31 | inferred | 26
T3-66 | 100 watt Incand | 100 | I100/1 | 100 | 26W CFL NEW FIX | 31 | inferred | 26
T3-67 | 150 watt Incand | 150 | I150/1 | 150 | 42W CFL S/I | 48 | inferred | 42
T3-68 | 150 watt Incand | 150 | I150/1 | 150 | 39W CFL NEW FIX | 45 | inferred | 39
T3-69 | 200 watt Incand | 200 | I200/1 | 200 | 50W HPS | 66 | HPS50/1 | 66
T3-70 | 200 watt Incand | 200 | I200/1 | 200 | 50W MH | 72 | MH50/1 | 72
T3-71 | 300 watt Incand | 300 | I300/1 | 300 | 70W HPS | 95 | HPS70/1 | 95
T3-72 | 300 watt Incand | 300 | I300/1 | 300 | 70W MH | 95 | MH70/1 | 95
T3-73 | 300 watt Incand | 300 | I300/1 | 300 | 32W CFL floodlight | 32 | inferred | 32
T3-74 | 500 watt Incand | 500 | I500/1 | 500 | 100W HPS | 128 | HPS100/1 | 138
T3-75 | 500 watt Incand | 500 | I500/1 | 500 | 150W MH | 185 | MH150/1 | 190
T3-76 | 1000 watt Incand | 1000 | I1000/1 | 1000 | 200W HPS | 245 | HPS200/1 | 250
T3-77 | 1000 watt Incand | 1000 | I1000/1 | 1000 | 250W MH | 294 | MH250/1 | 295
T3-78 | 1500 watt Incand | 1500 | I1500/1 | 1500 | 400W HPS | 467 | HPS400/1 | 465
T3-79 | 1500 watt Incand | 1500 | I1500/1 | 1500 | 400W MH | 458 | MH400/1 | 458
T3-8 | 2ft 1 lamp T-12 | 28 | F21SS | 28 | 2ft 1 lamp T-8 | 20 | F21ILL | 20
T3-80 | 50 watt MV | 74 | MV50/1 | 74 | 35W HPS | 43 | HPS35/1 | 46
T3-81 | 50 watt MV | 74 | MV50/1 | 74 | 26W CFL | 31 | inferred | 26
T3-82 | 75 watt MV | 93 | MV75/1 | 93 | 50W HPS | 64 | HPS50/1 | 66
T3-83 | 75 watt MV | 93 | MV75/1 | 93 | 50W MH | 67 | MH50/1 | 72
T3-84 | 100 watt MV | 125 | MV100/1 | 125 | 50W HPS | 64 | HPS50/1 | 66
T3-85 | 100 watt MV | 125 | MV100/1 | 125 | 50W MH | 67 | MH50/1 | 72
T3-86 | 160 watt Self-Ballasted | 175 | MV150/1 | 175 | 50W HPS | 64 | HPS50/1 | 66
T3-87 | 160 watt Self-Ballasted | 175 | MV150/1 | TBD | 50W MH | 67 | MH50/1 | 72
T3-88 | 175 watt MV | 205 | MV175/1 | 205 | 100W HPS | 128 | HPS100/1 | 138
T3-89 | 175 watt MV | 205 | MV175/1 | 205 | 100W MH | 130 | MH100/1 | 128
T3-9 | 2ft 2 lamp T-12 | 56 | F22SS | 56 | 2ft 2 lamp T-8 | 33 | F22ILL | 33
T3-90 | 250 watt MV | 290 | MV250/1 | 290 | 150W HPS | 189 | HPS150/1 | 188
T3-91 | 250 watt MV | 290 | MV250/1 | 290 | 175W MH | 213 | MH175/1 | 215
T3-92 | 250 watt MV | 290 | MV250/1 | 290 | 2 lamp 42W CFL Wallpack | 84 | inferred | 84
T3-93 | 400 watt MV | 455 | MV400/1 | 455 | 250W HPS | 295 | HPS250/1 | 295
T3-94 | 400 watt MV | 455 | MV400/1 | 455 | 250W MH | 294 | MH250/1 | 288
T3-95 | 700 watt MV | 780 | MV700/1 | 780 | 400W HPS | 467 | HPS400/1 | 465
T3-96 | 700 watt MV | 780 | MV700/1 | 780 | 400W MH | 458 | MH400/1 | 458
T3-99 | 1000 watt MV | 1075 | MV1000/1 | 1075 | 600W HPS | 695 | HPS600/1 | 700
Notes
1. For EIG "pre" fixtures: T-12 standard output fixtures assume an EE configuration (in interest of kWh savings calculation conservatism) unless
otherwise noted, per D Rowan/ASW email to P Sisson/S&A, 2/17/04; non-EE SPC table values have been used only when EE data not available.
2. EIG "post" fixture codes have been mapped to SPC codes by S&A as follows:
EIG code | Interpretation | SPC code mapping
REF | reflector | none (affects lumens output rather than kW load)
LP | low power | -R (ballast light output)
kit | retrofit kit | -R (ballast light output)
ultra | G3 fixture value | G3 fixture value
WM | watt miser lamp | WL (lamp type)
CFL S/I | CFL screw-in | not twin or quad type
Note on D8: PAS: per Dennis Rowan email, 3/10/04
Note on D10: PAS: per Dennis Rowan email, 3/10/04
Note on D36: PAS: per Dennis Rowan email, 3/10/04
Note on D37: PAS: per Dennis Rowan email, 3/10/04
Note on D85: PAS: per Dennis Rowan email, 3/10/04
Note on D86: PAS: per Dennis Rowan email, 3/10/04
Note on F8: PAS: per Dennis Rowan email, 3/10/04
Note on H22: PAS: per Dennis Rowan email, 3/10/04
Note on H35: PAS: per Dennis Rowan email, 3/10/04
Note on I97: PAS: per Dennis Rowan email suggestion, 3/10/04

## 11040
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 11040
Date of ASW SBEA Database Extract Used: |  |  | 2003-11-14
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-03-18 | 9935 | 9915 | 9935
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 9935 | 9915 | 9935
Comments: lighting "details" value based on line items 1-6.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.102 | 1.02 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 1266.72
Sales |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.102 | 1.734 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 3589.04
Sales |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.052 | 0.52 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 603.2
Sales |  | I75/1F | 25 | 0.075 | 1.875 | CFQ20/1 | 25 | 0.023 | 0.575 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 3920.8
Sales |  | I75/1 | 3 | 0.075 | 0.225 | CFQ23/1 | 3 | 0.026 | 0.078 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 443.352
Canopy |  | F43EE | 1 | 0.115 | 0.115 | F43ILL-R | 1 | 0.078 | 0.078 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 111.592
Total for EEM | [18 empty] | 9934.704
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 9934.704
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.098 | 0.98 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 1387.36
Sales |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.098 | 1.666 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 3794.128
Sales |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.051 | 0.51 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 633.36
Sales |  | I75/1F | 25 | 0.075 | 1.875 | CFQ20/1 | 25 | 0.023 | 0.575 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 3920.8
Sales |  | I75/1 | 3 | 0.075 | 0.225 | CFQ23/1 | 3 | 0.026 | 0.078 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 443.352
Canopy |  | F43EE | 1 | 0.115 | 0.115 | F43ILL-R | 1 | 0.076 | 0.076 | 10 | 10 | 10 | 10 | 10 | 8 | 0 | 58 | 52 | 117.624
Total for EEM | [18 empty] | 10296.624
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 10296.624
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.098 | 0.98 | 10 | 10 | 10 | 10 | 10 | 8 | 4 | 62 | 52.14 | 1487.0328
Sales |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.098 | 1.666 | 10 | 10 | 10 | 10 | 10 | 8 | 4 | 62 | 52.14 | 4066.7114
Sales |  | F42EE | 8 | 0.072 | 0.576 | F42ILL-R | 8 | 0.051 | 0.408 | 10 | 10 | 10 | 10 | 10 | 8 | 4 | 62 | 52.14 | 543.0902
Sales |  | F42EE | 2 | 0.072 | 0.144 | F42ILL-R | 2 | 0.051 | 0.102 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 367.8998
Sales |  | I75/1F | 25 | 0.075 | 1.875 | CFQ20/1 | 25 | 0.023 | 0.575 | 10 | 10 | 10 | 10 | 10 | 8 | 4 | 62 | 52.14 | 4202.484
Sales |  | I75/1 | 3 | 0.075 | 0.225 | CFQ23/1 | 3 | 0.026 | 0.078 | 10 | 10 | 10 | 10 | 10 | 8 | 4 | 62 | 52.14 | 475.204
Canopy |  | F43EE | 1 | 0.115 | 0.115 | F43ILL-R | 1 | 0.076 | 0.076 | 10 | 10 | 10 | 10 | 10 | 8 | 4 | 62 | 52.14 | 126.0745
Total for EEM | [18 empty] | 11268.4968
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response (i.e., re Sunday) and per recognition of 365 day year.
Survey response also indicated that 2 fixtures are left on 24/7, so the F42EE record (with relatively conservative demand savings) was split into 2 rows to incorporate those comments.
Overall Application Adjusted Savings: | [18 empty] | 11268.4968
CFL portion of Lighting Savings: | [18 empty] | 4677.688
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 11268.4968
Comments: none

## 14023
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 14023
Date of ASW SBEA Database Extract Used: |  |  | 2003-11-14
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-06-27 | 3774 | 3769 | 3774
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 3774 | 3769 | 3774
Comments: lighting "details" value based on line items 1-2 and 4-6.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Stairwell 1 |  | F41EE | 2 | 0.043 | 0.086 | F41ILL-R | 2 | 0.027 | 0.054 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 279.552
Stairwell 2 |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.052 | 0.312 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1048.32
Stairwell Dif |  | F42EE | 2 | 0.072 | 0.144 | F42ILL-R | 2 | 0.052 | 0.104 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 349.44
RR |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.052 | 0.52 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1747.2
Mech Rm |  | F42EE | 2 | 0.072 | 0.144 | F42ILL-R | 2 | 0.052 | 0.104 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 349.44
Total for EEM | [18 empty] | 3773.952
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3773.952
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Stairwell 1 |  | F41EE | 2 | 0.043 | 0.086 | F41ILL-R | 2 | 0.026 | 0.052 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 297.024
Stairwell 2 |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.051 | 0.306 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1100.736
Stairwell Dif |  | F42EE | 2 | 0.072 | 0.144 | F42ILL-R | 2 | 0.051 | 0.102 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 366.912
RR |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.051 | 0.51 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1834.56
Mech Rm |  | F42EE | 2 | 0.072 | 0.144 | F42ILL-R | 2 | 0.051 | 0.102 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 366.912
Total for EEM | [18 empty] | 3966.144
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F41ILL-R and F42ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3966.144
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Stairwell 1 |  | F41EE | 2 | 0.043 | 0.086 | F41ILL-R | 2 | 0.026 | 0.052 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 297.8237
Stairwell 2 |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.051 | 0.306 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1103.6995
Stairwell Dif |  | F42EE | 2 | 0.072 | 0.144 | F42ILL-R | 2 | 0.051 | 0.102 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 367.8998
RR |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.051 | 0.51 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1839.4992
Mech Rm |  | F42EE | 2 | 0.072 | 0.144 | F42ILL-R | 2 | 0.051 | 0.102 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 367.8998
Total for EEM | [18 empty] | 3976.8221
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 3976.8221
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 3976.8221
Comments: none

## 16023
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 16023
Date of ASW SBEA Database Extract Used: |  |  | 2003-11-14
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2002-11-08 | 1533 | 1693 | 1697
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 1533 | 1693 | 1697
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Salon |  | F43SE | 6 | 0.14 | 0.84 | F43ILL-R | 6 | 0.078 | 0.468 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52 | 1238.016
Salon |  | F42SE | 4 | 0.086 | 0.344 | F42ILL-R | 4 | 0.052 | 0.208 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52 | 452.608
Total for EEM | [18 empty] | 1690.624
Comments: all data per per paperwork. Note that paperwork "detail" savings (1697 kwh w/o AC savings, 2003 with AC savings) disagrees with paperwork page 1 & "measure status"
TBL data (2003 kwh). Paperwork detail savings data used, per recency and detail considerations.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1690.624
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Salon |  | F43SE | 6 | 0.14 | 0.84 | F43ILL-R | 6 | 0.076 | 0.456 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52 | 1277.952
Salon |  | F42SE | 4 | 0.086 | 0.344 | F42ILL-R | 4 | 0.051 | 0.204 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52 | 465.92
Total for EEM | [18 empty] | 1743.872
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F43ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1743.872
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Salon |  | F43SE | 6 | 0.14 | 0.84 | F43ILL-R | 6 | 0.076 | 0.456 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52.14 | 1281.3926
Salon |  | F42SE | 4 | 0.086 | 0.344 | F42ILL-R | 4 | 0.051 | 0.204 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52.14 | 467.1744
Total for EEM | [18 empty] | 1748.567
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year. Survey response indicated that 1 security
light is kept on 24/7, but it is not obvious that all lights were included in the retrofit, so comments re security lighting ignored for conservatism/defensibility in energy savings calcs.
Overall Application Adjusted Savings: | [18 empty] | 1748.567
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1748.567
Comments: none

## 16085
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 16085
Date of ASW SBEA Database Extract Used: |  |  | 2003-11-14
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-03-04 | 2523 | 2523 | 2523
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 2523 | 2523 | 2523
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F44ILL-R | 15 | 0.102 | 1.53 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52 | 2522.52
Total for EEM | [18 empty] | 2522.52
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2522.52
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F44ILL-R | 15 | 0.098 | 1.47 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52 | 2762.76
Total for EEM | [18 empty] | 2762.76
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R value derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2762.76
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F44ILL-R | 15 | 0.098 | 1.47 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 80.5 | 52.14 | 2896.1163
Total for EEM | [18 empty] | 2896.1163
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year, and per survey response re op hours.
Survey also indicated that one lamp is kept on 24/7, but since it is not obvious that all lights were included in the retrofit, comments re security lighting ignored for conservatism/defensibility
in energy savings calcs.
Overall Application Adjusted Savings: | [18 empty] | 2896.1163
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 2896.1163
Comments: none

## 16090
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 16090
Date of ASW SBEA Database Extract Used: |  |  | 2003-11-14
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-02-26 | 6956 | 6956 | 6956
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 6956 | 6956 | 6956
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Various |  | F44EE | 35 | 0.144 | 5.04 | F44ILL-R | 35 | 0.102 | 3.57 | 13 | 13 | 13 | 13 | 13 | 14 | 12 | 91 | 52 | 6956.04
Total for EEM | [18 empty] | 6956.04
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 6956.04
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Various |  | F44EE | 35 | 0.144 | 5.04 | F44ILL-R | 35 | 0.098 | 3.43 | 13 | 13 | 13 | 13 | 13 | 14 | 12 | 91 | 52 | 7618.52
Total for EEM | [18 empty] | 7618.52
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R value derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 7618.52
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Various |  | F44EE | 35 | 0.144 | 5.04 | F44ILL-R | 35 | 0.098 | 3.43 | 13 | 13 | 13 | 13 | 13 | 14 | 12 | 91 | 52.14 | 7639.0314
Total for EEM | [18 empty] | 7639.0314
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 7639.0314
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 7639.0314
Comments: none

## 16107
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 16107
Date of ASW SBEA Database Extract Used: |  |  | 2003-11-14
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-04-24 | 1579 | 1579 | 1579
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 1579 | 1579 | 1579
Comments: lighting "details" value based on line items 1-3.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Various |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.102 | 1.02 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 1375.92
Various |  | F82EE | 2 | 0.123 | 0.246 | F82ILL | 2 | 0.109 | 0.218 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 91.728
Various |  | F42EE | 1 | 0.086 | 0.086 | F42ILL-R | 1 | 0.052 | 0.052 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 111.384
Total for EEM | [18 empty] | 1579.032
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1579.032
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Various |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.098 | 0.98 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 1506.96
Various |  | F82EE | 2 | 0.123 | 0.246 | F82ILL | 2 | 0.109 | 0.218 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 91.728
Various |  | F42EE | 1 | 0.086 | 0.086 | F42ILL-R | 1 | 0.051 | 0.051 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 114.66
Total for EEM | [18 empty] | 1713.348
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1713.348
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Various |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.098 | 0.98 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 66 | 52.14 | 1582.9704
Various |  | F82EE | 2 | 0.123 | 0.246 | F82ILL | 2 | 0.109 | 0.218 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 66 | 52.14 | 96.3547
Various |  | F42EE | 1 | 0.086 | 0.086 | F42ILL-R | 1 | 0.051 | 0.051 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 66 | 52.14 | 120.4434
Total for EEM | [18 empty] | 1799.7685
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year, and based on survey response.
Overall Application Adjusted Savings: | [18 empty] | 1799.7685
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1799.7685
Comments: none

## 16145
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 16145
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-08-26 | 10297 | 9492 | 10297
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 10297 | 9492 | 10297
Comments: lighting "details" value based on line items 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Floor |  | F42SE | 59 | 0.086 | 5.074 | F42ILL-R | 59 | 0.052 | 3.068 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 91 | 52 | 9492.392
Total for EEM | [18 empty] | 9492.392
Comments: all data per per paperwork. Calculated savings differs from paperwork-indicated savings of 10,297. New fixture indicated as F42ILL on calc sheet, but F42ILL-R
on invoice (latter value used, since tied to an actual cost).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 9492.392
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Floor |  | F42SE | 59 | 0.086 | 5.074 | F42ILL-R | 59 | 0.051 | 3.009 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 91 | 52 | 9771.58
Total for EEM | [18 empty] | 9771.58
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 9771.58
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Floor |  | F42SE | 59 | 0.086 | 5.074 | F42ILL-R | 59 | 0.051 | 3.009 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 91 | 52.14 | 9797.8881
Total for EEM | [18 empty] | 9797.8881
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 9797.8881
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 9797.8881
Comments: none

## 17029
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17029
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-04-18 | 3894 | 4380 | 3894
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 3894 | 4380 | 3894
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 13 | 0.172 | 2.236 | F42ILL-R | 13 | 0.052 | 0.676 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 48 | 52 | 3893.76
Total for EEM | [18 empty] | 3893.76
Comments: all data per per paperwork. 8 hr/day, 6 day/week operation inferred from 48 hr/wk in paperwork. Installed fixture F42ILL-R determined from installation report (was
listed as F42ILL on calc sheet).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3893.76
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 13 | 0.172 | 2.236 | F42ILL-R | 13 | 0.051 | 0.663 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 48 | 52 | 3926.208
Total for EEM | [18 empty] | 3926.208
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3926.208
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 13 | 0.172 | 2.236 | F42ILL-R | 13 | 0.051 | 0.663 | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 54 | 52.14 | 4428.8759
Total for EEM | [18 empty] | 4428.8759
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 4428.8759
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 4428.8759
Comments: none

## 17041
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17041
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2002-12-20 | 2995 | 1747 | 2995
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 2995 | 1747 | 2995
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 16 | 0.174 | 2.784 | F44ILL-R | 16 | 0.102 | 1.632 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 52 | 2995.2
Total for EEM | [18 empty] | 2995.2
Comments: all data per per paperwork. kW value for F44SE appears to be typo (corrected in Step 3).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2995.2
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 16 | 0.144 | 2.304 | F44ILL-R | 16 | 0.098 | 1.568 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 52 | 1913.6
Total for EEM | [18 empty] | 1913.6
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: step 2 value corrected.
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1913.6
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 16 | 0.144 | 2.304 | F44ILL-R | 16 | 0.098 | 1.568 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 52.14 | 1918.752
Total for EEM | [18 empty] | 1918.752
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 1918.752
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1918.752
Comments: none

## 17044
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17044
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-03-14 | 811 | 811 | 811
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat | 2003-02-28 | 451 | 451 | 451
Overall |  | 1262 | 1262 | 1262
Comments: lighting "details" value based on line items 2-3; tstat "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Offices |  | F44EE | 6 | 0.144 | 0.864 | F44ILL-R | 6 | 0.102 | 0.612 | 9 | 9 | 9 | 9 | 9 | 5 | 0 | 50 | 52 | 655.2
Storage |  | F42SE | 3 | 0.072 | 0.216 | F42ILL-R | 3 | 0.052 | 0.156 | 9 | 9 | 9 | 9 | 9 | 5 | 0 | 50 | 52 | 156
Total for EEM | [18 empty] | 811.2
Comments: all data per per paperwork. Fixture listed as F42ILL on calc sheet, F42ILL-R on invoice (latter spec used, since tied to a cost).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 3.5 | 62% | 2600 | 1 | 8% | [12 empty] | 451.36
Comments: all data per per paperwork.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1262.56
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Offices |  | F44EE | 6 | 0.144 | 0.864 | F44ILL-R | 6 | 0.098 | 0.588 | 9 | 9 | 9 | 9 | 9 | 5 | 0 | 50 | 52 | 717.6
Storage |  | F42SE | 3 | 0.072 | 0.216 | F42ILL-R | 3 | 0.051 | 0.153 | 9 | 9 | 9 | 9 | 9 | 5 | 0 | 50 | 52 | 163.8
Total for EEM | [18 empty] | 881.4
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 3.5 | 0.62 | 1950 | 1.3 | 15% | [12 empty] | 825.1425
Comments: kW/ton and % savings data adjusted per S&A 2/04 research re package rooftop units. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1706.5425
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Offices |  | F44EE | 6 | 0.144 | 0.864 | F44ILL-R | 6 | 0.098 | 0.588 | 9 | 9 | 9 | 9 | 9 | 5 | 0 | 50 | 52.14 | 719.532
Storage |  | F42SE | 3 | 0.072 | 0.216 | F42ILL-R | 3 | 0.051 | 0.153 | 9 | 9 | 9 | 9 | 9 | 5 | 0 | 50 | 52.14 | 164.241
Total for EEM | [18 empty] | 883.773
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 1708.9155
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1708.9155
Comments: none

## 17048
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17048
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-04-11 | 2970 | 2953 | 2970
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 2970 | 2953 | 2970
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.102 | 1.734 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 48 | 52 | 2970.24
Total for EEM | [18 empty] | 2970.24
Comments: all data per per paperwork. 48 hr/wk assumption mapped to a 8 hour day for Mon-Sat.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2970.24
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.098 | 1.666 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 48 | 52 | 3139.968
Total for EEM | [18 empty] | 3139.968
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3139.968
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.098 | 1.666 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52.14 | 2951.6454
Total for EEM | [18 empty] | 2951.6454
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 2951.6454
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 2951.6454
Comments: none

## 17052
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17052
Date of ASW SBEA Database Extract Used: |  |  | 2003-11-14
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-06-30 | 1945 | 1944 | 1945
Refrig. Tune-up | 2003-05-27 | 1759 | 1759 | 1759
AC Tune-up | 2003-05-27 | 452 | 0 | 452
T-stat |  | 0 | 0 | 0
Overall |  | 4156 | 3703 | 4156
Comments: lighting "details" value based on line items 1-2; Refrig. Tune-up "details" value based on line item 1. No AC Tune-up "details" record available.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F42SE | 8 | 0.086 | 0.688 | F42ILL-R | 8 | 0.052 | 0.416 | 16 | 16 | 16 | 16 | 16 | 5 | 16 | 101 | 52 | 1428.544
Back Room |  | F42SE | 3 | 0.086 | 0.258 | F42ILL-R | 3 | 0.052 | 0.156 | 16 | 16 | 16 | 16 | 16 | 5 | 16 | 101 | 52 | 535.704
Total for EEM | [18 empty] | 1964.248
Comments: all data per per paperwork. Minor disagreement with database re Sunday hours.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Meats |  | 0.51 | 1.549 | 8760 | 80% | 6% | [12 empty] | 332.175
Milk |  | 0.46 | 1.549 | 8760 | 80% | 6% | [12 empty] | 299.6088
Cheese & H-Dogs |  | 0.48 | 1.549 | 8760 | 80% | 6% | [12 empty] | 312.6353
Bagged Produce |  | 0.205 | 1.549 | 8760 | 80% | 6% | [12 empty] | 133.5213
Cold Drinks |  | 0.535 | 1.549 | 8760 | 80% | 6% | [12 empty] | 348.4581
Frozen Food |  | 0.51 | 2.548 | 8760 | 80% | 6% | [12 empty] | 546.4054
Total for EEM | [18 empty] | 1972.8039
Comments: all data per per paperwork. Tonnage calcs in paperwork for frozen food case used 1.549 kW/ton, rather than the appropriate 2.548 kW/ton factor.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 3 | 58% | 5200 | 1 | 5% | [12 empty] | 452.4
Comments: all data per per paperwork.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 4389.4519
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F42SE | 8 | 0.086 | 0.688 | F42ILL-R | 8 | 0.051 | 0.408 | 16 | 16 | 16 | 16 | 16 | 5 | 16 | 101 | 52 | 1470.56
Back Room |  | F42SE | 3 | 0.086 | 0.258 | F42ILL-R | 3 | 0.051 | 0.153 | 16 | 16 | 16 | 16 | 16 | 5 | 16 | 101 | 52 | 551.46
Total for EEM | [18 empty] | 2022.02
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R value derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Meats |  | 0.5 | 2 | 8760 | 80% | 1.5% | [12 empty] | 105.12
Milk |  | 0.5 | 2 | 8760 | 80% | 1.5% | [12 empty] | 105.12
Cheese & H-Dogs |  | 0.5 | 2 | 8760 | 80% | 1.5% | [12 empty] | 105.12
Bagged Produce |  | 0.25 | 2 | 8760 | 80% | 1.5% | [12 empty] | 52.56
Cold Drinks |  | 0.75 | 2 | 8760 | 80% | 1.5% | [12 empty] | 157.68
Frozen Food |  | 0.69333 | 2.55 | 8760 | 80% | 1.5% | [12 empty] | 185.8522
Total for EEM | [18 empty] | 711.4522
Comments: tonnage data updated per ADL DOE study; kW/ton data updated per S&A 4/04 research; load factors rely on default/paperwork; % savings updated per S&A 4/04 research.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 3 | 58% | 3900 | 1.3 | 5% | [12 empty] | 441.09
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3174.5622
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F42SE | 8 | 0.086 | 0.688 | F42ILL-R | 8 | 0.051 | 0.408 | 16 | 16 | 16 | 16 | 16 | 0 | 15 | 95 | 52.14 | 1386.924
Back Room |  | F42SE | 3 | 0.086 | 0.258 | F42ILL-R | 3 | 0.051 | 0.153 | 16 | 16 | 16 | 16 | 16 | 0 | 15 | 95 | 52.14 | 520.0965
Total for EEM | [18 empty] | 1907.0205
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 3059.5627
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 3059.5627
Comments: none

## 17054
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17054
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-06-29 | 6238 | 6205 | 6238
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 6238 | 6205 | 6238
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Offices |  | F44SE | 30 | 0.172 | 5.16 | F44ILL-R | 30 | 0.102 | 3.06 | 9 | 9 | 9 | 9 | 9 | 6 | 0 | 51 | 52 | 5569.2
Storage |  | F82EE | 12 | 0.123 | 1.476 | F44ILL-R | 12 | 0.102 | 1.224 | 9 | 9 | 9 | 9 | 9 | 6 | 0 | 51 | 52 | 668.304
Total for EEM | [18 empty] | 6237.504
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 6237.504
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Offices |  | F44SE | 30 | 0.172 | 5.16 | F44ILL-R | 30 | 0.098 | 2.94 | 9 | 9 | 9 | 9 | 9 | 6 | 0 | 51 | 52 | 5887.44
Storage |  | F82EE | 12 | 0.123 | 1.476 | F44ILL-R | 12 | 0.098 | 1.176 | 9 | 9 | 9 | 9 | 9 | 6 | 0 | 51 | 52 | 795.6
Total for EEM | [18 empty] | 6683.04
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 6683.04
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Offices |  | F44SE | 30 | 0.172 | 5.16 | F44ILL-R | 30 | 0.098 | 2.94 | 9 | 9 | 9 | 9 | 9 | 6 | 0 | 51 | 52.14 | 5903.2908
Storage |  | F82EE | 12 | 0.123 | 1.476 | F44ILL-R | 12 | 0.098 | 1.176 | 9 | 9 | 9 | 9 | 9 | 6 | 0 | 51 | 52.14 | 797.742
Total for EEM | [18 empty] | 6701.0328
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 6701.0328
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 6701.0328
Comments: none

## 17058
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17058
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-07-02 | 1245 | 1238 | 1245
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 1245 | 1238 | 1245
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Show Room |  | F44SE | 6 | 0.172 | 1.032 | F44ILL-R | 6 | 0.102 | 0.612 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 57 | 52 | 1244.88
Total for EEM | [18 empty] | 1244.88
Comments: all data per per paperwork; op hrs also per "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1244.88
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Show Room |  | F44SE | 6 | 0.172 | 1.032 | F44ILL-R | 6 | 0.098 | 0.588 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 57 | 52 | 1316.016
Total for EEM | [18 empty] | 1316.016
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1316.016
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Show Room |  | F44SE | 6 | 0.172 | 1.032 | F44ILL-R | 6 | 0.098 | 0.588 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 57 | 52.14 | 1319.5591
Total for EEM | [18 empty] | 1319.5591
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 1319.5591
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1319.5591
Comments: none

## 17072
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17072
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2004-06-05 | 20049 | 20049 | 20049
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 20049 | 20049 | 20049
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling Cans |  | I60 | 48 | 0.06 | 2.88 | CFL15 | 48 | 0.015 | 0.72 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52 | 14152.32
Hanging Lamp |  | I65 | 18 | 0.065 | 1.17 | CFL15 | 18 | 0.015 | 0.27 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52 | 5896.8
Total for EEM | [18 empty] | 20049.12
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 20049.12
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling Cans |  | I60 | 48 | 0.06 | 2.88 | CFL15 | 48 | 0.015 | 0.72 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52 | 14152.32
Hanging Lamp |  | I65 | 18 | 0.065 | 1.17 | CFL15 | 18 | 0.015 | 0.27 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52 | 5896.8
Total for EEM | [18 empty] | 20049.12
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: values appear reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 20049.12
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling Cans |  | I60 | 48 | 0.06 | 2.88 | CFL15 | 48 | 0.015 | 0.72 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 20.5 | 20.5 | 138.5 | 52.14 | 15598.2024
Hanging Lamp |  | I65 | 18 | 0.065 | 1.17 | CFL15 | 18 | 0.015 | 0.27 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 20.5 | 20.5 | 138.5 | 52.14 | 6499.251
Total for EEM | [18 empty] | 22097.4534
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 22097.4534
CFL portion of Lighting Savings: | [18 empty] | 22097.4534
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 22097.4534
Comments: none

## 17089
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17089
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting |  | 0 | 0 | 0
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat | 2003-08-11 | 433 | 0 | 433
Overall |  | 433 | 0 | 433
Comments: no record in tstat "details" TBL.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  |  |  |  | 0 |  |  |  | kW: 0; Operational Data (hrs by day) Sum: 0; Operational Data (hrs by day) Wk/Yr: 52 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 3.5 | 62% | 2496 | 1 | 8% | [12 empty] | 433.3056
Comments: all data per per paperwork.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 433.3056
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 | 0.144 | 0 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 3.5 | 0.62 | 1872 | 1.3 | 15% | [12 empty] | 792.1368
Comments: kW/ton and % savings data adjusted per S&A 2/04 research re package rooftop units. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 792.1368
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 | 0.144 | 0 | 0 | 0 | 0.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.14 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Overall Application Adjusted Savings: | [18 empty] | 792.1368
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 792.1368
Comments: none

## 17096
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 17096
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-11-21 | 17816 | 17815 | 17816
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 17816 | 17815 | 17816
Comments: lighting "details" value based on line items 1-8 and 11.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
OFFICE |  | 8' 4-4' lamp T-12 | 3 | 0.144 | 0.432 | 8' 4-4' lamp T8 | 3 | 0.09 | 0.27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1419.0422
EXTERIOR |  | 400W MV | 14 | 0.458 | 6.412 | 250W MH | 14 | 0.295 | 4.13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 9994.6123
LOBBY/ENTRANCE |  | 8' 4-4' lamp T-12 | 5 | 0.144 | 0.72 | 8' 4-4' lamp T8 | 5 | 0.09 | 0.45 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 2365.0704
STORAGE |  | 75w Inca Fixture | 1 | 0.075 | 0.075 | 26w Ceiling Drum | 1 | 0.027 | 0.027 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52.14 | 112.6224
LOCKER |  | 8' 4-4' lamp T-12 | 2 | 0.144 | 0.288 | 8' 4-4' lamp T8 | 2 | 0.09 | 0.18 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 946.0282
MEN RESTROOM |  | 1-60w Incadescents | 3 | 0.06 | 0.18 | 1-18W CFL S/I | 3 | 0.02 | 0.06 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1051.1424
WOMEN RESTROOM |  | 1-60w Incadescents | 3 | 0.06 | 0.18 | 1-18W CFL S/I | 3 | 0.02 | 0.06 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1051.1424
RESTROOM HALL |  | 4' 2-4' lamp T-12 | 2 | 0.072 | 0.144 | 4' 2-4' lamp T-8 | 2 | 0.046 | 0.092 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 455.495
METER ROOM |  | 75w Inca Fixture | 1 | 0.075 | 0.075 | 26w Ceiling Drum | 1 | 0.027 | 0.027 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 420.457
Total for EEM | [18 empty] | 17815.6123
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 17815.6123
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
OFFICE |  | F44EE | 3 | 0.144 | 0.432 | F44ILL | 3 | 0.112 | 0.336 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 840.9139
EXTERIOR |  | MV400/1 | 14 | 0.455 | 6.37 | MH250/1 | 14 | 0.288 | 4.032 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 10239.8789
LOBBY/ENTRANCE |  | F44EE | 5 | 0.144 | 0.72 | F44ILL | 5 | 0.112 | 0.56 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1401.5232
STORAGE |  | I75/1 | 1 | 0.075 | 0.075 | CF26/1-SCRW | 1 | 0.026 | 0.026 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52.14 | 114.9687
LOCKER |  | F44EE | 2 | 0.144 | 0.288 | F44ILL | 2 | 0.112 | 0.224 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 560.6093
MEN RESTROOM |  | I60/1 | 3 | 0.06 | 0.18 | CF18/1-SCRW | 3 | 0.018 | 0.054 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1103.6995
WOMEN RESTROOM |  | I60/1 | 3 | 0.06 | 0.18 | CF18/1-SCRW | 3 | 0.018 | 0.054 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1103.6995
RESTROOM HALL |  | F42EE | 2 | 0.072 | 0.144 | F42ILL/T4 | 2 | 0.059 | 0.118 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 227.7475
METER ROOM |  | I75/1 | 1 | 0.075 | 0.075 | CF26/1-SCRW | 1 | 0.026 | 0.026 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 429.2165
Total for EEM | [18 empty] | 16022.257
Comments: step 2 fixture descriptions (non-standard EIG values) mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures assumed since
Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 16022.257
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 0.95
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
OFFICE |  | F44EE | 3 | 0.144 | 0.432 | F44ILL | 3 | 0.112 | 0.336 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 840.9139
EXTERIOR |  | MV400/1 | 14 | 0.455 | 6.37 | MH250/1 | 14 | 0.288 | 4.032 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 10239.8789
LOBBY/ENTRANCE |  | F44EE | 5 | 0.144 | 0.72 | F44ILL | 5 | 0.112 | 0.56 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1401.5232
STORAGE |  | I75/1 | 1 | 0.075 | 0.075 | CF26/1-SCRW | 1 | 0.026 | 0.026 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52.14 | 114.9687
LOCKER |  | F44EE | 2 | 0.144 | 0.288 | F44ILL | 2 | 0.112 | 0.224 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 560.6093
MEN RESTROOM |  | I60/1 | 3 | 0.06 | 0.18 | CF18/1-SCRW | 3 | 0.018 | 0.054 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1103.6995
WOMEN RESTROOM |  | I60/1 | 3 | 0.06 | 0.18 | CF18/1-SCRW | 3 | 0.018 | 0.054 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1103.6995
RESTROOM HALL |  | F42EE | 2 | 0.072 | 0.144 | F42ILL/T4 | 2 | 0.059 | 0.118 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 227.7475
METER ROOM |  | I75/1 | 1 | 0.075 | 0.075 | CF26/1-SCRW | 1 | 0.026 | 0.026 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 429.2165
Total for EEM | [18 empty] | 16022.257
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours left unchanged. Survey results "overridden" (i.e., not changed) for storage area
since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 15221.1442
CFL portion of Lighting Savings: | [18 empty] | 2751.5842
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 15221.1442
Comments: none

## 19058
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 19058
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-01-24 | 1743 | 1743 | 1743
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat | 2003-01-24 | 370 | 451 | 370
Overall |  | 2113 | 2194 | 2113
Comments: lighting "details" value based on line item 1; tstat "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Store |  | F44EE | 14 | 0.144 | 2.016 | F44ILL-R | 14 | 0.102 | 1.428 | 10 | 10 | 10 | 10 | 10 | 7 | 0 | 57 | 52 | 1742.832
Total for EEM | [18 empty] | 1742.832
Comments: all data per per paperwork. Fixture listed as F42ILL on calc sheet, F42ILL-R on invoice (latter spec used, since tied to a cost).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail No Economizer |  | 3 | 52% | 2964 | 1 | 8% | [12 empty] | 369.9072
Comments: all data per per paperwork. Note that LF of 52% is for Coastal, Small Retail, No Economizer, when in fact the 58% LF for Inland, Small Retail, No Economizer should have
been applied. This issue corrected in Step 3.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2112.7392
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Store |  | F44EE | 14 | 0.144 | 2.016 | F44ILL-R | 14 | 0.098 | 1.372 | 10 | 10 | 10 | 10 | 10 | 7 | 0 | 57 | 52 | 1908.816
Total for EEM | [18 empty] | 1908.816
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail No Economizer |  | 3 | 0.58 | 2223 | 1.3 | 15% | [12 empty] | 754.2639
Comments: kW/ton and % savings data adjusted per S&A 2/04 research re package rooftop units. Load factor corrected to reflect inland small retail with no economizer.
Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2663.0799
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Store |  | F44EE | 14 | 0.144 | 2.016 | F44ILL-R | 14 | 0.098 | 1.372 | 9 | 9 | 9 | 9 | 9 | 6.5 | 0 | 51.5 | 52.14 | 1729.2752
Total for EEM | [18 empty] | 1729.2752
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 2483.5391
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 2483.5391
Comments: none

## 20180
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 20180
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting |  | 0 | 0 | 0
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up | 2003-04-03 | 1949 | 1949 | 1949
T-stat |  | 0 | 0 | 0
Overall |  | 1949 | 1949 | 1949
Comments: AC tuneup "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  |  |  |  | 0 |  |  |  | kW: 0; Operational Data (hrs by day) Sum: 0; Operational Data (hrs by day) Wk/Yr: 52 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 23.5 | 58% | 2860 | 1 | 5% | [12 empty] | 1949.09
Comments: all data per per paperwork. Small retail load factor used for this premise (a manufacturing facility); all things considered, the most reasonable (and conservative) data.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1949.09
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 13.5 | 0.58 | 2145 | 1.1 | 5% | [12 empty] | 923.7442
Inland, Small Retail, No Economizer |  | 10 | 0.58 | 2145 | 1.3 | 5% | [12 empty] | 808.665
Total for EEM | [18 empty] | 1732.4092
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. Record split into 2 parts using details provided in EEM paperwork to accommodate AC unit tonnage
ranges (and corresponding S&A kW/ton factor). Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1732.4092
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM
- Refrig. Tune-up EEM
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM
- Refrig. Tune-up EEM
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.14 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Overall Application Adjusted Savings: | [18 empty] | 1732.4092
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1732.4092
Comments: none

## 22093
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 22093
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-05-16 | 3713 | 3692 | 3713
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 3713 | 3692 | 3713
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Salon |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.102 | 1.734 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 12.5 | 0 | 60 | 52 | 3712.8
Total for EEM | [18 empty] | 3712.8
Comments: all data per per paperwork (fixture spec per lighting installation rpt); op hrs also per "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3712.8
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Salon |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.098 | 1.666 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 12.5 | 0 | 60 | 52 | 3924.96
Total for EEM | [18 empty] | 3924.96
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3924.96
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Salon |  | F44SE | 17 | 0.172 | 2.924 | F44ILL-R | 17 | 0.098 | 1.666 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 12.5 | 0 | 60 | 52.14 | 3935.5272
Total for EEM | [18 empty] | 3935.5272
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 3935.5272
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 3935.5272
Comments: none

## 22110
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 22110
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-02-03 | 4093 | 4903 | 4093
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 4093 | 4903 | 4093
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Dining/Kitchen |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.102 | 1.02 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1834.56
Dining |  | I60 | 11 | 0.06 | 0.66 | CFQ11/1 | 11 | 0.013 | 0.143 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2258.256
Total for EEM | [18 empty] | 4092.816
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 4092.816
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Dining/Kitchen |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.098 | 0.98 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2009.28
Dining |  | I60 | 11 | 0.06 | 0.66 | CFQ18/1 | 11 | 0.026 | 0.286 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1633.632
Total for EEM | [18 empty] | 3642.912
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data. Fixture type changed to CFQ18/1 per Lighting Installation Report (kW value per 2003 SPC table).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3642.912
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Dining/Kitchen |  | F44EE | 10 | 0.144 | 1.44 | F44ILL-R | 10 | 0.098 | 0.98 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 2014.6896
Dining |  | I60 | 11 | 0.06 | 0.66 | CFQ18/1 | 11 | 0.026 | 0.286 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1638.0302
Total for EEM | [18 empty] | 3652.7198
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 3652.7198
CFL portion of Lighting Savings: | [18 empty] | 1638.0302
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 3652.7198
Comments: none

## 23079
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23079
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2002-10-11 | 2402 | 2402 | 2402
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 2402 | 2402 | 2402
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling |  | F44EE | 20 | 0.144 | 2.88 | F44ILL-R | 20 | 0.102 | 2.04 | 9 | 9 | 9 | 9 | 9 | 10 | 0 | 55 | 52 | 2402.4
Total for EEM | [18 empty] | 2402.4
Comments: all data per per paperwork. 55 hour week allocated to days using S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2402.4
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling |  | F44EE | 20 | 0.144 | 2.88 | F44ILL-R | 20 | 0.098 | 1.96 | 9 | 9 | 9 | 9 | 9 | 10 | 0 | 55 | 52 | 2631.2
Total for EEM | [18 empty] | 2631.2
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 2631.2
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling |  | F44EE | 20 | 0.144 | 2.88 | F44ILL-R | 20 | 0.098 | 1.96 | 9 | 9 | 9 | 10 | 9 | 10 | 0 | 56 | 52.14 | 2686.2528
Total for EEM | [18 empty] | 2686.2528
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 2686.2528
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 2686.2528
Comments: none

## 23086
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23086
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2002-10-11 | 3034 | 3034 | 3034
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 3034 | 3034 | 3034
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling |  | F44EE | 13 | 0.144 | 1.872 | F43ILL-R | 13 | 0.078 | 1.014 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 68 | 52 | 3033.888
Total for EEM | [18 empty] | 3033.888
Comments: all data per per paperwork. Hours by day per "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3033.888
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling |  | F44EE | 13 | 0.144 | 1.872 | F43ILL-R | 13 | 0.076 | 0.988 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 68 | 52 | 3125.824
Total for EEM | [18 empty] | 3125.824
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3125.824
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Ceiling |  | F44EE | 13 | 0.144 | 1.872 | F43ILL-R | 13 | 0.076 | 0.988 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 68 | 52.14 | 3134.2397
Total for EEM | [18 empty] | 3134.2397
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 3134.2397
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 3134.2397
Comments: none

## 23173
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23173
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2002-12-20 | 5257 | 4451 | 4455
Refrig. Tune-up | 2002-12-20 | 10421 | 10421 | 10421
AC Tune-up | 2002-12-20 | 950 | 950 | 950
T-stat |  | 0 | 0 | 0
Overall |  | 16628 | 15822 | 15826
Comments: lighting "details" value based on line item 1; Refrig. Tune-up and AC Tune-up "details" values each based on line item 1.
Lighting measure value in "Measure Status" TBL appears to include AC savings.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Main Area |  | F42EE | 34 | 0.072 | 2.448 | F42ILL-R | 34 | 0.052 | 1.768 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52 | 4455.36
Total for EEM | [18 empty] | 4455.36
Comments: all data per per paperwork (F42ILL in calc sheet adjusted to F42ILL-R per Lighting Installation Report).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Produce Prep |  | 16 | 1.549 | 8760 | 80% | 6% | [12 empty] | 10421.1763
Total for EEM | [18 empty] | 10421.1763
Comments: all data per per paperwork.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 5 | 58% | 6552 | 1 | 5% | [12 empty] | 950.04
Comments: all data per per paperwork.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 15826.5763
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Main Area |  | F42EE | 34 | 0.072 | 2.448 | F42ILL-R | 34 | 0.051 | 1.734 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52 | 4678.128
Total for EEM | [18 empty] | 4678.128
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R value derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Produce Prep |  | 1.6 | 2 | 8760 | 80% | 1.5% | [12 empty] | 336.384
Total for EEM | [18 empty] | 336.384
Comments: tonnage data updated per ADL DOE study; kW/ton data updated per S&A 4/04 research; load factors rely on default/paperwork; % savings updated per S&A 4/04 research.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 5 | 58% | 4914 | 1.3 | 5% | [12 empty] | 926.289
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 5940.801
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Main Area |  | F42EE | 34 | 0.072 | 2.448 | F42ILL-R | 34 | 0.051 | 1.734 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 140 | 52.14 | 5211.9144
Total for EEM | [18 empty] | 5211.9144
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response (1/3 of all lights left on 24/7, hence wtd avg hrs = 20), and
per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 6474.5874
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 6474.5874
Comments: none

## 23271
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23271
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2002-12-20 | 15215 | 15215 | 15215
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 15215 | 15215 | 15215
Comments: lighting "details" value based on line items 1-4.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F44SE | 63 | 0.144 | 9.072 | F44ILL-R | 63 | 0.102 | 6.426 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 9218.664
Sales Area |  | F42SE | 23 | 0.086 | 1.978 | F42ILL-R | 23 | 0.052 | 1.196 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 2724.488
Sales Area |  | F21SE | 3 | 0.028 | 0.084 | F21ILL-R | 3 | 0.015 | 0.045 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 135.876
Sales Area |  | I50/1 | 30 | 0.05 | 1.5 | CFQ15/1 | 30 | 0.02 | 0.6 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 3135.6
Total for EEM | [18 empty] | 15214.628
Comments: all data per per paperwork. ILL fixtures listed on calc sheet changed to ILL-R per Lighting Descriptions/Misc sheet.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 15214.628
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F44SE | 63 | 0.144 | 9.072 | F44ILL-R | 63 | 0.098 | 6.174 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 10096.632
Sales Area |  | F42SE | 23 | 0.086 | 1.978 | F42ILL-R | 23 | 0.051 | 1.173 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 2804.62
Sales Area |  | F21SE | 3 | 0.028 | 0.084 | F21ILL-R | 3 | 0.015 | 0.045 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 135.876
Sales Area |  | I50/1 | 0 | 0.05 | 0 | CFQ15/1 | 0 | 0.02 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 67 | 52 | 0
Total for EEM | [18 empty] | 13037.128
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R and F42ILL-R values derived using 2002 Sylvania catalog data. Incandescent to CFQ line item zeroed out per comments in Lighting Installation Report.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 13037.128
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F44SE | 63 | 0.144 | 9.072 | F44ILL-R | 63 | 0.098 | 6.174 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52.14 | 9670.5101
Sales Area |  | F42SE | 23 | 0.086 | 1.978 | F42ILL-R | 23 | 0.051 | 1.173 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52.14 | 2686.2528
Sales Area |  | F21SE | 3 | 0.028 | 0.084 | F21ILL-R | 3 | 0.015 | 0.045 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52.14 | 130.1414
Sales Area |  | I50/1 | 0 | 0.05 | 0 | CFQ15/1 | 0 | 0.02 | 0 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 7 | 64 | 52.14 | 0
Total for EEM | [18 empty] | 12486.9043
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 12486.9043
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 12486.9043
Comments: none

## 23478
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23478
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-06-02 | 13123 | 11721 | 13123
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 13123 | 11721 | 13123
Comments: lighting "details" value based on line items 1-4. Note: although AC Tune-up and T-stat measures ultimately were implemented for this particular customer, they were implemented
after the lighting measure, and after the lighting-focused phone survey; hence non-lighting EEM data have been zeroed out for purpose of the impact evaluation analysis for this customer ID.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 6 | 0.172 | 1.032 | F43ILL-R | 6 | 0.078 | 0.468 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 1759.68
Sales |  | F42SE | 32 | 0.086 | 2.752 | F42ILL-R | 32 | 0.052 | 1.664 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 3394.56
Sales |  | F43SE | 20 | 0.14 | 2.8 | F42ILL-R | 20 | 0.052 | 1.04 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 5491.2
Sales |  | I75/1 | 14 | 0.075 | 1.05 | CFQ23/1 | 14 | 0.026 | 0.364 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 2140.32
Sales |  | MV75/1 | 4 | 0.093 | 0.372 | CFQ26/2 | 4 | 0.066 | 0.264 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 336.96
Total for EEM | [18 empty] | 13122.72
Comments: all data per per paperwork. Op hours/week allocated to specific days per S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 13122.72
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 6 | 0.172 | 1.032 | F43ILL-R | 6 | 0.076 | 0.456 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 1797.12
Sales |  | F42SE | 32 | 0.086 | 2.752 | F42ILL-R | 32 | 0.051 | 1.632 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 3494.4
Sales |  | F43SE | 20 | 0.14 | 2.8 | F42ILL-R | 20 | 0.051 | 1.02 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 5553.6
Sales |  | I75/1 | 14 | 0.075 | 1.05 | CFQ23/1 | 14 | 0.026 | 0.364 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 2140.32
Sales |  | MV75/1 | 4 | 0.093 | 0.372 | CFQ26/2 | 4 | 0.066 | 0.264 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52 | 336.96
Total for EEM | [18 empty] | 13322.4
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R and F42ILL-R values derived using 2002 Sylvania catalog data. CFQ23/1 but in SPC tables, but value appears reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 13322.4
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 6 | 0.172 | 1.032 | F43ILL-R | 6 | 0.076 | 0.456 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 55 | 52.14 | 1651.7952
Sales |  | F42SE | 32 | 0.086 | 2.752 | F42ILL-R | 32 | 0.051 | 1.632 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 55 | 52.14 | 3211.824
Sales |  | F43SE | 20 | 0.14 | 2.8 | F42ILL-R | 20 | 0.051 | 1.02 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 55 | 52.14 | 5104.506
Sales |  | I75/1 | 14 | 0.075 | 1.05 | CFQ23/1 | 14 | 0.026 | 0.364 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 55 | 52.14 | 1967.2422
Sales |  | MV75/1 | 4 | 0.093 | 0.372 | CFQ26/2 | 4 | 0.066 | 0.264 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 55 | 52.14 | 309.7116
Total for EEM | [18 empty] | 12245.079
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 12245.079
CFL portion of Lighting Savings: | [18 empty] | 2276.9538
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 12245.079
Comments: none

## 23525
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23525
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-01-24 | 23374 | 23375 | 23374
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 23374 | 23375 | 23374
Comments: lighting "details" value based on line items 1-4.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
All |  | F44EE | 118 | 0.144 | 16.992 | F44ILL-R | 118 | 0.102 | 12.036 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 13529.88
All |  | I75/1 | 6 | 0.075 | 0.45 | CFQ23/1 | 6 | 0.026 | 0.156 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 802.62
All |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.052 | 0.312 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 327.6
All |  | F44EE | 76 | 0.144 | 10.944 | F44ILL-R | 76 | 0.102 | 7.752 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 8714.16
Total for EEM | [18 empty] | 23374.26
Comments: all data per per paperwork. Op hours per "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 23374.26
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
All |  | F44EE | 118 | 0.144 | 16.992 | F44ILL-R | 118 | 0.098 | 11.564 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 14818.44
All |  | I75/1 | 6 | 0.075 | 0.45 | CFQ23/1 | 6 | 0.026 | 0.156 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 802.62
All |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.051 | 0.306 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 343.98
All |  | F44EE | 76 | 0.144 | 10.944 | F44ILL-R | 76 | 0.098 | 7.448 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52 | 9544.08
Total for EEM | [18 empty] | 25509.12
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R and F42ILL-R values derived using 2002 Sylvania catalog data. CFQ value appears reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 25509.12
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
All |  | F44EE | 118 | 0.144 | 16.992 | F44ILL-R | 118 | 0.098 | 11.564 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52.14 | 14858.3358
All |  | I75/1 | 6 | 0.075 | 0.45 | CFQ23/1 | 6 | 0.026 | 0.156 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52.14 | 804.7809
All |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.051 | 0.306 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52.14 | 344.9061
All |  | F44EE | 76 | 0.144 | 10.944 | F44ILL-R | 76 | 0.098 | 7.448 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 0 | 52.5 | 52.14 | 9569.7756
Total for EEM | [18 empty] | 25577.7984
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 25577.7984
CFL portion of Lighting Savings: | [18 empty] | 804.7809
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 25577.7984
Comments: none

## 23581
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23581
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-02-13 | 4004 | 3993 | 4004
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 4004 | 3993 | 4004
Comments: lighting "details" value based on line items 1-3.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 18 | 0.158 | 2.844 | F82ILL | 18 | 0.109 | 1.962 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52 | 3210.48
Sales |  | F42SE | 2 | 0.086 | 0.172 | F42ILL-R | 2 | 0.052 | 0.104 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52 | 247.52
Sales |  | I75/1 | 3 | 0.075 | 0.225 | CFQ23/1 | 3 | 0.026 | 0.078 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52 | 535.08
Total for EEM | [18 empty] | 3993.08
Comments: all data per per paperwork. Op hours per "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3993.08
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 18 | 0.158 | 2.844 | F82ILL | 18 | 0.109 | 1.962 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52 | 3210.48
Sales |  | F42SE | 2 | 0.086 | 0.172 | F42ILL-R | 2 | 0.051 | 0.102 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52 | 254.8
Sales |  | I75/1 | 3 | 0.075 | 0.225 | CFQ23/1 | 3 | 0.026 | 0.078 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52 | 535.08
Total for EEM | [18 empty] | 4000.36
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F82ILL value per 1998 SPC tables; F42ILL-R values derived using 2002 Sylvania catalog data; CFQ value not in SPC tables but appears reasonable (hence
unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 4000.36
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 18 | 0.158 | 2.844 | F82ILL | 18 | 0.109 | 1.962 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52.14 | 3219.1236
Sales |  | F42SE | 2 | 0.086 | 0.172 | F42ILL-R | 2 | 0.051 | 0.102 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52.14 | 255.486
Sales |  | I75/1 | 3 | 0.075 | 0.225 | CFQ23/1 | 3 | 0.026 | 0.078 | 12 | 12 | 12 | 12 | 12 | 10 | 0 | 70 | 52.14 | 536.5206
Total for EEM | [18 empty] | 4011.1302
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 4011.1302
CFL portion of Lighting Savings: | [18 empty] | 536.5206
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 4011.1302
Comments: none

## 23587
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23587
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-02-04 | 5127 | 5119 | 5127
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 5127 | 5119 | 5127
Comments: lighting "details" value based on line items 1-3.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43SE | 19 | 0.14 | 2.66 | F43ILL-R | 19 | 0.078 | 1.482 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 61 | 52 | 3736.616
Sales |  | F44EE | 1 | 0.144 | 0.144 | F44ILL-R | 1 | 0.102 | 0.102 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 61 | 52 | 133.224
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 61 | 52 | 1243.424
Total for EEM | [18 empty] | 5113.264
Comments: all data per per paperwork. Op hours per "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 5113.264
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43SE | 19 | 0.14 | 2.66 | F43ILL-R | 19 | 0.076 | 1.444 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 61 | 52 | 3857.152
Sales |  | F44EE | 1 | 0.144 | 0.144 | F44ILL-R | 1 | 0.098 | 0.098 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 61 | 52 | 145.912
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 61 | 52 | 1243.424
Total for EEM | [18 empty] | 5246.488
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R and F44ILL-R values derived using 2002 Sylvania catalog data; CFQ value not in SPC tables but appears reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 5246.488
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43SE | 19 | 0.14 | 2.66 | F43ILL-R | 19 | 0.076 | 1.444 | 0 | 11 | 11 | 11 | 11 | 11 | 0 | 55 | 52.14 | 3487.1232
Sales |  | F44EE | 1 | 0.144 | 0.144 | F44ILL-R | 1 | 0.098 | 0.098 | 0 | 11 | 11 | 11 | 11 | 11 | 0 | 55 | 52.14 | 131.9142
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 0 | 11 | 11 | 11 | 11 | 11 | 0 | 55 | 52.14 | 1124.1384
Total for EEM | [18 empty] | 4743.1758
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 4743.1758
CFL portion of Lighting Savings: | [18 empty] | 1124.1384
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 4743.1758
Comments: none

## 23652
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23652
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-04-11 | 10940 | 11198 | 10490
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 10940 | 11198 | 10490
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 26 | 0.172 | 4.472 | F44ILL-R | 26 | 0.104 | 2.704 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 119 | 52 | 10940.384
Total for EEM | [18 empty] | 10940.384
Comments: all data per per paperwork. Op hours per "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 10940.384
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 26 | 0.172 | 4.472 | F44ILL-R | 26 | 0.098 | 2.548 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 119 | 52 | 11905.712
Total for EEM | [18 empty] | 11905.712
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 11905.712
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 26 | 0.172 | 4.472 | F44ILL-R | 26 | 0.098 | 2.548 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 119 | 52.14 | 11937.7658
Total for EEM | [18 empty] | 11937.7658
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year. Survey comments make reference to
some fixtures operated 24/7, but not included in this analysis, since not clear that those fixtures were included in the retrofit.
Overall Application Adjusted Savings: | [18 empty] | 11937.7658
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 11937.7658
Comments: none

## 23711
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23711
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-03-27 | 13296 | 13296 | 13296
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 13296 | 13296 | 13296
Comments: lighting "details" value based on line items 1-3.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Not specified |  | F42SE | 10 | 0.086 | 0.86 | F42ILL-R | 10 | 0.052 | 0.52 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1485.12
Not specified |  | I75/1F | 37 | 0.075 | 2.775 | CFQ20/1 | 37 | 0.023 | 0.851 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 8404.032
Not specified |  | I75/1F | 15 | 0.075 | 1.125 | CFQ20/1 | 15 | 0.023 | 0.345 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 3407.04
Total for EEM | [18 empty] | 13296.192
Comments: all data per per paperwork. Op hours per "customer information" TBL; op hours listed as 12AM-12PM 7 days/week in database and in paperwork as 6PM-6AM 7 days/week;
based on business type (property managers/agents), this statement interpreted/corrected as 6AM-6PM.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 13296.192
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Not specified |  | F42SE | 10 | 0.086 | 0.86 | F42ILL-R | 10 | 0.051 | 0.51 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1528.8
Not specified |  | I75/1F | 37 | 0.075 | 2.775 | CFQ20/1 | 37 | 0.023 | 0.851 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 8404.032
Not specified |  | I75/1F | 15 | 0.075 | 1.125 | CFQ20/1 | 15 | 0.023 | 0.345 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 3407.04
Total for EEM | [18 empty] | 13339.872
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R and F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 13339.872
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Not specified |  | F42SE | 10 | 0.086 | 0.86 | F42ILL-R | 10 | 0.051 | 0.51 | 16 | 16 | 16 | 16 | 16 | 12 | 12 | 104 | 52.14 | 1897.896
Not specified |  | I75/1F | 37 | 0.075 | 2.775 | CFQ20/1 | 37 | 0.023 | 0.851 | 16 | 16 | 16 | 16 | 16 | 12 | 12 | 104 | 52.14 | 10433.0054
Not specified |  | I75/1F | 15 | 0.075 | 1.125 | CFQ20/1 | 15 | 0.023 | 0.345 | 16 | 16 | 16 | 16 | 16 | 12 | 12 | 104 | 52.14 | 4229.5968
Total for EEM | [18 empty] | 16560.4982
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year, and based on survey response.
Regarding the latter: survey statement re "agents frequently work until 1AM" (i.e., an extra 7 hrs/day) interpreted (i.e., dampened somewhat) to be a weighted average of
4 extra hours/day, 5 days/week (Monday-Friday), and applied to all fixtures. Survey statement re several external lights (purportedly part of the install) being on 24/7 implicitly rolled
into the previously-mentioned hr/week adjustments.
Overall Application Adjusted Savings: | [18 empty] | 16560.4982
CFL portion of Lighting Savings: | [18 empty] | 14662.6022
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 16560.4982
Comments: none

## 23752
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23752
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-03-27 | 9331 | 9264 | 9331
Refrig. Tune-up | 2003-03-28 | 7032 | 7034 | 7032
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 16363 | 16298 | 16363
Comments: lighting "details" value based on line items 1-5; Refrig. Tune-up "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F44SE | 18 | 0.172 | 3.096 | F44ILL-R | 18 | 0.102 | 1.836 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 6420.96
Sales Area |  | F42SE | 2 | 0.086 | 0.172 | F42ILL-R | 2 | 0.052 | 0.104 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 346.528
Sales Area |  | F82SE | 5 | 0.158 | 0.79 | F44ILL-R | 5 | 0.102 | 0.51 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 1426.88
Sales Area |  | I75/1 | 4 | 0.075 | 0.3 | CFQ23/1 | 4 | 0.026 | 0.104 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 998.816
Sales Area |  | EI15/2 | 1 | 0.03 | 0.03 | ELED2/2 | 1 | 0.003 | 0.003 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 137.592
Total for EEM | [18 empty] | 9330.776
Comments: all data per per paperwork. Minor disagreement with database re Sunday hours.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Produce Prep |  | 10.8 | 1.549 | 8760 | 80% | 6% | [12 empty] | 7034.294
Total for EEM | [18 empty] | 7034.294
Comments: all data per per paperwork.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: all data per per paperwork.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 16365.07
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F44SE | 18 | 0.172 | 3.096 | F44ILL-R | 18 | 0.098 | 1.764 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 6787.872
Sales Area |  | F42SE | 2 | 0.086 | 0.172 | F42ILL-R | 2 | 0.051 | 0.102 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 356.72
Sales Area |  | F82SE | 5 | 0.158 | 0.79 | F44ILL-R | 5 | 0.098 | 0.49 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 1528.8
Sales Area |  | I75/1 | 4 | 0.075 | 0.3 | CFQ23/1 | 4 | 0.026 | 0.104 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 998.816
Sales Area |  | EI15/2 | 1 | 0.03 | 0.03 | ELED2/2 | 1 | 0.009 | 0.009 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 107.016
Total for EEM | [18 empty] | 9779.224
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F44ILL-R value derived using 2002 Sylvania catalog data; CFQ23 data not in SPC tables but appear reasonable (hence unchanged);
ELED2 value changed per SPC tables.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Produce Prep |  | 1.08 | 2 | 8760 | 80% | 1.5% | [12 empty] | 227.0592
Total for EEM | [18 empty] | 227.0592
Comments: tonnage data updated per ADL DOE study; kW/ton data updated per S&A 4/04 research; load factors rely on default/paperwork; % savings updated per S&A 4/04 research.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 10006.2832
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales Area |  | F44SE | 18 | 0.172 | 3.096 | F44ILL-R | 18 | 0.098 | 1.764 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 6806.147
Sales Area |  | F42SE | 2 | 0.086 | 0.172 | F42ILL-R | 2 | 0.051 | 0.102 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 613.1664
Sales Area |  | F82SE | 5 | 0.158 | 0.79 | F44ILL-R | 5 | 0.098 | 0.49 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 1532.916
Sales Area |  | I75/1 | 4 | 0.075 | 0.3 | CFQ23/1 | 4 | 0.026 | 0.104 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 1001.5051
Sales Area |  | EI15/2 | 1 | 0.03 | 0.03 | ELED2/2 | 1 | 0.009 | 0.009 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 183.9499
Total for EEM | [18 empty] | 10137.6845
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response (re F42SE), and per recognition of 365 day year.
Also, ELED2/2 hours adjusted to be 24/7 per common sense.
Overall Application Adjusted Savings: | [18 empty] | 10364.7437
CFL portion of Lighting Savings: | [18 empty] | 1001.5051
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 10364.7437
Comments: none

## 23755
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23755
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-03-27 | 15200 | 15205 | 15200
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 15200 | 15205 | 15200
Comments: lighting "details" value based on line items 1-4.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 40 | 0.158 | 6.32 | F44ILL-R | 40 | 0.102 | 4.08 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 11065.6
Sales |  | F42SE | 16 | 0.086 | 1.376 | F42ILL-R | 16 | 0.052 | 0.832 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 2687.36
Sales |  | I75/1 | 4 | 0.075 | 0.3 | CFQ23/1 | 4 | 0.026 | 0.104 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 968.24
Sales |  | F84SE | 1 | 0.316 | 0.316 | F84ILL | 1 | 0.219 | 0.219 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 479.18
Total for EEM | [18 empty] | 15200.38
Comments: all data per per paperwork. Op hours of 95 hr/week allocated to days using S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 15200.38
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 40 | 0.158 | 6.32 | F44ILL-R | 40 | 0.098 | 3.92 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 11856
Sales |  | F42SE | 16 | 0.086 | 1.376 | F42ILL-R | 16 | 0.051 | 0.816 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 2766.4
Sales |  | I75/1 | 4 | 0.075 | 0.3 | CFQ23/1 | 4 | 0.026 | 0.104 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 968.24
Sales |  | F84SE | 1 | 0.316 | 0.316 | F84ILL | 1 | 0.219 | 0.219 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 95 | 52 | 479.18
Total for EEM | [18 empty] | 16069.82
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R and F42ILL-R values derived using 2002 Sylvania catalog data. CFQ23 fixture not in SPC tables, but value appears reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 16069.82
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 40 | 0.158 | 6.32 | F44ILL-R | 40 | 0.098 | 3.92 | 19 | 19 | 19 | 19 | 19 | 8 | 0 | 103 | 52.14 | 12889.008
Sales |  | F42SE | 16 | 0.086 | 1.376 | F42ILL-R | 16 | 0.051 | 0.816 | 19 | 19 | 19 | 19 | 19 | 8 | 0 | 103 | 52.14 | 3007.4352
Sales |  | I75/1 | 4 | 0.075 | 0.3 | CFQ23/1 | 4 | 0.026 | 0.104 | 19 | 19 | 19 | 19 | 19 | 8 | 0 | 103 | 52.14 | 1052.6023
Sales |  | F84SE | 1 | 0.316 | 0.316 | F84ILL | 1 | 0.219 | 0.219 | 19 | 19 | 19 | 19 | 19 | 8 | 0 | 103 | 52.14 | 520.9307
Total for EEM | [18 empty] | 17469.9763
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 17469.9763
CFL portion of Lighting Savings: | [18 empty] | 1052.6023
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 17469.9763
Comments: none

## 23766
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23766
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-04-11 | 38351 | 38342 | 38351
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 38351 | 38342 | 38351
Comments: lighting "details" value based on line items 1-4 and 6.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F42SE | 8 | 0.086 | 0.688 | F42ILL-R | 8 | 0.052 | 0.416 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 2376.192
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 3424.512
Sales |  | I75/1F | 34 | 0.075 | 2.55 | CFQ20/1 | 34 | 0.023 | 0.782 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 15445.248
Sales |  | I100/1F | 18 | 0.1 | 1.8 | CFQ25/1 | 18 | 0.033 | 0.594 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 10535.616
Sales |  | EI25/2 | 16 | 0.05 | 0.8 | ELED2/1 | 16 | 0.003 | 0.048 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 6569.472
Total for EEM | [18 empty] | 38351.04
Comments: all data per per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 38351.04
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F42SE | 8 | 0.086 | 0.688 | F42ILL-R | 8 | 0.051 | 0.408 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 2446.08
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 3424.512
Sales |  | I75/1F | 34 | 0.075 | 2.55 | CFQ20/1 | 34 | 0.023 | 0.782 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 15445.248
Sales |  | I100/1F | 18 | 0.1 | 1.8 | CFQ25/1 | 18 | 0.033 | 0.594 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 10535.616
Sales |  | EI25/2 | 16 | 0.05 | 0.8 | ELED2/1 | 16 | 0.006 | 0.096 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 6150.144
Total for EEM | [18 empty] | 38001.6
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R values derived using 2002 Sylvania catalog data. CFQ23 fixture not in SPC tables, but value appears reasonable (hence unchanged).
ELED2/1 value is per SPC tables.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 38001.6
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F42SE | 8 | 0.086 | 0.688 | F42ILL-R | 8 | 0.051 | 0.408 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 161 | 52.14 | 2350.4712
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 161 | 52.14 | 3290.6597
Sales |  | I75/1F | 34 | 0.075 | 2.55 | CFQ20/1 | 34 | 0.023 | 0.782 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 161 | 52.14 | 14841.5467
Sales |  | I100/1F | 18 | 0.1 | 1.8 | CFQ25/1 | 18 | 0.033 | 0.594 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 161 | 52.14 | 10123.8152
Sales |  | EI25/2 | 16 | 0.05 | 0.8 | ELED2/1 | 16 | 0.006 | 0.096 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 161 | 52.14 | 5909.7562
Total for EEM | [18 empty] | 36516.249
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Adjustment to 23/7 operation has been based on respondent's comment that some lights are turned off in each room during 10pm-5am (7 hours).
Overall Application Adjusted Savings: | [18 empty] | 36516.249
CFL portion of Lighting Savings: | [18 empty] | 28256.0216
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 36516.249
Comments: none

## 23767
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23767
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-05-06 | 14640 | 14378 | 14640
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 14640 | 14378 | 14640
Comments: lighting "details" value based on line items 1-3.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F42SE | 66 | 0.086 | 5.676 | F42ILL-R | 66 | 0.052 | 3.432 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 75 | 52 | 8751.6
Sales |  | EI15/2 | 5 | 0.03 | 0.15 | ELED2/2 | 5 | 0.003 | 0.015 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1179.36
Outside Canopy |  | I75/1 | 22 | 0.075 | 1.65 | CFQ23/1 | 22 | 0.026 | 0.572 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 4708.704
Total for EEM | [18 empty] | 14639.664
Comments: all data per per paperwork. Daily operating schedule derived using S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 14639.664
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F42SE | 66 | 0.086 | 5.676 | F42ILL-R | 66 | 0.051 | 3.366 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 75 | 52 | 9009
Sales |  | EI15/2 | 5 | 0.03 | 0.15 | ELED2/2 | 5 | 0.009 | 0.045 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 917.28
Outside Canopy |  | I75/1 | 22 | 0.075 | 1.65 | CFQ23/1 | 22 | 0.026 | 0.572 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 4708.704
Total for EEM | [18 empty] | 14634.984
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R values derived using 2002 Sylvania catalog data. CFQ23 fixture not in SPC tables, but value appears reasonable (hence unchanged).
ELED2/2 value is per 2003 SPC tables.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 14634.984
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F42SE | 66 | 0.086 | 5.676 | F42ILL-R | 66 | 0.051 | 3.366 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52.14 | 8431.038
Sales |  | EI15/2 | 5 | 0.03 | 0.15 | ELED2/2 | 5 | 0.009 | 0.045 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 919.7496
Outside Canopy |  | I75/1 | 22 | 0.075 | 1.65 | CFQ23/1 | 22 | 0.026 | 0.572 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 4721.3813
Total for EEM | [18 empty] | 14072.1689
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Survey response "overridden" for op data re outside canopy (driven by photocell) and exit signs (on 24/7) since ASW data appear intuitively correct (i.e., it is extremely
likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 14072.1689
CFL portion of Lighting Savings: | [18 empty] | 4721.3813
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 14072.1689
Comments: none

## 23789
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23789
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-04-08 | 32376 | 32376 | 32376
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 32376 | 32376 | 32376
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 109 | 0.158 | 17.222 | F44ILL-R | 109 | 0.102 | 11.118 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 102 | 52 | 32375.616
Total for EEM | [18 empty] | 32375.616
Comments: all data per per paperwork. Daily operating schedule derived based on "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 32375.616
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 109 | 0.158 | 17.222 | F44ILL-R | 109 | 0.098 | 10.682 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 102 | 52 | 34688.16
Total for EEM | [18 empty] | 34688.16
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 34688.16
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 109 | 0.158 | 17.222 | F44ILL-R | 109 | 0.098 | 10.682 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 0 | 0 | 42.5 | 52.14 | 14492.313
Total for EEM | [18 empty] | 14492.313
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 14492.313
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 14492.313
Comments: none

## 23797
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23797
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-04-24 | 21128 | 21128 | 21128
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 21128 | 21128 | 21128
Comments: lighting "details" value based on line items 1-8.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 28 | 0.144 | 4.032 | F44ILL-R | 28 | 0.102 | 2.856 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 5992.896
Sales |  | F42EE | 20 | 0.072 | 1.44 | F42ILL-R | 20 | 0.052 | 1.04 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 2038.4
Sales |  | F43EE | 6 | 0.115 | 0.69 | F43ILL-R | 6 | 0.078 | 0.468 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 1131.312
Sales |  | F82EE | 20 | 0.123 | 2.46 | F44ILL-R | 20 | 0.102 | 2.04 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 2140.32
Sales |  | F44EE | 22 | 0.144 | 3.168 | F44ILL-R | 22 | 0.102 | 2.244 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 4708.704
Sales |  | FU2SE | 4 | 0.086 | 0.344 | FU2ILL-R | 4 | 0.052 | 0.208 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 693.056
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 1997.632
Meat Case |  | F42SE | 14 | 0.086 | 1.204 | F42ILL-R | 14 | 0.052 | 0.728 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 2425.696
Total for EEM | [18 empty] | 21128.016
Comments: all data per per paperwork. Daily operating schedule derived based on "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 21128.016
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 28 | 0.144 | 4.032 | F44ILL-R | 28 | 0.098 | 2.744 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 6563.648
Sales |  | F42EE | 20 | 0.072 | 1.44 | F42ILL-R | 20 | 0.051 | 1.02 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 2140.32
Sales |  | F43EE | 6 | 0.115 | 0.69 | F43ILL-R | 6 | 0.076 | 0.456 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 1192.464
Sales |  | F82EE | 20 | 0.123 | 2.46 | F44ILL-R | 20 | 0.098 | 1.96 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 2548
Sales |  | F44EE | 22 | 0.144 | 3.168 | F44ILL-R | 22 | 0.098 | 2.156 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 5157.152
Sales |  | FU2SE | 4 | 0.086 | 0.344 | FU2ILL-R | 4 | 0.052 | 0.208 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 693.056
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 1997.632
Meat Case |  | F42SE | 14 | 0.086 | 1.204 | F42ILL-R | 14 | 0.051 | 0.714 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52 | 2497.04
Total for EEM | [18 empty] | 22789.312
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F44ILL-R values derived using 2002 Sylvania catalog data. CFQ23 fixture not in SPC tables but value appears reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 22789.312
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 28 | 0.144 | 4.032 | F44ILL-R | 28 | 0.098 | 2.744 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 6581.3194
Sales |  | F42EE | 20 | 0.072 | 1.44 | F42ILL-R | 20 | 0.051 | 1.02 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 2146.0824
Sales |  | F43EE | 6 | 0.115 | 0.69 | F43ILL-R | 6 | 0.076 | 0.456 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52.14 | 1366.4851
Sales |  | F82EE | 20 | 0.123 | 2.46 | F44ILL-R | 20 | 0.098 | 1.96 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 2554.86
Sales |  | F44EE | 22 | 0.144 | 3.168 | F44ILL-R | 22 | 0.098 | 2.156 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 5171.0366
Sales |  | FU2SE | 4 | 0.086 | 0.344 | FU2ILL-R | 4 | 0.052 | 0.208 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 694.9219
Sales |  | I75/1 | 8 | 0.075 | 0.6 | CFQ23/1 | 8 | 0.026 | 0.208 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 2003.0102
Meat Case |  | F42SE | 14 | 0.086 | 1.204 | F42ILL-R | 14 | 0.051 | 0.714 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 98 | 52.14 | 2503.7628
Total for EEM | [18 empty] | 23021.4785
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 23021.4785
CFL portion of Lighting Savings: | [18 empty] | 2003.0102
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 23021.4785
Comments: none

## 23817
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23817
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2004-05-22 | 7362 | 7362 | 7362
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 7362 | 7362 | 7362
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 20 | 0.158 | 3.16 | F44ILL-R | 20 | 0.102 | 2.04 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52 | 6522.88
Sales |  | F62SE | 4 | 0.122 | 0.488 | F34ILL-R | 4 | 0.086 | 0.344 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52 | 838.656
Total for EEM | [18 empty] | 7361.536
Comments: all data per per paperwork. Daily operating schedule derived based on "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 7361.536
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 20 | 0.158 | 3.16 | F44ILL-R | 20 | 0.098 | 1.96 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52 | 6988.8
Sales |  | F62SE | 4 | 0.122 | 0.488 | F34ILL-R | 4 | 0.086 | 0.344 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52 | 838.656
Total for EEM | [18 empty] | 7827.456
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 7827.456
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 20 | 0.158 | 3.16 | F44ILL-R | 20 | 0.098 | 1.96 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52.14 | 7007.616
Sales |  | F62SE | 4 | 0.122 | 0.488 | F34ILL-R | 4 | 0.086 | 0.344 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52.14 | 840.9139
Total for EEM | [18 empty] | 7848.5299
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 7848.5299
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 7848.5299
Comments: none

## 23818
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23818
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2004-05-21 | 5137 | 5105 | 5422
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 5137 | 5105 | 5422
Comments: lighting "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 19 | 0.158 | 3.002 | F82ILL-R | 19 | 0.109 | 2.071 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52 | 5422.144
Total for EEM | [18 empty] | 5422.144
Comments: all data per per paperwork. Daily operating schedule derived based on "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 5422.144
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 18 | 0.158 | 2.844 | F82ILL-R | 18 | 0.109 | 1.962 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52 | 5136.768
Total for EEM | [18 empty] | 5136.768
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F82ILL values derived using per 2003 SPC tables; F82ILL used per Lighting Installation Report (had been listed as F82ILL-R on calc sheet).
Both fixtures: fixture count dropped to 18 per Lighting Installation Report.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 5136.768
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82SE | 18 | 0.158 | 2.844 | F82ILL-R | 18 | 0.109 | 1.962 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112 | 52.14 | 5150.5978
Total for EEM | [18 empty] | 5150.5978
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 5150.5978
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 5150.5978
Comments: none

## 23836
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23836
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-07-16 | 131201 | 127565 | 131201
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 131201 | 127565 | 131201
Comments: lighting "details" value based on line items 1-6.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | 4 lamp 4' T12 wrap, magnetic ballasts | 34 | 0.168 | 5.712 | 2 4' T8 lamps, reflector, 1/2 4-lamp electronic ballast in tandem | 34 | 0.054 | 1.836 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 16975.9498
Office |  | 2-lamp 4' T12 wrap, magnetic ballast | 14 | 0.08 | 1.12 | 2 4' T8 lamps, reflector, 2-lamp electronic ballast | 14 | 0.051 | 0.714 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1778.1826
Warehouse |  | 8' 2-lamp fluorescent, magnetic ballast | 9 | 0.14 | 1.26 | 4 4' T8 lamps, electronic ballast | 9 | 0.096 | 0.864 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1734.385
Exterior |  | 400W mercury vapor | 6 | 0.45 | 2.7 | 250W metal halide lamp, ballast | 6 | 0.275 | 1.65 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 4598.748
Mfg Area |  | 400W metal halide | 54 | 0.455 | 24.57 | New 6-lamp T8 fluorescent fixture,electronic ballasts | 54 | 0.166 | 8.964 | 24 | 24 | 24 | 24 | 24 | 10 | 0 | 130 | 52.14 | 105780.5892
Mfg Area |  | EXIT sign, 2 20W lamps | 1 | 0.04 | 0.04 | new LED EXIT sign w/battery backup | 1 | 0.002 | 0.002 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 332.8618
Total for EEM | [18 empty] | 131200.7162
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 131200.7162
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 34 | 0.172 | 5.848 | F42ILL/T4 | 34 | 0.056 | 1.904 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 17273.7734
Office |  | F42SE | 14 | 0.086 | 1.204 | F42ILL | 14 | 0.059 | 0.826 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1655.5493
Warehouse |  | F82SE | 9 | 0.158 | 1.422 | F44ILL | 9 | 0.112 | 1.008 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1813.2206
Exterior |  | MV400/1 | 6 | 0.455 | 2.73 | MH250/1 | 6 | 0.295 | 1.77 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 4204.5696
Mfg Area |  | MH400/1 | 54 | 0.458 | 24.732 | F46ILL | 54 | 0.175 | 9.45 | 24 | 24 | 24 | 24 | 24 | 10 | 0 | 130 | 52.14 | 103584.4524
Mfg Area |  | EI20/2 | 1 | 0.04 | 0.04 | ELED2/2 | 1 | 0.009 | 0.009 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 271.5451
Total for EEM | [18 empty] | 128803.1105
Comments: step 2 fixture descriptions (non-standard EIG values) mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures assumed per
paperwork notes.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 128803.1105
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 34 | 0.172 | 5.848 | F42ILL/T4 | 34 | 0.056 | 1.904 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52.14 | 16451.2128
Office |  | F42SE | 14 | 0.086 | 1.204 | F42ILL | 14 | 0.059 | 0.826 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52.14 | 1576.7136
Warehouse |  | F82SE | 9 | 0.158 | 1.422 | F44ILL | 9 | 0.112 | 1.008 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52.14 | 1726.8768
Exterior |  | MV400/1 | 6 | 0.455 | 2.73 | MH250/1 | 6 | 0.295 | 1.77 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52.14 | 4004.352
Mfg Area |  | MH400/1 | 54 | 0.458 | 24.732 | F46ILL | 54 | 0.175 | 9.45 | 24 | 24 | 24 | 24 | 24 | 10 | 0 | 130 | 52.14 | 103584.4524
Mfg Area |  | EI20/2 | 1 | 0.04 | 0.04 | ELED2/2 | 1 | 0.009 | 0.009 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 271.5451
Total for EEM | [18 empty] | 127615.1527
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours modified per survey response. Survey results "overridden" for non exit signs in the manufacturing
area, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response), op hrs in mfg area take into
custodial work and line maintenance.
Overall Application Adjusted Savings: | [18 empty] | 127615.1527
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 127615.1527
Comments: none

## 23840
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23840
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-07-03 | 204102 | 204105 | 204102
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 204102 | 204105 | 204102
Comments: lighting "details" value based on line items 1-20.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
room lamps |  | 60 Watt Incandescent | 397 | 0.06 | 23.82 | 14W CFL S/I | 397 | 0.014 | 5.558 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 53178.944
office lamps |  | 65 Watt Incandescent | 1 | 0.065 | 0.065 | 14W CFL S/I | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 148.512
office lamps |  | 65 Watt Incandescent | 2 | 0.065 | 0.13 | 15W Reflector CFL S/I | 2 | 0.015 | 0.03 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 291.2
pool table area |  | 65 Watt Incandescent | 3 | 0.065 | 0.195 | 14W CFL S/I | 3 | 0.014 | 0.042 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 668.304
pool table area |  | 65 Watt Incandescent | 24 | 0.065 | 1.56 | 15W Reflector CFL S/I | 24 | 0.015 | 0.36 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 5241.6
pool table area |  | 65 Watt Incandescent | 8 | 0.065 | 0.52 | 27W CFL S/I | 8 | 0.027 | 0.216 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1327.872
game room |  | 65 Watt Incandescent | 1 | 0.065 | 0.065 | 14W CFL S/I | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 148.512
game room |  | 65 Watt Incandescent | 7 | 0.065 | 0.455 | 15W Reflector CFL S/I | 7 | 0.015 | 0.105 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 1019.2
laundry |  | 65 Watt Incandescent | 2 | 0.065 | 0.13 | 15W Reflector CFL S/I | 2 | 0.015 | 0.03 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52 | 202.8
elevator area |  | 65 Watt Incandescent | 14 | 0.065 | 0.91 | 15W Reflector CFL S/I | 14 | 0.015 | 0.21 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 3057.6
balconys |  | 60 Watt Incandescent | 150 | 0.06 | 9 | 14W CFL S/I | 150 | 0.014 | 2.1 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52 | 13993.2
room lamps |  | 75 Watt Incandescent | 442 | 0.075 | 33.15 | 27W CFL S/I | 442 | 0.027 | 11.934 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 61780.992
residents baths |  | 65 Watt Incandescent | 149 | 0.065 | 9.685 | 15W Reflector CFL S/I | 149 | 0.015 | 2.235 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52 | 15108.6
room entry |  | 75 Watt Incandescent | 150 | 0.075 | 11.25 | 14W CFL S/I | 150 | 0.014 | 2.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 26644.8
lobby hall |  | 75 Watt Incandescent | 6 | 0.075 | 0.45 | 14W CFL S/I | 6 | 0.014 | 0.084 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1598.688
lobby hall |  | 75 Watt Incandescent | 57 | 0.075 | 4.275 | 15W Reflector CFL S/I | 57 | 0.015 | 0.855 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 14938.56
dining |  | 75 Watt Incandescent | 5 | 0.075 | 0.375 | 14W CFL S/I | 5 | 0.014 | 0.07 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 14 | 52 | 222.04
dining |  | 75 Watt Incandescent | 58 | 0.075 | 4.35 | 15W Reflector CFL S/I | 58 | 0.015 | 0.87 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 14 | 52 | 2533.44
kitchen area |  | 65 Watt Incandescent | 10 | 0.065 | 0.65 | 15W Reflector CFL S/I | 10 | 0.015 | 0.15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 1820
assisted living office |  | 75 Watt Incandescent | 1 | 0.075 | 0.075 | 14W CFL S/I | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 177.632
204102.496
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 177.632
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
room lamps |  | I60/1 | 397 | 0.06 | 23.82 | CF14/1-SCRW | 397 | 0.014 | 5.558 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 53178.944
office lamps |  | I65/1 | 1 | 0.065 | 0.065 | CF14/1-SCRW | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 148.512
office lamps |  | I65/1 | 2 | 0.065 | 0.13 | CF15/1-SCRW | 2 | 0.015 | 0.03 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 291.2
pool table area |  | I65/1 | 3 | 0.065 | 0.195 | CF14/1-SCRW | 3 | 0.014 | 0.042 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 668.304
pool table area |  | I65/1 | 24 | 0.065 | 1.56 | CF15/1-SCRW | 24 | 0.015 | 0.36 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 5241.6
pool table area |  | I65/1 | 8 | 0.065 | 0.52 | CF27/1-SCRW | 8 | 0.027 | 0.216 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1327.872
game room |  | I65/1 | 1 | 0.065 | 0.065 | CF14/1-SCRW | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 148.512
game room |  | I65/1 | 7 | 0.065 | 0.455 | CF15/1-SCRW | 7 | 0.015 | 0.105 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 1019.2
laundry |  | I65/1 | 2 | 0.065 | 0.13 | CF15/1-SCRW | 2 | 0.015 | 0.03 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52 | 202.8
elevator area |  | I65/1 | 14 | 0.065 | 0.91 | CF15/1-SCRW | 14 | 0.015 | 0.21 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 3057.6
balconys |  | I60/1 | 150 | 0.06 | 9 | CF14/1-SCRW | 150 | 0.014 | 2.1 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52 | 13993.2
room lamps |  | I75/1 | 442 | 0.075 | 33.15 | CF27/1-SCRW | 442 | 0.027 | 11.934 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 61780.992
residents baths |  | I65/1 | 149 | 0.065 | 9.685 | CF15/1-SCRW | 149 | 0.015 | 2.235 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52 | 15108.6
room entry |  | I75/1 | 150 | 0.075 | 11.25 | CF14/1-SCRW | 150 | 0.014 | 2.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 26644.8
lobby hall |  | I75/1 | 6 | 0.075 | 0.45 | CF14/1-SCRW | 6 | 0.014 | 0.084 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1598.688
lobby hall |  | I75/1 | 57 | 0.075 | 4.275 | CF15/1-SCRW | 57 | 0.015 | 0.855 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 14938.56
dining |  | I75/1 | 5 | 0.075 | 0.375 | CF14/1-SCRW | 5 | 0.014 | 0.07 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 14 | 52 | 222.04
dining |  | I75/1 | 58 | 0.075 | 4.35 | CF15/1-SCRW | 58 | 0.015 | 0.87 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 14 | 52 | 2533.44
kitchen area |  | I65/1 | 10 | 0.065 | 0.65 | CF15/1-SCRW | 10 | 0.015 | 0.15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 1820
assisted living office |  | I75/1 | 1 | 0.075 | 0.075 | CF14/1-SCRW | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 177.632
Total for EEM | [18 empty] | 204102.496
Comments: step 2 fixture descriptions (some of which were non-standard EIG values) mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 204102.496
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
room lamps |  | I60/1 | 397 | 0.06 | 23.82 | CF14/1-SCRW | 397 | 0.014 | 5.558 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 53322.1181
office lamps |  | I65/1 | 1 | 0.065 | 0.065 | CF14/1-SCRW | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 148.9118
office lamps |  | I65/1 | 2 | 0.065 | 0.13 | CF15/1-SCRW | 2 | 0.015 | 0.03 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 291.984
pool table area |  | I65/1 | 3 | 0.065 | 0.195 | CF14/1-SCRW | 3 | 0.014 | 0.042 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 670.1033
pool table area |  | I65/1 | 24 | 0.065 | 1.56 | CF15/1-SCRW | 24 | 0.015 | 0.36 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 5255.712
pool table area |  | I65/1 | 8 | 0.065 | 0.52 | CF27/1-SCRW | 8 | 0.027 | 0.216 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1331.447
game room |  | I65/1 | 1 | 0.065 | 0.065 | CF14/1-SCRW | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 148.9118
game room |  | I65/1 | 7 | 0.065 | 0.455 | CF15/1-SCRW | 7 | 0.015 | 0.105 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 1021.944
laundry |  | I65/1 | 2 | 0.065 | 0.13 | CF15/1-SCRW | 2 | 0.015 | 0.03 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52.14 | 203.346
elevator area |  | I65/1 | 14 | 0.065 | 0.91 | CF15/1-SCRW | 14 | 0.015 | 0.21 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 6131.664
balconys |  | I60/1 | 150 | 0.06 | 9 | CF14/1-SCRW | 150 | 0.014 | 2.1 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52.14 | 14030.874
room lamps |  | I75/1 | 442 | 0.075 | 33.15 | CF27/1-SCRW | 442 | 0.027 | 11.934 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 61947.3254
residents baths |  | I65/1 | 149 | 0.065 | 9.685 | CF15/1-SCRW | 149 | 0.015 | 2.235 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 39 | 52.14 | 15149.277
room entry |  | I75/1 | 150 | 0.075 | 11.25 | CF14/1-SCRW | 150 | 0.014 | 2.1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 26716.536
lobby hall |  | I75/1 | 6 | 0.075 | 0.45 | CF14/1-SCRW | 6 | 0.014 | 0.084 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 3205.9843
lobby hall |  | I75/1 | 57 | 0.075 | 4.275 | CF15/1-SCRW | 57 | 0.015 | 0.855 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 14978.7792
dining |  | I75/1 | 5 | 0.075 | 0.375 | CF14/1-SCRW | 5 | 0.014 | 0.07 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 14 | 52.14 | 222.6378
dining |  | I75/1 | 58 | 0.075 | 4.35 | CF15/1-SCRW | 58 | 0.015 | 0.87 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 14 | 52.14 | 2540.2608
kitchen area |  | I65/1 | 10 | 0.065 | 0.65 | CF15/1-SCRW | 10 | 0.015 | 0.15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52.14 | 1824.9
assisted living office |  | I75/1 | 1 | 0.075 | 0.075 | CF14/1-SCRW | 1 | 0.014 | 0.014 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52.14 | 178.1102
Total for EEM | [18 empty] | 209320.8269
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours revised for elevator area and portion of lobby hall to be 24/7. Survey results "overridden"
(i.e., not changed) most areas since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 209320.8269
CFL portion of Lighting Savings: | [18 empty] | 209320.8269
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 209320.8269
Comments: none

## 23845
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23845
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-07-15 | 36971 | 36936 | 36971
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 36971 | 36936 | 36971
Comments: lighting "details" value based on line items 2, 5-6, 8, and 10-14.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 8 | 0.172 | 1.376 | F44ILL-R | 8 | 0.102 | 0.816 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2446.08
Office |  | I75/1 | 24 | 0.075 | 1.8 | CFQ23/1 | 24 | 0.026 | 0.624 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 5136.768
Laundry |  | F44SE | 8 | 0.172 | 1.376 | F44ILL-R | 8 | 0.102 | 0.816 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2446.08
Fitness Center |  | F44SE | 4 | 0.172 | 0.688 | F44ILL-R | 4 | 0.102 | 0.408 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1223.04
Pole Lights |  | I75/1 | 34 | 0.075 | 2.55 | CFQ23/1 | 34 | 0.026 | 0.884 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 7277.088
Porch Lights |  | I75/1 | 38 | 0.075 | 2.85 | CFQ23/1 | 38 | 0.026 | 0.988 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 8133.216
Carports |  | F41SE | 60 | 0.05 | 3 | F41ILL-R | 60 | 0.027 | 1.62 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 6027.84
Carports |  | I100/1F | 6 | 0.1 | 0.6 | CFQ25/1 | 6 | 0.033 | 0.198 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1755.936
Mailbox Area |  | F42SE | 1 | 0.086 | 0.086 | F42ILL-R | 1 | 0.052 | 0.052 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 148.512
RR / Racquet Ball |  | F42SE | 16 | 0.086 | 1.376 | F42ILL-R | 16 | 0.052 | 0.832 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2376.192
Total for EEM | [18 empty] | 36970.752
Comments: all data per per paperwork. Daily operating schedule consistent with data in "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 36970.752
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 8 | 0.172 | 1.376 | F44ILL-R | 8 | 0.098 | 0.784 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2585.856
Office |  | I75/1 | 24 | 0.075 | 1.8 | CFQ23/1 | 24 | 0.026 | 0.624 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 5136.768
Laundry |  | F44SE | 8 | 0.172 | 1.376 | F44ILL-R | 8 | 0.098 | 0.784 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2585.856
Fitness Center |  | F44SE | 4 | 0.172 | 0.688 | F44ILL-R | 4 | 0.098 | 0.392 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1292.928
Pole Lights |  | I75/1 | 34 | 0.075 | 2.55 | CFQ23/1 | 34 | 0.026 | 0.884 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 7277.088
Porch Lights |  | I75/1 | 38 | 0.075 | 2.85 | CFQ23/1 | 38 | 0.026 | 0.988 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 8133.216
Carports |  | F41SE | 60 | 0.05 | 3 | F41ILL-R | 60 | 0.026 | 1.56 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 6289.92
Carports |  | I100/1F | 6 | 0.1 | 0.6 | CFQ25/1 | 6 | 0.033 | 0.198 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1755.936
Mailbox Area |  | F42SE | 1 | 0.086 | 0.086 | F42ILL-R | 1 | 0.051 | 0.051 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 152.88
RR / Racquet Ball |  | F42SE | 16 | 0.086 | 1.376 | F42ILL-R | 16 | 0.051 | 0.816 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2446.08
Total for EEM | [18 empty] | 37656.528
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F41ILL-R, F42ILL-R, and F44ILL-R values derived using 2002 Sylvania catalog data. CFQ23 data not in SPC tables, but appear reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 37656.528
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 8 | 0.172 | 1.376 | F44ILL-R | 8 | 0.098 | 0.784 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 59 | 52.14 | 1821.1459
Office |  | I75/1 | 24 | 0.075 | 1.8 | CFQ23/1 | 24 | 0.026 | 0.624 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 59 | 52.14 | 3617.6818
Laundry |  | F44SE | 8 | 0.172 | 1.376 | F44ILL-R | 8 | 0.098 | 0.784 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 59 | 52.14 | 1821.1459
Fitness Center |  | F44SE | 4 | 0.172 | 0.688 | F44ILL-R | 4 | 0.098 | 0.392 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 59 | 52.14 | 910.573
Pole Lights |  | I75/1 | 34 | 0.075 | 2.55 | CFQ23/1 | 34 | 0.026 | 0.884 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 7296.6802
Porch Lights |  | I75/1 | 38 | 0.075 | 2.85 | CFQ23/1 | 38 | 0.026 | 0.988 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 8155.1131
Carports |  | F41SE | 60 | 0.05 | 3 | F41ILL-R | 60 | 0.026 | 1.56 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 6306.8544
Carports |  | I100/1F | 6 | 0.1 | 0.6 | CFQ25/1 | 6 | 0.033 | 0.198 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1760.6635
Mailbox Area |  | F42SE | 1 | 0.086 | 0.086 | F42ILL-R | 1 | 0.051 | 0.051 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 153.2916
RR / Racquet Ball |  | F42SE | 16 | 0.086 | 1.376 | F42ILL-R | 16 | 0.051 | 0.816 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 59 | 52.14 | 1722.7056
Total for EEM | [18 empty] | 33565.855
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours changed for office, laundry, fitness center, and RR/racquet ball areas per survey response.
Survey results "overridden" for outside areas, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
custodial work and line maintenance.
Overall Application Adjusted Savings: | [18 empty] | 33565.855
CFL portion of Lighting Savings: | [18 empty] | 20830.1386
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 33565.855
Comments: none

## 23847
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23847
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-06-20 | 20177 | 20132 | 20177
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 20177 | 20132 | 20177
Comments: lighting "details" value based on line items 1-5.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 24 | 0.172 | 4.128 | F44ILL-R | 24 | 0.102 | 2.448 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 7949.76
Office |  | I75/1 | 12 | 0.075 | 0.9 | CFQ23/1 | 12 | 0.026 | 0.312 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 2782.416
Office |  | F42SE | 4 | 0.086 | 0.344 | F42ILL-R | 4 | 0.052 | 0.208 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 643.552
Warehouse |  | F81SE | 46 | 0.09 | 4.14 | F42ILL-R | 46 | 0.052 | 2.392 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 8271.536
Warehouse |  | F82SE | 2 | 0.158 | 0.316 | F44ILL-R | 2 | 0.102 | 0.204 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 529.984
Total for EEM | [18 empty] | 20177.248
Comments: all data per per paperwork. Daily operating schedule consistent with data in "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 20177.248
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 24 | 0.172 | 4.128 | F44ILL-R | 24 | 0.098 | 2.352 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 8404.032
Office |  | I75/1 | 12 | 0.075 | 0.9 | CFQ23/1 | 12 | 0.026 | 0.312 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 2782.416
Office |  | F42SE | 4 | 0.086 | 0.344 | F42ILL-R | 4 | 0.051 | 0.204 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 662.48
Warehouse |  | F81SE | 46 | 0.09 | 4.14 | F42ILL-R | 46 | 0.051 | 2.346 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 8489.208
Warehouse |  | F82SE | 2 | 0.158 | 0.316 | F44ILL-R | 2 | 0.098 | 0.196 | 16 | 16 | 16 | 16 | 16 | 11 | 0 | 91 | 52 | 567.84
Total for EEM | [18 empty] | 20905.976
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R, and F44ILL-R values derived using 2002 Sylvania catalog data. CFQ23 data not in SPC tables, but appear reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 20905.976
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44SE | 24 | 0.172 | 4.128 | F44ILL-R | 24 | 0.098 | 2.352 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 4 | 115 | 52.14 | 10649.0736
Office |  | I75/1 | 12 | 0.075 | 0.9 | CFQ23/1 | 12 | 0.026 | 0.312 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 4 | 115 | 52.14 | 3525.7068
Office |  | F42SE | 4 | 0.086 | 0.344 | F42ILL-R | 4 | 0.051 | 0.204 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 4 | 115 | 52.14 | 839.454
Warehouse |  | F81SE | 46 | 0.09 | 4.14 | F42ILL-R | 46 | 0.051 | 2.346 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 4 | 115 | 52.14 | 10757.0034
Warehouse |  | F82SE | 2 | 0.158 | 0.316 | F44ILL-R | 2 | 0.098 | 0.196 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 4 | 115 | 52.14 | 719.532
Total for EEM | [18 empty] | 26490.7698
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours changed per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 26490.7698
CFL portion of Lighting Savings: | [18 empty] | 3525.7068
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 26490.7698
Comments: none

## 23849
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23849
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-06-20 | 81302 | 81302 | 81302
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 81302 | 81302 | 81302
Comments: lighting "details" value based on line items 1-5.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82EE | 57 | 0.123 | 7.011 | F42ILL-R | 57 | 0.052 | 2.964 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 133 | 52 | 27989.052
Sales |  | F82EE | 58 | 0.123 | 7.134 | F42ILL-R | 58 | 0.052 | 3.016 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 35974.848
Sales |  | F82EE | 49 | 0.123 | 6.027 | F44ILL-R | 49 | 0.102 | 4.998 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 133 | 52 | 7116.564
Sales |  | F82EE | 50 | 0.123 | 6.15 | F44ILL-R | 50 | 0.102 | 5.1 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 9172.8
Sales |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.052 | 0.312 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1048.32
Total for EEM | [18 empty] | 81301.584
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 81301.584
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82EE | 57 | 0.123 | 7.011 | F42ILL-R | 57 | 0.051 | 2.907 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 133 | 52 | 28383.264
Sales |  | F82EE | 58 | 0.123 | 7.134 | F42ILL-R | 58 | 0.051 | 2.958 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 36481.536
Sales |  | F82EE | 49 | 0.123 | 6.027 | F44ILL-R | 49 | 0.098 | 4.802 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 133 | 52 | 8472.1
Sales |  | F82EE | 50 | 0.123 | 6.15 | F44ILL-R | 50 | 0.098 | 4.9 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 10920
Sales |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.051 | 0.306 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1100.736
Total for EEM | [18 empty] | 85357.636
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F44ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 85357.636
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F82EE | 57 | 0.123 | 7.011 | F42ILL-R | 57 | 0.051 | 2.907 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 147 | 52.14 | 31455.4363
Sales |  | F82EE | 58 | 0.123 | 7.134 | F42ILL-R | 58 | 0.051 | 2.958 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 36579.7555
Sales |  | F82EE | 49 | 0.123 | 6.027 | F44ILL-R | 49 | 0.098 | 4.802 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 147 | 52.14 | 9389.1105
Sales |  | F82EE | 50 | 0.123 | 6.15 | F44ILL-R | 50 | 0.098 | 4.9 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 10949.4
Sales |  | F42EE | 6 | 0.072 | 0.432 | F42ILL-R | 6 | 0.051 | 0.306 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1103.6995
Total for EEM | [18 empty] | 89477.4019
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours changed per survey response, and per recognition of 365 day year.
Lighting system - at least some parts - acknowledged as being on 24/7, with some load reductions during 1-4am; load reductions attributed to those lamps originally identified as being
on 133 hr/week (19 hr/day).
Overall Application Adjusted Savings: | [18 empty] | 89477.4019
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 89477.4019
Comments: none

## 23862
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23862
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting |  | 0 | 0 | 0
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat | 2003-08-01 | 3639 | 3639 | 3639
Overall |  | 3639 | 3639 | 3639
Comments: Tstat "details" value based on line item 1. Note that although this customer also implemented lighting measures, the lighting implementation was completed in a different month
than the tstat, hence the respondent was only questioned re measure matters regarding tstat issues. Accordingly, lighting has been excluded from this particular customer ID
impact evaluation analysis.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Not applicable |  |  |  |  | 0 |  |  |  | kW: 0; Operational Data (hrs by day) Sum: 0; Operational Data (hrs by day) Wk/Yr: 52 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Not applicable | [18 empty] | 0
Comments: none
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 21 | 62% | 3494 | 1 | 8% | [12 empty] | 3639.3504
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3639.3504
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Not applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0
Total for EEM | [18 empty] | 0
Comments: none
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Not applicable | [18 empty] | 0
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 21 | 0.62 | 2620.5 | 1.1 | 15% | [12 empty] | 5629.6201
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 5629.6201
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Not applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 52.14 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Overall Application Adjusted Savings: | [18 empty] | 5629.6201
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 5629.6201
Comments: none

## 23874
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23874
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-07-31 | 67641 | 67640 | 67641
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 67641 | 67640 | 67641
Comments: lighting "details" value based on line items 1-4.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office 2X4 4L |  | 4' 4 lamp T-12 | 132 | 0.164 | 21.648 | 4' 2 lamp ULTRA WM ref | 132 | 0.046 | 6.072 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52.14 | 56849.2848
4th Fl Hallway 2X4 4L |  | 4' 4 lamp T-12 | 4 | 0.164 | 0.656 | 4' 2 lamp ULTRA WM ref | 4 | 0.046 | 0.184 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 4134.4934
Hallway 1X4 2L |  | 4' 2 lamp T-12 | 17 | 0.082 | 1.394 | 4' 2 lamp ULTRA LP WM | 17 | 0.046 | 0.782 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 5360.8262
Exit Signs |  | Incand, Battery BU 2ckt | 4 | 0.04 | 0.16 | LED, BBU/2CKT Bug Eye | 4 | 0.003 | 0.012 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1296.409
67641.0134
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 67641.0134
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office 2X4 4L |  | F44SE | 132 | 0.172 | 22.704 | F42WLL | 132 | 0.051 | 6.732 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52.14 | 58294.6056
4th Fl Hallway 2X4 4L |  | F44SE | 4 | 0.172 | 0.688 | F42WLL | 4 | 0.051 | 0.204 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 4239.6077
Hallway 1X4 2L |  | F42SE | 17 | 0.086 | 1.462 | F42WLL-R | 17 | 0.045 | 0.765 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 6105.3854
Exit Signs |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.009 | 0.036 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1086.1805
Total for EEM | [18 empty] | 69725.7792
Comments: step 2 fixture descriptions (some of which were non-standard EIG values) mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 69725.7792
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office 2X4 4L |  | F44SE | 132 | 0.172 | 22.704 | F42WLL | 132 | 0.051 | 6.732 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 33311.2032
4th Fl Hallway 2X4 4L |  | F44SE | 4 | 0.172 | 0.688 | F42WLL | 4 | 0.051 | 0.204 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 4239.6077
Hallway 1X4 2L |  | F42SE | 17 | 0.086 | 1.462 | F42WLL-R | 17 | 0.045 | 0.765 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 6105.3854
Exit Signs |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.009 | 0.036 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1086.1805
Total for EEM | [18 empty] | 44742.3768
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data adjusted per survey response. Survey response "overridden" (i.e., not changed) for hallways
and exit signs since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 44742.3768
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 44742.3768
Comments: none

## 23901
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23901
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-09-24 | 18371 | 18371 | 18371
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 18371 | 18371 | 18371
Comments: lighting "details" value based on line items 1-14.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
cleaning room, meds room, rec room, atrium, group room, consultation room, staff meeting room |  | 4' 4 lamp T-12 | 16 | 0.144 | 2.304 | 4' 2 lamp ULTRA WM REF | 16 | 0.046 | 0.736 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52 | 2853.76
dark-walled room |  | 4' 4 lamp T-12 | 3 | 0.144 | 0.432 | 4' 2 lamp ULTRA WM REF | 3 | 0.046 | 0.138 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 10 | 52 | 152.88
throughout |  | 75W flood incand | 6 | 0.075 | 0.45 | 18W CFL S/I | 6 | 0.018 | 0.108 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 1244.88
exterior |  | 4' 2 lamp T-12 | 2 | 0.072 | 0.144 | 4' 2 lamp ULTRA LP WM | 2 | 0.046 | 0.092 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 189.28
exterior |  | 175 watt | 5 | 0.205 | 1.025 | 100W MH | 5 | 0.128 | 0.64 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1681.68
exterior |  | 150W flood | 4 | 0.15 | 0.6 | 26W CFL S/I | 4 | 0.027 | 0.108 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2149.056
throughout |  | EXIT SIGN | 9 | 0.04 | 0.36 | LED, BBU/2CKT | 9 | 0.003 | 0.027 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 2909.088
janitor closet |  | 60 watt | 1 | 0.06 | 0.06 | 13W CFL S/I | 1 | 0.015 | 0.015 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 10 | 52 | 23.4
storage |  | 4' 4 lamp T-12 | 2 | 0.144 | 0.288 | 4' 2 lamp ULTRA WM REF | 2 | 0.046 | 0.092 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 21 | 52 | 214.032
restrooms, private offices |  | 4' 4 lamp T-12 | 8 | 0.144 | 1.152 | 4' 2 lamp ULTRA WM REF | 8 | 0.046 | 0.368 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 2283.008
east corridor |  | 4' 4 lamp T-12 | 8 | 0.144 | 1.152 | 4' 2 lamp ULTRA WM REF | 8 | 0.046 | 0.368 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 2853.76
corridors |  | 2' 2 lamp T-12 U-tube | 6 | 0.072 | 0.432 | 2' 2 lamp T-8,U-Tube | 6 | 0.052 | 0.312 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 436.8
group room |  | 4' 4 lamp T-12 | 1 | 0.144 | 0.144 | 4' 2 lamp ULTRA WM REF | 1 | 0.046 | 0.046 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52 | 178.36
group room, restrooms, obs rooms, offices |  | 2' 2 lamp T-12 U-tube | 33 | 0.072 | 2.376 | 2' 2 lamp T-8,U-Tube | 33 | 0.052 | 1.716 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52 | 1201.2
18371.184
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 18371.184
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
cleaning room, meds room, rec room, atrium, group room, consultation room, staff meeting room |  | F44EE | 16 | 0.144 | 2.304 | F42WLL | 16 | 0.051 | 0.816 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52 | 2708.16
dark-walled room |  | F44EE | 3 | 0.144 | 0.432 | F42WLL | 3 | 0.051 | 0.153 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 10 | 52 | 145.08
throughout |  | I75/1F | 6 | 0.075 | 0.45 | CF18/1-SCRW | 6 | 0.018 | 0.108 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 1244.88
exterior |  | F42EE | 2 | 0.072 | 0.144 | F42WLL-R | 2 | 0.045 | 0.09 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 196.56
exterior |  | MV175/1 | 5 | 0.205 | 1.025 | MH100/1 | 5 | 0.128 | 0.64 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 1681.68
exterior |  | I150/1F | 4 | 0.15 | 0.6 | CF26/1-SCRW | 4 | 0.026 | 0.104 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52 | 2166.528
throughout |  | EI20/2 | 9 | 0.04 | 0.36 | ELED2/2 | 9 | 0.009 | 0.081 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 2437.344
janitor closet |  | I60/1 | 1 | 0.06 | 0.06 | CF13/1-SCRW | 1 | 0.013 | 0.013 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 10 | 52 | 24.44
storage |  | F44EE | 2 | 0.144 | 0.288 | F42WLL | 2 | 0.051 | 0.102 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 21 | 52 | 203.112
restrooms, private offices |  | F44EE | 8 | 0.144 | 1.152 | F42WLL | 8 | 0.051 | 0.408 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 52 | 2166.528
east corridor |  | F44EE | 8 | 0.144 | 1.152 | F42WLL | 8 | 0.051 | 0.408 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 2708.16
corridors |  | FU2EE | 6 | 0.072 | 0.432 | FU2ILL | 6 | 0.059 | 0.354 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52 | 283.92
group room |  | F44EE | 1 | 0.144 | 0.144 | F42WLL | 1 | 0.051 | 0.051 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52 | 169.26
group room, restrooms, obs rooms, offices |  | FU2EE | 33 | 0.072 | 2.376 | F42WLL | 33 | 0.059 | 1.947 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52 | 780.78
Total for EEM | [18 empty] | 16916.432
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 16916.432
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
cleaning room, meds room, rec room, atrium, group room, consultation room, staff meeting room |  | F44EE | 16 | 0.144 | 2.304 | F42WLL | 16 | 0.051 | 0.816 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 63 | 52.14 | 4887.8122
dark-walled room |  | F44EE | 3 | 0.144 | 0.432 | F42WLL | 3 | 0.051 | 0.153 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 10 | 52.14 | 145.4706
throughout |  | I75/1F | 6 | 0.075 | 0.45 | CF18/1-SCRW | 6 | 0.018 | 0.108 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 63 | 52.14 | 1123.4084
exterior |  | F42EE | 2 | 0.072 | 0.144 | F42WLL-R | 2 | 0.045 | 0.09 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 52.14 | 197.0892
exterior |  | MV175/1 | 5 | 0.205 | 1.025 | MH100/1 | 5 | 0.128 | 0.64 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1686.2076
exterior |  | I150/1F | 4 | 0.15 | 0.6 | CF26/1-SCRW | 4 | 0.026 | 0.104 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 2172.361
throughout |  | EI20/2 | 9 | 0.04 | 0.36 | ELED2/2 | 9 | 0.009 | 0.081 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 2443.9061
janitor closet |  | I60/1 | 1 | 0.06 | 0.06 | CF13/1-SCRW | 1 | 0.013 | 0.013 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 10 | 52.14 | 24.5058
storage |  | F44EE | 2 | 0.144 | 0.288 | F42WLL | 2 | 0.051 | 0.102 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 21 | 52.14 | 203.6588
restrooms, private offices |  | F44EE | 8 | 0.144 | 1.152 | F42WLL | 8 | 0.051 | 0.408 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 63 | 52.14 | 2443.9061
east corridor |  | F44EE | 8 | 0.144 | 1.152 | F42WLL | 8 | 0.051 | 0.408 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 63 | 52.14 | 2443.9061
corridors |  | FU2EE | 6 | 0.072 | 0.432 | FU2ILL | 6 | 0.059 | 0.354 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 63 | 52.14 | 256.216
group room |  | F44EE | 1 | 0.144 | 0.144 | F42WLL | 1 | 0.051 | 0.051 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52.14 | 169.7157
group room, restrooms, obs rooms, offices |  | FU2EE | 33 | 0.072 | 2.376 | F42WLL | 33 | 0.059 | 1.947 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 52.14 | 782.8821
Total for EEM | [18 empty] | 18981.0456
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data adjusted per survey response, and per recognition of 365 day year. Survey response
applied to main areas of building (cleaning room, throughout, restrooms/private offices, and corridors); survey response "overridden" for other areas (e.g., storage)
and exit signs since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 18981.0456
CFL portion of Lighting Savings: | [18 empty] | 3320.2752
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 18981.0456
Comments: none

## 23913
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23913
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-11-09 | 88671 | 88671 | 88671
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 88671 | 88671 | 88671
Comments: lighting "details" value based on line items 1-11.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
OFFICES |  | 4' 3 lamp T-12 | 8 | 0.115 | 0.92 | 4' 2 lamp ULTRA WM REF | 8 | 0.046 | 0.368 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1457.28
PORTABLE EXTERIOR, |  | 60 watt | 8 | 0.06 | 0.48 | 13W CFL S/I | 8 | 0.013 | 0.104 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 25 | 44 | 413.6
RESTROOMS |  | 60 watt | 4 | 0.06 | 0.24 | 13W CFL S/I | 4 | 0.013 | 0.052 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 496.32
CLASSROOMS, LIBRARY, CUSTODIAN ROOM |  | 4' 3 lamp T-12 | 263 | 0.115 | 30.245 | 4' 2 lamp ULTRA WM REF | 263 | 0.046 | 12.098 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 47908.08
CLASSROOMS |  | 4' 3 lamp T-12 | 82 | 0.115 | 9.43 | 4' 2 lamp ULTRA WM REF | 82 | 0.046 | 3.772 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 14937.12
RESTROOMS, HALLS |  | 4' 2 lamp T-12 | 38 | 0.072 | 2.736 | 4' 2 lamp T/W ULTRA LP WM | 38 | 0.044 | 1.672 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2808.96
PORTABLES |  | 4' 3 lamp T-12 | 66 | 0.115 | 7.59 | 4' 2 lamp ULTRA WM REF | 66 | 0.046 | 3.036 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 12022.56
PORTABLES |  | 4' 4 lamp T-12 | 16 | 0.144 | 2.304 | 4' 2 lamp ULTRA WM REF | 16 | 0.046 | 0.736 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 4139.52
LUNCHROOM, LEVLAD LIBRARY, MULTIPURPOSE ROOMS |  | 4' 3 lamp T-8 | 33 | 0.086 | 2.838 | 4'2 lamp w/ REF | 33 | 0.058 | 1.914 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2439.36
WORK ROOM |  | 4' 4 lamp T-8 Wrap | 4 | 0.112 | 0.448 | 4' 3 lamp T-8 REF | 4 | 0.086 | 0.344 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 274.56
STAGE AREA, MULTIPURPOSE ROOM |  | 4' 3 lamp T-8 20 Feet | 24 | 0.086 | 2.064 | 4' 2 lamp T-8 REF | 24 | 0.058 | 1.392 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1774.08
88671.44
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 88671.44
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
OFFICES |  | F43EE | 8 | 0.115 | 0.92 | F42WLL | 8 | 0.051 | 0.408 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1351.68
PORTABLE EXTERIOR, |  | I60/1 | 8 | 0.06 | 0.48 | CF13/1-SCRW | 8 | 0.013 | 0.104 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 25 | 44 | 413.6
RESTROOMS |  | I60/1 | 4 | 0.06 | 0.24 | CF13/1-SCRW | 4 | 0.013 | 0.052 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 496.32
CLASSROOMS, LIBRARY, CUSTODIAN ROOM |  | F43EE | 263 | 0.115 | 30.245 | F42WLL | 263 | 0.051 | 13.413 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 44436.48
CLASSROOMS |  | F43EE | 82 | 0.115 | 9.43 | F42WLL | 82 | 0.051 | 4.182 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 13854.72
RESTROOMS, HALLS |  | F42EE | 38 | 0.072 | 2.736 | F42ILL/T2-R | 38 | 0.045 | 1.71 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2708.64
PORTABLES |  | F43EE | 66 | 0.115 | 7.59 | F42WLL | 66 | 0.051 | 3.366 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 11151.36
PORTABLES |  | F44EE | 16 | 0.144 | 2.304 | F42WLL | 16 | 0.051 | 0.816 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3928.32
LUNCHROOM, LEVLAD LIBRARY, MULTIPURPOSE ROOMS |  | F43LE | 33 | 0.11 | 3.63 | F42ILL | 33 | 0.059 | 1.947 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 4443.12
WORK ROOM |  | F44ILL | 4 | 0.112 | 0.448 | F43ILL | 4 | 0.089 | 0.356 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 242.88
STAGE AREA, MULTIPURPOSE ROOM |  | F43LE | 24 | 0.11 | 2.64 | F42ILL | 24 | 0.059 | 1.416 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3231.36
Total for EEM | [18 empty] | 86258.48
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 86258.48
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
OFFICES |  | F43EE | 8 | 0.115 | 0.92 | F42WLL | 8 | 0.051 | 0.408 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1351.68
PORTABLE EXTERIOR, |  | I60/1 | 8 | 0.06 | 0.48 | CF13/1-SCRW | 8 | 0.013 | 0.104 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 25 | 44 | 413.6
RESTROOMS |  | I60/1 | 4 | 0.06 | 0.24 | CF13/1-SCRW | 4 | 0.013 | 0.052 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 496.32
CLASSROOMS, LIBRARY, CUSTODIAN ROOM |  | F43EE | 263 | 0.115 | 30.245 | F42WLL | 263 | 0.051 | 13.413 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 44436.48
CLASSROOMS |  | F43EE | 82 | 0.115 | 9.43 | F42WLL | 82 | 0.051 | 4.182 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 13854.72
RESTROOMS, HALLS |  | F42EE | 38 | 0.072 | 2.736 | F42ILL/T2-R | 38 | 0.045 | 1.71 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2708.64
PORTABLES |  | F43EE | 66 | 0.115 | 7.59 | F42WLL | 66 | 0.051 | 3.366 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 11151.36
PORTABLES |  | F44EE | 16 | 0.144 | 2.304 | F42WLL | 16 | 0.051 | 0.816 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3928.32
LUNCHROOM, LEVLAD LIBRARY, MULTIPURPOSE ROOMS |  | F43LE | 33 | 0.11 | 3.63 | F42ILL | 33 | 0.059 | 1.947 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 4443.12
WORK ROOM |  | F44ILL | 4 | 0.112 | 0.448 | F43ILL | 4 | 0.089 | 0.356 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 242.88
STAGE AREA, MULTIPURPOSE ROOM |  | F43LE | 24 | 0.11 | 2.64 | F42ILL | 24 | 0.059 | 1.416 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3231.36
Total for EEM | [18 empty] | 86258.48
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted per survey response. Survey response
"overridden" for portables exterior area, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 86258.48
CFL portion of Lighting Savings: | [18 empty] | 909.92
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 86258.48
Comments: none

## 23914
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23914
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-12-29 | 78589 | 78589 | 78589
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 78589 | 78589 | 78589
Comments: lighting "details" value based on line items 1-11.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
LIBRARY |  | 4' 4 lamp T8 12 feet | 60 | 0.112 | 6.72 | 4' 3 lamp T8 REF | 60 | 0.086 | 5.16 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 4118.4
EXTERIOR PORTABLES |  | 60 watt | 10 | 0.06 | 0.6 | 13W CFL S/I | 10 | 0.013 | 0.13 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 723.8
GYM* |  | 400 Watt Metal Halide | 20 | 0.458 | 9.16 | New 4 Lamp T5 35 feet | 20 | 0.234 | 4.68 | 16 | 16 | 16 | 16 | 16 | 16 | 5 | 101 | 52 | 23528.96
CLASSROOMS |  | 4' 4 lamp T8 | 366 | 0.112 | 40.992 | 4' 3 lamp T8 REF | 366 | 0.086 | 31.476 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 25122.24
PORTABLES |  | 4' 3 lamp T8 | 204 | 0.086 | 17.544 | 4' 2 lamp T8 REF | 204 | 0.058 | 11.832 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 15079.68
SHOP |  | 4' 3 lamp T8 Wrap | 24 | 0.086 | 2.064 | 4' 2 lamp T8 REF | 24 | 0.058 | 1.392 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1774.08
COACHES AND RECREATION OFFICES |  | 4' 3 lamp T8 | 10 | 0.086 | 0.86 | 4' 2 lamp T8 REF | 10 | 0.058 | 0.58 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 739.2
EXERCISE ROOM |  | 4' 3 lamp T8 25 feet | 24 | 0.086 | 2.064 | 4' 2 lamp T8 REF | 24 | 0.058 | 1.392 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1774.08
KITCHEN |  | 4' 4 lamp T-12 | 9 | 0.144 | 1.296 | 4' 2 lamp ULTRA WM REF | 9 | 0.046 | 0.414 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2328.48
OFFICE |  | 4' 3 lamp T8 | 40 | 0.086 | 3.44 | 4' 2 lamp T8 REF | 40 | 0.058 | 2.32 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2956.8
OFFICE |  | 4' 3 lamp T8 Wrap | 6 | 0.086 | 0.516 | 4' 2 lamp T8 REF | 6 | 0.058 | 0.348 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 443.52
78589.24
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible);
gym 52 wk/yr assumption per paperwork.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 78589.24
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
LIBRARY |  | F44ILL | 60 | 0.112 | 6.72 | F43ILL | 60 | 0.089 | 5.34 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3643.2
EXTERIOR PORTABLES |  | I60/1 | 10 | 0.06 | 0.6 | CF13/1-SCRW | 10 | 0.013 | 0.13 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 723.8
GYM* |  | MH400/1 | 20 | 0.458 | 9.16 | F44PHL/2 | 20 | 0.234 | 4.68 | 16 | 16 | 16 | 16 | 16 | 16 | 5 | 101 | 52 | 23528.96
CLASSROOMS |  | F44ILL | 366 | 0.112 | 40.992 | F43ILL | 366 | 0.089 | 32.574 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 22223.52
PORTABLES |  | F43ILL | 204 | 0.089 | 18.156 | F42ILL | 204 | 0.059 | 12.036 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 16156.8
SHOP |  | F43ILL | 24 | 0.089 | 2.136 | F42ILL | 24 | 0.059 | 1.416 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1900.8
COACHES AND RECREATION OFFICES |  | F43ILL | 10 | 0.089 | 0.89 | F42ILL | 10 | 0.059 | 0.59 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 792
EXERCISE ROOM |  | F43ILL | 24 | 0.089 | 2.136 | F42ILL | 24 | 0.059 | 1.416 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1900.8
KITCHEN |  | F44EE | 9 | 0.144 | 1.296 | F42WLL | 9 | 0.051 | 0.459 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2209.68
OFFICE |  | F43ILL | 40 | 0.089 | 3.56 | F42ILL | 40 | 0.059 | 2.36 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3168
OFFICE |  | F43ILL | 6 | 0.089 | 0.534 | F42ILL | 6 | 0.059 | 0.354 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 475.2
Total for EEM | [18 empty] | 76722.76
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 76722.76
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
LIBRARY |  | F44ILL | 60 | 0.112 | 6.72 | F43ILL | 60 | 0.089 | 5.34 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3643.2
EXTERIOR PORTABLES |  | I60/1 | 10 | 0.06 | 0.6 | CF13/1-SCRW | 10 | 0.013 | 0.13 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 723.8
GYM* |  | MH400/1 | 20 | 0.458 | 9.16 | F44PHL/2 | 20 | 0.234 | 4.68 | 16 | 16 | 16 | 16 | 16 | 16 | 5 | 101 | 52 | 23528.96
CLASSROOMS |  | F44ILL | 366 | 0.112 | 40.992 | F43ILL | 366 | 0.089 | 32.574 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 22223.52
PORTABLES |  | F43ILL | 204 | 0.089 | 18.156 | F42ILL | 204 | 0.059 | 12.036 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 16156.8
SHOP |  | F43ILL | 24 | 0.089 | 2.136 | F42ILL | 24 | 0.059 | 1.416 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1900.8
COACHES AND RECREATION OFFICES |  | F43ILL | 10 | 0.089 | 0.89 | F42ILL | 10 | 0.059 | 0.59 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 792
EXERCISE ROOM |  | F43ILL | 24 | 0.089 | 2.136 | F42ILL | 24 | 0.059 | 1.416 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1900.8
KITCHEN |  | F44EE | 9 | 0.144 | 1.296 | F42WLL | 9 | 0.051 | 0.459 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2209.68
OFFICE |  | F43ILL | 40 | 0.089 | 3.56 | F42ILL | 40 | 0.059 | 2.36 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 3168
OFFICE |  | F43ILL | 6 | 0.089 | 0.534 | F42ILL | 6 | 0.059 | 0.354 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 475.2
Total for EEM | [18 empty] | 76722.76
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted per survey response. Survey response
"overridden" for exterior portables and gym, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 76722.76
CFL portion of Lighting Savings: | [18 empty] | 723.8
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 76722.76
Comments: none

## 23915
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23915
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-08-29 | 3517 | 3517 | 3517
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 3517 | 3517 | 3517
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F43ILL-R | 15 | 0.078 | 1.17 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 60 | 52 | 3088.8
Sales |  | I75/1 | 1 | 0.075 | 0.075 | CFQ23/1 | 1 | 0.026 | 0.026 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 428.064
Total for EEM | [18 empty] | 3516.864
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3516.864
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F43ILL-R | 15 | 0.076 | 1.14 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 60 | 52 | 3182.4
Sales |  | I75/1 | 1 | 0.075 | 0.075 | CFQ23/1 | 1 | 0.026 | 0.026 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 428.064
Total for EEM | [18 empty] | 3610.464
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R values derived using 2002 Sylvania catalog data. CFQ23 value not in SPC tables, but appears reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3610.464
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F43ILL-R | 15 | 0.076 | 1.14 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 60 | 52.14 | 3190.968
Sales |  | I75/1 | 0 | 0.075 | 0 | CFQ23/1 | 0 | 0.026 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 0
Total for EEM | [18 empty] | 3190.968
Comments: Op hours changed per recognition of 365 day year. CFQ23 fixture zeroed out since not included in Lighting Installation Report.
Overall Application Adjusted Savings: | [18 empty] | 3190.968
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 3190.968
Comments: none

## 23918
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23918
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-09-19 | 20968 | 20968 | 20968
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 20968 | 20968 | 20968
Comments: lighting "details" value based on line items 1-5.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | 4' 4 lamp T-12 | 8 | 0.144 | 1.152 | 4' 2 lamp Ultra WM Ref | 8 | 0.046 | 0.368 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 1635.1104
Main Work Area |  | 4' 4 lamp T-12 | 26 | 0.144 | 3.744 | 4' 2 lamp Ultra WM Ref | 26 | 0.046 | 1.196 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52.14 | 16739.4427
Office |  | 2' 2 lamp T-12 U-tube | 1 | 0.072 | 0.072 | 2' 2 lamp T-8, REF | 1 | 0.033 | 0.033 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 81.3384
Coolers/ Rest / Main |  | 4' 2 lamp T-12 | 9 | 0.072 | 0.648 | 4' 2 lamp Ultra LP WM | 9 | 0.046 | 0.414 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52.14 | 1537.2958
Exit Signs / Main |  | Incand, AC only | 3 | 0.04 | 0.12 | LED Exit Sign | 3 | 0.003 | 0.009 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 972.3067
20965.494
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Exit sign assumption in paperwork re 169 hr/wk overridden and changed
to 168 hr/wk (24/7 operation).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 20965.494
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44EE | 8 | 0.144 | 1.152 | F42WLL | 8 | 0.051 | 0.408 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 1551.6864
Main Work Area |  | F44EE | 26 | 0.144 | 3.744 | F42WLL | 26 | 0.051 | 1.326 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52.14 | 15885.3895
Office |  | FU2EE | 1 | 0.072 | 0.072 | F22ILL | 1 | 0.033 | 0.033 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 81.3384
Coolers/ Rest / Main |  | F42EE | 9 | 0.072 | 0.648 | F42WLL-R | 9 | 0.045 | 0.405 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52.14 | 1596.4225
Exit Signs / Main |  | EI20/2 | 3 | 0.04 | 0.12 | ELED2/2 | 3 | 0.009 | 0.027 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 814.6354
Total for EEM | [18 empty] | 19929.4722
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 19929.4722
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F44EE | 8 | 0.144 | 1.152 | F42WLL | 8 | 0.051 | 0.408 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 1551.6864
Main Work Area |  | F44EE | 26 | 0.144 | 3.744 | F42WLL | 26 | 0.051 | 1.326 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52.14 | 15885.3895
Office |  | FU2EE | 1 | 0.072 | 0.072 | F22ILL | 1 | 0.033 | 0.033 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 81.3384
Coolers/ Rest / Main |  | F42EE | 9 | 0.072 | 0.648 | F42WLL-R | 9 | 0.045 | 0.405 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 126 | 52.14 | 1596.4225
Exit Signs / Main |  | EI20/2 | 3 | 0.04 | 0.12 | ELED2/2 | 3 | 0.009 | 0.027 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 814.6354
Total for EEM | [18 empty] | 19929.4722
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted per survey response. Survey response "overridden" for
office and exit sign data, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 19929.4722
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 19929.4722
Comments: none

## 23919
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23919
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-09-09 | 73091 | 73113 | 73091
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up | 2003-10-15 | 1086 | 1086 | 1086
T-stat | 2003-10-15 | 1738 | 1738 | 1738
Overall |  | 75915 | 75937 | 75915
Comments: lighting "details" value based on line items 2-3 and 6-8; AC Tune-up "details" value based on line item 1. Tstat "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F42SE | 12 | 0.086 | 1.032 | F42ILL-R | 12 | 0.052 | 0.624 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 1188.096
Office |  | F43SE | 74 | 0.14 | 10.36 | F43ILL-R | 74 | 0.078 | 5.772 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 13360.256
Office |  | I100/1 | 6 | 0.1 | 0.6 | CFT32/1-L | 6 | 0.034 | 0.204 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 1153.152
Office |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.003 | 0.012 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1292.928
Warehouse |  | MH400/1 | 86 | 0.458 | 39.388 | F44T5 | 86 | 0.234 | 20.124 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 56096.768
Total for EEM | [18 empty] | 73091.2
Comments: all data per per paperwork. Weekly hours for non-24/7 items mapped to days using S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 12 | 62% | 2920 | 1 | 5% | [12 empty] | 1086.24
Comments: all data per per paperwork.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable |  | 12 | 62% | 2920 | 1 | 8% | [12 empty] | 1737.984
Comments: all data per per paperwork.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 75915.424
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F42SE | 12 | 0.086 | 1.032 | F42ILL-R | 12 | 0.051 | 0.612 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 1223.04
Office |  | F43SE | 74 | 0.14 | 10.36 | F43ILL-R | 74 | 0.076 | 5.624 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 13791.232
Office |  | I100/1 | 6 | 0.1 | 0.6 | CFT32/1-L | 6 | 0.034 | 0.204 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 1153.152
Office |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.009 | 0.036 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 1083.264
Warehouse |  | MH400/1 | 86 | 0.458 | 39.388 | F44PHL/2 | 86 | 0.234 | 20.124 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52 | 56096.768
Total for EEM | [18 empty] | 73347.456
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F43ILL-R values derived using 2002 Sylvania catalog data; CFT32/1-L and ELED2/2 values per SPC tables;
F44T5 listing mapped to F44PHL/2 value in SPC tables.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 12 | 62% | 2190 | 1.3 | 5% | [12 empty] | 1059.084
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. 1.3 kW/ton factor (associated with units <=5 tons) used (even though pertains to 12 tons),
since 4 tuneups were conducted, implying each unit was 12/4 = 3 tons. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable |  | 12 | 62% | 2190 | 1.3 | 15% | [12 empty] | 3177.252
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. 1.3 kW/ton factor (associated with units <=5 tons) used (even though pertains to 12 tons),
since 4 tuneups were conducted, implying each unit was 12/4 = 3 tons. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 77583.792
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | F42SE | 12 | 0.086 | 1.032 | F42ILL-R | 12 | 0.051 | 0.612 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52.14 | 1226.3328
Office |  | F43SE | 74 | 0.14 | 10.36 | F43ILL-R | 74 | 0.076 | 5.624 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52.14 | 13828.3622
Office |  | I100/1 | 6 | 0.1 | 0.6 | CFT32/1-L | 6 | 0.034 | 0.204 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52.14 | 1156.2566
Office |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.009 | 0.036 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1086.1805
Warehouse |  | MH400/1 | 86 | 0.458 | 39.388 | F44PHL/2 | 86 | 0.234 | 20.124 | 10 | 10 | 10 | 10 | 10 | 6 | 0 | 56 | 52.14 | 56247.7978
Total for EEM | [18 empty] | 73544.9299
Comments: kWh/yr savings data are same as step 3, except for operational data. Survey response "overridden" for op data re exit signs since ASW data appear intuitively
correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 77781.2659
CFL portion of Lighting Savings: | [18 empty] | 1156.2566
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 77781.2659
Comments: none

## 23921
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23921
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-08-29 | 3517 | 3517 | 3517
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 3517 | 3517 | 3517
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F43ILL-R | 15 | 0.078 | 1.17 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 60 | 52 | 3088.8
Sales |  | I75/1 | 1 | 0.075 | 0.075 | CFQ23/1 | 1 | 0.026 | 0.026 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 428.064
Total for EEM | [18 empty] | 3516.864
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3516.864
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F43ILL-R | 15 | 0.076 | 1.14 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 60 | 52 | 3182.4
Sales |  | I75/1 | 1 | 0.075 | 0.075 | CFQ23/1 | 1 | 0.026 | 0.026 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 428.064
Total for EEM | [18 empty] | 3610.464
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R values derived using 2002 Sylvania catalog data. CFQ23 value not in SPC tables, but appears reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 3610.464
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 15 | 0.144 | 2.16 | F43ILL-R | 15 | 0.076 | 1.14 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 10 | 0 | 52.5 | 52.14 | 2792.097
Sales |  | I75/1 | 1 | 0.075 | 0.075 | CFQ23/1 | 1 | 0.026 | 0.026 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 429.2165
Total for EEM | [18 empty] | 3221.3135
Comments: Op hours changed per survey response, and per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 3221.3135
CFL portion of Lighting Savings: | [18 empty] | 429.2165
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 3221.3135
Comments: none

## 23924
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23924
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-09-19 | 41681 | 41681 | 41681
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 41681 | 41681 | 41681
Comments: lighting "details" value based on line items 1-9.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office Surface 4X4 |  | 4' 4 lamp T12 | 20 | 0.144 | 2.88 | 4' 2 lamp Ultra WM REF | 20 | 0.046 | 0.92 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 4087.776
Office Surface 2X4 |  | 4' 4 lamp T12 | 30 | 0.144 | 4.32 | 4' 2 lamp Ultra WM REF | 30 | 0.046 | 1.38 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 6131.664
Operations 2X4 |  | 4' 2 lamp T12 | 38 | 0.072 | 2.736 | 4' 2 lamp Ultra LP WM | 38 | 0.046 | 1.748 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 8654.4058
Restroom 1X4 |  | 4' 2 lamp T12 | 6 | 0.072 | 0.432 | 4' 2 lamp Ultra LP WM | 6 | 0.046 | 0.276 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 325.3536
Operations 1X4 |  | 4' 2 lamp T12 | 19 | 0.072 | 1.368 | 4' 2 lamp Ultra LP WM | 19 | 0.046 | 0.874 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 4327.2029
Dry Chemicals |  | 4' 2 lamp T12 | 30 | 0.072 | 2.16 | 4' 2 lamp Ultra LP WM | 30 | 0.046 | 1.38 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 6832.4256
Chorine |  | 4' 2 lamp T12 | 40 | 0.072 | 2.88 | 4' 2 lamp Ultra LP WM | 40 | 0.046 | 1.84 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 9109.9008
Hydro |  | 4' 2 lamp T12 | 9 | 0.072 | 0.648 | 4' 2 lamp Ultra LP WM | 9 | 0.046 | 0.414 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 2049.7277
Office Recessed 2X2 |  | 2' 2 lamp T12 U-tube | 2 | 0.072 | 0.144 | 2' 2 lamp T-8 REF | 2 | 0.033 | 0.066 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 162.6768
41681.1331
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Exit sign assumption in paperwork re 169 hr/wk overridden and changed
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 41681.1331
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office Surface 4X4 |  | F44EE | 20 | 0.144 | 2.88 | F42WLL | 20 | 0.051 | 1.02 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 3879.216
Office Surface 2X4 |  | F44EE | 30 | 0.144 | 4.32 | F42WLL | 30 | 0.051 | 1.53 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 5818.824
Operations 2X4 |  | F42EE | 38 | 0.072 | 2.736 | F42WLL-R | 38 | 0.045 | 1.71 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 8987.2675
Restroom 1X4 |  | F42EE | 6 | 0.072 | 0.432 | F42WLL-R | 6 | 0.045 | 0.27 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 337.8672
Operations 1X4 |  | F42EE | 19 | 0.072 | 1.368 | F42WLL-R | 19 | 0.045 | 0.855 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 4493.6338
Dry Chemicals |  | F42EE | 30 | 0.072 | 2.16 | F42WLL-R | 30 | 0.045 | 1.35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 7095.2112
Chorine |  | F42EE | 40 | 0.072 | 2.88 | F42WLL-R | 40 | 0.045 | 1.8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 9460.2816
Hydro |  | F42EE | 9 | 0.072 | 0.648 | F42WLL-R | 9 | 0.045 | 0.405 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 2128.5634
Office Recessed 2X2 |  | FU2EE | 2 | 0.072 | 0.144 | F42WLL-R | 2 | 0.045 | 0.09 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 112.6224
Total for EEM | [18 empty] | 42313.487
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 42313.487
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office Surface 4X4 |  | F44EE | 20 | 0.144 | 2.88 | F42WLL | 20 | 0.051 | 1.02 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 3879.216
Office Surface 2X4 |  | F44EE | 30 | 0.144 | 4.32 | F42WLL | 30 | 0.051 | 1.53 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 5818.824
Operations 2X4 |  | F42EE | 38 | 0.072 | 2.736 | F42WLL-R | 38 | 0.045 | 1.71 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 8987.2675
Restroom 1X4 |  | F42EE | 6 | 0.072 | 0.432 | F42WLL-R | 6 | 0.045 | 0.27 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 337.8672
Operations 1X4 |  | F42EE | 19 | 0.072 | 1.368 | F42WLL-R | 19 | 0.045 | 0.855 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 4493.6338
Dry Chemicals |  | F42EE | 30 | 0.072 | 2.16 | F42WLL-R | 30 | 0.045 | 1.35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 7095.2112
Chorine |  | F42EE | 40 | 0.072 | 2.88 | F42WLL-R | 40 | 0.045 | 1.8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 9460.2816
Hydro |  | F42EE | 9 | 0.072 | 0.648 | F42WLL-R | 9 | 0.045 | 0.405 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 2128.5634
Office Recessed 2X2 |  | FU2EE | 2 | 0.072 | 0.144 | F42WLL-R | 2 | 0.045 | 0.09 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 112.6224
Total for EEM | [18 empty] | 42313.487
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted, per survey response.
Overall Application Adjusted Savings: | [18 empty] | 42313.487
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 42313.487
Comments: none

## 23925
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23925
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-09-30 | 15493 | 15494 | 15493
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 15493 | 15494 | 15493
Comments: lighting "details" value based on line items 1-5.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Main Kitchen Area |  | 4' 4 lamp T-12 | 26 | 0.144 | 3.744 | 4' 2 lamp Ultra WM Ref | 26 | 0.046 | 1.196 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 13949.5356
Coolers |  | 4' 2 lamp T-12 | 2 | 0.072 | 0.144 | 4' 2 lamp Ultra LP WM | 2 | 0.046 | 0.092 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 284.6844
Main Kitchen Area |  | 2' 2 lamp T-12 U-tube | 1 | 0.072 | 0.072 | 2' 2 lamp T-8, Ref | 1 | 0.033 | 0.033 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 213.5133
Front Customer Counter |  | 40 watt | 3 | 0.04 | 0.12 | 11W CFL S/I | 3 | 0.013 | 0.039 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 443.4507
Restroom |  | 75 watt | 2 | 0.075 | 0.15 | 18W CFL S/I | 2 | 0.02 | 0.04 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 602.217
15493.401
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 15493.401
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Main Kitchen Area |  | F44EE | 26 | 0.144 | 3.744 | F42WLL | 26 | 0.051 | 1.326 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 13237.8246
Coolers |  | F42EE | 2 | 0.072 | 0.144 | F42WLL-R | 2 | 0.045 | 0.09 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 295.6338
Main Kitchen Area |  | FU2EE | 1 | 0.072 | 0.072 | F22ILL | 1 | 0.033 | 0.033 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 213.5133
Front Customer Counter |  | I40/1 | 3 | 0.04 | 0.12 | CF11/1-SCRW | 3 | 0.011 | 0.033 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 476.2989
Restroom |  | I75/1 | 2 | 0.075 | 0.15 | CF18/1-SCRW | 2 | 0.018 | 0.036 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 624.1158
Total for EEM | [18 empty] | 14847.3864
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 14847.3864
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Main Kitchen Area |  | F44EE | 26 | 0.144 | 3.744 | F42WLL | 26 | 0.051 | 1.326 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 13237.8246
Coolers |  | F42EE | 2 | 0.072 | 0.144 | F42WLL-R | 2 | 0.045 | 0.09 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 295.6338
Main Kitchen Area |  | FU2EE | 1 | 0.072 | 0.072 | F22ILL | 1 | 0.033 | 0.033 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 213.5133
Front Customer Counter |  | I40/1 | 3 | 0.04 | 0.12 | CF11/1-SCRW | 3 | 0.011 | 0.033 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 476.2989
Restroom |  | I75/1 | 2 | 0.075 | 0.15 | CF18/1-SCRW | 2 | 0.018 | 0.036 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105 | 52.14 | 624.1158
Total for EEM | [18 empty] | 14847.3864
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted, per survey response.
Overall Application Adjusted Savings: | [18 empty] | 14847.3864
CFL portion of Lighting Savings: | [18 empty] | 1100.4147
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 14847.3864
Comments: none

## 23931
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23931
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-09-23 | 27269 | 27269 | 27269
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up | 2003-10-21 | 2382 | 2382 | 2382
T-stat |  | 0 | 0 | 0
Overall |  | 29651 | 29651 | 29651
Comments: lighting "details" value based on line items 1-4; AC Tune-up "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43EE | 126 | 0.115 | 14.49 | F42ILL-R | 126 | 0.052 | 6.552 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 26004.888
Sales |  | F42SE | 6 | 0.086 | 0.516 | F42ILL-R | 6 | 0.052 | 0.312 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 668.304
Sales |  | FU2SE | 1 | 0.086 | 0.086 | FU2ILL-R | 1 | 0.052 | 0.052 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 111.384
Sales |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.003 | 0.012 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 484.848
Total for EEM | [18 empty] | 27269.424
Comments: all data per per paperwork. Weekly hours for non-24/7 items mapped to days based on data in "customer information" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 25 | 58% | 3285 | 1 | 5% | [12 empty] | 2381.625
Comments: all data per per paperwork.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: all data per per paperwork.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 29651.049
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43EE | 126 | 0.115 | 14.49 | F42ILL-R | 126 | 0.051 | 6.426 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 26417.664
Sales |  | F42SE | 6 | 0.086 | 0.516 | F42ILL-R | 6 | 0.051 | 0.306 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 687.96
Sales |  | FU2SE | 1 | 0.086 | 0.086 | FU2ILL-R | 1 | 0.052 | 0.052 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 111.384
Sales |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.009 | 0.036 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52 | 406.224
Total for EEM | [18 empty] | 27623.232
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F42ILL-R and F43ILL-R values derived using 2002 Sylvania catalog data; FU2ILL-R per SPC tables;
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Retail, No Economizer |  | 25 | 58% | 2463.75 | 1.1 | 5% | [12 empty] | 1964.8406
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. 1.1 kW/ton factor (associated with units >5 tons) used, since
since 3 tuneups were conducted, implying typical size of each unit was 25/3 = 8.33 tons. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. 1.3 kW/ton factor (associated with units <=5 tons) used (even though pertains to 12 tons),
since 4 tuneups were conducted, implying each unit was 12/4 = 3 tons.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 29588.0726
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM | [18 empty] | 1
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM | [18 empty] | 1
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43EE | 126 | 0.115 | 14.49 | F42ILL-R | 126 | 0.051 | 6.426 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52.14 | 26488.7885
Sales |  | F42SE | 6 | 0.086 | 0.516 | F42ILL-R | 6 | 0.051 | 0.306 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52.14 | 689.8122
Sales |  | FU2SE | 1 | 0.086 | 0.086 | FU2ILL-R | 1 | 0.052 | 0.052 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 63 | 52.14 | 111.6839
Sales |  | EI20/2 | 4 | 0.04 | 0.16 | ELED2/2 | 4 | 0.009 | 0.036 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52.14 | 1086.1805
Total for EEM | [18 empty] | 28376.465
Comments: kWh/yr savings data are same as step 3, except for operational data. Op hours changed per recognition of 365 day year, and to reflect 24/7 operation for exit signs.
Overall Application Adjusted Savings: | [18 empty] | 30341.3057
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 30341.3057
Comments: none

## 23951
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23951
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-12-29 | 72014 | 72014 | 72014
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 72014 | 72014 | 72014
Comments: lighting "details" value based on line items 1-5.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
CLASSROOMS, LIBRARY,ART DEPT., PE LOCKEROOMS, OFFICES |  | 4' 4-lamp T8 | 691 | 0.11 | 76.01 | 4' 3-lamp, existing ballast, reflector | 691 | 0.088 | 60.808 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 40133.28
KITCHEN |  | 4' 4 lamp T-12 | 9 | 0.144 | 1.296 | 4' 2 lamp ULTRA WM REF | 9 | 0.046 | 0.414 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2328.48
PORTABLES |  | 4' 4 lamp T-12 | 54 | 0.144 | 7.776 | 4' 2 lamp ULTRA WM REF | 54 | 0.046 | 2.484 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 13970.88
LAB |  | 4' 3 lamp T8 | 12 | 0.086 | 1.032 | 4' 2 lamp. Existing ballast T8 REF. | 12 | 0.069 | 0.828 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 538.56
GYM |  | 400 Watt Metal Hallide | 16 | 0.46 | 7.36 | New 4-lamp T5 Fixture | 16 | 0.234 | 3.744 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52 | 15042.56
72013.76
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible),
except for gym (52 wk/yr).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 72013.76
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
CLASSROOMS, LIBRARY,ART DEPT., PE LOCKEROOMS, OFFICES |  | F44ILL | 691 | 0.112 | 77.392 | F43ILL | 691 | 0.089 | 61.499 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 41957.52
KITCHEN |  | F44EE | 9 | 0.144 | 1.296 | F42WLL | 9 | 0.051 | 0.459 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2209.68
PORTABLES |  | F44EE | 54 | 0.144 | 7.776 | F42WLL | 54 | 0.051 | 2.754 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 13258.08
LAB |  | F43ILL | 12 | 0.089 | 1.068 | F42ILL | 12 | 0.059 | 0.708 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 950.4
GYM |  | MH400/1 | 16 | 0.458 | 7.328 | F44PHL/2 | 16 | 0.234 | 3.744 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52 | 14909.44
Total for EEM | [18 empty] | 73285.12
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 73285.12
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
CLASSROOMS, LIBRARY,ART DEPT., PE LOCKEROOMS, OFFICES |  | F44ILL | 691 | 0.112 | 77.392 | F43ILL | 691 | 0.089 | 61.499 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 41957.52
KITCHEN |  | F44EE | 9 | 0.144 | 1.296 | F42WLL | 9 | 0.051 | 0.459 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2209.68
PORTABLES |  | F44EE | 54 | 0.144 | 7.776 | F42WLL | 54 | 0.051 | 2.754 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 13258.08
LAB |  | F43ILL | 12 | 0.089 | 1.068 | F42ILL | 12 | 0.059 | 0.708 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 950.4
GYM |  | MH400/1 | 16 | 0.458 | 7.328 | F44PHL/2 | 16 | 0.234 | 3.744 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52 | 14909.44
Total for EEM | [18 empty] | 73285.12
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted per survey response. Survey response
"overridden" for gym, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 73285.12
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 73285.12
Comments: none

## 23952
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23952
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-12-29 | 70838 | 70837 | 70838
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 70838 | 70837 | 70838
Comments: lighting "details" value based on line items 1-7.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
CLASSROOMS, LIBRARY, TEACHER'S WORKROOM. SCIENCE LAB, BAND ROOM, SHOP OFFICES |  | 4 ft 4-lamp T8 | 365 | 0.11 | 40.15 | 4' 3-lamp, existing ballast, reflector | 365 | 0.088 | 32.12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 21199.2
PORTABLES, KITCHEN, COPIER ROOM |  | 4' 4 lamp T-12 | 81 | 0.144 | 11.664 | 4' 2 lamp ULTRA WM REF | 81 | 0.046 | 3.726 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 20956.32
COPIER ROOM, LOCKEROOMS |  | 4' 2 lamp T-12 | 29 | 0.072 | 2.088 | 4' 2 lamp ULTRA LP WM | 29 | 0.046 | 1.334 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1990.56
LOCKEROOMS |  | 4' 2 lamp T-12 | 58 | 0.072 | 4.176 | 4' 2 lamp T/W ULTRA LP WM | 58 | 0.044 | 2.552 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 4287.36
CLASSROOM, LIBRARY, BAND, SHOP |  | 8' 2-8' lamp T-12 | 68 | 0.123 | 8.364 | 4' 4 lamp ULTRA KIT LP WM | 68 | 0.088 | 5.984 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 6283.2
GYM |  | 250 Watt Metal Hallide | 24 | 0.293 | 7.032 | New 4 lamp T8 Fixt/ High Drive ballast 25 feet | 24 | 0.138 | 3.312 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52 | 15475.2
THROUGHOUT |  | Incand, Battery BU, 2ckt | 2 | 0.04 | 0.08 | LED, BBU/2CKT | 2 | 0.003 | 0.006 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 646.464
70838.304
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible),
except for gym & exit lights (52 wk/yr).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 70838.304
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
CLASSROOMS, LIBRARY, TEACHER'S WORKROOM. SCIENCE LAB, BAND ROOM, SHOP OFFICES |  | F44ILL | 365 | 0.112 | 40.88 | F43ILL | 365 | 0.089 | 32.485 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 22162.8
PORTABLES, KITCHEN, COPIER ROOM |  | F44EE | 81 | 0.144 | 11.664 | F42WLL | 81 | 0.051 | 4.131 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 19887.12
COPIER ROOM, LOCKEROOMS |  | F42EE | 29 | 0.072 | 2.088 | F42WLL-R | 29 | 0.045 | 1.305 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2067.12
LOCKEROOMS |  | F42EE | 58 | 0.072 | 4.176 | F42WLL/T2 | 58 | 0.045 | 2.61 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 4134.24
CLASSROOM, LIBRARY, BAND, SHOP |  | F82EE | 68 | 0.123 | 8.364 | F44WLL-R | 68 | 0.09 | 6.12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 5924.16
GYM |  | MH250/1 | 24 | 0.288 | 6.912 | F44ILL-V | 24 | 0.151 | 3.624 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52 | 13678.08
THROUGHOUT |  | EI20/2 | 2 | 0.04 | 0.08 | ELED2/2 | 2 | 0.009 | 0.018 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 541.632
Total for EEM | [18 empty] | 68395.152
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 68395.152
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
CLASSROOMS, LIBRARY, TEACHER'S WORKROOM. SCIENCE LAB, BAND ROOM, SHOP OFFICES |  | F44ILL | 365 | 0.112 | 40.88 | F43ILL | 365 | 0.089 | 32.485 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 22162.8
PORTABLES, KITCHEN, COPIER ROOM |  | F44EE | 81 | 0.144 | 11.664 | F42WLL | 81 | 0.051 | 4.131 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 19887.12
COPIER ROOM, LOCKEROOMS |  | F42EE | 29 | 0.072 | 2.088 | F42WLL-R | 29 | 0.045 | 1.305 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2067.12
LOCKEROOMS |  | F42EE | 58 | 0.072 | 4.176 | F42WLL/T2 | 58 | 0.045 | 2.61 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 4134.24
CLASSROOM, LIBRARY, BAND, SHOP |  | F82EE | 68 | 0.123 | 8.364 | F44WLL-R | 68 | 0.09 | 6.12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 5924.16
GYM |  | MH250/1 | 24 | 0.288 | 6.912 | F44ILL-V | 24 | 0.151 | 3.624 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 80 | 52 | 13678.08
THROUGHOUT |  | EI20/2 | 2 | 0.04 | 0.08 | ELED2/2 | 2 | 0.009 | 0.018 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168 | 52 | 541.632
Total for EEM | [18 empty] | 68395.152
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted per survey response. Survey response
"overridden" for gym and exit lights, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 68395.152
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 68395.152
Comments: none

## 23954
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23954
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-10-02 | 1592 | 1606 | 1592
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 1592 | 1606 | 1592
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | I65/1F | 17 | 0.065 | 1.105 | CFQ20/1 | 17 | 0.023 | 0.391 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52 | 1485.12
Office |  | FC60 | 2 | 0.06 | 0.12 | CFQ13/2 | 2 | 0.034 | 0.068 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52 | 108.16
Total for EEM | [18 empty] | 1593.28
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1593.28
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | I65/1F | 17 | 0.065 | 1.105 | CFQ20/1 | 17 | 0.023 | 0.391 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52 | 1485.12
Office |  | FC60 | 2 | 0.063 | 0.126 | CFQ13/2 | 2 | 0.031 | 0.062 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52 | 133.12
Total for EEM | [18 empty] | 1618.24
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: I65 value appear reasonable (hence unchanged); FC60 fixture not in SPC tables, so
wattages inferred from FC40 value. Installed kW/fixture data: CFQ23 value not in SPC tables, but appears reasonable (hence unchanged). CFQ13/2 value changed per SPC tables.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1618.24
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office |  | I65/1F | 17 | 0.065 | 1.105 | CFQ20/1 | 17 | 0.023 | 0.391 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 1489.1184
Office |  | FC60 | 2 | 0.063 | 0.126 | CFQ13/2 | 2 | 0.031 | 0.062 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 52.14 | 133.4784
Total for EEM | [18 empty] | 1622.5968
Comments: Op hours changed per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 1622.5968
CFL portion of Lighting Savings: | [18 empty] | 1622.5968
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1622.5968
Comments: none

## 23958
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23958
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-12-29 | 32580 | 32581 | 32580
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 32580 | 32581 | 32580
Comments: lighting "details" value based on line items 1-16.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
closet |  | 200W inc | 1 | 0.2 | 0.2 | 20W CFL S/I | 1 | 0.02 | 0.02 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 79.2
lunch room soffit |  | 8' 1-8' lamp T-12 | 2 | 0.081 | 0.162 | 4' 2 lamp T-8,KIT-LP | 2 | 0.046 | 0.092 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 154
copy center, warehouse, maint, spec ed |  | 8' 2-8' lamp T-12 | 38 | 0.123 | 4.674 | 4' 4 lamp ULTRA KIT LP WM | 38 | 0.088 | 3.344 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2926
copy center office, loft area |  | 8' 2-lamp; T-12 | 2 | 0.128 | 0.256 | New 8' strip 4 4' T8 lamps & LP Ballast | 2 | 0.096 | 0.192 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 140.8
copy center office |  | 8' 2-lamp; T-12 | 1 | 0.128 | 0.128 | New 4ft Wrap fixt 2 lamps with Reflector | 1 | 0.058 | 0.058 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 154
carpenter shop |  | 8' 4-lamp T-12 | 1 | 0.246 | 0.246 | New 8' strip 4 4' T8 lamps | 1 | 0.108 | 0.108 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 303.6
lunchroom |  | 90W inc | 1 | 0.09 | 0.09 | 20W CFL S/I | 1 | 0.02 | 0.02 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 154
D1, D2, open area, offices |  | 4' 4-lamp T8 | 48 | 0.108 | 5.184 | 4' 2-lamp T8, reflector 8/41 Lamps | 48 | 0.046 | 2.208 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 6547.2
lofts |  | 300W inc | 1 | 0.3 | 0.3 | 20W CFL S/I | 1 | 0.02 | 0.02 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 616
closet |  | 40W inc | 1 | 0.04 | 0.04 | 15W CFL S/I | 1 | 0.015 | 0.015 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 11
hall |  | 4' 1 lamp T-12 | 2 | 0.128 | 0.256 | 4' 1 lamp ULTRA LP WM | 2 | 0.023 | 0.046 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 462
loft, offices, restrooms, lunchroom, pupil services |  | 4' 2 lamp T-12 | 68 | 0.072 | 4.896 | 4' 2 lamp ULTRA LP WM | 68 | 0.046 | 3.128 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 3889.6
lead office closet |  | 4' 3 lamp T-12 | 5 | 0.115 | 0.575 | 4' 3 lamp ULTRA LP WM | 5 | 0.067 | 0.335 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 105.6
text book storage. Copy center, locksmith, admin bldg, hall, reception |  | 4' 4 lamp T-12 | 83 | 0.128 | 10.624 | 4' 2 lamp ULTRA WM REF | 83 | 0.046 | 3.818 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 14973.2
restrooms, closets, outside |  | 52W inc | 24 | 0.052 | 1.248 | 15W CFL S/I | 24 | 0.015 | 0.36 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 1953.6
utility closet |  | 65W inc flood | 1 | 0.065 | 0.065 | 15W CFL S/I | 1 | 0.015 | 0.015 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 110
32579.8
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 32579.8
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
closet |  | I200/1 | 1 | 0.2 | 0.2 | CF20/1-SCRW | 1 | 0.02 | 0.02 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 79.2
lunch room soffit |  | F81ES | 2 | 0.075 | 0.15 | F42ILL-R | 2 | 0.052 | 0.104 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 101.2
copy center, warehouse, maint, spec ed |  | F82EE | 38 | 0.123 | 4.674 | F44WLL-R | 38 | 0.09 | 3.42 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2758.8
copy center office, loft area |  | F82EE | 2 | 0.123 | 0.246 | F44ILL-R | 2 | 0.102 | 0.204 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 92.4
copy center office |  | F82EE | 1 | 0.123 | 0.123 | F42ILL | 1 | 0.059 | 0.059 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 140.8
carpenter shop |  | F84EE | 1 | 0.246 | 0.246 | F44ILL | 1 | 0.112 | 0.112 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 294.8
lunchroom |  | I90/1 | 1 | 0.09 | 0.09 | CF20/1-SCRW | 1 | 0.02 | 0.02 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 154
D1, D2, open area, offices |  | F44ILL | 48 | 0.112 | 5.376 | F42ILL | 48 | 0.059 | 2.832 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 5596.8
lofts |  | I300/1 | 1 | 0.3 | 0.3 | CF20/1-SCRW | 1 | 0.02 | 0.02 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 616
closet |  | I40/1 | 1 | 0.04 | 0.04 | CF15/1-SCRW | 1 | 0.015 | 0.015 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 11
hall |  | F41EE | 2 | 0.043 | 0.086 | F41WLL-R | 2 | 0.024 | 0.048 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 83.6
loft, offices, restrooms, lunchroom, pupil services |  | F42EE | 68 | 0.072 | 4.896 | F42WLL-R | 68 | 0.045 | 3.06 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 4039.2
lead office closet |  | F43EE | 5 | 0.115 | 0.575 | F43WLL-R | 5 | 0.067 | 0.335 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 105.6
text book storage. Copy center, locksmith, admin bldg, hall, reception |  | F44EE | 83 | 0.144 | 11.952 | F42WLL-R | 83 | 0.045 | 3.735 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 18077.4
restrooms, closets, outside |  | I52/1 | 24 | 0.052 | 1.248 | CF15/1-SCRW | 24 | 0.015 | 0.36 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 1953.6
utility closet |  | I65/1F | 1 | 0.065 | 0.065 | CF15/1-SCRW | 1 | 0.015 | 0.015 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 110
Total for EEM | [18 empty] | 34214.4
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 34214.4
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
closet |  | I200/1 | 1 | 0.2 | 0.2 | CF20/1-SCRW | 1 | 0.02 | 0.02 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 79.2
lunch room soffit |  | F81ES | 2 | 0.075 | 0.15 | F42ILL-R | 2 | 0.052 | 0.104 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 101.2
copy center, warehouse, maint, spec ed |  | F82EE | 38 | 0.123 | 4.674 | F44WLL-R | 38 | 0.09 | 3.42 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2758.8
copy center office, loft area |  | F82EE | 2 | 0.123 | 0.246 | F44ILL-R | 2 | 0.102 | 0.204 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 92.4
copy center office |  | F82EE | 1 | 0.123 | 0.123 | F42ILL | 1 | 0.059 | 0.059 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 140.8
carpenter shop |  | F84EE | 1 | 0.246 | 0.246 | F44ILL | 1 | 0.112 | 0.112 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 294.8
lunchroom |  | I90/1 | 1 | 0.09 | 0.09 | CF20/1-SCRW | 1 | 0.02 | 0.02 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 154
D1, D2, open area, offices |  | F44ILL | 48 | 0.112 | 5.376 | F42ILL | 48 | 0.059 | 2.832 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 5596.8
lofts |  | I300/1 | 1 | 0.3 | 0.3 | CF20/1-SCRW | 1 | 0.02 | 0.02 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 616
closet |  | I40/1 | 1 | 0.04 | 0.04 | CF15/1-SCRW | 1 | 0.015 | 0.015 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 11
hall |  | F41EE | 2 | 0.043 | 0.086 | F41WLL-R | 2 | 0.024 | 0.048 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 83.6
loft, offices, restrooms, lunchroom, pupil services |  | F42EE | 68 | 0.072 | 4.896 | F42WLL-R | 68 | 0.045 | 3.06 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 4039.2
lead office closet |  | F43EE | 5 | 0.115 | 0.575 | F43WLL-R | 5 | 0.067 | 0.335 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 10 | 44 | 105.6
text book storage. Copy center, locksmith, admin bldg, hall, reception |  | F44EE | 83 | 0.144 | 11.952 | F42WLL-R | 83 | 0.045 | 3.735 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 18077.4
restrooms, closets, outside |  | I52/1 | 24 | 0.052 | 1.248 | CF15/1-SCRW | 24 | 0.015 | 0.36 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 1953.6
utility closet |  | I65/1F | 1 | 0.065 | 0.065 | CF15/1-SCRW | 1 | 0.015 | 0.015 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 110
Total for EEM | [18 empty] | 34214.4
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted per survey response. Survey response
"overridden" for closets, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 34214.4
CFL portion of Lighting Savings: | [18 empty] | 2923.8
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 34214.4
Comments: none

## 23964
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23964
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-12-01 | 68413 | 68413 | 68413
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 68413 | 68413 | 68413
Comments: lighting "details" value based on line items 1-8.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
classrooms |  | 4' 4 lamp T-8 | 288 | 0.11 | 31.68 | 4' 2-lamp, reflector 8/41 Lamps | 288 | 0.058 | 16.704 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 32947.2
Bungalows D1 to D6 |  | 4' 4 lamp T-12 | 72 | 0.144 | 10.368 | 4' 2 lamp ULTRA WM REF | 72 | 0.046 | 3.312 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 15523.2
Bungalow D7 |  | 4' 3 lamp T-12 | 16 | 0.115 | 1.84 | 4' 2 lamp ULTRA WM REF | 16 | 0.046 | 0.736 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2428.8
Bungalow D7 toilets used as storage |  | 4' 2 lamp T-12 | 2 | 0.072 | 0.144 | 4' 2 lamp ULTRA LP WM | 2 | 0.046 | 0.092 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 20 | 44 | 45.76
multipurpose bldg |  | 4' 4 lamp T-12 | 48 | 0.144 | 6.912 | 4' 2 lamp ULTRA WM REF | 48 | 0.046 | 2.208 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 10348.8
library |  | 4' 3-lamp T-8 | 32 | 0.086 | 2.752 | 2 lamps, reflector, existing ballast | 32 | 0.069 | 2.208 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 1196.8
admin |  | 4' 3-lamp T-8 | 36 | 0.086 | 3.096 | 2 lamps, reflector, existing ballast | 36 | 0.069 | 2.484 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 1346.4
kindergarten rooms |  | 4' 4 lamp T-8 | 40 | 0.11 | 4.4 | 4' 2-lamp, reflector 8/41 Lamps | 40 | 0.058 | 2.32 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 4576
68412.96
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 68412.96
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
classrooms |  | F44ILL | 288 | 0.112 | 32.256 | F42ILL | 288 | 0.059 | 16.992 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 33580.8
Bungalows D1 to D6 |  | F44EE | 72 | 0.144 | 10.368 | F42WLL | 72 | 0.051 | 3.672 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 14731.2
Bungalow D7 |  | F43EE | 16 | 0.115 | 1.84 | F42WLL | 16 | 0.051 | 0.816 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2252.8
Bungalow D7 toilets used as storage |  | F42EE | 2 | 0.072 | 0.144 | F42WLL | 2 | 0.051 | 0.102 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 20 | 44 | 36.96
multipurpose bldg |  | F44EE | 48 | 0.144 | 6.912 | F42WLL | 48 | 0.051 | 2.448 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 9820.8
library |  | F43ILL | 32 | 0.089 | 2.848 | F42ILL | 32 | 0.059 | 1.888 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2112
admin |  | F43ILL | 36 | 0.089 | 3.204 | F42ILL | 36 | 0.059 | 2.124 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2376
kindergarten rooms |  | F44ILL | 40 | 0.112 | 4.48 | F42ILL | 40 | 0.059 | 2.36 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 4664
Total for EEM | [18 empty] | 69574.56
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 69574.56
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
classrooms |  | F44ILL | 288 | 0.112 | 32.256 | F42ILL | 288 | 0.059 | 16.992 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 33580.8
Bungalows D1 to D6 |  | F44EE | 72 | 0.144 | 10.368 | F42WLL | 72 | 0.051 | 3.672 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 14731.2
Bungalow D7 |  | F43EE | 16 | 0.115 | 1.84 | F42WLL | 16 | 0.051 | 0.816 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2252.8
Bungalow D7 toilets used as storage |  | F42EE | 2 | 0.072 | 0.144 | F42WLL | 2 | 0.051 | 0.102 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 20 | 44 | 36.96
multipurpose bldg |  | F44EE | 48 | 0.144 | 6.912 | F42WLL | 48 | 0.051 | 2.448 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 9820.8
library |  | F43ILL | 32 | 0.089 | 2.848 | F42ILL | 32 | 0.059 | 1.888 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2112
admin |  | F43ILL | 36 | 0.089 | 3.204 | F42ILL | 36 | 0.059 | 2.124 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 2376
kindergarten rooms |  | F44ILL | 40 | 0.112 | 4.48 | F42ILL | 40 | 0.059 | 2.36 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 4664
Total for EEM | [18 empty] | 69574.56
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not adjusted per survey response. Survey response
"overridden" for storage area, since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 69574.56
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 69574.56
Comments: none

## 23965
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23965
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-11-12 | 29195 | 29194 | 29195
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 29195 | 29194 | 29195
Comments: lighting "details" value based on line items 1-4.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
restroom in multipurpose bldg |  | 4' 4 lamp T-8 | 1 | 0.11 | 0.11 | 4' 2-lamp, reflector 8/41 Lamps | 1 | 0.058 | 0.058 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 25 | 44 | 57.2
custodian office |  | 4' 4 lamp T-8 | 1 | 0.11 | 0.11 | 4' 2-lamp, reflector 8/41 Lamps | 1 | 0.058 | 0.058 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 80.08
classrooms, library, kindergarten |  | 4' 4 lamp T-8 | 246 | 0.11 | 27.06 | 4' 2-lamp, reflector 8/41 Lamps | 246 | 0.058 | 14.268 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 28142.4
office 26, 27 |  | 4' 4 lamp T-8 | 8 | 0.11 | 0.88 | 4' 2-lamp, reflector 8/41 Lamps | 8 | 0.058 | 0.464 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 915.2
29194.88
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 29194.88
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
restroom in multipurpose bldg |  | F44ILL | 1 | 0.112 | 0.112 | F42ILL | 1 | 0.059 | 0.059 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 25 | 44 | 58.3
custodian office |  | F44ILL | 1 | 0.112 | 0.112 | F42ILL | 1 | 0.059 | 0.059 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 81.62
classrooms, library, kindergarten |  | F44ILL | 246 | 0.112 | 27.552 | F42ILL | 246 | 0.059 | 14.514 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 28683.6
office 26, 27 |  | F44ILL | 8 | 0.112 | 0.896 | F42ILL | 8 | 0.059 | 0.472 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 932.8
Total for EEM | [18 empty] | 29756.32
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 29756.32
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
restroom in multipurpose bldg |  | F44ILL | 1 | 0.112 | 0.112 | F42ILL | 1 | 0.059 | 0.059 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 25 | 44 | 58.3
custodian office |  | F44ILL | 1 | 0.112 | 0.112 | F42ILL | 1 | 0.059 | 0.059 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 81.62
classrooms, library, kindergarten |  | F44ILL | 246 | 0.112 | 27.552 | F42ILL | 246 | 0.059 | 14.514 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 28683.6
office 26, 27 |  | F44ILL | 8 | 0.112 | 0.896 | F42ILL | 8 | 0.059 | 0.472 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 44 | 932.8
Total for EEM | [18 empty] | 29756.32
Comments: kWh/yr savings data are same as step 3, except for operational data. Survey response "overridden" for op data re restroom and custodian office since ASW data appear intuitively
correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 29756.32
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 29756.32
Comments: none

## 23968
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23968
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-12-29 | 58255 | 58255 | 58258
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 58255 | 58255 | 58258
Comments: lighting "details" value based on line items 1-6.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
classrooms, kindergarten bldg |  | 4' 4 lamp T-8 | 252 | 0.11 | 27.72 | 4' 2 lamp ULTRA REF | 252 | 0.046 | 11.592 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 42577.92
restroom |  | 60 watt | 1 | 0.06 | 0.06 | 13W CFL NEW FIX | 1 | 0.015 | 0.015 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 69.3
P.E. bungalow, classroom bungalow |  | 4' 4 lamp T-12 | 30 | 0.144 | 4.32 | 4' 2 lamp T-8,REF | 30 | 0.058 | 1.74 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 6811.2
bungalow classrooms |  | 4' 3 lamp T-12 | 36 | 0.115 | 4.14 | 4' 2 lamp T-8,REF | 36 | 0.058 | 2.088 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 5417.28
TAP room, teacher lounge, reading lab |  | 4' 4 lamp T-8 | 12 | 0.11 | 1.32 | 4' 2 lamp ULTRA REF | 12 | 0.046 | 0.552 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 2027.52
auditorium |  | 4' 4 lamp T-8 | 32 | 0.11 | 3.52 | 4' 3 lamp exstg blst, REF | 32 | 0.086 | 2.752 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 44 | 1351.68
58254.9
Comments: all data per per paperwork. Daily operating schedule derived based on S&A judgment. Note use of 44 wk/yr (somewhat aggressive for schools but not wildly implausible).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 58254.9
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
classrooms, kindergarten bldg |  | F44ILL | 252 | 0.112 | 28.224 | F42ILL | 252 | 0.054 | 13.608 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 38586.24
restroom |  | I60/1 | 1 | 0.06 | 0.06 | CF13/1-SCRW | 1 | 0.015 | 0.015 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 69.3
P.E. bungalow, classroom bungalow |  | F44EE | 30 | 0.144 | 4.32 | F42ILL | 30 | 0.059 | 1.77 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 6732
bungalow classrooms |  | F43EE | 36 | 0.115 | 4.14 | F42ILL | 36 | 0.059 | 2.124 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 5322.24
TAP room, teacher lounge, reading lab |  | F44ILL | 12 | 0.112 | 1.344 | F42ILL | 12 | 0.054 | 0.648 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1837.44
auditorium |  | F44ILL | 32 | 0.112 | 3.584 | F43ILL | 32 | 0.089 | 2.848 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 44 | 1295.36
Total for EEM | [18 empty] | 53842.58
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 53842.58
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
classrooms, kindergarten bldg |  | F44ILL | 252 | 0.112 | 28.224 | F42ILL | 252 | 0.054 | 13.608 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 38586.24
restroom |  | I60/1 | 1 | 0.06 | 0.06 | CF13/1-SCRW | 1 | 0.015 | 0.015 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 35 | 44 | 69.3
P.E. bungalow, classroom bungalow |  | F44EE | 30 | 0.144 | 4.32 | F42ILL | 30 | 0.059 | 1.77 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 6732
bungalow classrooms |  | F43EE | 36 | 0.115 | 4.14 | F42ILL | 36 | 0.059 | 2.124 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 5322.24
TAP room, teacher lounge, reading lab |  | F44ILL | 12 | 0.112 | 1.344 | F42ILL | 12 | 0.054 | 0.648 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 44 | 1837.44
auditorium |  | F44ILL | 32 | 0.112 | 3.584 | F43ILL | 32 | 0.089 | 2.848 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 44 | 1295.36
Total for EEM | [18 empty] | 53842.58
Comments: kWh/yr savings data are same as step 3, except for operational data. Survey response "overridden" for op data re restroom and auditorium since ASW data appear intuitively
correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 53842.58
CFL portion of Lighting Savings: | [18 empty] | 69.3
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 53842.58
Comments: none

## 23971
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23971
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting |  | 0 | 0 | 0
Refrig. Tune-up | 2003-12-17 | 3907 | 16283 | 3907
AC Tune-up | 2003-12-17 | 2910 | 2909 | 2910
T-stat |  | 0 | 0 | 0
Overall |  | 6817 | 19192 | 6817
Comments: Refrig. Tune-up and AC Tune-up "details" values each based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  |  |  |  | 0 |  |  |  | kW: 0; Operational Data (hrs by day) Sum: 0 | 0
Total for EEM | [18 empty] | 0
Comments: none
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Produce Prep |  | 6 | 1.549 | 8760 | 80% | 6% | [12 empty] | 3907.9411
Total for EEM | [18 empty] | 3907.9411
Comments: all data per per paperwork.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 25 | 62% | 3754 | 1 | 5% | [12 empty] | 2909.35
Comments: all data per per paperwork.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 6817.2911
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total for EEM | [18 empty] | 0
Comments: none
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Produce Prep |  | 0.6 | 2 | 8760 | 80% | 1.5% | [12 empty] | 126.144
Total for EEM | [18 empty] | 126.144
Comments: tonnage data updated per ADL DOE study; kW/ton data updated per S&A 4/04 research; load factors rely on default/paperwork; % savings updated per S&A 4/04 research.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
Inland, Small Office, No Economizer |  | 25 | 62% | 1560 | 1.3 | 5% | [12 empty] | 1571.7
Comments: kW/ton data adjusted per S&A 2/04 research re package rooftop units. Hr/yr data adjusted by S&A, assuming cooling is applicable 9/12 of the year.
Also, basic hr/yr adjusted per survey response (open 8 hr/day, 5 days/week, 52 wk/yr, not 12 hr/day, 6 day/week, 52 wk/yr).
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1697.844
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM | [18 empty] | 1
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kW: 0; Operational Data (hrs by day) Sum: 0; Operational Data (hrs by day) Wk/Yr: 52.14 | 0
Total for EEM | [18 empty] | 0
Comments: none
Overall Application Adjusted Savings: | [18 empty] | 1697.844
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 1697.844
Comments: none

## 23985
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23985
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-11-19 | 4524 | 4525 | 4524
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 4524 | 4525 | 4524
Comments: lighting "details" value based on line items 1-5.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office/Showroom/Acct. |  | 4' 2 lamp T-12 | 14 | 0.072 | 1.008 | 4' 2 lamp Ultra LP WM | 14 | 0.046 | 0.644 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 1138.7376
Sales / Warehouse |  | 8' 2 lamp T-12 | 7 | 0.123 | 0.861 | 4' 4 lamp Ultra Kit LP WM | 7 | 0.09 | 0.63 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 722.6604
Show Room / Rest |  | 40 watt | 11 | 0.04 | 0.44 | 11W CFL S/I | 11 | 0.013 | 0.143 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 929.1348
Warehouse |  | 150 watt | 1 | 0.15 | 0.15 | 26W CFL S/I | 1 | 0.027 | 0.027 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 384.7932
Outside Parking |  | 175 watt | 4 | 0.205 | 0.82 | 100W MH | 4 | 0.128 | 0.512 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1348.9661
Total for EEM | [18 empty] | 4524.2921
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 4524.2921
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office/Showroom/Acct. |  | F42EE | 14 | 0.072 | 1.008 | F42WLL-R | 14 | 0.045 | 0.63 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 1182.5352
Sales / Warehouse |  | F82EE | 7 | 0.123 | 0.861 | F44WLL-R | 7 | 0.09 | 0.63 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 722.6604
Show Room / Rest |  | I40/1 | 11 | 0.04 | 0.44 | CF11/1-SCRW | 11 | 0.011 | 0.121 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 997.9596
Warehouse |  | I150/1F | 1 | 0.15 | 0.15 | CF11/1-SCRW | 1 | 0.026 | 0.026 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 387.9216
Outside Parking |  | MV175/1 | 4 | 0.205 | 0.82 | MH100/1 | 4 | 0.128 | 0.512 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1348.9661
Total for EEM | [18 empty] | 4640.0429
Comments: step 2 fixture descriptions mapped in corresponding table positions to SPC codes per S&A judgment; non-standard EIG fixtures
assumed since Step 2 descriptions not in EIG Fixture TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 4640.0429
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Office/Showroom/Acct. |  | F42EE | 14 | 0.072 | 1.008 | F42WLL-R | 14 | 0.045 | 0.63 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 1182.5352
Sales / Warehouse |  | F82EE | 7 | 0.123 | 0.861 | F44WLL-R | 7 | 0.09 | 0.63 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 722.6604
Show Room / Rest |  | I40/1 | 11 | 0.04 | 0.44 | CF11/1-SCRW | 11 | 0.011 | 0.121 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 997.9596
Warehouse |  | I150/1F | 1 | 0.15 | 0.15 | CF11/1-SCRW | 1 | 0.026 | 0.026 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 60 | 52.14 | 387.9216
Outside Parking |  | MV175/1 | 4 | 0.205 | 0.82 | MH100/1 | 4 | 0.128 | 0.512 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 84 | 52.14 | 1348.9661
Total for EEM | [18 empty] | 4640.0429
Comments: kWh/yr savings data are same as step 3, except for operational data. Op data not changed, per survey response. Survey response "overridden" for op data re outside parking
since ASW data appear intuitively correct (i.e., it is extremely likely respondent was not thinking about those areas in context of the response).
Overall Application Adjusted Savings: | [18 empty] | 4640.0429
CFL portion of Lighting Savings: | [18 empty] | 1385.8812
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 4640.0429
Comments: none

## 23986
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23986
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-10-30 | 25561 | 25737 | 25561
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 25561 | 25737 | 25561
Comments: lighting "details" value based on line items 1-4.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 92 | 0.144 | 13.248 | F43ILL-R | 92 | 0.078 | 7.176 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 23680.8
Sales |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.052 | 0.52 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 780
Sales |  | F81ES | 3 | 0.075 | 0.225 | F42ILL-R | 3 | 0.052 | 0.156 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 269.1
Sales |  | F82EE | 3 | 0.123 | 0.369 | F42ILL-R | 3 | 0.052 | 0.156 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 830.7
Total for EEM | [18 empty] | 25560.6
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 25560.6
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 92 | 0.144 | 13.248 | F43ILL-R | 92 | 0.076 | 6.992 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 24398.4
Sales |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.051 | 0.51 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 819
Sales |  | F81ES | 3 | 0.075 | 0.225 | F42ILL-R | 3 | 0.051 | 0.153 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 280.8
Sales |  | F82EE | 3 | 0.123 | 0.369 | F42ILL-R | 3 | 0.051 | 0.153 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52 | 842.4
Total for EEM | [18 empty] | 26340.6
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R and F42ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 26340.6
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44EE | 92 | 0.144 | 13.248 | F43ILL-R | 92 | 0.076 | 6.992 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52.14 | 24464.088
Sales |  | F42EE | 10 | 0.072 | 0.72 | F42ILL-R | 10 | 0.051 | 0.51 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52.14 | 821.205
Sales |  | F81ES | 3 | 0.075 | 0.225 | F42ILL-R | 3 | 0.051 | 0.153 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52.14 | 281.556
Sales |  | F82EE | 3 | 0.123 | 0.369 | F42ILL-R | 3 | 0.051 | 0.153 | 13 | 13 | 13 | 13 | 13 | 10 | 0 | 75 | 52.14 | 844.668
Total for EEM | [18 empty] | 26411.517
Comments: Op hours changed per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 26411.517
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 26411.517
Comments: none

## 23991
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23991
Date of ASW SBEA Database Extract Used: |  |  | 2004-02-17
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2003-11-03 | 6494 | 6494 | 6494
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 6494 | 6494 | 6494
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43EE | 42 | 0.115 | 4.83 | F43ILL-R | 42 | 0.078 | 3.276 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52 | 6222.216
Sales |  | I60/1 | 2 | 0.06 | 0.12 | CFQ18/1 | 2 | 0.026 | 0.052 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52 | 272.272
Total for EEM | [18 empty] | 6494.488
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 6494.488
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43EE | 42 | 0.115 | 4.83 | F43ILL-R | 42 | 0.076 | 3.192 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52 | 6558.552
Sales |  | I60/1 | 2 | 0.06 | 0.12 | CFQ18/1 | 2 | 0.026 | 0.052 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52 | 272.272
Total for EEM | [18 empty] | 6830.824
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R values derived using 2002 Sylvania catalog data; FQ18/1 values appear reasonable (hence unchanged).
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 6830.824
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F43EE | 42 | 0.115 | 4.83 | F43ILL-R | 42 | 0.076 | 3.192 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52.14 | 6576.2096
Sales |  | I60/1 | 2 | 0.06 | 0.12 | CFQ18/1 | 2 | 0.026 | 0.052 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 77 | 52.14 | 273.005
Total for EEM | [18 empty] | 6849.2147
Comments: Op hours changed per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 6849.2147
CFL portion of Lighting Savings: | [18 empty] | 273.005
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 6849.2147
Comments: none

## 23993
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23993
Date of ASW SBEA Database Extract Used: |  |  | 2004-03-15
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting |  | 0 | 0 | 0
Refrig. Tune-up | 2004-01-20 | 16480 | 16490 | 16480
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 16480 | 16490 | 16480
Comments: refrigeration tune-up "details" value based on line item 1.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  |  |  |  | 0 |  |  |  | kW: 0; Operational Data (hrs by day) Sum: 0 | 0
Total for EEM | [18 empty] | 0
Comments: none.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Cold Drinks |  | 0.535 | 1.549 | 8760 | 80% | 6% |  | 0.82871 | [10 empty] | 348.4581
Frozen Food |  | 2.295 | 2.548 | 8760 | 80% | 6% |  | 5.8477 | [10 empty] | 2458.8241
Produce Prep Cooler |  | 21 | 1.549 | 8760 | 80% | 6% |  | 32.529 | [10 empty] | 13677.7939
Total for EEM | [18 empty] | 16485.0761
Comments: all data per per paperwork.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 16485.0761
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total for EEM | [18 empty] | 0
Comments: none
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
Cold Drinks |  | 0.75 | 2 | 8760 | 80% | 1.5% | [12 empty] | 157.68
Frozen Food |  | 3.12 | 2.55 | 8760 | 80% | 1.5% | [12 empty] | 836.3347
Produce Prep Cooler |  | 2.1 | 2 | 8760 | 80% | 1.5% | [12 empty] | 441.504
Total for EEM | [18 empty] | 1435.5187
Comments: tonnage data updated per ADL DOE study; kW/ton data updated per S&A 4/04 research; load factors rely on default/paperwork; % savings updated per S&A 4/04 research.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 1435.5187
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM
- Refrig. Tune-up EEM | [18 empty] | 1
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM
- Refrig. Tune-up EEM | [18 empty] | 0.5
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
not applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.14 | 0
Total for EEM | [18 empty] | 0
Comments: none
Overall Application Adjusted Savings: | [18 empty] | 717.7594
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 717.7594
Comments: none

## 23998
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer ID: | 23998
Date of ASW SBEA Database Extract Used: |  |  | 2004-03-15
Step 1: Reference Information for sampled applications
Annual kWh Savings
EEM | Verification and Reconciliation Date ("Measure Status" TBL) | "Measure Status" TBL Database Value | "Details" TBL Database Value | Paperwork Value
Lighting | 2004-01-05 | 4502 | 4509 | 4502
Refrig. Tune-up |  | 0 | 0 | 0
AC Tune-up |  | 0 | 0 | 0
T-stat |  | 0 | 0 | 0
Overall |  | 4502 | 4509 | 4502
Comments: lighting "details" value based on line items 1-2.
Step 2: Reverse Engineering of ASW Annual kWh Savings Figures Using ASW Data Inputs
Lighting EEM |  | Existing |  |  |  | Installed |  |  |  | Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 2 | 0.172 | 0.344 | F43ILL-R | 2 | 0.078 | 0.156 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52 | 439.92
Sales |  | F43SE | 28 | 0.14 | 3.92 | F43ILL-R | 28 | 0.078 | 2.184 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52 | 4062.24
Total for EEM | [18 empty] | 4502.16
Comments: all data per per paperwork. Daily operating schedule consistent with data in "lighting details" TBL.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: none.
AC Tune-up EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Description |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 4502.16
Step 3: Reverse Engineering of ASW Annual kWh Savings Figures Using Selected Primary Source Data Inputs Obtained by S&A
(adjustments are made relative data derived in Step 2)
Lighting EEM |  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 2 | 0.172 | 0.344 | F43ILL-R | 2 | 0.076 | 0.152 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52 | 449.28
Sales |  | F43SE | 28 | 0.14 | 3.92 | F43ILL-R | 28 | 0.076 | 2.128 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52 | 4193.28
Total for EEM | [18 empty] | 4642.56
Comments: step 2 values used automatically, except for kW/fixture data. Existing kW/fixture data: values appear reasonable (hence unchanged).
Installed kW/fixture data: F43ILL-R values derived using 2002 Sylvania catalog data.
Refrig. Tune-up EEM
Description |  | Tons | kW/Ton | Hr/Yr | LF | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Total for EEM | [18 empty] | 0
Comments: step 2 values used.
AC Tune-up EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
T-Stat EEM
Unit Number |  | Tons | LF | Hr/Yr | kW/ton | % Savings | [12 empty] | kWh/Yr Savings
not applicable | [18 empty] | 0
Comments: none.
Total, All EEM's
Item | [18 empty] | kWh/Yr Savings
Sum of above | [18 empty] | 4642.56
Step 4: Participant Self-reported Verification-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 3)
Value
Basic Customer / Contact / Service Location / Business Type Verification (per survey Q's 1-4) | [18 empty] | 1
Basic SBEA Program Participation: Verification of EEM Types and Numbers Implemented (per survey Q's 5 & 7)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
EEM Persistence Verification: EEM's Removed or Rendered Non-operational after Installation / Implementation (per survey Q's 8a & 8b)
- Lighting EEM | [18 empty] | 1
- Refrig. Tune-up EEM
- AC Tune-up EEM
- T-stat EEM
Lighting EEM: Operating Hours (per survey Q's 9 & 10)
|  | Existing |  |  |  | Installed |  |  | Operational Data (hrs by day) M: Operational Data (hrs by day)
Location |  | Fixture Type | Fixtures | kW/ Fixture | kW | Fixture Type | Fixtures | kW/ Fixture | kW | M | T | W | Th | F | S | S | Sum | Wk/Yr | kWh/Yr Savings
Sales |  | F44SE | 2 | 0.172 | 0.344 | F43ILL-R | 2 | 0.076 | 0.152 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52.14 | 450.4896
Sales |  | F43SE | 28 | 0.14 | 3.92 | F43ILL-R | 28 | 0.076 | 2.128 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 45 | 52.14 | 4204.5696
Total for EEM | [18 empty] | 4655.0592
Comments: Op hours changed per recognition of 365 day year.
Overall Application Adjusted Savings: | [18 empty] | 4655.0592
CFL portion of Lighting Savings: | [18 empty] | 0
Step 5: Application Paperwork Formal Verification Audit-based Gross Savings Adjustments
(e.g., 1.0 = no adjustment, .8=20% reduction, 0=complete zeroing out; adjustments are made relative data derived in Step 4)
Service address acceptable? | [18 empty] | 1
Equipment scope appropriate? | [18 empty] | 1
Completion date acceptable? | [18 empty] | 1
Overall Application Adjusted Savings: | [18 empty] | 4655.0592
Comments: none

## Cust Size
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
Customer Size Assessment
Customer ID | Completed date sample bin | Business Type (per Database) | Floorspace (sq ft; per Database) | Size Classification (per Database) | S&A Assessment: Is Size Classification Plausible? | Comments | Ct
23079 | 2002-10-01 | Retail Book Store | 1240 | Very Small {0-19kW} | yes |  | 1
23086 | 2002-10-01 | Resturaunt | 1200 | Very Small {0-19kW} | yes |  | 1
16023 | 2002-11-01 | Beauty Salon | 1200 | Very Small {0-19kW} | yes |  | 1
17041 | 2002-12-01 | Hair Salon | 1000 | Very Small {0-19kW} | yes |  | 1
23173 | 2002-12-01 | Liquor Mart | 2000 | Small {20-100kW} | yes |  | 1
23271 | 2002-12-01 | Retail | 5000 | Very Small {0-19kW} | yes |  | 1
19058 | 2003-01-01 | Mail Services | 1100 | Very Small {0-19kW} | yes |  | 1
23525 | 2003-01-01 | Private School | 20000 | Small {20-100kW} | yes |  | 1
16090 | 2003-02-01 | Meat Market | 4000 | Very Small {0-19kW} | yes |  | 1
17044 | 2003-02-01 | Small Retail | 1267 | Very Small {0-19kW} | yes |  | 1
22110 | 2003-02-01 | Italian Restaurant | 1944 | Small {20-100kW} | yes |  | 1
23581 | 2003-02-01 | Cleaners | 2000 | Small {20-100kW} | yes |  | 1
23587 | 2003-02-01 | Hair & Nail Salon | 2400 | Very Small {0-19kW} | yes |  | 1
11040 | 2003-03-01 | Retail | 3000 | Small {20-100kW} | yes |  | 1
16085 | 2003-03-01 | Retail | 2200 | Very Small {0-19kW} | yes |  | 1
23711 | 2003-03-01 | Office | 10000 | Small {20-100kW} | yes |  | 1
23752 | 2003-03-01 | Office | 2500 | Small {20-100kW} | yes |  | 1
23755 | 2003-03-01 | Industrial | 5000 | Small {20-100kW} | yes |  | 1
16107 | 2003-04-01 | Salon | 1200 | Very Small {0-19kW} | yes |  | 1
17029 | 2003-04-01 | Insurance Services | 790 | Very Small {0-19kW} | yes |  | 1
17048 | 2003-04-01 | Insurance Sales | 1350 | Very Small {0-19kW} | yes |  | 1
20180 | 2003-04-01 | Manufacturing | 48000 | Medium {<500kW} | yes |  | 1
23652 | 2003-04-01 | Retail | 1800 | Small {20-100kW} | yes |  | 1
23766 | 2003-04-01 | Office | 20000 | Small {20-100kW} | yes |  | 1
23789 | 2003-04-01 | Industrial | 10000 | Very Small {0-19kW} | yes |  | 1
23797 | 2003-04-01 | Retail | 8000 | Small {20-100kW} | yes |  | 1
17052 | 2003-05-01 | Small Retail | 900 | Small {20-100kW} | yes |  | 1
22093 | 2003-05-01 | Hair Salon | 1200 | Very Small {0-19kW} | yes |  | 1
23767 | 2003-05-01 | Office | 1000 | Small {20-100kW} | yes |  | 1
23817 | 2003-05-01 | Laundromat | 4000 | Small {20-100kW} | yes |  | 1
23818 | 2003-05-01 | Laundromat | 4000 | Small {20-100kW} | yes |  | 1
14023 | 2003-06-01 | Office Space | outside | Medium {<500kW} | yes |  | 1
17054 | 2003-06-01 | Small Retail | 5000 | Very Small {0-19kW} | yes |  | 1
17072 | 2003-06-01 | Restaurant | 2000 | Small {20-100kW} | yes |  | 1
23478 | 2003-06-01 | Bank Office | 4360 | Small {20-100kW} | yes |  | 1
23847 | 2003-06-01 | Commercial | 10000 | Small {20-100kW} | yes |  | 1
23849 | 2003-06-01 | Retail | 40000 | Small {20-100kW} | yes |  | 1
17058 | 2003-07-01 | Small Retail |  | Very Small {0-19kW} | yes | sq ft not included | 1
23836 | 2003-07-01 | MFG | 20000 | Small {20-100kW} | yes |  | 1
23840 | 2003-07-01 | Hotel | 100000 | Small {20-100kW} | yes |  | 1
23845 | 2003-07-01 | Apartments | 250000 | Small {20-100kW} | yes | common & office areas of apartment complex | 1
23874 | 2003-07-01 | Office |  | Very Small {0-19kW} | yes | sq ft not included; appears to be small office | 1
16145 | 2003-08-01 | Real Estate | 3300 | Small {20-100kW} | yes |  | 1
17089 | 2003-08-01 | Small Office | 1350 | Very Small {0-19kW} | yes |  | 1
23862 | 2003-08-01 | Office | 8400 | Small {20-100kW} | yes |  | 1
23915 | 2003-08-01 | Retail | 1200 | Very Small {0-19kW} | yes |  | 1
23921 | 2003-08-01 | Retail | 1200 | Very Small {0-19kW} | yes |  | 1
23901 | 2003-09-01 | Office | 4000 | Very Small {0-19kW} | yes |  | 1
23918 | 2003-09-01 | School | 30000 | Small {20-100kW} | yes |  | 1
23924 | 2003-09-01 | Commercial | 10000 | Small {20-100kW} | yes |  | 1
23925 | 2003-09-01 | Resturant | 2400 | Small {20-100kW} | yes |  | 1
23919 | 2003-10-01 | Commercial | 64000 | Medium {<500kW} | yes |  | 1
23931 | 2003-10-01 | Retail | 9862 | Small {20-100kW} | yes |  | 1
23954 | 2003-10-01 | Office | 10000 | Small {20-100kW} | yes |  | 1
28986 | 2003-10-01 | Retail | 11000 | Small {20-100kW} | yes |  | 1
17096 | 2003-11-01 | Med-Retail | 900 | Small {20-100kW} | yes |  | 1
23913 | 2003-11-01 | School | 30000 | Small {20-100kW} | yes |  | 1
23965 | 2003-11-01 | School | 35000 | Small {20-100kW} | yes |  | 1
23985 | 2003-11-01 | Retail | 4000 | Small {20-100kW} | yes |  | 1
23991 | 2003-11-01 | Retail | 4800 | Very Small {0-19kW} | yes |  | 1
23914 | 2003-12-01 | School | 30000 | Small {20-100kW} | yes |  | 1
23951 | 2003-12-01 | School | 35000 | Small {20-100kW} | yes | bus. type corrected; originally listed as retail | 1
23952 | 2003-12-01 | School | 35000 | Small {20-100kW} | yes |  | 1
23958 | 2003-12-01 | School | 35000 | Small {20-100kW} | yes |  | 1
23964 | 2003-12-01 | School | 35000 | Small {20-100kW} | yes |  | 1
23968 | 2003-12-01 | School | 35000 | Small {20-100kW} | yes |  | 1
23971 | 2003-12-01 | Office | 10000 | Small {20-100kW} | yes |  | 1
23993 | 2004-01-01 | Retail | 2700 | Small {20-100kW} | yes |  | 1
23998 | 2004-01-01 | Office | 1800 | Very Small {0-19kW} | yes |  | 1
Customer Size Counts
Medium |  | 3 | 4.348%
Small |  | 42 | 60.87%
Very Small |  | 24 | 34.78%
TBD |  | 0 | 0%
Sum |  | 69 | 100%

## CFL Issue
S&A EM&V Impact Evaluations - ASW SBEA Sampled Applications
CFL Savings (relative to overall Lighting Measure Savings)
Customer ID | Completed date sample bin | Step 4 CFL Lighting Measure Savings | Step 4 Overall Lighting Measure Savings | CFL Savings as % of Overall Lighting Measure Savings
23079 | 2002-10-01 | 0 | 2686.2528 | 0%
23086 | 2002-10-01 | 0 | 3134.2397 | 0%
16023 | 2002-11-01 | 0 | 1748.567 | 0%
17041 | 2002-12-01 | 0 | 1918.752 | 0%
23173 | 2002-12-01 | 0 | 5211.9144 | 0%
23271 | 2002-12-01 | 0 | 12486.9043 | 0%
19058 | 2003-01-01 | 0 | 1729.2752 | 0%
23525 | 2003-01-01 | 804.7809 | 25577.7984 | 3.146%
16090 | 2003-02-01 | 0 | 7639.0314 | 0%
17044 | 2003-02-01 | 0 | 883.773 | 0%
22110 | 2003-02-01 | 1638.0302 | 3652.7198 | 44.84%
23581 | 2003-02-01 | 536.5206 | 4011.1302 | 13.38%
23587 | 2003-02-01 | 1124.1384 | 4743.1758 | 23.7%
11040 | 2003-03-01 | 4677.688 | 11268.4968 | 41.51%
16085 | 2003-03-01 | 0 | 2896.1163 | 0%
23711 | 2003-03-01 | 14662.6022 | 16560.4982 | 88.54%
23752 | 2003-03-01 | 1001.5051 | 10137.6845 | 9.879%
23755 | 2003-03-01 | 1052.6023 | 17469.9763 | 6.025%
16107 | 2003-04-01 | 0 | 1799.7685 | 0%
17029 | 2003-04-01 | 0 | 4428.8759 | 0%
17048 | 2003-04-01 | 0 | 2951.6454 | 0%
20180 | 2003-04-01 | 0 | 0 | #DIV/0!
23652 | 2003-04-01 | 0 | 11937.7658 | 0%
23766 | 2003-04-01 | 28256.0216 | 36516.249 | 77.38%
23789 | 2003-04-01 | 0 | 14492.313 | 0%
23797 | 2003-04-01 | 2003.0102 | 23021.4785 | 8.701%
17052 | 2003-05-01 | 0 | 1907.0205 | 0%
22093 | 2003-05-01 | 0 | 3935.5272 | 0%
23767 | 2003-05-01 | 4721.3813 | 14072.1689 | 33.55%
23817 | 2003-05-01 | 0 | 7848.5299 | 0%
23818 | 2003-05-01 | 0 | 5150.5978 | 0%
14023 | 2003-06-01 | 0 | 3976.8221 | 0%
17054 | 2003-06-01 | 0 | 6701.0328 | 0%
17072 | 2003-06-01 | 22097.4534 | 22097.4534 | 100%
23478 | 2003-06-01 | 2276.9538 | 12245.079 | 18.59%
23847 | 2003-06-01 | 3525.7068 | 26490.7698 | 13.31%
23849 | 2003-06-01 | 0 | 89477.4019 | 0%
17058 | 2003-07-01 | 0 | 1319.5591 | 0%
23836 | 2003-07-01 | 0 | 127615.1527 | 0%
23840 | 2003-07-01 | 209320.8269 | 209320.8269 | 100%
23845 | 2003-07-01 | 20830.1386 | 33565.855 | 62.06%
23874 | 2003-07-01 | 0 | 44742.3768 | 0%
16145 | 2003-08-01 |  |  | #DIV/0!
17089 | 2003-08-01 | 0 | 0 | #DIV/0!
23862 | 2003-08-01 | 0 | 0 | #DIV/0!
23915 | 2003-08-01 | 0 | 3190.968 | 0%
23921 | 2003-08-01 | 429.2165 | 3221.3135 | 13.32%
23901 | 2003-09-01 | 3320.2752 | 18981.0456 | 17.49%
23918 | 2003-09-01 | 0 | 19929.4722 | 0%
23924 | 2003-09-01 | 0 | 42313.487 | 0%
23925 | 2003-09-01 | 1100.4147 | 14847.3864 | 7.412%
23919 | 2003-10-01 | 1156.2566 | 73544.9299 | 1.572%
23931 | 2003-10-01 | 0 | 28376.465 | 0%
23954 | 2003-10-01 | 1622.5968 | 1622.5968 | 100%
28986 | 2003-10-01 | 0 | 26411.517 | 0%
17096 | 2003-11-01 | 2751.5842 | 16022.257 | 17.17%
23913 | 2003-11-01 | 909.92 | 86258.48 | 1.055%
23965 | 2003-11-01 | 0 | 29756.32 | 0%
23985 | 2003-11-01 | 1385.8812 | 4640.0429 | 29.87%
23991 | 2003-11-01 | 273.005 | 6849.2147 | 3.986%
23914 | 2003-12-01 | 723.8 | 76722.76 | 0.9434%
23951 | 2003-12-01 | 0 | 73285.12 | 0%
23952 | 2003-12-01 | 0 | 68395.152 | 0%
23958 | 2003-12-01 | 2923.8 | 34214.4 | 8.546%
23964 | 2003-12-01 | 0 | 69574.56 | 0%
23968 | 2003-12-01 | 69.3 | 53842.58 | 0.1287%
23971 | 2003-12-01 | 0 | 0 | #DIV/0!
23993 | 2004-01-01 | 0 | 0 | #DIV/0!
23998 | 2004-01-01 | 0 | 4655.0592 | 0%
Totals |  | 335195.4107 | 1596025.7033 | 21%
Derivation of Savings Weighted Lighting Measure EUL
Lighting Measure Portion |  | kWh Savings | % | EUL
CFLs |  | 335195.4107 | 21% | 8
All Other Lighting |  | 1260830.2926 | 79% | 16
Overall |  | 1596025.7033 | 100% | 14.3198
Lighting Measure Savings as % of All Measure Savings
Lighting Measure Gross Annual kWh Savings (per Step 4) |  |  |  | 1596025.7033
Total Gross Annual kWh Savings (per Step 5) |  |  |  | #REF!
Lighting Measure Savings as % of Total |  |  |  | #REF!